## Initial
PV_types | STC_eff | temp_coeff | pv_cost | O_M | kW_stc
Mono Bifacial | 0.225 | -0.0036 | 1230 | 20 | 0.36
Battery Data
BATTERY_TYPES | B_rt_eff | B_dod | B_cost_e | B_cost_p | B_power_rating | B_O_M | Energy_Life | Power_Life | Replacement_Fraction_E | Replacement_Fraction_P
Li-ion LFP | 0.875 | 0.9 | 487 | 530 | 1 | 9 | 10 | 10 | 0.85 | 0.8
Sweep Parameters
itc_pv | itc_bat | enable_sell | enforce_limit_flag | A_tot | offset_price | insolation_mult | sweep_file
0 | 0.3 | 1 | 1 | 2000 | 0 | 1 | src\microgrid\Launch_files\sweep_1_itc_area.csv
PV Sizing Limits
Metric | Value
Final Allowed System Size (kW) | 1010.988

## H_A2000_Mono_BF_Li-io_Sweep_A20
Installed PV Size Limit (kW) | Max PV Array Area | Total Cost ($) | Switch Count | Number of Panels | Installed Area (m^2) | PV Capacity (kW) | Battery Energy Capacity (kWh) | Battery Power (kW) | Annual PV Generation (kWh) | Annual Grid Import (kWh) | Annual Grid Export (kWh) | Annual % Load from PV | Annual % Load from Battery | Annual % Load from Grid | Annual % Batt Charge from PV | Annual % Batt Charge from Grid
1010.988 | 2000 | 633568.1845 | 106 | 625 | 1000 | 225 | 74.3936 | 12.3989 | 361777.4954 | 6124429.338 | 0 | 5.53 | 0.35 | 94.12 | 13.69 | 86.31
Hour | Consumption | Insolation | Temperature | Total PV Generation | PV to Load | PV to Grid | PV to Battery | Total Battery Charge | Charge from Grid | Total Battery Discharge | Battery to Load | Battery to Grid | SOC | Grid Import | Grid Export | Grid Price | EF_grid | PV_Charged_Discharge_to_Load | PV_Charged_Discharge_to_Grid | SOC_renew | Abatement_Energy_kWh | On_peak/Off_peak | Grid to Load | %Batt_Charge_from_PV | %Batt_Charge_from_Grid | %Load_from_PV | %Load_from_Battery | %Load_from_Grid | Abated_Emissions | Abatement_Value_$
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 37.1968 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | off_peak | 0 | [5 empty] | 0 | 0
1 | 531.38 | 0 | 22.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 37.1968 | 531.38 | 0 | 0.05921 | 5.9568 | 0 | 0 | 0 | 0 | off_peak | 531.38 |  |  | 0 | 0 | 100 | 0 | 0
2 | 524.77 | 0 | 22.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 37.1968 | 524.77 | 0 | 0.05921 | 5.5568 | 0 | 0 | 0 | 0 | off_peak | 524.77 |  |  | 0 | 0 | 100 | 0 | 0
3 | 563.46 | 0 | 22.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 37.1968 | 563.46 | 0 | 0.05921 | 4.9807 | 0 | 0 | 0 | 0 | off_peak | 563.46 |  |  | 0 | 0 | 100 | 0 | 0
4 | 506.28 | 0 | 22.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 37.1968 | 506.28 | 0 | 0.05921 | 4.5051 | 0 | 0 | 0 | 0 | off_peak | 506.28 |  |  | 0 | 0 | 100 | 0 | 0
5 | 542.58 | 0 | 22.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 37.1968 | 542.58 | 0 | 0.05921 | 4.0751 | 0 | 0 | 0 | 0 | off_peak | 542.58 |  |  | 0 | 0 | 100 | 0 | 0
6 | 588.2 | 0 | 22.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 37.1968 | 588.2 | 0 | 0.05921 | 3.8681 | 0 | 0 | 0 | 0 | off_peak | 588.2 |  |  | 0 | 0 | 100 | 0 | 0
7 | 603.97 | 0 | 23.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 37.1968 | 603.97 | 0 | 0.05921 | 3.4937 | 0 | 0 | 0 | 0 | off_peak | 603.97 |  |  | 0 | 0 | 100 | 0 | 0
8 | 633.99 | 33.2315 | 23.5 | 6.7657 | 6.7657 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 37.1968 | 627.2243 | 0 | 0.05921 | 3.2911 | 0 | 0 | 0 | 6.7657 | off_peak | 627.2243 |  |  | 1.07 | 0 | 98.93 | 22.2666 | 0
9 | 608.88 | 202.289 | 24.2 | 41.0815 | 41.0815 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 37.1968 | 567.7985 | 0 | 0.05921 | 3.0059 | 0 | 0 | 0 | 41.0815 | off_peak | 567.7985 |  |  | 6.75 | 0 | 93.25 | 123.4861 | 0
10 | 620.18 | 377.901 | 24.8 | 76.5801 | 76.5801 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 37.1968 | 543.5999 | 0 | 0.05921 | 2.7361 | 0 | 0 | 0 | 76.5801 | off_peak | 543.5999 |  |  | 12.35 | 0 | 87.65 | 209.5339 | 0
11 | 617.58 | 124.45 | 25.3 | 25.1739 | 25.1739 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 37.1968 | 592.4061 | 0 | 0.05921 | 2.6008 | 0 | 0 | 0 | 25.1739 | off_peak | 592.4061 |  |  | 4.08 | 0 | 95.92 | 65.472 | 0
12 | 623.52 | 475.2 | 25.6 | 96.0201 | 96.0201 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 37.1968 | 527.4999 | 0 | 0.05921 | 2.5747 | 0 | 0 | 0 | 96.0201 | off_peak | 527.4999 |  |  | 15.4 | 0 | 84.6 | 247.2262 | 0
13 | 553.4 | 369.042 | 25.7 | 74.5427 | 74.5427 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 37.1968 | 478.8573 | 0 | 0.05921 | 2.6772 | 0 | 0 | 0 | 74.5427 | off_peak | 478.8573 |  |  | 13.47 | 0 | 86.53 | 199.5649 | 0
14 | 523.02 | 193.445 | 25.7 | 39.0739 | 39.0739 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 37.1968 | 483.9461 | 0 | 0.05921 | 2.8145 | 0 | 0 | 0 | 39.0739 | off_peak | 483.9461 |  |  | 7.47 | 0 | 92.53 | 109.974 | 0
15 | 525.29 | 165.812 | 25.5 | 33.5165 | 22.3329 | 0 | 11.1835 | 11.1835 | 0 | 0 | 0 | 0 | 47.6581 | 502.9571 | 0 | 0.05921 | 3.1865 | 0 | 0 | 10.4613 | 22.3329 | off_peak | 502.9571 | 100 | 0 | 4.25 | 0 | 95.75 | 71.1638 | 0
16 | 529.7 | 83.6 | 25.3 | 16.9107 | 4.5118 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 0 | 59.2562 | 525.1882 | 0 | 0.05921 | 3.6633 | 0 | 0 | 22.0594 | 4.5118 | off_peak | 525.1882 | 100 | 0 | 0.85 | 0 | 99.15 | 16.5281 | 0
17 | 511.5 | 172.225 | 24.9 | 34.8881 | 22.4892 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 0 | 70.8544 | 489.0108 | 0 | 0.05921 | 3.9222 | 0 | 0 | 33.6575 | 22.4892 | off_peak | 489.0108 | 100 | 0 | 4.4 | 0 | 95.6 | 88.2069 | 0
18 | 516.63 | 17.4465 | 24.5 | 3.5393 | 0 | 0 | 3.5393 | 3.5393 | 0 | 0 | 0 | 0 | 74.1651 | 516.63 | 0 | 0.05921 | 4.1203 | 0 | 0 | 36.9682 | 0 | off_peak | 516.63 | 100 | 0 | 0 | 0 | 100 | 0 | 0
19 | 511.42 | 0 | 24.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1651 | 511.42 | 0 | 0.05921 | 4.4428 | 0 | 0 | 36.9682 | 0 | off_peak | 511.42 |  |  | 0 | 0 | 100 | 0 | 0
20 | 500.8 | 0 | 24.3 | 0 | 0 | 0 | 0 | 0.22859 | 0.22859 | 0 | 0 | 0 | 74.3789 | 501.0286 | 0 | 0.05921 | 4.7239 | 0 | 0 | 36.9682 | 0 | off_peak | 500.8 | 0 | 100 | 0 | 0 | 100 | 0 | 0
21 | 503.63 | 0 | 24.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3789 | 503.63 | 0 | 0.05921 | 4.9839 | 0 | 0 | 36.9682 | 0 | off_peak | 503.63 |  |  | 0 | 0 | 100 | 0 | 0
22 | 494.11 | 0 | 24.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3789 | 494.11 | 0 | 0.05921 | 5.1804 | 0 | 0 | 36.9682 | 0 | off_peak | 494.11 |  |  | 0 | 0 | 100 | 0 | 0
23 | 502.97 | 0 | 24.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3789 | 502.97 | 0 | 0.05921 | 5.3914 | 0 | 0 | 36.9682 | 0 | off_peak | 502.97 |  |  | 0 | 0 | 100 | 0 | 0
24 | 488.34 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3789 | 488.34 | 0 | 0.05921 | 5.4856 | 0 | 0 | 36.9682 | 0 | off_peak | 488.34 |  |  | 0 | 0 | 100 | 0 | 0
25 | 497.81 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3789 | 497.81 | 0 | 0.05921 | 5.4744 | 0 | 0 | 36.9682 | 0 | off_peak | 497.81 |  |  | 0 | 0 | 100 | 0 | 0
26 | 532.79 | 0 | 23.9 | 0 | 0 | 0 | 0 | 0.014763 | 0.014763 | 0 | 0 | 0 | 74.3927 | 532.8048 | 0 | 0.05921 | 5.1948 | 0 | 0 | 36.9682 | 0 | off_peak | 532.79 | 0 | 100 | 0 | 0 | 100 | 0 | 0
27 | 501.31 | 0 | 23.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3927 | 501.31 | 0 | 0.05921 | 4.8676 | 0 | 0 | 36.9682 | 0 | off_peak | 501.31 |  |  | 0 | 0 | 100 | 0 | 0
28 | 529.55 | 0 | 23.8 | 0 | 0 | 0 | 0 | 0.0009535 | 0.0009535 | 0 | 0 | 0 | 74.3936 | 529.551 | 0 | 0.05921 | 4.4899 | 0 | 0 | 36.9682 | 0 | off_peak | 529.55 | 0 | 100 | 0 | 0 | 100 | 0 | 0
29 | 523.1 | 0 | 23.7 | 0 | 0 | 0 | 0 | 6.5835e-05 | 6.5835e-05 | 0 | 0 | 0 | 74.3936 | 523.1001 | 0 | 0.05921 | 4.1419 | 0 | 0 | 36.9682 | 0 | off_peak | 523.1 | 0 | 100 | 0 | 0 | 100 | 0 | 0
30 | 675.53 | 0 | 23.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 675.53 | 0 | 0.05921 | 3.6568 | 0 | 0 | 36.9682 | 0 | off_peak | 675.53 |  |  | 0 | 0 | 100 | 0 | 0
31 | 686.99 | 0 | 23.7 | 0 | 0 | 0 | 0 | 0 | 0 | 62.63 | 62.63 | 0 | 7.4394 | 624.36 | 0 | 0.088511 | 3.2669 | 34.5806 | 0 | 0 | 34.5806 | on_peak | 624.36 |  |  | 0 | 9.12 | 90.88 | 112.9729 | 0
32 | 684.66 | 34.1904 | 24.3 | 6.941 | 6.941 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 677.719 | 0 | 0.088511 | 2.9109 | 0 | 0 | 0 | 6.941 | on_peak | 677.719 |  |  | 1.01 | 0 | 98.99 | 20.2045 | 0
33 | 686.98 | 205.065 | 25 | 41.5257 | 41.5257 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 645.4543 | 0 | 0.088511 | 2.69 | 0 | 0 | 0 | 41.5257 | on_peak | 645.4543 |  |  | 6.04 | 0 | 93.96 | 111.7052 | 0
34 | 668.24 | 380.134 | 25.5 | 76.8386 | 76.8386 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 591.4014 | 0 | 0.088511 | 2.5729 | 0 | 0 | 0 | 76.8386 | on_peak | 591.4014 |  |  | 11.5 | 0 | 88.5 | 197.6971 | 0
35 | 686.54 | 519.82 | 26 | 104.8846 | 104.8846 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 19.0375 | 594.0543 | 0 | 0.05921 | 2.5438 | 0 | 0 | 0 | 104.8846 | off_peak | 581.6554 | 0 | 100 | 15.28 | 0 | 84.72 | 266.8086 | 0
36 | 718.85 | 422.547 | 26.2 | 85.1961 | 72.7972 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 0 | 30.6357 | 646.0528 | 0 | 0.05921 | 2.6441 | 0 | 0 | 11.5981 | 72.7972 | off_peak | 646.0528 | 100 | 0 | 10.13 | 0 | 89.87 | 192.4819 | 0
37 | 622.47 | 207.727 | 26.4 | 41.8527 | 41.8527 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 42.2338 | 593.0162 | 0 | 0.05921 | 2.829 | 0 | 0 | 11.5981 | 41.8527 | off_peak | 580.6173 | 0 | 100 | 6.72 | 0 | 93.28 | 118.4018 | 0
38 | 623.76 | 193.446 | 26.4 | 38.9754 | 26.5764 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 0 | 53.832 | 597.1836 | 0 | 0.05921 | 3.0786 | 0 | 0 | 23.1963 | 26.5764 | off_peak | 597.1836 | 100 | 0 | 4.26 | 0 | 95.74 | 81.818 | 0
39 | 613.75 | 296.891 | 26.3 | 59.8391 | 47.4401 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 0 | 65.4301 | 566.3099 | 0 | 0.05921 | 3.3996 | 0 | 0 | 34.7944 | 47.4401 | off_peak | 566.3099 | 100 | 0 | 7.73 | 0 | 92.27 | 161.2772 | 0
40 | 577.73 | 347.366 | 26 | 70.0884 | 61.1248 | 0 | 8.9635 | 8.9635 | 0 | 0 | 0 | 0 | 73.8147 | 516.6052 | 0 | 0.05921 | 3.7017 | 0 | 0 | 43.1791 | 61.1248 | off_peak | 516.6052 | 100 | 0 | 10.58 | 0 | 89.42 | 226.2678 | 0
41 | 572.7 | 117.757 | 25.5 | 23.8029 | 23.224 | 0 | 0.57892 | 0.57892 | 0 | 0 | 0 | 0 | 74.3563 | 549.476 | 0 | 0.05921 | 4.02 | 0 | 0 | 43.7206 | 23.224 | off_peak | 549.476 | 100 | 0 | 4.06 | 0 | 95.94 | 93.3602 | 0
42 | 522.44 | 17.2992 | 25 | 3.5031 | 3.5031 | 0 | 0 | 0.03739 | 0.03739 | 0 | 0 | 0 | 74.3912 | 518.9743 | 0 | 0.05921 | 4.3091 | 0 | 0 | 43.7206 | 3.5031 | off_peak | 518.9369 | 0 | 100 | 0.67 | 0 | 99.33 | 15.0952 | 0
43 | 537.46 | 0 | 24.7 | 0 | 0 | 0 | 0 | 0 | 0 | 62.6277 | 62.6277 | 0 | 7.4394 | 474.8323 | 0 | 0.088511 | 4.5774 | 0 | 0 | 43.7206 | 0 | on_peak | 474.8323 |  |  | 0 | 11.65 | 88.35 | 0 | 0
44 | 523.26 | 0 | 24.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 523.26 | 0 | 0.088511 | 4.7446 | 0 | 0 | 43.7206 | 0 | on_peak | 523.26 |  |  | 0 | 0 | 100 | 0 | 0
45 | 508.2 | 0 | 24.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 508.2 | 0 | 0.088511 | 4.9584 | 0 | 0 | 43.7206 | 0 | on_peak | 508.2 |  |  | 0 | 0 | 100 | 0 | 0
46 | 517.42 | 0 | 24.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 517.42 | 0 | 0.088511 | 5.2563 | 0 | 0 | 43.7206 | 0 | on_peak | 517.42 |  |  | 0 | 0 | 100 | 0 | 0
47 | 498.13 | 0 | 24.3 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 19.0375 | 510.5289 | 0 | 0.05921 | 5.5907 | 0 | 0 | 43.7206 | 0 | off_peak | 498.13 | 0 | 100 | 0 | 0 | 100 | 0 | 0
48 | 528.69 | 0 | 24.3 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 30.6357 | 541.0889 | 0 | 0.05921 | 5.81 | 0 | 0 | 43.7206 | 0 | off_peak | 528.69 | 0 | 100 | 0 | 0 | 100 | 0 | 0
49 | 512.65 | 0 | 24.3 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 42.2338 | 525.0489 | 0 | 0.05921 | 5.9242 | 0 | 0 | 43.7206 | 0 | off_peak | 512.65 | 0 | 100 | 0 | 0 | 100 | 0 | 0
50 | 515.23 | 0 | 24.2 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 53.832 | 527.6289 | 0 | 0.05921 | 5.5488 | 0 | 0 | 43.7206 | 0 | off_peak | 515.23 | 0 | 100 | 0 | 0 | 100 | 0 | 0
51 | 552.16 | 0 | 24.2 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 65.4301 | 564.5589 | 0 | 0.05921 | 5.1595 | 0 | 0 | 43.7206 | 0 | off_peak | 552.16 | 0 | 100 | 0 | 0 | 100 | 0 | 0
52 | 516.52 | 0 | 24.2 | 0 | 0 | 0 | 0 | 8.9635 | 8.9635 | 0 | 0 | 0 | 73.8147 | 525.4835 | 0 | 0.05921 | 4.7666 | 0 | 0 | 43.7206 | 0 | off_peak | 516.52 | 0 | 100 | 0 | 0 | 100 | 0 | 0
53 | 589.27 | 0 | 24.2 | 0 | 0 | 0 | 0 | 0.57892 | 0.57892 | 0 | 0 | 0 | 74.3563 | 589.8489 | 0 | 0.05921 | 4.3901 | 0 | 0 | 43.7206 | 0 | off_peak | 589.27 | 0 | 100 | 0 | 0 | 100 | 0 | 0
54 | 643.08 | 0 | 24.3 | 0 | 0 | 0 | 0 | 0.03739 | 0.03739 | 0 | 0 | 0 | 74.3912 | 643.1174 | 0 | 0.05921 | 3.9311 | 0 | 0 | 43.7206 | 0 | off_peak | 643.08 | 0 | 100 | 0 | 0 | 100 | 0 | 0
55 | 763.27 | 0 | 24.6 | 0 | 0 | 0 | 0 | 0 | 0 | 62.6277 | 62.6277 | 0 | 7.4394 | 700.6423 | 0 | 0.088511 | 3.4383 | 0 | 0 | 43.7206 | 0 | on_peak | 700.6423 |  |  | 0 | 8.21 | 91.79 | 0 | 0
56 | 780.24 | 32.8003 | 25.1 | 6.6397 | 6.6397 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 773.6003 | 0 | 0.088511 | 3.0499 | 0 | 0 | 43.7206 | 6.6397 | on_peak | 773.6003 |  |  | 0.85 | 0 | 99.15 | 20.2503 | 0
57 | 764.81 | 203.018 | 25.7 | 41.0075 | 41.0075 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 723.8025 | 0 | 0.088511 | 2.839 | 0 | 0 | 43.7206 | 41.0075 | on_peak | 723.8025 |  |  | 5.36 | 0 | 94.64 | 116.4199 | 0
58 | 813.52 | 114.95 | 26 | 23.1936 | 23.1936 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 790.3264 | 0 | 0.088511 | 2.7457 | 0 | 0 | 43.7206 | 23.1936 | on_peak | 790.3264 |  |  | 2.85 | 0 | 97.15 | 63.6828 | 0
59 | 764.84 | 250.162 | 26.3 | 50.4207 | 50.4207 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 19.0375 | 726.8182 | 0 | 0.05921 | 2.7378 | 0 | 0 | 43.7206 | 50.4207 | off_peak | 714.4193 | 0 | 100 | 6.59 | 0 | 93.41 | 138.0428 | 0
60 | 777.85 | 614.3 | 26.4 | 123.7688 | 111.3699 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 0 | 30.6357 | 666.4801 | 0 | 0.05921 | 2.9708 | 0 | 0 | 55.3187 | 111.3699 | off_peak | 666.4801 | 100 | 0 | 14.32 | 0 | 85.68 | 330.8553 | 0
61 | 789.22 | 462.441 | 26.5 | 93.1386 | 93.1386 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 42.2338 | 708.4803 | 0 | 0.05921 | 3.3636 | 0 | 0 | 55.3187 | 93.1386 | off_peak | 696.0814 | 0 | 100 | 11.8 | 0 | 88.2 | 313.2833 | 0
62 | 790.34 | 527.2 | 26.6 | 106.1431 | 106.1431 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 53.832 | 696.5959 | 0 | 0.05921 | 3.6886 | 0 | 0 | 55.3187 | 106.1431 | off_peak | 684.1969 | 0 | 100 | 13.43 | 0 | 86.57 | 391.5219 | 0
63 | 820.57 | 425.885 | 26.5 | 85.776 | 73.3771 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 0 | 65.4301 | 747.1929 | 0 | 0.05921 | 3.8339 | 0 | 0 | 66.9169 | 73.3771 | off_peak | 747.1929 | 100 | 0 | 8.94 | 0 | 91.06 | 281.3191 | 0
64 | 773.29 | 359.692 | 26.3 | 72.4967 | 72.4967 | 0 | 0 | 8.9635 | 8.9635 | 0 | 0 | 0 | 73.8147 | 709.7568 | 0 | 0.05921 | 3.9307 | 0 | 0 | 66.9169 | 72.4967 | off_peak | 700.7933 | 0 | 100 | 9.38 | 0 | 90.62 | 284.965 | 0
65 | 735.37 | 101.03 | 26 | 20.3849 | 20.3849 | 0 | 0 | 0.57892 | 0.57892 | 0 | 0 | 0 | 74.3563 | 715.564 | 0 | 0.05921 | 4.2528 | 0 | 0 | 66.9169 | 20.3849 | off_peak | 714.9851 | 0 | 100 | 2.77 | 0 | 97.23 | 86.6922 | 0
66 | 744.16 | 13.3 | 25.7 | 2.6865 | 2.6491 | 0 | 0.03739 | 0.03739 | 0 | 0 | 0 | 0 | 74.3912 | 741.5109 | 0 | 0.05921 | 4.5647 | 0 | 0 | 66.9519 | 2.6491 | off_peak | 741.5109 | 100 | 0 | 0.36 | 0 | 99.64 | 12.0923 | 0
67 | 723.25 | 0 | 25.6 | 0 | 0 | 0 | 0 | 0 | 0 | 62.6277 | 62.6277 | 0 | 7.4394 | 660.6223 | 0 | 0.088511 | 4.9942 | 0 | 0 | 66.9519 | 0 | on_peak | 660.6223 |  |  | 0 | 8.66 | 91.34 | 0 | 0
68 | 719.4 | 0 | 25.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 719.4 | 0 | 0.088511 | 5.2412 | 0 | 0 | 66.9519 | 0 | on_peak | 719.4 |  |  | 0 | 0 | 100 | 0 | 0
69 | 668.31 | 0 | 25.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 668.31 | 0 | 0.088511 | 5.4172 | 0 | 0 | 66.9519 | 0 | on_peak | 668.31 |  |  | 0 | 0 | 100 | 0 | 0
70 | 668.49 | 0 | 25.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 668.49 | 0 | 0.088511 | 5.6047 | 0 | 0 | 66.9519 | 0 | on_peak | 668.49 |  |  | 0 | 0 | 100 | 0 | 0
71 | 689.14 | 0 | 25.3 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 19.0375 | 701.5389 | 0 | 0.05921 | 5.8983 | 0 | 0 | 66.9519 | 0 | off_peak | 689.14 | 0 | 100 | 0 | 0 | 100 | 0 | 0
72 | 655.37 | 0 | 25.2 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 30.6357 | 667.7689 | 0 | 0.05921 | 6.0439 | 0 | 0 | 66.9519 | 0 | off_peak | 655.37 | 0 | 100 | 0 | 0 | 100 | 0 | 0
73 | 623.33 | 0 | 25.2 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 42.2338 | 635.7289 | 0 | 0.05921 | 6.1816 | 0 | 0 | 66.9519 | 0 | off_peak | 623.33 | 0 | 100 | 0 | 0 | 100 | 0 | 0
74 | 565.79 | 0 | 25.1 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 53.832 | 578.1889 | 0 | 0.05921 | 5.9388 | 0 | 0 | 66.9519 | 0 | off_peak | 565.79 | 0 | 100 | 0 | 0 | 100 | 0 | 0
75 | 499.28 | 0 | 25 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 65.4301 | 511.6789 | 0 | 0.05921 | 5.5251 | 0 | 0 | 66.9519 | 0 | off_peak | 499.28 | 0 | 100 | 0 | 0 | 100 | 0 | 0
76 | 523.2 | 0 | 24.9 | 0 | 0 | 0 | 0 | 8.9635 | 8.9635 | 0 | 0 | 0 | 73.8147 | 532.1635 | 0 | 0.05921 | 5.1591 | 0 | 0 | 66.9519 | 0 | off_peak | 523.2 | 0 | 100 | 0 | 0 | 100 | 0 | 0
77 | 516.74 | 0 | 24.8 | 0 | 0 | 0 | 0 | 0.57892 | 0.57892 | 0 | 0 | 0 | 74.3563 | 517.3189 | 0 | 0.05921 | 4.7625 | 0 | 0 | 66.9519 | 0 | off_peak | 516.74 | 0 | 100 | 0 | 0 | 100 | 0 | 0
78 | 620.7 | 0 | 24.7 | 0 | 0 | 0 | 0 | 0.03739 | 0.03739 | 0 | 0 | 0 | 74.3912 | 620.7374 | 0 | 0.05921 | 4.2547 | 0 | 0 | 66.9519 | 0 | off_peak | 620.7 | 0 | 100 | 0 | 0 | 100 | 0 | 0
79 | 656.92 | 0 | 24.8 | 0 | 0 | 0 | 0 | 0 | 0 | 62.6277 | 62.6277 | 0 | 7.4394 | 594.2923 | 0 | 0.088511 | 3.685 | 62.6277 | 0 | 0 | 62.6277 | on_peak | 594.2923 |  |  | 0 | 9.53 | 90.47 | 230.783 | 0
80 | 706.33 | 18.0175 | 25.2 | 3.6459 | 3.6459 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 702.6841 | 0 | 0.088511 | 3.3035 | 0 | 0 | 0 | 3.6459 | on_peak | 702.6841 |  |  | 0.52 | 0 | 99.48 | 12.0443 | 0
81 | 753.64 | 106.684 | 25.7 | 21.5491 | 21.5491 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 732.0909 | 0 | 0.088511 | 3.0402 | 0 | 0 | 0 | 21.5491 | on_peak | 732.0909 |  |  | 2.86 | 0 | 97.14 | 65.5131 | 0
82 | 740.72 | 283.869 | 26 | 57.2765 | 57.2765 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 683.4435 | 0 | 0.088511 | 2.9359 | 0 | 0 | 0 | 57.2765 | on_peak | 683.4435 |  |  | 7.73 | 0 | 92.27 | 168.1602 | 0
83 | 751.48 | 241.811 | 26.3 | 48.7376 | 48.7376 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 19.0375 | 715.1414 | 0 | 0.05921 | 2.9293 | 0 | 0 | 0 | 48.7376 | off_peak | 702.7424 | 0 | 100 | 6.49 | 0 | 93.51 | 142.7672 | 0
84 | 765.02 | 530.559 | 26.5 | 106.858 | 106.858 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 30.6357 | 670.5609 | 0 | 0.05921 | 3.1481 | 0 | 0 | 0 | 106.858 | off_peak | 658.162 | 0 | 100 | 13.97 | 0 | 86.03 | 336.3973 | 0
85 | 697.64 | 175.75 | 26.6 | 35.3844 | 35.3844 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 42.2338 | 674.6546 | 0 | 0.05921 | 3.5463 | 0 | 0 | 0 | 35.3844 | off_peak | 662.2556 | 0 | 100 | 5.07 | 0 | 94.93 | 125.4835 | 0
86 | 724.8 | 389.078 | 26.7 | 78.3061 | 65.9072 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 0 | 53.832 | 658.8928 | 0 | 0.05921 | 3.8548 | 0 | 0 | 11.5981 | 65.9072 | off_peak | 658.8928 | 100 | 0 | 9.09 | 0 | 90.91 | 254.0564 | 0
87 | 797.16 | 327.919 | 26.6 | 66.0211 | 53.6222 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 0 | 65.4301 | 743.5378 | 0 | 0.05921 | 4.1389 | 0 | 0 | 23.1963 | 53.6222 | off_peak | 743.5378 | 100 | 0 | 6.73 | 0 | 93.27 | 221.9387 | 0
88 | 779.42 | 288.153 | 26.4 | 58.0569 | 58.0569 | 0 | 0 | 8.9635 | 8.9635 | 0 | 0 | 0 | 73.8147 | 730.3267 | 0 | 0.05921 | 4.417 | 0 | 0 | 23.1963 | 58.0569 | off_peak | 721.3631 | 0 | 100 | 7.45 | 0 | 92.55 | 256.4381 | 0
89 | 787.46 | 134.381 | 26 | 27.1142 | 27.1142 | 0 | 0 | 0.57892 | 0.57892 | 0 | 0 | 0 | 74.3563 | 760.9247 | 0 | 0.05921 | 4.6371 | 0 | 0 | 23.1963 | 27.1142 | off_peak | 760.3458 | 0 | 100 | 3.44 | 0 | 96.56 | 125.731 | 0
90 | 749.12 | 14.25 | 25.4 | 2.8815 | 2.8441 | 0 | 0.03739 | 0.03739 | 0 | 0 | 0 | 0 | 74.3912 | 746.2759 | 0 | 0.05921 | 4.9059 | 0 | 0 | 23.2313 | 2.8441 | off_peak | 746.2759 | 100 | 0 | 0.38 | 0 | 99.62 | 13.9528 | 0
91 | 731.12 | 0 | 25.2 | 0 | 0 | 0 | 0 | 0 | 0 | 62.6277 | 62.6277 | 0 | 7.4394 | 668.4923 | 0 | 0.088511 | 5.2836 | 0 | 0 | 23.2313 | 0 | on_peak | 668.4923 |  |  | 0 | 8.57 | 91.43 | 0 | 0
92 | 746.91 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 746.91 | 0 | 0.088511 | 5.553 | 0 | 0 | 23.2313 | 0 | on_peak | 746.91 |  |  | 0 | 0 | 100 | 0 | 0
93 | 722.82 | 0 | 24.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 722.82 | 0 | 0.088511 | 5.7665 | 0 | 0 | 23.2313 | 0 | on_peak | 722.82 |  |  | 0 | 0 | 100 | 0 | 0
94 | 697.04 | 0 | 24.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 697.04 | 0 | 0.088511 | 6.0912 | 0 | 0 | 23.2313 | 0 | on_peak | 697.04 |  |  | 0 | 0 | 100 | 0 | 0
95 | 721.9 | 0 | 24.6 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 19.0375 | 734.2989 | 0 | 0.05921 | 6.2512 | 0 | 0 | 23.2313 | 0 | off_peak | 721.9 | 0 | 100 | 0 | 0 | 100 | 0 | 0
96 | 698.97 | 0 | 24.6 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 30.6357 | 711.3689 | 0 | 0.05921 | 6.3175 | 0 | 0 | 23.2313 | 0 | off_peak | 698.97 | 0 | 100 | 0 | 0 | 100 | 0 | 0
97 | 655.92 | 0 | 24.5 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 42.2338 | 668.3189 | 0 | 0.05921 | 6.3825 | 0 | 0 | 23.2313 | 0 | off_peak | 655.92 | 0 | 100 | 0 | 0 | 100 | 0 | 0
98 | 636.36 | 0 | 24.5 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 53.832 | 648.7589 | 0 | 0.05921 | 6.1937 | 0 | 0 | 23.2313 | 0 | off_peak | 636.36 | 0 | 100 | 0 | 0 | 100 | 0 | 0
99 | 575.58 | 0 | 24.4 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 65.4301 | 587.9789 | 0 | 0.05921 | 5.7264 | 0 | 0 | 23.2313 | 0 | off_peak | 575.58 | 0 | 100 | 0 | 0 | 100 | 0 | 0
100 | 576.47 | 0 | 24.3 | 0 | 0 | 0 | 0 | 8.9635 | 8.9635 | 0 | 0 | 0 | 73.8147 | 585.4335 | 0 | 0.05921 | 5.2621 | 0 | 0 | 23.2313 | 0 | off_peak | 576.47 | 0 | 100 | 0 | 0 | 100 | 0 | 0
101 | 580.04 | 0 | 24.2 | 0 | 0 | 0 | 0 | 0.57892 | 0.57892 | 0 | 0 | 0 | 74.3563 | 580.6189 | 0 | 0.05921 | 4.7501 | 0 | 0 | 23.2313 | 0 | off_peak | 580.04 | 0 | 100 | 0 | 0 | 100 | 0 | 0
102 | 665.06 | 0 | 24.1 | 0 | 0 | 0 | 0 | 0.03739 | 0.03739 | 0 | 0 | 0 | 74.3912 | 665.0974 | 0 | 0.05921 | 4.1765 | 0 | 0 | 23.2313 | 0 | off_peak | 665.06 | 0 | 100 | 0 | 0 | 100 | 0 | 0
103 | 748.44 | 0 | 24.2 | 0 | 0 | 0 | 0 | 0 | 0 | 62.6277 | 62.6277 | 0 | 7.4394 | 685.8123 | 0 | 0.088511 | 3.7369 | 0 | 0 | 23.2313 | 0 | on_peak | 685.8123 |  |  | 0 | 8.37 | 91.63 | 0 | 0
104 | 725.21 | 34.8872 | 24.7 | 7.0723 | 7.0723 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 718.1377 | 0 | 0.088511 | 3.3266 | 0 | 0 | 23.2313 | 7.0723 | on_peak | 718.1377 |  |  | 0.98 | 0 | 99.02 | 23.5267 | 0
105 | 750.66 | 170.267 | 25.3 | 34.4418 | 34.4418 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 716.2182 | 0 | 0.088511 | 3.118 | 0 | 0 | 23.2313 | 34.4418 | on_peak | 716.2182 |  |  | 4.59 | 0 | 95.41 | 107.3896 | 0
106 | 777.58 | 393.45 | 25.8 | 79.4442 | 79.4442 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 698.1358 | 0 | 0.088511 | 2.9697 | 0 | 0 | 23.2313 | 79.4442 | on_peak | 698.1358 |  |  | 10.22 | 0 | 89.78 | 235.9281 | 0
107 | 794.41 | 470.036 | 26.3 | 94.7368 | 82.3379 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 0 | 19.0375 | 712.0721 | 0 | 0.05921 | 2.9508 | 0 | 0 | 34.8294 | 82.3379 | off_peak | 712.0721 | 100 | 0 | 10.36 | 0 | 89.64 | 242.9611 | 0
108 | 911.97 | 629.254 | 26.7 | 126.6441 | 114.2452 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 0 | 30.6357 | 797.7248 | 0 | 0.05921 | 3.1531 | 0 | 0 | 46.4276 | 114.2452 | off_peak | 797.7248 | 100 | 0 | 12.53 | 0 | 87.47 | 360.2301 | 0
109 | 829.64 | 655.571 | 27 | 131.7973 | 131.7973 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 42.2338 | 710.2416 | 0 | 0.05921 | 3.5627 | 0 | 0 | 46.4276 | 131.7973 | off_peak | 697.8427 | 0 | 100 | 15.89 | 0 | 84.11 | 469.5583 | 0
110 | 883.77 | 628.744 | 27.1 | 126.3581 | 126.3581 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 53.832 | 769.8108 | 0 | 0.05921 | 3.9229 | 0 | 0 | 46.4276 | 126.3581 | off_peak | 757.4119 | 0 | 100 | 14.3 | 0 | 85.7 | 495.6852 | 0
111 | 911.51 | 527.951 | 27.1 | 106.1018 | 106.1018 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 65.4301 | 817.8071 | 0 | 0.05921 | 4.1771 | 0 | 0 | 46.4276 | 106.1018 | off_peak | 805.4082 | 0 | 100 | 11.64 | 0 | 88.36 | 443.1962 | 0
112 | 891.73 | 376.425 | 26.8 | 75.7321 | 75.7321 | 0 | 0 | 8.9635 | 8.9635 | 0 | 0 | 0 | 73.8147 | 824.9614 | 0 | 0.05921 | 4.286 | 0 | 0 | 46.4276 | 75.7321 | off_peak | 815.9979 | 0 | 100 | 8.49 | 0 | 91.51 | 324.5886 | 0
113 | 868.67 | 191.859 | 26 | 38.7116 | 38.1327 | 0 | 0.57892 | 0.57892 | 0 | 0 | 0 | 0 | 74.3563 | 830.5373 | 0 | 0.05921 | 4.3698 | 0 | 0 | 46.9691 | 38.1327 | off_peak | 830.5373 | 100 | 0 | 4.39 | 0 | 95.61 | 166.6321 | 0
114 | 872.17 | 23.2185 | 25.2 | 4.6984 | 4.6984 | 0 | 0 | 0.03739 | 0.03739 | 0 | 0 | 0 | 74.3912 | 867.509 | 0 | 0.05921 | 4.6662 | 0 | 0 | 46.9691 | 4.6984 | off_peak | 867.4716 | 0 | 100 | 0.54 | 0 | 99.46 | 21.9233 | 0
115 | 794.27 | 0 | 24.8 | 0 | 0 | 0 | 0 | 0 | 0 | 35.2836 | 35.2836 | 0 | 36.6715 | 758.9864 | 0 | 0.088511 | 4.9803 | 0 | 0 | 46.9691 | 0 | on_peak | 758.9864 |  |  | 0 | 4.44 | 95.56 | 0 | 0
116 | 846.67 | 0 | 24.1 | 0 | 0 | 0 | 0 | 0 | 0 | 27.3442 | 27.3442 | 0 | 7.4394 | 819.3258 | 0 | 0.088511 | 5.438 | 0 | 0 | 46.9691 | 0 | on_peak | 819.3258 |  |  | 0 | 3.23 | 96.77 | 0 | 0
117 | 805.5 | 0 | 23.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 805.5 | 0 | 0.088511 | 5.5995 | 0 | 0 | 46.9691 | 0 | on_peak | 805.5 |  |  | 0 | 0 | 100 | 0 | 0
118 | 789.04 | 0 | 23.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 789.04 | 0 | 0.088511 | 5.7008 | 0 | 0 | 46.9691 | 0 | on_peak | 789.04 |  |  | 0 | 0 | 100 | 0 | 0
119 | 783.91 | 0 | 23.7 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 19.0375 | 796.3089 | 0 | 0.05921 | 5.8055 | 0 | 0 | 46.9691 | 0 | off_peak | 783.91 | 0 | 100 | 0 | 0 | 100 | 0 | 0
120 | 755.57 | 0 | 23.7 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 30.6357 | 767.9689 | 0 | 0.05921 | 6.0091 | 0 | 0 | 46.9691 | 0 | off_peak | 755.57 | 0 | 100 | 0 | 0 | 100 | 0 | 0
121 | 735.54 | 0 | 23.7 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 42.2338 | 747.9389 | 0 | 0.05921 | 6.1559 | 0 | 0 | 46.9691 | 0 | off_peak | 735.54 | 0 | 100 | 0 | 0 | 100 | 0 | 0
122 | 656.71 | 0 | 23.6 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 53.832 | 669.1089 | 0 | 0.05921 | 5.9015 | 0 | 0 | 46.9691 | 0 | off_peak | 656.71 | 0 | 100 | 0 | 0 | 100 | 0 | 0
123 | 635.01 | 0 | 23.5 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 65.4301 | 647.4089 | 0 | 0.05921 | 5.5042 | 0 | 0 | 46.9691 | 0 | off_peak | 635.01 | 0 | 100 | 0 | 0 | 100 | 0 | 0
124 | 622.1 | 0 | 23.4 | 0 | 0 | 0 | 0 | 8.9635 | 8.9635 | 0 | 0 | 0 | 73.8147 | 631.0635 | 0 | 0.05921 | 4.9625 | 0 | 0 | 46.9691 | 0 | off_peak | 622.1 | 0 | 100 | 0 | 0 | 100 | 0 | 0
125 | 635.59 | 0 | 23.3 | 0 | 0 | 0 | 0 | 0.57892 | 0.57892 | 0 | 0 | 0 | 74.3563 | 636.1689 | 0 | 0.05921 | 4.4999 | 0 | 0 | 46.9691 | 0 | off_peak | 635.59 | 0 | 100 | 0 | 0 | 100 | 0 | 0
126 | 703.08 | 0 | 23.3 | 0 | 0 | 0 | 0 | 0.03739 | 0.03739 | 0 | 0 | 0 | 74.3912 | 703.1174 | 0 | 0.05921 | 3.8718 | 0 | 0 | 46.9691 | 0 | off_peak | 703.08 | 0 | 100 | 0 | 0 | 100 | 0 | 0
127 | 767.76 | 0 | 23.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3912 | 767.76 | 0 | 0.088511 | 3.4465 | 0 | 0 | 46.9691 | 0 | on_peak | 767.76 |  |  | 0 | 0 | 100 | 0 | 0
128 | 760.34 | 32.8886 | 24.1 | 6.6815 | 6.6815 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3912 | 753.6585 | 0 | 0.088511 | 3.0586 | 0 | 0 | 46.9691 | 6.6815 | on_peak | 753.6585 |  |  | 0.88 | 0 | 99.12 | 20.4363 | 0
129 | 772.37 | 204.107 | 24.9 | 41.3465 | 41.3465 | 0 | 0 | 0 | 0 | 62.6277 | 62.6277 | 0 | 7.4394 | 668.3957 | 0 | 0.088511 | 2.8492 | 0 | 0 | 46.9691 | 41.3465 | on_peak | 668.3957 |  |  | 5.35 | 8.11 | 86.54 | 117.8052 | 0
130 | 746.33 | 381.111 | 25.4 | 77.0638 | 77.0638 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 669.2662 | 0 | 0.088511 | 2.7526 | 0 | 0 | 46.9691 | 77.0638 | on_peak | 669.2662 |  |  | 10.33 | 0 | 89.67 | 212.123 | 0
131 | 737.21 | 522.043 | 25.9 | 105.3712 | 92.9723 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 0 | 19.0375 | 644.2377 | 0 | 0.05921 | 2.7477 | 0 | 0 | 58.5672 | 92.9723 | off_peak | 644.2377 | 100 | 0 | 12.61 | 0 | 87.39 | 255.4604 | 0
132 | 807.64 | 608.572 | 26.3 | 122.6591 | 110.2601 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 0 | 30.6357 | 697.3799 | 0 | 0.05921 | 3.0043 | 0 | 0 | 70.1654 | 110.2601 | off_peak | 697.3799 | 100 | 0 | 13.65 | 0 | 86.35 | 331.2536 | 0
133 | 746.33 | 633.456 | 26.5 | 127.5822 | 115.1832 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 0 | 42.2338 | 631.1468 | 0 | 0.05921 | 3.4763 | 0 | 0 | 81.7635 | 115.1832 | off_peak | 631.1468 | 100 | 0 | 15.43 | 0 | 84.57 | 400.4129 | 0
134 | 784.07 | 573.928 | 26.6 | 115.551 | 115.551 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 53.832 | 680.918 | 0 | 0.05921 | 3.8971 | 0 | 0 | 81.7635 | 115.551 | off_peak | 668.519 | 0 | 100 | 14.74 | 0 | 85.26 | 450.3183 | 0
135 | 800.58 | 262.623 | 26.6 | 52.8748 | 40.4759 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 0 | 65.4301 | 760.1041 | 0 | 0.05921 | 3.9327 | 0 | 0 | 93.3617 | 40.4759 | off_peak | 760.1041 | 100 | 0 | 5.06 | 0 | 94.94 | 159.1788 | 0
136 | 813.37 | 213.97 | 26.4 | 43.1105 | 43.1105 | 0 | 0 | 8.9635 | 8.9635 | 0 | 0 | 0 | 73.8147 | 779.223 | 0 | 0.05921 | 3.624 | 0 | 0 | 93.3617 | 43.1105 | off_peak | 770.2595 | 0 | 100 | 5.3 | 0 | 94.7 | 156.233 | 0
137 | 753.32 | 173.916 | 26 | 35.0912 | 34.5123 | 0 | 0.57892 | 0.57892 | 0 | 0 | 0 | 0 | 74.3563 | 718.8077 | 0 | 0.05921 | 3.5748 | 0 | 0 | 93.9032 | 34.5123 | off_peak | 718.8077 | 100 | 0 | 4.58 | 0 | 95.42 | 123.3754 | 0
138 | 770.19 | 11.4 | 25.5 | 2.3043 | 2.267 | 0 | 0.03739 | 0.03739 | 0 | 0 | 0 | 0 | 74.3912 | 767.923 | 0 | 0.05921 | 3.4823 | 0 | 0 | 93.9382 | 2.267 | off_peak | 767.923 | 100 | 0 | 0.29 | 0 | 99.71 | 7.8943 | 0
139 | 756.83 | 0 | 25.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3912 | 756.83 | 0 | 0.088511 | 3.4996 | 0 | 0 | 93.9382 | 0 | on_peak | 756.83 |  |  | 0 | 0 | 100 | 0 | 0
140 | 747.62 | 0 | 24.9 | 0 | 0 | 0 | 0 | 0 | 0 | 62.6277 | 62.6277 | 0 | 7.4394 | 684.9923 | 0 | 0.088511 | 3.5914 | 0 | 0 | 93.9382 | 0 | on_peak | 684.9923 |  |  | 0 | 8.38 | 91.62 | 0 | 0
141 | 712.58 | 0 | 24.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 712.58 | 0 | 0.088511 | 3.7058 | 0 | 0 | 93.9382 | 0 | on_peak | 712.58 |  |  | 0 | 0 | 100 | 0 | 0
142 | 703.91 | 0 | 24.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 703.91 | 0 | 0.088511 | 3.9865 | 0 | 0 | 93.9382 | 0 | on_peak | 703.91 |  |  | 0 | 0 | 100 | 0 | 0
143 | 689.9 | 0 | 24.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 689.9 | 0 | 0.05921 | 4.516 | 0 | 0 | 93.9382 | 0 | off_peak | 689.9 |  |  | 0 | 0 | 100 | 0 | 0
144 | 730.97 | 0 | 23.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 730.97 | 0 | 0.05921 | 4.9681 | 0 | 0 | 93.9382 | 0 | off_peak | 730.97 |  |  | 0 | 0 | 100 | 0 | 0
145 | 645.57 | 0 | 23.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 645.57 | 0 | 0.05921 | 5.1383 | 0 | 0 | 93.9382 | 0 | off_peak | 645.57 |  |  | 0 | 0 | 100 | 0 | 0
146 | 619.36 | 0 | 23.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 619.36 | 0 | 0.05921 | 4.957 | 0 | 0 | 93.9382 | 0 | off_peak | 619.36 |  |  | 0 | 0 | 100 | 0 | 0
147 | 570.98 | 0 | 23.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 570.98 | 0 | 0.05921 | 4.6814 | 0 | 0 | 93.9382 | 0 | off_peak | 570.98 |  |  | 0 | 0 | 100 | 0 | 0
148 | 570.47 | 0 | 23.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 570.47 | 0 | 0.05921 | 4.4219 | 0 | 0 | 93.9382 | 0 | off_peak | 570.47 |  |  | 0 | 0 | 100 | 0 | 0
149 | 582.47 | 0 | 23.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 582.47 | 0 | 0.05921 | 4.0417 | 0 | 0 | 93.9382 | 0 | off_peak | 582.47 |  |  | 0 | 0 | 100 | 0 | 0
150 | 659.41 | 0 | 22.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 659.41 | 0 | 0.05921 | 3.6094 | 0 | 0 | 93.9382 | 0 | off_peak | 659.41 |  |  | 0 | 0 | 100 | 0 | 0
151 | 668.43 | 0 | 22.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 668.43 | 0 | 0.05921 | 3.363 | 0 | 0 | 93.9382 | 0 | off_peak | 668.43 |  |  | 0 | 0 | 100 | 0 | 0
152 | 680.52 | 28.1777 | 22.6 | 5.7553 | 5.7553 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 674.7647 | 0 | 0.05921 | 3.0777 | 0 | 0 | 93.9382 | 5.7553 | off_peak | 674.7647 |  |  | 0.85 | 0 | 99.15 | 17.713 | 0
153 | 725.4 | 194.003 | 22.7 | 39.6109 | 39.6109 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 685.7891 | 0 | 0.05921 | 2.921 | 0 | 0 | 93.9382 | 39.6109 | off_peak | 685.7891 |  |  | 5.46 | 0 | 94.54 | 115.703 | 0
154 | 701.32 | 370.695 | 23.1 | 75.5792 | 75.5792 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 625.7408 | 0 | 0.05921 | 2.8836 | 0 | 0 | 93.9382 | 75.5792 | off_peak | 625.7408 |  |  | 10.78 | 0 | 89.22 | 217.942 | 0
155 | 721.82 | 515.763 | 23.8 | 104.8932 | 104.8932 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 616.9268 | 0 | 0.05921 | 2.8993 | 0 | 0 | 93.9382 | 104.8932 | off_peak | 616.9268 |  |  | 14.53 | 0 | 85.47 | 304.1154 | 0
156 | 721.35 | 606.311 | 24.4 | 123.0432 | 123.0432 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 598.3068 | 0 | 0.05921 | 3.0398 | 0 | 0 | 93.9382 | 123.0432 | off_peak | 598.3068 |  |  | 17.06 | 0 | 82.94 | 374.0327 | 0
157 | 695.28 | 466.087 | 24.9 | 94.4166 | 94.4166 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 600.8634 | 0 | 0.05921 | 3.3813 | 0 | 0 | 93.9382 | 94.4166 | off_peak | 600.8634 |  |  | 13.58 | 0 | 86.42 | 319.248 | 0
158 | 660.79 | 117.455 | 25.2 | 23.7675 | 23.7675 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 637.0225 | 0 | 0.05921 | 3.9272 | 0 | 0 | 93.9382 | 23.7675 | off_peak | 637.0225 |  |  | 3.6 | 0 | 96.4 | 93.3396 | 0
159 | 625.65 | 254.162 | 25.4 | 51.3937 | 38.9948 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 0 | 19.0375 | 586.6552 | 0 | 0.05921 | 3.9496 | 0 | 0 | 105.5363 | 38.9948 | off_peak | 586.6552 | 100 | 0 | 6.23 | 0 | 93.77 | 154.0129 | 0
160 | 627.58 | 35.15 | 25.4 | 7.1076 | 7.1076 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19.0375 | 620.4724 | 0 | 0.05921 | 3.6729 | 0 | 0 | 105.5363 | 7.1076 | off_peak | 620.4724 |  |  | 1.13 | 0 | 98.87 | 26.1059 | 0
161 | 602.92 | 85.7155 | 25 | 17.3574 | 17.3574 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19.0375 | 585.5626 | 0 | 0.05921 | 3.4665 | 0 | 0 | 105.5363 | 17.3574 | off_peak | 585.5626 |  |  | 2.88 | 0 | 97.12 | 60.169 | 0
162 | 570.45 | 4.75 | 24.3 | 0.9643 | 0.9643 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19.0375 | 569.4857 | 0 | 0.05921 | 3.2594 | 0 | 0 | 105.5363 | 0.9643 | off_peak | 569.4857 |  |  | 0.17 | 0 | 99.83 | 3.1431 | 0
163 | 549.28 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19.0375 | 549.28 | 0 | 0.05921 | 3.263 | 0 | 0 | 105.5363 | 0 | off_peak | 549.28 |  |  | 0 | 0 | 100 | 0 | 0
164 | 505.18 | 0 | 22.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19.0375 | 505.18 | 0 | 0.05921 | 3.3097 | 0 | 0 | 105.5363 | 0 | off_peak | 505.18 |  |  | 0 | 0 | 100 | 0 | 0
165 | 534.63 | 0 | 21.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19.0375 | 534.63 | 0 | 0.05921 | 3.4478 | 0 | 0 | 105.5363 | 0 | off_peak | 534.63 |  |  | 0 | 0 | 100 | 0 | 0
166 | 504.31 | 0 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19.0375 | 504.31 | 0 | 0.05921 | 3.7534 | 0 | 0 | 105.5363 | 0 | off_peak | 504.31 |  |  | 0 | 0 | 100 | 0 | 0
167 | 520.65 | 0 | 20.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19.0375 | 520.65 | 0 | 0.05921 | 4.2573 | 0 | 0 | 105.5363 | 0 | off_peak | 520.65 |  |  | 0 | 0 | 100 | 0 | 0
168 | 528.55 | 0 | 19.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19.0375 | 528.55 | 0 | 0.05921 | 4.6642 | 0 | 0 | 105.5363 | 0 | off_peak | 528.55 |  |  | 0 | 0 | 100 | 0 | 0
169 | 499.41 | 0 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19.0375 | 499.41 | 0 | 0.05921 | 4.8552 | 0 | 0 | 105.5363 | 0 | off_peak | 499.41 |  |  | 0 | 0 | 100 | 0 | 0
170 | 554 | 0 | 18.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19.0375 | 554 | 0 | 0.05921 | 4.6595 | 0 | 0 | 105.5363 | 0 | off_peak | 554 |  |  | 0 | 0 | 100 | 0 | 0
171 | 552.65 | 0 | 17.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19.0375 | 552.65 | 0 | 0.05921 | 4.4161 | 0 | 0 | 105.5363 | 0 | off_peak | 552.65 |  |  | 0 | 0 | 100 | 0 | 0
172 | 525.44 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19.0375 | 525.44 | 0 | 0.05921 | 4.1597 | 0 | 0 | 105.5363 | 0 | off_peak | 525.44 |  |  | 0 | 0 | 100 | 0 | 0
173 | 526.94 | 0 | 16.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19.0375 | 526.94 | 0 | 0.05921 | 3.8636 | 0 | 0 | 105.5363 | 0 | off_peak | 526.94 |  |  | 0 | 0 | 100 | 0 | 0
174 | 560.98 | 0 | 16.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19.0375 | 560.98 | 0 | 0.05921 | 3.507 | 0 | 0 | 105.5363 | 0 | off_peak | 560.98 |  |  | 0 | 0 | 100 | 0 | 0
175 | 649.14 | 0 | 15.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19.0375 | 649.14 | 0 | 0.05921 | 3.2173 | 0 | 0 | 105.5363 | 0 | off_peak | 649.14 |  |  | 0 | 0 | 100 | 0 | 0
176 | 640.05 | 32.242 | 16.2 | 6.7358 | 6.7358 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19.0375 | 633.3142 | 0 | 0.05921 | 2.9434 | 0 | 0 | 105.5363 | 6.7358 | off_peak | 633.3142 |  |  | 1.05 | 0 | 98.95 | 19.8264 | 0
177 | 637.43 | 210.867 | 17 | 43.9303 | 43.9303 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19.0375 | 593.4997 | 0 | 0.05921 | 2.8066 | 0 | 0 | 105.5363 | 43.9303 | off_peak | 593.4997 |  |  | 6.89 | 0 | 93.11 | 123.2931 | 0
178 | 674.87 | 400.005 | 18.3 | 82.9548 | 82.9548 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19.0375 | 591.9152 | 0 | 0.05921 | 2.7508 | 0 | 0 | 105.5363 | 82.9548 | off_peak | 591.9152 |  |  | 12.29 | 0 | 87.71 | 228.196 | 0
179 | 618.45 | 553.776 | 19.5 | 114.36 | 114.36 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19.0375 | 504.09 | 0 | 0.05921 | 2.755 | 0 | 0 | 105.5363 | 114.36 | off_peak | 504.09 |  |  | 18.49 | 0 | 81.51 | 315.066 | 0
180 | 642.16 | 652.689 | 20.3 | 134.4058 | 125.6795 | 0 | 8.7263 | 8.7263 | 0 | 0 | 0 | 0 | 27.2003 | 516.4805 | 0 | 0.05921 | 2.891 | 0 | 0 | 113.6991 | 125.6795 | off_peak | 516.4805 | 100 | 0 | 19.57 | 0 | 80.43 | 363.3385 | 0
181 | 621.77 | 682.59 | 20.9 | 140.2647 | 140.2647 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27.2003 | 481.5053 | 0 | 0.05921 | 3.1352 | 0 | 0 | 113.6991 | 140.2647 | off_peak | 481.5053 |  |  | 22.56 | 0 | 77.44 | 439.7641 | 0
182 | 594.91 | 646.219 | 21.2 | 132.6495 | 132.6495 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27.2003 | 462.2605 | 0 | 0.05921 | 3.5512 | 0 | 0 | 113.6991 | 132.6495 | off_peak | 462.2605 |  |  | 22.3 | 0 | 77.7 | 471.0675 | 0
183 | 617.49 | 547.594 | 21.2 | 112.4047 | 112.4047 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27.2003 | 505.0853 | 0 | 0.05921 | 3.752 | 0 | 0 | 113.6991 | 112.4047 | off_peak | 505.0853 |  |  | 18.2 | 0 | 81.8 | 421.7406 | 0
184 | 587.52 | 391.283 | 21.1 | 80.3473 | 80.3473 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27.2003 | 507.1727 | 0 | 0.05921 | 3.5786 | 0 | 0 | 113.6991 | 80.3473 | off_peak | 507.1727 |  |  | 13.68 | 0 | 86.32 | 287.5322 | 0
185 | 617.31 | 200.857 | 20.9 | 41.2739 | 28.8749 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 0 | 38.7984 | 588.4351 | 0 | 0.05921 | 3.4652 | 0 | 0 | 125.2972 | 28.8749 | off_peak | 588.4351 | 100 | 0 | 4.68 | 0 | 95.32 | 100.0583 | 0
186 | 555.24 | 24.6514 | 20.8 | 5.0674 | 5.0674 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 38.7984 | 550.1726 | 0 | 0.05921 | 3.6129 | 0 | 0 | 125.2972 | 5.0674 | off_peak | 550.1726 |  |  | 0.91 | 0 | 99.09 | 18.308 | 0
187 | 557.43 | 0 | 20.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 38.7984 | 557.43 | 0 | 0.05921 | 3.739 | 0 | 0 | 125.2972 | 0 | off_peak | 557.43 |  |  | 0 | 0 | 100 | 0 | 0
188 | 529.05 | 0 | 20.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 38.7984 | 529.05 | 0 | 0.05921 | 3.8649 | 0 | 0 | 125.2972 | 0 | off_peak | 529.05 |  |  | 0 | 0 | 100 | 0 | 0
189 | 508.7 | 0 | 20.9 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 50.3966 | 521.0989 | 0 | 0.05921 | 4.0754 | 0 | 0 | 125.2972 | 0 | off_peak | 508.7 | 0 | 100 | 0 | 0 | 100 | 0 | 0
190 | 506.93 | 0 | 20.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50.3966 | 506.93 | 0 | 0.05921 | 4.3274 | 0 | 0 | 125.2972 | 0 | off_peak | 506.93 |  |  | 0 | 0 | 100 | 0 | 0
191 | 507.89 | 0 | 20.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50.3966 | 507.89 | 0 | 0.05921 | 4.6948 | 0 | 0 | 125.2972 | 0 | off_peak | 507.89 |  |  | 0 | 0 | 100 | 0 | 0
192 | 494.64 | 0 | 20.9 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 61.9947 | 507.0389 | 0 | 0.05921 | 5.0539 | 0 | 0 | 125.2972 | 0 | off_peak | 494.64 | 0 | 100 | 0 | 0 | 100 | 0 | 0
193 | 518.56 | 0 | 20.9 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 73.5928 | 530.9589 | 0 | 0.05921 | 5.2595 | 0 | 0 | 125.2972 | 0 | off_peak | 518.56 | 0 | 100 | 0 | 0 | 100 | 0 | 0
194 | 504.72 | 0 | 20.9 | 0 | 0 | 0 | 0 | 0.80079 | 0.80079 | 0 | 0 | 0 | 74.3419 | 505.5208 | 0 | 0.05921 | 5.0554 | 0 | 0 | 125.2972 | 0 | off_peak | 504.72 | 0 | 100 | 0 | 0 | 100 | 0 | 0
195 | 507.78 | 0 | 20.9 | 0 | 0 | 0 | 0 | 0.05172 | 0.05172 | 0 | 0 | 0 | 74.3903 | 507.8317 | 0 | 0.05921 | 4.7467 | 0 | 0 | 125.2972 | 0 | off_peak | 507.78 | 0 | 100 | 0 | 0 | 100 | 0 | 0
196 | 518.91 | 0 | 20.9 | 0 | 0 | 0 | 0 | 0.0033404 | 0.0033404 | 0 | 0 | 0 | 74.3934 | 518.9133 | 0 | 0.05921 | 4.3693 | 0 | 0 | 125.2972 | 0 | off_peak | 518.91 | 0 | 100 | 0 | 0 | 100 | 0 | 0
197 | 535.62 | 0 | 21 | 0 | 0 | 0 | 0 | 0.00021574 | 0.00021574 | 0 | 0 | 0 | 74.3936 | 535.6202 | 0 | 0.05921 | 3.924 | 0 | 0 | 125.2972 | 0 | off_peak | 535.62 | 0 | 100 | 0 | 0 | 100 | 0 | 0
198 | 634.83 | 0 | 21.1 | 0 | 0 | 0 | 0 | 1.3934e-05 | 1.3934e-05 | 0 | 0 | 0 | 74.3936 | 634.83 | 0 | 0.05921 | 3.4127 | 0 | 0 | 125.2972 | 0 | off_peak | 634.83 | 0 | 100 | 0 | 0 | 100 | 0 | 0
199 | 719.73 | 0 | 21.3 | 0 | 0 | 0 | 0 | 0 | 0 | 62.63 | 62.63 | 0 | 7.4394 | 657.1 | 0 | 0.088511 | 2.9105 | 0 | 0 | 125.2972 | 0 | on_peak | 657.1 |  |  | 0 | 8.7 | 91.3 | 0 | 0
200 | 777.71 | 32.075 | 21.9 | 6.5677 | 6.5677 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 771.1423 | 0 | 0.088511 | 2.6501 | 0 | 0 | 125.2972 | 6.5677 | on_peak | 771.1423 |  |  | 0.84 | 0 | 99.16 | 17.405 | 0
201 | 770.3 | 207.483 | 22.7 | 42.3632 | 42.3632 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 727.9368 | 0 | 0.088511 | 2.5161 | 0 | 0 | 125.2972 | 42.3632 | on_peak | 727.9368 |  |  | 5.5 | 0 | 94.5 | 106.5913 | 0
202 | 836.04 | 392.781 | 23.2 | 80.0536 | 80.0536 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 755.9864 | 0 | 0.088511 | 2.469 | 0 | 0 | 125.2972 | 80.0536 | on_peak | 755.9864 |  |  | 9.58 | 0 | 90.42 | 197.6524 | 0
203 | 819.64 | 299.003 | 23.5 | 60.8751 | 48.4761 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 0 | 19.0375 | 771.1639 | 0 | 0.05921 | 2.5525 | 0 | 0 | 136.8954 | 48.4761 | off_peak | 771.1639 | 100 | 0 | 5.91 | 0 | 94.09 | 123.7365 | 0
204 | 874.27 | 470.348 | 23.7 | 95.6912 | 95.6912 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 30.6357 | 790.9777 | 0 | 0.05921 | 2.9107 | 0 | 0 | 136.8954 | 95.6912 | off_peak | 778.5788 | 0 | 100 | 10.95 | 0 | 89.05 | 278.5291 | 0
205 | 833.95 | 679.811 | 23.7 | 138.306 | 138.306 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 42.2338 | 708.043 | 0 | 0.05921 | 3.4778 | 0 | 0 | 136.8954 | 138.306 | off_peak | 695.644 | 0 | 100 | 16.58 | 0 | 83.42 | 480.998 | 0
206 | 871.71 | 652.608 | 23.7 | 132.7716 | 120.3727 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 0 | 53.832 | 751.3373 | 0 | 0.05921 | 3.8323 | 0 | 0 | 148.4935 | 120.3727 | off_peak | 751.3373 | 100 | 0 | 13.81 | 0 | 86.19 | 461.3023 | 0
207 | 831.8 | 553.051 | 23.6 | 112.5573 | 112.5573 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 65.4301 | 731.6417 | 0 | 0.05921 | 3.7913 | 0 | 0 | 148.4935 | 112.5573 | off_peak | 719.2427 | 0 | 100 | 13.53 | 0 | 86.47 | 426.7432 | 0
208 | 839.46 | 398.344 | 23.5 | 81.1002 | 81.1002 | 0 | 0 | 8.9635 | 8.9635 | 0 | 0 | 0 | 73.8147 | 767.3233 | 0 | 0.05921 | 3.5663 | 0 | 0 | 148.4935 | 81.1002 | off_peak | 758.3598 | 0 | 100 | 9.66 | 0 | 90.34 | 289.2287 | 0
209 | 798.72 | 42.75 | 23.3 | 8.7099 | 8.7099 | 0 | 0 | 0.57892 | 0.57892 | 0 | 0 | 0 | 74.3563 | 790.5891 | 0 | 0.05921 | 3.4135 | 0 | 0 | 148.4935 | 8.7099 | off_peak | 790.0101 | 0 | 100 | 1.09 | 0 | 98.91 | 29.7315 | 0
210 | 808.72 | 28.4621 | 23.1 | 5.803 | 5.7656 | 0 | 0.03739 | 0.03739 | 0 | 0 | 0 | 0 | 74.3912 | 802.9544 | 0 | 0.05921 | 3.4302 | 0 | 0 | 148.5285 | 5.7656 | off_peak | 802.9544 | 100 | 0 | 0.71 | 0 | 99.29 | 19.7773 | 0
211 | 778.28 | 0 | 23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3912 | 778.28 | 0 | 0.088511 | 3.5255 | 0 | 0 | 148.5285 | 0 | on_peak | 778.28 |  |  | 0 | 0 | 100 | 0 | 0
212 | 808.23 | 0 | 22.7 | 0 | 0 | 0 | 0 | 0 | 0 | 62.6277 | 62.6277 | 0 | 7.4394 | 745.6023 | 0 | 0.088511 | 3.6586 | 0 | 0 | 148.5285 | 0 | on_peak | 745.6023 |  |  | 0 | 7.75 | 92.25 | 0 | 0
213 | 746.54 | 0 | 22.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 746.54 | 0 | 0.088511 | 3.8765 | 0 | 0 | 148.5285 | 0 | on_peak | 746.54 |  |  | 0 | 0 | 100 | 0 | 0
214 | 708.99 | 0 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 708.99 | 0 | 0.088511 | 4.2085 | 0 | 0 | 148.5285 | 0 | on_peak | 708.99 |  |  | 0 | 0 | 100 | 0 | 0
215 | 745.9 | 0 | 21.4 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 19.0375 | 758.2989 | 0 | 0.05921 | 4.7418 | 0 | 0 | 148.5285 | 0 | off_peak | 745.9 | 0 | 100 | 0 | 0 | 100 | 0 | 0
216 | 705.86 | 0 | 20.8 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 30.6357 | 718.2589 | 0 | 0.05921 | 5.1884 | 0 | 0 | 148.5285 | 0 | off_peak | 705.86 | 0 | 100 | 0 | 0 | 100 | 0 | 0
217 | 661.04 | 0 | 20.2 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 42.2338 | 673.4389 | 0 | 0.05921 | 5.3396 | 0 | 0 | 148.5285 | 0 | off_peak | 661.04 | 0 | 100 | 0 | 0 | 100 | 0 | 0
218 | 567.56 | 0 | 19.6 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 53.832 | 579.9589 | 0 | 0.05921 | 5.2182 | 0 | 0 | 148.5285 | 0 | off_peak | 567.56 | 0 | 100 | 0 | 0 | 100 | 0 | 0
219 | 590.04 | 0 | 19 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 65.4301 | 602.4389 | 0 | 0.05921 | 4.8625 | 0 | 0 | 148.5285 | 0 | off_peak | 590.04 | 0 | 100 | 0 | 0 | 100 | 0 | 0
220 | 559.7 | 0 | 18.5 | 0 | 0 | 0 | 0 | 8.9635 | 8.9635 | 0 | 0 | 0 | 73.8147 | 568.6635 | 0 | 0.05921 | 4.4499 | 0 | 0 | 148.5285 | 0 | off_peak | 559.7 | 0 | 100 | 0 | 0 | 100 | 0 | 0
221 | 593.9 | 0 | 18.1 | 0 | 0 | 0 | 0 | 0.57892 | 0.57892 | 0 | 0 | 0 | 74.3563 | 594.4789 | 0 | 0.05921 | 4.0293 | 0 | 0 | 148.5285 | 0 | off_peak | 593.9 | 0 | 100 | 0 | 0 | 100 | 0 | 0
222 | 702.82 | 0 | 17.9 | 0 | 0 | 0 | 0 | 0.03739 | 0.03739 | 0 | 0 | 0 | 74.3912 | 702.8574 | 0 | 0.05921 | 3.4953 | 0 | 0 | 148.5285 | 0 | off_peak | 702.82 | 0 | 100 | 0 | 0 | 100 | 0 | 0
223 | 753.69 | 0 | 17.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3912 | 753.69 | 0 | 0.088511 | 3.0781 | 0 | 0 | 148.5285 | 0 | on_peak | 753.69 |  |  | 0 | 0 | 100 | 0 | 0
224 | 769.8 | 14.25 | 17.9 | 2.9594 | 2.9594 | 0 | 0 | 0 | 0 | 62.6277 | 62.6277 | 0 | 7.4394 | 704.2129 | 0 | 0.088511 | 2.7894 | 0 | 0 | 148.5285 | 2.9594 | on_peak | 704.2129 |  |  | 0.38 | 8.14 | 91.48 | 8.255 | 0
225 | 753.4 | 48.45 | 18.5 | 10.0407 | 10.0407 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 743.3593 | 0 | 0.088511 | 2.6614 | 0 | 0 | 148.5285 | 10.0407 | on_peak | 743.3593 |  |  | 1.33 | 0 | 98.67 | 26.7219 | 0
226 | 813.74 | 170.2 | 19.7 | 35.1231 | 35.1231 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 778.6169 | 0 | 0.088511 | 2.6343 | 0 | 0 | 148.5285 | 35.1231 | on_peak | 778.6169 |  |  | 4.32 | 0 | 95.68 | 92.5231 | 0
227 | 759.56 | 389.136 | 21.1 | 79.9064 | 79.9064 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 19.0375 | 692.0525 | 0 | 0.05921 | 2.7296 | 0 | 0 | 148.5285 | 79.9064 | off_peak | 679.6536 | 0 | 100 | 10.52 | 0 | 89.48 | 218.1127 | 0
228 | 828.64 | 646.118 | 22.4 | 132.0635 | 119.6646 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 0 | 30.6357 | 708.9754 | 0 | 0.05921 | 3.1254 | 0 | 0 | 160.1266 | 119.6646 | off_peak | 708.9754 | 100 | 0 | 14.44 | 0 | 85.56 | 374.0045 | 0
229 | 780.57 | 677.308 | 23.3 | 137.9943 | 137.9943 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 42.2338 | 654.9747 | 0 | 0.05921 | 3.7444 | 0 | 0 | 160.1266 | 137.9943 | off_peak | 642.5757 | 0 | 100 | 17.68 | 0 | 82.32 | 516.7098 | 0
230 | 808.3 | 144.4 | 23.8 | 29.3673 | 29.3673 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 53.832 | 791.3316 | 0 | 0.05921 | 4.1098 | 0 | 0 | 160.1266 | 29.3673 | off_peak | 778.9327 | 0 | 100 | 3.63 | 0 | 96.37 | 120.6949 | 0
231 | 857.22 | 368.807 | 24 | 74.9523 | 62.5533 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 0 | 65.4301 | 794.6667 | 0 | 0.05921 | 4.1144 | 0 | 0 | 171.7248 | 62.5533 | off_peak | 794.6667 | 100 | 0 | 7.3 | 0 | 92.7 | 257.3667 | 0
232 | 799.58 | 104.5 | 23.9 | 21.245 | 21.245 | 0 | 0 | 8.9635 | 8.9635 | 0 | 0 | 0 | 73.8147 | 787.2985 | 0 | 0.05921 | 3.7979 | 0 | 0 | 171.7248 | 21.245 | off_peak | 778.335 | 0 | 100 | 2.66 | 0 | 97.34 | 80.6873 | 0
233 | 821.27 | 75.2909 | 23.5 | 15.3287 | 14.7498 | 0 | 0.57892 | 0.57892 | 0 | 0 | 0 | 0 | 74.3563 | 806.5202 | 0 | 0.05921 | 3.5793 | 0 | 0 | 172.2663 | 14.7498 | off_peak | 806.5202 | 100 | 0 | 1.8 | 0 | 98.2 | 52.7947 | 0
234 | 794.64 | 11.4 | 23 | 2.3251 | 2.3251 | 0 | 0 | 0.03739 | 0.03739 | 0 | 0 | 0 | 74.3912 | 792.3523 | 0 | 0.05921 | 3.3467 | 0 | 0 | 172.2663 | 2.3251 | off_peak | 792.3149 | 0 | 100 | 0.29 | 0 | 99.71 | 7.7816 | 0
235 | 768.02 | 0 | 22.8 | 0 | 0 | 0 | 0 | 0 | 0 | 62.6277 | 62.6277 | 0 | 7.4394 | 705.3923 | 0 | 0.088511 | 3.3139 | 0 | 0 | 172.2663 | 0 | on_peak | 705.3923 |  |  | 0 | 8.15 | 91.85 | 0 | 0
236 | 782.16 | 0 | 22.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 782.16 | 0 | 0.088511 | 3.3528 | 0 | 0 | 172.2663 | 0 | on_peak | 782.16 |  |  | 0 | 0 | 100 | 0 | 0
237 | 773.31 | 0 | 22.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 773.31 | 0 | 0.088511 | 3.4464 | 0 | 0 | 172.2663 | 0 | on_peak | 773.31 |  |  | 0 | 0 | 100 | 0 | 0
238 | 725.41 | 0 | 22.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 725.41 | 0 | 0.088511 | 3.7718 | 0 | 0 | 172.2663 | 0 | on_peak | 725.41 |  |  | 0 | 0 | 100 | 0 | 0
239 | 726.85 | 0 | 22.3 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 19.0375 | 739.2489 | 0 | 0.05921 | 4.3543 | 0 | 0 | 172.2663 | 0 | off_peak | 726.85 | 0 | 100 | 0 | 0 | 100 | 0 | 0
240 | 736.16 | 0 | 22.2 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 30.6357 | 748.5589 | 0 | 0.05921 | 4.868 | 0 | 0 | 172.2663 | 0 | off_peak | 736.16 | 0 | 100 | 0 | 0 | 100 | 0 | 0
241 | 656.04 | 0 | 22.3 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 42.2338 | 668.4389 | 0 | 0.05921 | 5.1044 | 0 | 0 | 172.2663 | 0 | off_peak | 656.04 | 0 | 100 | 0 | 0 | 100 | 0 | 0
242 | 589.97 | 0 | 22.3 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 53.832 | 602.3689 | 0 | 0.05921 | 5.0042 | 0 | 0 | 172.2663 | 0 | off_peak | 589.97 | 0 | 100 | 0 | 0 | 100 | 0 | 0
243 | 586.37 | 0 | 22.3 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 65.4301 | 598.7689 | 0 | 0.05921 | 4.7263 | 0 | 0 | 172.2663 | 0 | off_peak | 586.37 | 0 | 100 | 0 | 0 | 100 | 0 | 0
244 | 573.97 | 0 | 22.3 | 0 | 0 | 0 | 0 | 8.9635 | 8.9635 | 0 | 0 | 0 | 73.8147 | 582.9335 | 0 | 0.05921 | 4.335 | 0 | 0 | 172.2663 | 0 | off_peak | 573.97 | 0 | 100 | 0 | 0 | 100 | 0 | 0
245 | 593.67 | 0 | 22.3 | 0 | 0 | 0 | 0 | 0.57892 | 0.57892 | 0 | 0 | 0 | 74.3563 | 594.2489 | 0 | 0.05921 | 3.878 | 0 | 0 | 172.2663 | 0 | off_peak | 593.67 | 0 | 100 | 0 | 0 | 100 | 0 | 0
246 | 688.61 | 0 | 22.4 | 0 | 0 | 0 | 0 | 0.03739 | 0.03739 | 0 | 0 | 0 | 74.3912 | 688.6474 | 0 | 0.05921 | 3.4184 | 0 | 0 | 172.2663 | 0 | off_peak | 688.61 | 0 | 100 | 0 | 0 | 100 | 0 | 0
247 | 767.66 | 0 | 22.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3912 | 767.66 | 0 | 0.088511 | 3.0758 | 0 | 0 | 172.2663 | 0 | on_peak | 767.66 |  |  | 0 | 0 | 100 | 0 | 0
248 | 778.82 | 16.15 | 23.2 | 3.2916 | 3.2916 | 0 | 0 | 0 | 0 | 62.6277 | 62.6277 | 0 | 7.4394 | 712.9007 | 0 | 0.088511 | 2.8636 | 0 | 0 | 172.2663 | 3.2916 | on_peak | 712.9007 |  |  | 0.42 | 8.04 | 91.54 | 9.4258 | 0
249 | 804.75 | 205.12 | 23.9 | 41.7013 | 41.7013 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 763.0487 | 0 | 0.088511 | 2.7779 | 0 | 0 | 172.2663 | 41.7013 | on_peak | 763.0487 |  |  | 5.18 | 0 | 94.82 | 115.8409 | 0
250 | 850.28 | 295.185 | 24.4 | 59.9041 | 59.9041 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 790.3759 | 0 | 0.088511 | 2.753 | 0 | 0 | 172.2663 | 59.9041 | on_peak | 790.3759 |  |  | 7.05 | 0 | 92.95 | 164.9129 | 0
251 | 832.02 | 544.191 | 24.7 | 110.3177 | 110.3177 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 19.0375 | 734.1012 | 0 | 0.05921 | 2.8938 | 0 | 0 | 172.2663 | 110.3177 | off_peak | 721.7023 | 0 | 100 | 13.26 | 0 | 86.74 | 319.24 | 0
252 | 861.5 | 250.13 | 24.8 | 50.6878 | 38.2889 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 0 | 30.6357 | 823.2111 | 0 | 0.05921 | 3.2984 | 0 | 0 | 183.8645 | 38.2889 | off_peak | 823.2111 | 100 | 0 | 4.44 | 0 | 95.56 | 126.2909 | 0
253 | 818.26 | 396.151 | 24.8 | 80.2783 | 67.8794 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 0 | 42.2338 | 750.3806 | 0 | 0.05921 | 4.0526 | 0 | 0 | 195.4626 | 67.8794 | off_peak | 750.3806 | 100 | 0 | 8.3 | 0 | 91.7 | 275.088 | 0
254 | 813.74 | 637.968 | 24.7 | 129.328 | 129.328 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 53.832 | 696.8109 | 0 | 0.05921 | 4.5429 | 0 | 0 | 195.4626 | 129.328 | off_peak | 684.412 | 0 | 100 | 15.89 | 0 | 84.11 | 587.518 | 0
255 | 877.08 | 540.6 | 24.4 | 109.708 | 109.708 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 65.4301 | 779.771 | 0 | 0.05921 | 4.3206 | 0 | 0 | 195.4626 | 109.708 | off_peak | 767.372 | 0 | 100 | 12.51 | 0 | 87.49 | 474.0038 | 0
256 | 857.84 | 205.349 | 24.3 | 41.688 | 32.7244 | 0 | 8.9635 | 8.9635 | 0 | 0 | 0 | 0 | 73.8147 | 825.1156 | 0 | 0.05921 | 3.7531 | 0 | 0 | 203.8472 | 32.7244 | off_peak | 825.1156 | 100 | 0 | 3.81 | 0 | 96.19 | 122.8178 | 0
257 | 803.01 | 137.432 | 24.1 | 27.9201 | 27.9201 | 0 | 0 | 0.57892 | 0.57892 | 0 | 0 | 0 | 74.3563 | 775.6688 | 0 | 0.05921 | 3.3861 | 0 | 0 | 203.8472 | 27.9201 | off_peak | 775.0899 | 0 | 100 | 3.48 | 0 | 96.52 | 94.5416 | 0
258 | 800.8 | 17.0512 | 24 | 3.4653 | 3.4279 | 0 | 0.03739 | 0.03739 | 0 | 0 | 0 | 0 | 74.3912 | 797.3721 | 0 | 0.05921 | 3.1141 | 0 | 0 | 203.8822 | 3.4279 | off_peak | 797.3721 | 100 | 0 | 0.43 | 0 | 99.57 | 10.6749 | 0
259 | 807.38 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 62.6277 | 62.6277 | 0 | 7.4394 | 744.7523 | 0 | 0.088511 | 3.0959 | 0 | 0 | 203.8822 | 0 | on_peak | 744.7523 |  |  | 0 | 7.76 | 92.24 | 0 | 0
260 | 805.92 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 805.92 | 0 | 0.088511 | 3.1666 | 0 | 0 | 203.8822 | 0 | on_peak | 805.92 |  |  | 0 | 0 | 100 | 0 | 0
261 | 796.23 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 796.23 | 0 | 0.088511 | 3.1437 | 0 | 0 | 203.8822 | 0 | on_peak | 796.23 |  |  | 0 | 0 | 100 | 0 | 0
262 | 743.38 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 743.38 | 0 | 0.088511 | 3.4301 | 0 | 0 | 203.8822 | 0 | on_peak | 743.38 |  |  | 0 | 0 | 100 | 0 | 0
263 | 840.76 | 0 | 23.9 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 19.0375 | 853.1589 | 0 | 0.05921 | 4.1446 | 0 | 0 | 203.8822 | 0 | off_peak | 840.76 | 0 | 100 | 0 | 0 | 100 | 0 | 0
264 | 738.4 | 0 | 23.8 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 30.6357 | 750.7989 | 0 | 0.05921 | 4.637 | 0 | 0 | 203.8822 | 0 | off_peak | 738.4 | 0 | 100 | 0 | 0 | 100 | 0 | 0
265 | 700.86 | 0 | 23.7 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 42.2338 | 713.2589 | 0 | 0.05921 | 4.9734 | 0 | 0 | 203.8822 | 0 | off_peak | 700.86 | 0 | 100 | 0 | 0 | 100 | 0 | 0
266 | 651.61 | 0 | 23.7 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 53.832 | 664.0089 | 0 | 0.05921 | 4.855 | 0 | 0 | 203.8822 | 0 | off_peak | 651.61 | 0 | 100 | 0 | 0 | 100 | 0 | 0
267 | 569.62 | 0 | 23.7 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 65.4301 | 582.0189 | 0 | 0.05921 | 4.6415 | 0 | 0 | 203.8822 | 0 | off_peak | 569.62 | 0 | 100 | 0 | 0 | 100 | 0 | 0
268 | 601.2 | 0 | 23.6 | 0 | 0 | 0 | 0 | 8.9635 | 8.9635 | 0 | 0 | 0 | 73.8147 | 610.1635 | 0 | 0.05921 | 4.2793 | 0 | 0 | 203.8822 | 0 | off_peak | 601.2 | 0 | 100 | 0 | 0 | 100 | 0 | 0
269 | 589.54 | 0 | 23.7 | 0 | 0 | 0 | 0 | 0.57892 | 0.57892 | 0 | 0 | 0 | 74.3563 | 590.1189 | 0 | 0.05921 | 3.8496 | 0 | 0 | 203.8822 | 0 | off_peak | 589.54 | 0 | 100 | 0 | 0 | 100 | 0 | 0
270 | 686.6 | 0 | 23.7 | 0 | 0 | 0 | 0 | 0.03739 | 0.03739 | 0 | 0 | 0 | 74.3912 | 686.6374 | 0 | 0.05921 | 3.4138 | 0 | 0 | 203.8822 | 0 | off_peak | 686.6 | 0 | 100 | 0 | 0 | 100 | 0 | 0
271 | 787.76 | 0 | 23.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3912 | 787.76 | 0 | 0.088511 | 2.9946 | 0 | 0 | 203.8822 | 0 | on_peak | 787.76 |  |  | 0 | 0 | 100 | 0 | 0
272 | 766.39 | 19.8274 | 24 | 4.0295 | 4.0295 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3912 | 762.3605 | 0 | 0.088511 | 2.7736 | 0 | 0 | 203.8822 | 4.0295 | on_peak | 762.3605 |  |  | 0.53 | 0 | 99.47 | 11.1764 | 0
273 | 815.53 | 211.175 | 24.3 | 42.8707 | 42.8707 | 0 | 0 | 0 | 0 | 44.1431 | 44.1431 | 0 | 27.2003 | 728.5162 | 0 | 0.088511 | 2.6886 | 0 | 0 | 203.8822 | 42.8707 | on_peak | 728.5162 |  |  | 5.26 | 5.41 | 89.33 | 115.2634 | 0
274 | 813.34 | 91.2 | 24.5 | 18.5012 | 18.5012 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27.2003 | 794.8388 | 0 | 0.088511 | 2.6729 | 0 | 0 | 203.8822 | 18.5012 | on_peak | 794.8388 |  |  | 2.27 | 0 | 97.73 | 49.4523 | 0
275 | 773.33 | 152.95 | 24.7 | 31.0058 | 18.6069 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 0 | 38.7984 | 754.7231 | 0 | 0.05921 | 2.7925 | 0 | 0 | 215.4804 | 18.6069 | off_peak | 754.7231 | 100 | 0 | 2.41 | 0 | 97.59 | 51.9592 | 0
276 | 894.05 | 501.159 | 24.7 | 101.5943 | 101.5943 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 50.3966 | 804.8546 | 0 | 0.05921 | 3.1544 | 0 | 0 | 215.4804 | 101.5943 | off_peak | 792.4557 | 0 | 100 | 11.36 | 0 | 88.64 | 320.4679 | 0
277 | 845.08 | 516.349 | 24.6 | 104.7112 | 92.3123 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 0 | 61.9947 | 752.7677 | 0 | 0.05921 | 3.8055 | 0 | 0 | 227.0785 | 92.3123 | off_peak | 752.7677 | 100 | 0 | 10.92 | 0 | 89.08 | 351.2932 | 0
278 | 845.29 | 405.303 | 24.5 | 82.2216 | 82.2216 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 73.5928 | 775.4674 | 0 | 0.05921 | 4.2694 | 0 | 0 | 227.0785 | 82.2216 | off_peak | 763.0684 | 0 | 100 | 9.73 | 0 | 90.27 | 351.0349 | 0
279 | 927.72 | 244.355 | 24.4 | 49.5888 | 49.5888 | 0 | 0 | 0.80079 | 0.80079 | 0 | 0 | 0 | 74.3419 | 878.932 | 0 | 0.05921 | 4.0443 | 0 | 0 | 227.0785 | 49.5888 | off_peak | 878.1312 | 0 | 100 | 5.35 | 0 | 94.65 | 200.5499 | 0
280 | 959.8 | 57 | 24.3 | 11.5716 | 11.5716 | 0 | 0 | 0 | 0 | 62.5816 | 62.5816 | 0 | 7.4394 | 885.6468 | 0 | 0.05921 | 3.5482 | 0 | 0 | 227.0785 | 11.5716 | off_peak | 885.6468 |  |  | 1.21 | 6.52 | 92.27 | 41.0583 | 0
281 | 897.02 | 212.794 | 24 | 43.2459 | 43.2459 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 19.0375 | 866.173 | 0 | 0.05921 | 3.3189 | 0 | 0 | 227.0785 | 43.2459 | off_peak | 853.7741 | 0 | 100 | 4.82 | 0 | 95.18 | 143.5307 | 0
282 | 841.26 | 33.4928 | 23.8 | 6.8116 | 6.8116 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 30.6357 | 846.8473 | 0 | 0.05921 | 3.2554 | 0 | 0 | 227.0785 | 6.8116 | off_peak | 834.4484 | 0 | 100 | 0.81 | 0 | 99.19 | 22.1748 | 0
283 | 796.09 | 0 | 23.8 | 0 | 0 | 0 | 0 | 0 | 0 | 21.6981 | 21.6981 | 0 | 7.4394 | 774.3919 | 0 | 0.088511 | 3.3158 | 0 | 0 | 227.0785 | 0 | on_peak | 774.3919 |  |  | 0 | 2.73 | 97.27 | 0 | 0
284 | 791.66 | 0 | 23.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 791.66 | 0 | 0.088511 | 3.468 | 0 | 0 | 227.0785 | 0 | on_peak | 791.66 |  |  | 0 | 0 | 100 | 0 | 0
285 | 798.05 | 0 | 23.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 798.05 | 0 | 0.088511 | 3.6069 | 0 | 0 | 227.0785 | 0 | on_peak | 798.05 |  |  | 0 | 0 | 100 | 0 | 0
286 | 762.21 | 0 | 23.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 762.21 | 0 | 0.088511 | 3.9853 | 0 | 0 | 227.0785 | 0 | on_peak | 762.21 |  |  | 0 | 0 | 100 | 0 | 0
287 | 775.92 | 0 | 23.6 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 19.0375 | 788.3189 | 0 | 0.05921 | 4.5606 | 0 | 0 | 227.0785 | 0 | off_peak | 775.92 | 0 | 100 | 0 | 0 | 100 | 0 | 0
288 | 755.66 | 0 | 23.5 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 30.6357 | 768.0589 | 0 | 0.05921 | 4.9878 | 0 | 0 | 227.0785 | 0 | off_peak | 755.66 | 0 | 100 | 0 | 0 | 100 | 0 | 0
289 | 715.4 | 0 | 23.5 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 42.2338 | 727.7989 | 0 | 0.05921 | 5.2524 | 0 | 0 | 227.0785 | 0 | off_peak | 715.4 | 0 | 100 | 0 | 0 | 100 | 0 | 0
290 | 623.93 | 0 | 23.4 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 53.832 | 636.3289 | 0 | 0.05921 | 5.0409 | 0 | 0 | 227.0785 | 0 | off_peak | 623.93 | 0 | 100 | 0 | 0 | 100 | 0 | 0
291 | 638.65 | 0 | 23.4 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 65.4301 | 651.0489 | 0 | 0.05921 | 4.679 | 0 | 0 | 227.0785 | 0 | off_peak | 638.65 | 0 | 100 | 0 | 0 | 100 | 0 | 0
292 | 606.03 | 0 | 23.3 | 0 | 0 | 0 | 0 | 8.9635 | 8.9635 | 0 | 0 | 0 | 73.8147 | 614.9935 | 0 | 0.05921 | 4.2856 | 0 | 0 | 227.0785 | 0 | off_peak | 606.03 | 0 | 100 | 0 | 0 | 100 | 0 | 0
293 | 619.17 | 0 | 23.1 | 0 | 0 | 0 | 0 | 0.57892 | 0.57892 | 0 | 0 | 0 | 74.3563 | 619.7489 | 0 | 0.05921 | 3.835 | 0 | 0 | 227.0785 | 0 | off_peak | 619.17 | 0 | 100 | 0 | 0 | 100 | 0 | 0
294 | 673.42 | 0 | 22.9 | 0 | 0 | 0 | 0 | 0.03739 | 0.03739 | 0 | 0 | 0 | 74.3912 | 673.4574 | 0 | 0.05921 | 3.3298 | 0 | 0 | 227.0785 | 0 | off_peak | 673.42 | 0 | 100 | 0 | 0 | 100 | 0 | 0
295 | 815.47 | 0 | 22.8 | 0 | 0 | 0 | 0 | 0.0024148 | 0.0024148 | 0 | 0 | 0 | 74.3935 | 815.4724 | 0 | 0.088511 | 2.9017 | 0 | 0 | 227.0785 | 0 | on_peak | 815.47 | 0 | 100 | 0 | 0 | 100 | 0 | 0
296 | 888.72 | 33.1652 | 23 | 6.7643 | 6.7643 | 0 | 0 | 0 | 0 | 62.6298 | 62.6298 | 0 | 7.4394 | 819.3258 | 0 | 0.088511 | 2.6281 | 0 | 0 | 227.0785 | 6.7643 | on_peak | 819.3258 |  |  | 0.76 | 7.05 | 92.19 | 17.7776 | 0
297 | 798.04 | 149.858 | 23.4 | 30.521 | 18.1221 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 0 | 19.0375 | 779.9179 | 0 | 0.088511 | 2.5063 | 0 | 0 | 238.6766 | 18.1221 | on_peak | 779.9179 | 100 | 0 | 2.27 | 0 | 97.73 | 45.4202 | 0
298 | 864.96 | 171.162 | 24 | 34.7851 | 34.7851 | 0 | 0 | 0 | 0 | 10.8491 | 10.8491 | 0 | 7.4394 | 819.3258 | 0 | 0.088511 | 2.4587 | 0 | 0 | 238.6766 | 34.7851 | on_peak | 819.3258 |  |  | 4.02 | 1.25 | 94.72 | 85.5266 | 0
299 | 840.1 | 548.844 | 24.5 | 111.341 | 111.341 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 19.0375 | 741.158 | 0 | 0.05921 | 2.5067 | 0 | 0 | 238.6766 | 111.341 | off_peak | 728.759 | 0 | 100 | 13.25 | 0 | 86.75 | 279.095 | 0
300 | 914.96 | 644.958 | 24.8 | 130.698 | 130.698 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 30.6357 | 796.6609 | 0 | 0.05921 | 2.7709 | 0 | 0 | 238.6766 | 130.698 | off_peak | 784.262 | 0 | 100 | 14.28 | 0 | 85.72 | 362.1488 | 0
301 | 812.68 | 506.626 | 25 | 102.5918 | 102.5918 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 42.2338 | 722.4872 | 0 | 0.05921 | 3.3281 | 0 | 0 | 238.6766 | 102.5918 | off_peak | 710.0882 | 0 | 100 | 12.62 | 0 | 87.38 | 341.439 | 0
302 | 831.34 | 648.771 | 25 | 131.3761 | 118.9772 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 0 | 53.832 | 712.3628 | 0 | 0.05921 | 3.7587 | 0 | 0 | 250.2748 | 118.9772 | off_peak | 712.3628 | 100 | 0 | 14.31 | 0 | 85.69 | 447.1996 | 0
303 | 869.04 | 552.695 | 24.9 | 111.961 | 111.961 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 65.4301 | 769.4779 | 0 | 0.05921 | 4.0113 | 0 | 0 | 250.2748 | 111.961 | off_peak | 757.079 | 0 | 100 | 12.88 | 0 | 87.12 | 449.1071 | 0
304 | 796.76 | 400.792 | 24.8 | 81.2188 | 81.2188 | 0 | 0 | 8.9635 | 8.9635 | 0 | 0 | 0 | 73.8147 | 724.5047 | 0 | 0.05921 | 4.1716 | 0 | 0 | 250.2748 | 81.2188 | off_peak | 715.5412 | 0 | 100 | 10.19 | 0 | 89.81 | 338.8121 | 0
305 | 813.25 | 111.445 | 24.5 | 22.6082 | 22.6082 | 0 | 0 | 0.57892 | 0.57892 | 0 | 0 | 0 | 74.3563 | 791.2207 | 0 | 0.05921 | 4.2586 | 0 | 0 | 250.2748 | 22.6082 | off_peak | 790.6418 | 0 | 100 | 2.78 | 0 | 97.22 | 96.2785 | 0
306 | 831.49 | 34.2194 | 24.2 | 6.9494 | 6.912 | 0 | 0.03739 | 0.03739 | 0 | 0 | 0 | 0 | 74.3912 | 824.578 | 0 | 0.05921 | 4.2851 | 0 | 0 | 250.3098 | 6.912 | off_peak | 824.578 | 100 | 0 | 0.83 | 0 | 99.17 | 29.6183 | 0
307 | 737.41 | 0 | 24.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3912 | 737.41 | 0 | 0.088511 | 4.1948 | 0 | 0 | 250.3098 | 0 | on_peak | 737.41 |  |  | 0 | 0 | 100 | 0 | 0
308 | 775.9 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 62.6277 | 62.6277 | 0 | 7.4394 | 713.2723 | 0 | 0.088511 | 4.0306 | 0 | 0 | 250.3098 | 0 | on_peak | 713.2723 |  |  | 0 | 8.07 | 91.93 | 0 | 0
309 | 717.86 | 0 | 23.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 717.86 | 0 | 0.088511 | 3.7773 | 0 | 0 | 250.3098 | 0 | on_peak | 717.86 |  |  | 0 | 0 | 100 | 0 | 0
310 | 716.65 | 0 | 23.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 716.65 | 0 | 0.088511 | 3.8896 | 0 | 0 | 250.3098 | 0 | on_peak | 716.65 |  |  | 0 | 0 | 100 | 0 | 0
311 | 747.66 | 0 | 23.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 747.66 | 0 | 0.05921 | 4.1519 | 0 | 0 | 250.3098 | 0 | off_peak | 747.66 |  |  | 0 | 0 | 100 | 0 | 0
312 | 750.31 | 0 | 22.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 750.31 | 0 | 0.05921 | 4.6388 | 0 | 0 | 250.3098 | 0 | off_peak | 750.31 |  |  | 0 | 0 | 100 | 0 | 0
313 | 710.89 | 0 | 22.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 710.89 | 0 | 0.05921 | 4.9531 | 0 | 0 | 250.3098 | 0 | off_peak | 710.89 |  |  | 0 | 0 | 100 | 0 | 0
314 | 631.28 | 0 | 22.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 631.28 | 0 | 0.05921 | 4.8503 | 0 | 0 | 250.3098 | 0 | off_peak | 631.28 |  |  | 0 | 0 | 100 | 0 | 0
315 | 549.97 | 0 | 22.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 549.97 | 0 | 0.05921 | 4.6462 | 0 | 0 | 250.3098 | 0 | off_peak | 549.97 |  |  | 0 | 0 | 100 | 0 | 0
316 | 626.56 | 0 | 22.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 626.56 | 0 | 0.05921 | 4.4229 | 0 | 0 | 250.3098 | 0 | off_peak | 626.56 |  |  | 0 | 0 | 100 | 0 | 0
317 | 566.72 | 0 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 566.72 | 0 | 0.05921 | 4.0798 | 0 | 0 | 250.3098 | 0 | off_peak | 566.72 |  |  | 0 | 0 | 100 | 0 | 0
318 | 679.61 | 0 | 21.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 679.61 | 0 | 0.05921 | 3.7042 | 0 | 0 | 250.3098 | 0 | off_peak | 679.61 |  |  | 0 | 0 | 100 | 0 | 0
319 | 719.11 | 0 | 21.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 719.11 | 0 | 0.05921 | 3.5591 | 0 | 0 | 250.3098 | 0 | off_peak | 719.11 |  |  | 0 | 0 | 100 | 0 | 0
320 | 786.81 | 12.35 | 22 | 2.5279 | 2.5279 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 784.2821 | 0 | 0.05921 | 3.4435 | 0 | 0 | 250.3098 | 2.5279 | off_peak | 784.2821 |  |  | 0.32 | 0 | 99.68 | 8.7047 | 0
321 | 782.98 | 212.315 | 22.5 | 43.3807 | 43.3807 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 739.5993 | 0 | 0.05921 | 3.4188 | 0 | 0 | 250.3098 | 43.3807 | off_peak | 739.5993 |  |  | 5.54 | 0 | 94.46 | 148.3102 | 0
322 | 777.37 | 287.233 | 23.2 | 58.5416 | 58.5416 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 718.8284 | 0 | 0.05921 | 3.4966 | 0 | 0 | 250.3098 | 58.5416 | off_peak | 718.8284 |  |  | 7.53 | 0 | 92.47 | 204.697 | 0
323 | 706.16 | 549.73 | 23.9 | 111.7612 | 111.7612 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 594.3988 | 0 | 0.05921 | 3.6497 | 0 | 0 | 250.3098 | 111.7612 | off_peak | 594.3988 |  |  | 15.83 | 0 | 84.17 | 407.8919 | 0
324 | 723.3 | 164.35 | 24.3 | 33.3647 | 33.3647 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 689.9353 | 0 | 0.05921 | 3.9832 | 0 | 0 | 250.3098 | 33.3647 | off_peak | 689.9353 |  |  | 4.61 | 0 | 95.39 | 132.8991 | 0
325 | 759.09 | 379.792 | 24.7 | 76.9909 | 76.9909 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 682.0991 | 0 | 0.05921 | 4.4031 | 0 | 0 | 250.3098 | 76.9909 | off_peak | 682.0991 |  |  | 10.14 | 0 | 89.86 | 338.995 | 0
326 | 668.88 | 419.247 | 24.9 | 84.9281 | 84.9281 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 583.9519 | 0 | 0.05921 | 4.9416 | 0 | 0 | 250.3098 | 84.9281 | off_peak | 583.9519 |  |  | 12.7 | 0 | 87.3 | 419.6844 | 0
327 | 669.76 | 111.15 | 24.9 | 22.516 | 22.516 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 647.244 | 0 | 0.05921 | 5.0578 | 0 | 0 | 250.3098 | 22.516 | off_peak | 647.244 |  |  | 3.36 | 0 | 96.64 | 113.8806 | 0
328 | 625.25 | 186.56 | 24.8 | 37.8056 | 37.8056 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 587.4444 | 0 | 0.05921 | 4.7576 | 0 | 0 | 250.3098 | 37.8056 | off_peak | 587.4444 |  |  | 6.05 | 0 | 93.95 | 179.8644 | 0
329 | 612.39 | 159.285 | 24.3 | 32.3365 | 32.3365 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 580.0535 | 0 | 0.05921 | 4.3356 | 0 | 0 | 250.3098 | 32.3365 | off_peak | 580.0535 |  |  | 5.28 | 0 | 94.72 | 140.1989 | 0
330 | 620.02 | 37.3402 | 23.7 | 7.5968 | 7.5968 | 0 | 0 | 11.6758 | 11.6758 | 0 | 0 | 0 | 18.3611 | 624.0991 | 0 | 0.05921 | 4.0427 | 0 | 0 | 250.3098 | 7.5968 | off_peak | 612.4232 | 0 | 100 | 1.23 | 0 | 98.77 | 30.7118 | 0
331 | 642.95 | 0 | 23.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18.3611 | 642.95 | 0 | 0.05921 | 3.7694 | 0 | 0 | 250.3098 | 0 | off_peak | 642.95 |  |  | 0 | 0 | 100 | 0 | 0
332 | 605.32 | 0 | 22.8 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 29.9593 | 617.7189 | 0 | 0.05921 | 3.5335 | 0 | 0 | 250.3098 | 0 | off_peak | 605.32 | 0 | 100 | 0 | 0 | 100 | 0 | 0
333 | 647.25 | 0 | 22.3 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 41.5574 | 659.6489 | 0 | 0.05921 | 3.3099 | 0 | 0 | 250.3098 | 0 | off_peak | 647.25 | 0 | 100 | 0 | 0 | 100 | 0 | 0
334 | 584.85 | 0 | 21.9 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 53.1556 | 597.2489 | 0 | 0.05921 | 3.3893 | 0 | 0 | 250.3098 | 0 | off_peak | 584.85 | 0 | 100 | 0 | 0 | 100 | 0 | 0
335 | 559.46 | 0 | 21.6 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 64.7537 | 571.8589 | 0 | 0.05921 | 4.0581 | 0 | 0 | 250.3098 | 0 | off_peak | 559.46 | 0 | 100 | 0 | 0 | 100 | 0 | 0
336 | 578.14 | 0 | 21.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 64.7537 | 578.14 | 0 | 0.05921 | 4.992 | 0 | 0 | 250.3098 | 0 | off_peak | 578.14 |  |  | 0 | 0 | 100 | 0 | 0
337 | 537.06 | 0 | 21.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 64.7537 | 537.06 | 0 | 0.05921 | 5.642 | 0 | 0 | 250.3098 | 0 | off_peak | 537.06 |  |  | 0 | 0 | 100 | 0 | 0
338 | 575.88 | 0 | 20.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 64.7537 | 575.88 | 0 | 0.05921 | 5.6421 | 0 | 0 | 250.3098 | 0 | off_peak | 575.88 |  |  | 0 | 0 | 100 | 0 | 0
339 | 603.95 | 0 | 20.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 64.7537 | 603.95 | 0 | 0.05921 | 5.5936 | 0 | 0 | 250.3098 | 0 | off_peak | 603.95 |  |  | 0 | 0 | 100 | 0 | 0
340 | 568.87 | 0 | 20.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 64.7537 | 568.87 | 0 | 0.05921 | 5.5335 | 0 | 0 | 250.3098 | 0 | off_peak | 568.87 |  |  | 0 | 0 | 100 | 0 | 0
341 | 600.89 | 0 | 20.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 64.7537 | 600.89 | 0 | 0.05921 | 5.3072 | 0 | 0 | 250.3098 | 0 | off_peak | 600.89 |  |  | 0 | 0 | 100 | 0 | 0
342 | 715.55 | 0 | 19.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 64.7537 | 715.55 | 0 | 0.05921 | 5.1251 | 0 | 0 | 250.3098 | 0 | off_peak | 715.55 |  |  | 0 | 0 | 100 | 0 | 0
343 | 678.03 | 0 | 19.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 64.7537 | 678.03 | 0 | 0.05921 | 5.0568 | 0 | 0 | 250.3098 | 0 | off_peak | 678.03 |  |  | 0 | 0 | 100 | 0 | 0
344 | 735.55 | 11.4 | 20.2 | 2.3484 | 0 | 0 | 2.3484 | 2.3484 | 0 | 0 | 0 | 0 | 66.9504 | 735.55 | 0 | 0.05921 | 5.0867 | 0 | 0 | 252.5065 | 0 | off_peak | 735.55 | 100 | 0 | 0 | 0 | 100 | 0 | 0
345 | 719.06 | 71.25 | 21 | 14.6359 | 14.6359 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 66.9504 | 704.4241 | 0 | 0.05921 | 5.1649 | 0 | 0 | 252.5065 | 14.6359 | off_peak | 704.4241 |  |  | 2.04 | 0 | 97.96 | 75.5929 | 0
346 | 712.99 | 114.95 | 22.1 | 23.5204 | 23.5204 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 66.9504 | 689.4696 | 0 | 0.05921 | 5.2763 | 0 | 0 | 252.5065 | 23.5204 | off_peak | 689.4696 |  |  | 3.3 | 0 | 96.7 | 124.1011 | 0
347 | 640.3 | 141.55 | 23 | 28.8703 | 28.8703 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 66.9504 | 611.4297 | 0 | 0.05921 | 5.4521 | 0 | 0 | 252.5065 | 28.8703 | off_peak | 611.4297 |  |  | 4.51 | 0 | 95.49 | 157.4035 | 0
348 | 685.31 | 155.8 | 23.6 | 31.7085 | 31.7085 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 66.9504 | 653.6015 | 0 | 0.05921 | 5.6092 | 0 | 0 | 252.5065 | 31.7085 | off_peak | 653.6015 |  |  | 4.63 | 0 | 95.37 | 177.8589 | 0
349 | 640 | 490.213 | 24 | 99.6255 | 99.6255 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 66.9504 | 540.3745 | 0 | 0.05921 | 6.0858 | 0 | 0 | 252.5065 | 99.6255 | off_peak | 540.3745 |  |  | 15.57 | 0 | 84.43 | 606.3052 | 0
350 | 640.52 | 440.538 | 24.1 | 89.498 | 89.498 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 66.9504 | 551.022 | 0 | 0.05921 | 6.6211 | 0 | 0 | 252.5065 | 89.498 | off_peak | 551.022 |  |  | 13.97 | 0 | 86.03 | 592.5746 | 0
351 | 632.68 | 416.489 | 24.1 | 84.6123 | 84.6123 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 66.9504 | 548.0677 | 0 | 0.05921 | 6.5084 | 0 | 0 | 252.5065 | 84.6123 | off_peak | 548.0677 |  |  | 13.37 | 0 | 86.63 | 550.6922 | 0
352 | 585.91 | 202.289 | 24.1 | 41.0962 | 41.0962 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 66.9504 | 544.8138 | 0 | 0.05921 | 5.9185 | 0 | 0 | 252.5065 | 41.0962 | off_peak | 544.8138 |  |  | 7.01 | 0 | 92.99 | 243.2268 | 0
353 | 570.87 | 61.75 | 23.8 | 12.5584 | 12.5584 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 66.9504 | 558.3116 | 0 | 0.05921 | 5.0662 | 0 | 0 | 252.5065 | 12.5584 | off_peak | 558.3116 |  |  | 2.2 | 0 | 97.8 | 63.6238 | 0
354 | 550.73 | 36.5592 | 23.5 | 7.4432 | 0 | 0 | 7.4432 | 7.4432 | 0 | 0 | 0 | 0 | 73.9129 | 550.73 | 0 | 0.05921 | 4.3793 | 0 | 0 | 259.469 | 0 | off_peak | 550.73 | 100 | 0 | 0 | 0 | 100 | 0 | 0
355 | 498.49 | 0 | 23.3 | 0 | 0 | 0 | 0 | 0.48072 | 0.48072 | 0 | 0 | 0 | 74.3626 | 498.9707 | 0 | 0.05921 | 3.894 | 0 | 0 | 259.469 | 0 | off_peak | 498.49 | 0 | 100 | 0 | 0 | 100 | 0 | 0
356 | 540.44 | 0 | 23 | 0 | 0 | 0 | 0 | 0.031048 | 0.031048 | 0 | 0 | 0 | 74.3916 | 540.471 | 0 | 0.05921 | 3.5032 | 0 | 0 | 259.469 | 0 | off_peak | 540.44 | 0 | 100 | 0 | 0 | 100 | 0 | 0
357 | 518.54 | 0 | 22.7 | 0 | 0 | 0 | 0 | 0.0020053 | 0.0020053 | 0 | 0 | 0 | 74.3935 | 518.542 | 0 | 0.05921 | 3.2129 | 0 | 0 | 259.469 | 0 | off_peak | 518.54 | 0 | 100 | 0 | 0 | 100 | 0 | 0
358 | 534.09 | 0 | 22.3 | 0 | 0 | 0 | 0 | 0.00012951 | 0.00012951 | 0 | 0 | 0 | 74.3936 | 534.0901 | 0 | 0.05921 | 3.2445 | 0 | 0 | 259.469 | 0 | off_peak | 534.09 | 0 | 100 | 0 | 0 | 100 | 0 | 0
359 | 554.7 | 0 | 21.9 | 0 | 0 | 0 | 0 | 8.942e-06 | 8.942e-06 | 0 | 0 | 0 | 74.3936 | 554.7 | 0 | 0.05921 | 3.7981 | 0 | 0 | 259.469 | 0 | off_peak | 554.7 | 0 | 100 | 0 | 0 | 100 | 0 | 0
360 | 504.31 | 0 | 21.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 504.31 | 0 | 0.05921 | 4.7358 | 0 | 0 | 259.469 | 0 | off_peak | 504.31 |  |  | 0 | 0 | 100 | 0 | 0
361 | 554.9 | 0 | 21.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 554.9 | 0 | 0.05921 | 5.3865 | 0 | 0 | 259.469 | 0 | off_peak | 554.9 |  |  | 0 | 0 | 100 | 0 | 0
362 | 540.94 | 0 | 20.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 540.94 | 0 | 0.05921 | 5.4488 | 0 | 0 | 259.469 | 0 | off_peak | 540.94 |  |  | 0 | 0 | 100 | 0 | 0
363 | 524.67 | 0 | 20.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 524.67 | 0 | 0.05921 | 5.5146 | 0 | 0 | 259.469 | 0 | off_peak | 524.67 |  |  | 0 | 0 | 100 | 0 | 0
364 | 526.44 | 0 | 20.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 526.44 | 0 | 0.05921 | 5.4363 | 0 | 0 | 259.469 | 0 | off_peak | 526.44 |  |  | 0 | 0 | 100 | 0 | 0
365 | 548.05 | 0 | 19.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 548.05 | 0 | 0.05921 | 5.3168 | 0 | 0 | 259.469 | 0 | off_peak | 548.05 |  |  | 0 | 0 | 100 | 0 | 0
366 | 679.56 | 0 | 19.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 679.56 | 0 | 0.05921 | 5.1902 | 0 | 0 | 259.469 | 0 | off_peak | 679.56 |  |  | 0 | 0 | 100 | 0 | 0
367 | 703.4 | 0 | 19.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 703.4 | 0 | 0.088511 | 4.947 | 0 | 0 | 259.469 | 0 | on_peak | 703.4 |  |  | 0 | 0 | 100 | 0 | 0
368 | 770.06 | 34.1113 | 19.2 | 7.0518 | 7.0518 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 763.0082 | 0 | 0.088511 | 4.9498 | 0 | 0 | 259.469 | 7.0518 | on_peak | 763.0082 |  |  | 0.92 | 0 | 99.08 | 34.9046 | 0
369 | 799.54 | 213.225 | 19.4 | 44.0485 | 44.0485 | 0 | 0 | 0 | 0 | 62.63 | 62.63 | 0 | 7.4394 | 692.8615 | 0 | 0.088511 | 4.981 | 0 | 0 | 259.469 | 44.0485 | on_peak | 692.8615 |  |  | 5.51 | 7.83 | 86.66 | 219.4076 | 0
370 | 734.93 | 336.312 | 19.9 | 69.3536 | 69.3536 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 665.5764 | 0 | 0.088511 | 5.1095 | 0 | 0 | 259.469 | 69.3536 | on_peak | 665.5764 |  |  | 9.44 | 0 | 90.56 | 354.3619 | 0
371 | 689.69 | 431.638 | 20.6 | 88.7912 | 88.7912 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 19.0375 | 613.2977 | 0 | 0.05921 | 5.382 | 0 | 0 | 259.469 | 88.7912 | off_peak | 600.8988 | 0 | 100 | 12.87 | 0 | 87.13 | 477.8707 | 0
372 | 824.81 | 345.897 | 21.4 | 70.9519 | 70.9519 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 30.6357 | 766.257 | 0 | 0.05921 | 5.7823 | 0 | 0 | 259.469 | 70.9519 | off_peak | 753.8581 | 0 | 100 | 8.6 | 0 | 91.4 | 410.2654 | 0
373 | 679.39 | 117.8 | 21.8 | 24.1293 | 24.1293 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 42.2338 | 667.6596 | 0 | 0.05921 | 6.2745 | 0 | 0 | 259.469 | 24.1293 | off_peak | 655.2607 | 0 | 100 | 3.55 | 0 | 96.45 | 151.4003 | 0
374 | 666.4 | 652.732 | 21.9 | 133.6533 | 133.6533 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 53.832 | 545.1456 | 0 | 0.05921 | 6.903 | 0 | 0 | 259.469 | 133.6533 | off_peak | 532.7467 | 0 | 100 | 20.06 | 0 | 79.94 | 922.6111 | 0
375 | 603.24 | 392.065 | 21.8 | 80.3078 | 80.3078 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 65.4301 | 535.3312 | 0 | 0.05921 | 6.6918 | 0 | 0 | 259.469 | 80.3078 | off_peak | 522.9322 | 0 | 100 | 13.31 | 0 | 86.69 | 537.4047 | 0
376 | 641.49 | 79.8 | 21.5 | 16.3631 | 7.3996 | 0 | 8.9635 | 8.9635 | 0 | 0 | 0 | 0 | 73.8147 | 634.0904 | 0 | 0.05921 | 5.5791 | 0 | 0 | 267.8536 | 7.3996 | off_peak | 634.0904 | 100 | 0 | 1.15 | 0 | 98.85 | 41.2827 | 0
377 | 601.67 | 150.894 | 21.1 | 30.985 | 30.985 | 0 | 0 | 0.57892 | 0.57892 | 0 | 0 | 0 | 74.3563 | 571.2639 | 0 | 0.05921 | 4.7298 | 0 | 0 | 267.8536 | 30.985 | off_peak | 570.685 | 0 | 100 | 5.15 | 0 | 94.85 | 146.5527 | 0
378 | 578.56 | 39.8723 | 20.7 | 8.1991 | 8.1991 | 0 | 0 | 0.03739 | 0.03739 | 0 | 0 | 0 | 74.3912 | 570.3983 | 0 | 0.05921 | 3.9607 | 0 | 0 | 267.8536 | 8.1991 | off_peak | 570.3609 | 0 | 100 | 1.42 | 0 | 98.58 | 32.4741 | 0
379 | 569.14 | 0 | 20.5 | 0 | 0 | 0 | 0 | 0 | 0 | 62.6277 | 62.6277 | 0 | 7.4394 | 506.5123 | 0 | 0.088511 | 3.5115 | 62.6277 | 0 | 200.9017 | 62.6277 | on_peak | 506.5123 |  |  | 0 | 11 | 89 | 219.9154 | 0
380 | 612.94 | 0 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 612.94 | 0 | 0.088511 | 3.2211 | 0 | 0 | 200.9017 | 0 | on_peak | 612.94 |  |  | 0 | 0 | 100 | 0 | 0
381 | 629.33 | 0 | 19.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 629.33 | 0 | 0.088511 | 3.0634 | 0 | 0 | 200.9017 | 0 | on_peak | 629.33 |  |  | 0 | 0 | 100 | 0 | 0
382 | 607.73 | 0 | 19.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 607.73 | 0 | 0.088511 | 3.2101 | 0 | 0 | 200.9017 | 0 | on_peak | 607.73 |  |  | 0 | 0 | 100 | 0 | 0
383 | 558.52 | 0 | 19 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 19.0375 | 570.9189 | 0 | 0.05921 | 3.7904 | 0 | 0 | 200.9017 | 0 | off_peak | 558.52 | 0 | 100 | 0 | 0 | 100 | 0 | 0
384 | 570.69 | 0 | 18.6 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 30.6357 | 583.0889 | 0 | 0.05921 | 4.4994 | 0 | 0 | 200.9017 | 0 | off_peak | 570.69 | 0 | 100 | 0 | 0 | 100 | 0 | 0
385 | 539.4 | 0 | 18.3 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 42.2338 | 551.7989 | 0 | 0.05921 | 5.1739 | 0 | 0 | 200.9017 | 0 | off_peak | 539.4 | 0 | 100 | 0 | 0 | 100 | 0 | 0
386 | 563.08 | 0 | 18.2 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 53.832 | 575.4789 | 0 | 0.05921 | 5.1869 | 0 | 0 | 200.9017 | 0 | off_peak | 563.08 | 0 | 100 | 0 | 0 | 100 | 0 | 0
387 | 552.34 | 0 | 18.1 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 65.4301 | 564.7389 | 0 | 0.05921 | 5.054 | 0 | 0 | 200.9017 | 0 | off_peak | 552.34 | 0 | 100 | 0 | 0 | 100 | 0 | 0
388 | 549.09 | 0 | 18 | 0 | 0 | 0 | 0 | 8.9635 | 8.9635 | 0 | 0 | 0 | 73.8147 | 558.0535 | 0 | 0.05921 | 4.8046 | 0 | 0 | 200.9017 | 0 | off_peak | 549.09 | 0 | 100 | 0 | 0 | 100 | 0 | 0
389 | 584.62 | 0 | 17.9 | 0 | 0 | 0 | 0 | 0.57892 | 0.57892 | 0 | 0 | 0 | 74.3563 | 585.1989 | 0 | 0.05921 | 4.4033 | 0 | 0 | 200.9017 | 0 | off_peak | 584.62 | 0 | 100 | 0 | 0 | 100 | 0 | 0
390 | 652.9 | 0 | 17.9 | 0 | 0 | 0 | 0 | 0.03739 | 0.03739 | 0 | 0 | 0 | 74.3912 | 652.9374 | 0 | 0.05921 | 4.2053 | 0 | 0 | 200.9017 | 0 | off_peak | 652.9 | 0 | 100 | 0 | 0 | 100 | 0 | 0
391 | 715.63 | 0 | 18.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3912 | 715.63 | 0 | 0.088511 | 3.6733 | 0 | 0 | 200.9017 | 0 | on_peak | 715.63 |  |  | 0 | 0 | 100 | 0 | 0
392 | 785.95 | 35.6211 | 19 | 7.3691 | 7.3691 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3912 | 778.5809 | 0 | 0.088511 | 3.632 | 0 | 0 | 200.9017 | 7.3691 | on_peak | 778.5809 |  |  | 0.94 | 0 | 99.06 | 26.7647 | 0
393 | 829.83 | 218.826 | 20.2 | 45.078 | 45.078 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3912 | 784.752 | 0 | 0.088511 | 3.6178 | 0 | 0 | 200.9017 | 45.078 | on_peak | 784.752 |  |  | 5.43 | 0 | 94.57 | 163.0824 | 0
394 | 778.31 | 406.446 | 21.4 | 83.372 | 83.372 | 0 | 0 | 0 | 0 | 62.6277 | 62.6277 | 0 | 7.4394 | 632.3103 | 0 | 0.088511 | 3.742 | 0 | 0 | 200.9017 | 83.372 | on_peak | 632.3103 |  |  | 10.71 | 8.05 | 81.24 | 311.9755 | 0
395 | 737.55 | 560.613 | 22.3 | 114.6276 | 114.6276 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 19.0375 | 635.3214 | 0 | 0.05921 | 3.9636 | 0 | 0 | 200.9017 | 114.6276 | off_peak | 622.9224 | 0 | 100 | 15.54 | 0 | 84.46 | 454.3364 | 0
396 | 831.8 | 406.232 | 22.8 | 82.9135 | 82.9135 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 30.6357 | 761.2854 | 0 | 0.05921 | 4.5744 | 0 | 0 | 200.9017 | 82.9135 | off_peak | 748.8865 | 0 | 100 | 9.97 | 0 | 90.03 | 379.2798 | 0
397 | 832.97 | 694.498 | 23.1 | 141.5978 | 141.5978 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 42.2338 | 703.7711 | 0 | 0.05921 | 5.4082 | 0 | 0 | 200.9017 | 141.5978 | off_peak | 691.3722 | 0 | 100 | 17 | 0 | 83 | 765.7962 | 0
398 | 768.84 | 530.936 | 23.2 | 108.2112 | 95.8123 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 0 | 53.832 | 673.0277 | 0 | 0.05921 | 6.0951 | 0 | 0 | 212.4999 | 95.8123 | off_peak | 673.0277 | 100 | 0 | 12.46 | 0 | 87.54 | 583.9852 | 0
399 | 864.73 | 500.411 | 23.2 | 101.9899 | 101.9899 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 65.4301 | 775.1391 | 0 | 0.05921 | 5.4626 | 0 | 0 | 212.4999 | 101.9899 | off_peak | 762.7401 | 0 | 100 | 11.79 | 0 | 88.21 | 557.1327 | 0
400 | 825.61 | 243.695 | 23 | 49.7035 | 49.7035 | 0 | 0 | 8.9635 | 8.9635 | 0 | 0 | 0 | 73.8147 | 784.87 | 0 | 0.05921 | 4.3485 | 0 | 0 | 212.4999 | 49.7035 | off_peak | 775.9065 | 0 | 100 | 6.02 | 0 | 93.98 | 216.1375 | 0
401 | 755.05 | 168.839 | 22.4 | 34.5099 | 34.5099 | 0 | 0 | 0.57892 | 0.57892 | 0 | 0 | 0 | 74.3563 | 721.119 | 0 | 0.05921 | 3.5366 | 0 | 0 | 212.4999 | 34.5099 | off_peak | 720.5401 | 0 | 100 | 4.57 | 0 | 95.43 | 122.0493 | 0
402 | 782.73 | 43.9821 | 21.8 | 9.009 | 9.009 | 0 | 0 | 0.03739 | 0.03739 | 0 | 0 | 0 | 74.3912 | 773.7584 | 0 | 0.05921 | 3.0687 | 0 | 0 | 212.4999 | 9.009 | off_peak | 773.721 | 0 | 100 | 1.15 | 0 | 98.85 | 27.6461 | 0
403 | 751.17 | 0 | 21.6 | 0 | 0 | 0 | 0 | 0 | 0 | 62.6277 | 62.6277 | 0 | 7.4394 | 688.5423 | 0 | 0.088511 | 2.9363 | 62.6277 | 0 | 145.548 | 62.6277 | on_peak | 688.5423 |  |  | 0 | 8.34 | 91.66 | 183.8964 | 0
404 | 760.65 | 0 | 21.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 760.65 | 0 | 0.088511 | 2.8969 | 0 | 0 | 145.548 | 0 | on_peak | 760.65 |  |  | 0 | 0 | 100 | 0 | 0
405 | 744.26 | 0 | 21.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 744.26 | 0 | 0.088511 | 2.9636 | 0 | 0 | 145.548 | 0 | on_peak | 744.26 |  |  | 0 | 0 | 100 | 0 | 0
406 | 709.84 | 0 | 21.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 709.84 | 0 | 0.088511 | 3.1851 | 0 | 0 | 145.548 | 0 | on_peak | 709.84 |  |  | 0 | 0 | 100 | 0 | 0
407 | 780.96 | 0 | 21.5 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 19.0375 | 793.3589 | 0 | 0.05921 | 3.7943 | 0 | 0 | 145.548 | 0 | off_peak | 780.96 | 0 | 100 | 0 | 0 | 100 | 0 | 0
408 | 710.79 | 0 | 21.5 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 30.6357 | 723.1889 | 0 | 0.05921 | 4.3731 | 0 | 0 | 145.548 | 0 | off_peak | 710.79 | 0 | 100 | 0 | 0 | 100 | 0 | 0
409 | 693.35 | 0 | 21.6 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 42.2338 | 705.7489 | 0 | 0.05921 | 4.7753 | 0 | 0 | 145.548 | 0 | off_peak | 693.35 | 0 | 100 | 0 | 0 | 100 | 0 | 0
410 | 609.33 | 0 | 21.6 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 53.832 | 621.7289 | 0 | 0.05921 | 4.6619 | 0 | 0 | 145.548 | 0 | off_peak | 609.33 | 0 | 100 | 0 | 0 | 100 | 0 | 0
411 | 597.22 | 0 | 21.7 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 65.4301 | 609.6189 | 0 | 0.05921 | 4.4022 | 0 | 0 | 145.548 | 0 | off_peak | 597.22 | 0 | 100 | 0 | 0 | 100 | 0 | 0
412 | 564.93 | 0 | 21.7 | 0 | 0 | 0 | 0 | 8.9635 | 8.9635 | 0 | 0 | 0 | 73.8147 | 573.8935 | 0 | 0.05921 | 4.0747 | 0 | 0 | 145.548 | 0 | off_peak | 564.93 | 0 | 100 | 0 | 0 | 100 | 0 | 0
413 | 594.41 | 0 | 21.6 | 0 | 0 | 0 | 0 | 0.57892 | 0.57892 | 0 | 0 | 0 | 74.3563 | 594.9889 | 0 | 0.05921 | 3.7799 | 0 | 0 | 145.548 | 0 | off_peak | 594.41 | 0 | 100 | 0 | 0 | 100 | 0 | 0
414 | 682.07 | 0 | 21.4 | 0 | 0 | 0 | 0 | 0.03739 | 0.03739 | 0 | 0 | 0 | 74.3912 | 682.1074 | 0 | 0.05921 | 3.355 | 0 | 0 | 145.548 | 0 | off_peak | 682.07 | 0 | 100 | 0 | 0 | 100 | 0 | 0
415 | 806.66 | 0 | 21.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3912 | 806.66 | 0 | 0.088511 | 2.7662 | 0 | 0 | 145.548 | 0 | on_peak | 806.66 |  |  | 0 | 0 | 100 | 0 | 0
416 | 808.26 | 37.5822 | 21.6 | 7.7035 | 7.7035 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3912 | 800.5565 | 0 | 0.088511 | 2.576 | 0 | 0 | 145.548 | 7.7035 | on_peak | 800.5565 |  |  | 0.95 | 0 | 99.05 | 19.8443 | 0
417 | 822.59 | 224.836 | 22.2 | 45.9882 | 45.9882 | 0 | 0 | 0 | 0 | 62.6277 | 62.6277 | 0 | 7.4394 | 713.974 | 0 | 0.088511 | 2.4922 | 0 | 0 | 145.548 | 45.9882 | on_peak | 713.974 |  |  | 5.59 | 7.61 | 86.8 | 114.6103 | 0
418 | 804.33 | 413.99 | 22.8 | 84.4969 | 84.4969 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 719.8331 | 0 | 0.088511 | 2.4957 | 0 | 0 | 145.548 | 84.4969 | on_peak | 719.8331 |  |  | 10.51 | 0 | 89.49 | 210.88 | 0
419 | 773.18 | 568.43 | 23.3 | 115.8115 | 115.8115 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 19.0375 | 669.7674 | 0 | 0.05921 | 2.6496 | 0 | 0 | 145.548 | 115.8115 | off_peak | 657.3685 | 0 | 100 | 14.98 | 0 | 85.02 | 306.8494 | 0
420 | 769.75 | 486.59 | 23.6 | 99.0311 | 99.0311 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 30.6357 | 683.1179 | 0 | 0.05921 | 3.062 | 0 | 0 | 145.548 | 99.0311 | off_peak | 670.7189 | 0 | 100 | 12.87 | 0 | 87.13 | 303.2316 | 0
421 | 788.04 | 631.721 | 23.8 | 128.4761 | 128.4761 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 42.2338 | 671.9628 | 0 | 0.05921 | 3.85 | 0 | 0 | 145.548 | 128.4761 | off_peak | 659.5639 | 0 | 100 | 16.3 | 0 | 83.7 | 494.6392 | 0
422 | 845.46 | 518.669 | 24 | 105.4086 | 105.4086 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 53.832 | 752.4504 | 0 | 0.05921 | 4.2645 | 0 | 0 | 145.548 | 105.4086 | off_peak | 740.0514 | 0 | 100 | 12.47 | 0 | 87.53 | 449.5188 | 0
423 | 820.64 | 361.646 | 24.1 | 73.4706 | 73.4706 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 65.4301 | 759.5683 | 0 | 0.05921 | 4.0172 | 0 | 0 | 145.548 | 73.4706 | off_peak | 747.1694 | 0 | 100 | 8.95 | 0 | 91.05 | 295.1484 | 0
424 | 835.52 | 261.252 | 24 | 53.094 | 44.1304 | 0 | 8.9635 | 8.9635 | 0 | 0 | 0 | 0 | 73.8147 | 791.3896 | 0 | 0.05921 | 3.5124 | 0 | 0 | 153.9327 | 44.1304 | off_peak | 791.3896 | 100 | 0 | 5.28 | 0 | 94.72 | 155.0041 | 0
425 | 803.26 | 154.659 | 23.5 | 31.4876 | 31.4876 | 0 | 0 | 0.57892 | 0.57892 | 0 | 0 | 0 | 74.3563 | 772.3513 | 0 | 0.05921 | 3.2077 | 0 | 0 | 153.9327 | 31.4876 | off_peak | 771.7724 | 0 | 100 | 3.92 | 0 | 96.08 | 101.0041 | 0
426 | 837.8 | 31.1809 | 22.7 | 6.3664 | 6.3664 | 0 | 0 | 0.03739 | 0.03739 | 0 | 0 | 0 | 74.3912 | 831.471 | 0 | 0.05921 | 3.1034 | 0 | 0 | 153.9327 | 6.3664 | off_peak | 831.4336 | 0 | 100 | 0.76 | 0 | 99.24 | 19.7573 | 0
427 | 791.06 | 0 | 22.4 | 0 | 0 | 0 | 0 | 0 | 0 | 62.6277 | 62.6277 | 0 | 7.4394 | 728.4323 | 0 | 0.088511 | 3.1216 | 0 | 0 | 153.9327 | 0 | on_peak | 728.4323 |  |  | 0 | 7.92 | 92.08 | 0 | 0
428 | 773.77 | 0 | 21.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 773.77 | 0 | 0.088511 | 3.2448 | 0 | 0 | 153.9327 | 0 | on_peak | 773.77 |  |  | 0 | 0 | 100 | 0 | 0
429 | 763.19 | 0 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 763.19 | 0 | 0.088511 | 3.436 | 0 | 0 | 153.9327 | 0 | on_peak | 763.19 |  |  | 0 | 0 | 100 | 0 | 0
430 | 714.1 | 0 | 20.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 714.1 | 0 | 0.088511 | 3.7611 | 0 | 0 | 153.9327 | 0 | on_peak | 714.1 |  |  | 0 | 0 | 100 | 0 | 0
431 | 713.9 | 0 | 20 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 19.0375 | 726.2989 | 0 | 0.05921 | 4.1629 | 0 | 0 | 153.9327 | 0 | off_peak | 713.9 | 0 | 100 | 0 | 0 | 100 | 0 | 0
432 | 757.41 | 0 | 19.5 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 30.6357 | 769.8089 | 0 | 0.05921 | 4.6517 | 0 | 0 | 153.9327 | 0 | off_peak | 757.41 | 0 | 100 | 0 | 0 | 100 | 0 | 0
433 | 697.95 | 0 | 19.1 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 42.2338 | 710.3489 | 0 | 0.05921 | 5.0038 | 0 | 0 | 153.9327 | 0 | off_peak | 697.95 | 0 | 100 | 0 | 0 | 100 | 0 | 0
434 | 623.26 | 0 | 18.6 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 53.832 | 635.6589 | 0 | 0.05921 | 4.8857 | 0 | 0 | 153.9327 | 0 | off_peak | 623.26 | 0 | 100 | 0 | 0 | 100 | 0 | 0
435 | 571.64 | 0 | 18.2 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 65.4301 | 584.0389 | 0 | 0.05921 | 4.5895 | 0 | 0 | 153.9327 | 0 | off_peak | 571.64 | 0 | 100 | 0 | 0 | 100 | 0 | 0
436 | 559.23 | 0 | 17.7 | 0 | 0 | 0 | 0 | 8.9635 | 8.9635 | 0 | 0 | 0 | 73.8147 | 568.1935 | 0 | 0.05921 | 4.2 | 0 | 0 | 153.9327 | 0 | off_peak | 559.23 | 0 | 100 | 0 | 0 | 100 | 0 | 0
437 | 561.92 | 0 | 17.3 | 0 | 0 | 0 | 0 | 0.57892 | 0.57892 | 0 | 0 | 0 | 74.3563 | 562.4989 | 0 | 0.05921 | 3.7272 | 0 | 0 | 153.9327 | 0 | off_peak | 561.92 | 0 | 100 | 0 | 0 | 100 | 0 | 0
438 | 684.3 | 0 | 17.1 | 0 | 0 | 0 | 0 | 0.03739 | 0.03739 | 0 | 0 | 0 | 74.3912 | 684.3374 | 0 | 0.05921 | 3.2194 | 0 | 0 | 153.9327 | 0 | off_peak | 684.3 | 0 | 100 | 0 | 0 | 100 | 0 | 0
439 | 706.06 | 0 | 17.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3912 | 706.06 | 0 | 0.088511 | 2.7714 | 0 | 0 | 153.9327 | 0 | on_peak | 706.06 |  |  | 0 | 0 | 100 | 0 | 0
440 | 775.99 | 33.9932 | 17.6 | 7.067 | 7.067 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3912 | 768.923 | 0 | 0.088511 | 2.5123 | 0 | 0 | 153.9327 | 7.067 | on_peak | 768.923 |  |  | 0.91 | 0 | 99.09 | 17.7546 | 0
441 | 791.87 | 214.823 | 18.6 | 44.5039 | 44.5039 | 0 | 0 | 0 | 0 | 62.6277 | 62.6277 | 0 | 7.4394 | 684.7383 | 0 | 0.088511 | 2.3733 | 0 | 0 | 153.9327 | 44.5039 | on_peak | 684.7383 |  |  | 5.62 | 7.91 | 86.47 | 105.6232 | 0
442 | 795.86 | 402.273 | 19.5 | 83.0732 | 83.0732 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 712.7868 | 0 | 0.088511 | 2.3192 | 0 | 0 | 153.9327 | 83.0732 | on_peak | 712.7868 |  |  | 10.44 | 0 | 89.56 | 192.6632 | 0
443 | 773.91 | 555.011 | 20.4 | 114.2509 | 114.2509 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 19.0375 | 672.058 | 0 | 0.05921 | 2.3578 | 0 | 0 | 153.9327 | 114.2509 | off_peak | 659.6591 | 0 | 100 | 14.76 | 0 | 85.24 | 269.3815 | 0
444 | 875.88 | 653.653 | 21.2 | 134.1755 | 121.7765 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 0 | 30.6357 | 754.1035 | 0 | 0.05921 | 2.7124 | 0 | 0 | 165.5308 | 121.7765 | off_peak | 754.1035 | 100 | 0 | 13.9 | 0 | 86.1 | 330.3028 | 0
445 | 817.75 | 689.946 | 21.7 | 141.3739 | 141.3739 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 42.2338 | 688.7751 | 0 | 0.05921 | 3.3541 | 0 | 0 | 165.5308 | 141.3739 | off_peak | 676.3761 | 0 | 100 | 17.29 | 0 | 82.71 | 474.182 | 0
446 | 833.89 | 663.098 | 22.1 | 135.6792 | 135.6792 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 53.832 | 710.6097 | 0 | 0.05921 | 3.7257 | 0 | 0 | 165.5308 | 135.6792 | off_peak | 698.2108 | 0 | 100 | 16.27 | 0 | 83.73 | 505.4952 | 0
447 | 864.96 | 425.434 | 22.3 | 86.9878 | 74.5888 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 0 | 65.4301 | 790.3712 | 0 | 0.05921 | 3.6098 | 0 | 0 | 177.1289 | 74.5888 | off_peak | 790.3712 | 100 | 0 | 8.62 | 0 | 91.38 | 269.2486 | 0
448 | 818.4 | 418.077 | 22.2 | 85.514 | 85.514 | 0 | 0 | 8.9635 | 8.9635 | 0 | 0 | 0 | 73.8147 | 741.8496 | 0 | 0.05921 | 3.3897 | 0 | 0 | 177.1289 | 85.514 | off_peak | 732.886 | 0 | 100 | 10.45 | 0 | 89.55 | 289.8638 | 0
449 | 822.73 | 230.666 | 21.7 | 47.2648 | 46.6859 | 0 | 0.57892 | 0.57892 | 0 | 0 | 0 | 0 | 74.3563 | 776.0441 | 0 | 0.05921 | 3.2906 | 0 | 0 | 177.6705 | 46.6859 | off_peak | 776.0441 | 100 | 0 | 5.67 | 0 | 94.33 | 153.6231 | 0
450 | 812.72 | 46.5514 | 21.2 | 9.5556 | 9.5182 | 0 | 0.03739 | 0.03739 | 0 | 0 | 0 | 0 | 74.3912 | 803.2018 | 0 | 0.05921 | 3.3243 | 0 | 0 | 177.7055 | 9.5182 | off_peak | 803.2018 | 100 | 0 | 1.17 | 0 | 98.83 | 31.6414 | 0
451 | 799.45 | 0 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 36.9136 | 36.9136 | 0 | 34.929 | 762.5364 | 0 | 0.088511 | 3.5372 | 36.9136 | 0 | 138.2432 | 36.9136 | on_peak | 762.5364 |  |  | 0 | 4.62 | 95.38 | 130.5691 | 0
452 | 845.04 | 0 | 20.9 | 0 | 0 | 0 | 0 | 0 | 0 | 25.7142 | 25.7142 | 0 | 7.4394 | 819.3258 | 0 | 0.088511 | 3.8695 | 0 | 0 | 138.2432 | 0 | on_peak | 819.3258 |  |  | 0 | 3.04 | 96.96 | 0 | 0
453 | 813.7 | 0 | 20.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 813.7 | 0 | 0.088511 | 4.3749 | 0 | 0 | 138.2432 | 0 | on_peak | 813.7 |  |  | 0 | 0 | 100 | 0 | 0
454 | 753.93 | 0 | 20.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 753.93 | 0 | 0.088511 | 4.7001 | 0 | 0 | 138.2432 | 0 | on_peak | 753.93 |  |  | 0 | 0 | 100 | 0 | 0
455 | 832.1 | 0 | 20.8 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 19.0375 | 844.4989 | 0 | 0.05921 | 5.0309 | 0 | 0 | 138.2432 | 0 | off_peak | 832.1 | 0 | 100 | 0 | 0 | 100 | 0 | 0
456 | 747.77 | 0 | 20.7 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 30.6357 | 760.1689 | 0 | 0.05921 | 5.2812 | 0 | 0 | 138.2432 | 0 | off_peak | 747.77 | 0 | 100 | 0 | 0 | 100 | 0 | 0
457 | 712.83 | 0 | 20.7 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 42.2338 | 725.2289 | 0 | 0.05921 | 5.4514 | 0 | 0 | 138.2432 | 0 | off_peak | 712.83 | 0 | 100 | 0 | 0 | 100 | 0 | 0
458 | 646.22 | 0 | 20.7 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 53.832 | 658.6189 | 0 | 0.05921 | 5.3439 | 0 | 0 | 138.2432 | 0 | off_peak | 646.22 | 0 | 100 | 0 | 0 | 100 | 0 | 0
459 | 571.03 | 0 | 20.7 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 65.4301 | 583.4289 | 0 | 0.05921 | 5.0187 | 0 | 0 | 138.2432 | 0 | off_peak | 571.03 | 0 | 100 | 0 | 0 | 100 | 0 | 0
460 | 585.33 | 0 | 20.7 | 0 | 0 | 0 | 0 | 8.9635 | 8.9635 | 0 | 0 | 0 | 73.8147 | 594.2935 | 0 | 0.05921 | 4.6466 | 0 | 0 | 138.2432 | 0 | off_peak | 585.33 | 0 | 100 | 0 | 0 | 100 | 0 | 0
461 | 587.41 | 0 | 20.7 | 0 | 0 | 0 | 0 | 0.57892 | 0.57892 | 0 | 0 | 0 | 74.3563 | 587.9889 | 0 | 0.05921 | 4.1662 | 0 | 0 | 138.2432 | 0 | off_peak | 587.41 | 0 | 100 | 0 | 0 | 100 | 0 | 0
462 | 704.7 | 0 | 20.8 | 0 | 0 | 0 | 0 | 0.03739 | 0.03739 | 0 | 0 | 0 | 74.3912 | 704.7374 | 0 | 0.05921 | 3.6547 | 0 | 0 | 138.2432 | 0 | off_peak | 704.7 | 0 | 100 | 0 | 0 | 100 | 0 | 0
463 | 770.92 | 0 | 20.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3912 | 770.92 | 0 | 0.088511 | 3.0622 | 0 | 0 | 138.2432 | 0 | on_peak | 770.92 |  |  | 0 | 0 | 100 | 0 | 0
464 | 807.22 | 27.431 | 21.4 | 5.6268 | 5.6268 | 0 | 0 | 0 | 0 | 62.6277 | 62.6277 | 0 | 7.4394 | 738.9655 | 0 | 0.088511 | 2.6624 | 0 | 0 | 138.2432 | 5.6268 | on_peak | 738.9655 |  |  | 0.7 | 7.76 | 91.54 | 14.9805 | 0
465 | 776.44 | 172.436 | 22 | 35.2954 | 35.2954 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 741.1446 | 0 | 0.088511 | 2.5018 | 0 | 0 | 138.2432 | 35.2954 | on_peak | 741.1446 |  |  | 4.55 | 0 | 95.45 | 88.3032 | 0
466 | 822.45 | 410.637 | 22.4 | 83.9323 | 83.9323 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 738.5177 | 0 | 0.088511 | 2.42 | 0 | 0 | 138.2432 | 83.9323 | on_peak | 738.5177 |  |  | 10.21 | 0 | 89.79 | 203.113 | 0
467 | 793.54 | 563.153 | 22.7 | 114.9827 | 114.9827 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 19.0375 | 690.9562 | 0 | 0.05921 | 2.4599 | 0 | 0 | 138.2432 | 114.9827 | off_peak | 678.5573 | 0 | 100 | 14.49 | 0 | 85.51 | 282.8412 | 0
468 | 848.52 | 527.379 | 22.8 | 107.6401 | 95.2411 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 0 | 30.6357 | 753.2789 | 0 | 0.05921 | 2.734 | 0 | 0 | 149.8413 | 95.2411 | off_peak | 753.2789 | 100 | 0 | 11.22 | 0 | 88.78 | 260.3928 | 0
469 | 826.33 | 693.845 | 22.9 | 141.5658 | 141.5658 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 42.2338 | 697.1631 | 0 | 0.05921 | 3.3165 | 0 | 0 | 149.8413 | 141.5658 | off_peak | 684.7642 | 0 | 100 | 17.13 | 0 | 82.87 | 469.4989 | 0
470 | 891.83 | 661.463 | 22.8 | 135.0071 | 135.0071 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 53.832 | 769.2218 | 0 | 0.05921 | 3.7053 | 0 | 0 | 149.8413 | 135.0071 | off_peak | 756.8229 | 0 | 100 | 15.14 | 0 | 84.86 | 500.2397 | 0
471 | 869.43 | 378.861 | 22.8 | 77.327 | 64.928 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 0 | 65.4301 | 804.502 | 0 | 0.05921 | 3.7776 | 0 | 0 | 161.4395 | 64.928 | off_peak | 804.502 | 100 | 0 | 7.47 | 0 | 92.53 | 245.2742 | 0
472 | 863.55 | 161.417 | 22.7 | 32.9576 | 32.9576 | 0 | 0 | 8.9635 | 8.9635 | 0 | 0 | 0 | 73.8147 | 839.556 | 0 | 0.05921 | 3.7977 | 0 | 0 | 161.4395 | 32.9576 | off_peak | 830.5924 | 0 | 100 | 3.82 | 0 | 96.18 | 125.1639 | 0
473 | 852.99 | 185.124 | 22.3 | 37.852 | 37.852 | 0 | 0 | 0.57892 | 0.57892 | 0 | 0 | 0 | 74.3563 | 815.7169 | 0 | 0.05921 | 3.8821 | 0 | 0 | 161.4395 | 37.852 | off_peak | 815.138 | 0 | 100 | 4.44 | 0 | 95.56 | 146.9462 | 0
474 | 847.33 | 46.3127 | 22 | 9.4796 | 9.4422 | 0 | 0.03739 | 0.03739 | 0 | 0 | 0 | 0 | 74.3912 | 837.8878 | 0 | 0.05921 | 3.8969 | 0 | 0 | 161.4744 | 9.4422 | off_peak | 837.8878 | 100 | 0 | 1.11 | 0 | 98.89 | 36.7951 | 0
475 | 795.02 | 0 | 21.9 | 0 | 0 | 0 | 0 | 0 | 0 | 62.6277 | 62.6277 | 0 | 7.4394 | 732.3923 | 0 | 0.088511 | 4.1488 | 0 | 0 | 161.4744 | 0 | on_peak | 732.3923 |  |  | 0 | 7.88 | 92.12 | 0 | 0
476 | 766.07 | 0 | 21.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 766.07 | 0 | 0.088511 | 4.2491 | 0 | 0 | 161.4744 | 0 | on_peak | 766.07 |  |  | 0 | 0 | 100 | 0 | 0
477 | 772.07 | 0 | 21.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 772.07 | 0 | 0.088511 | 4.385 | 0 | 0 | 161.4744 | 0 | on_peak | 772.07 |  |  | 0 | 0 | 100 | 0 | 0
478 | 756.99 | 0 | 21.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 756.99 | 0 | 0.088511 | 4.639 | 0 | 0 | 161.4744 | 0 | on_peak | 756.99 |  |  | 0 | 0 | 100 | 0 | 0
479 | 768.71 | 0 | 21.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 768.71 | 0 | 0.05921 | 5.0226 | 0 | 0 | 161.4744 | 0 | off_peak | 768.71 |  |  | 0 | 0 | 100 | 0 | 0
480 | 752.87 | 0 | 21.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 752.87 | 0 | 0.05921 | 5.2759 | 0 | 0 | 161.4744 | 0 | off_peak | 752.87 |  |  | 0 | 0 | 100 | 0 | 0
481 | 673.18 | 0 | 21.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 673.18 | 0 | 0.05921 | 5.4388 | 0 | 0 | 161.4744 | 0 | off_peak | 673.18 |  |  | 0 | 0 | 100 | 0 | 0
482 | 645.34 | 0 | 21.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 645.34 | 0 | 0.05921 | 5.155 | 0 | 0 | 161.4744 | 0 | off_peak | 645.34 |  |  | 0 | 0 | 100 | 0 | 0
483 | 596.95 | 0 | 21.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 596.95 | 0 | 0.05921 | 4.8314 | 0 | 0 | 161.4744 | 0 | off_peak | 596.95 |  |  | 0 | 0 | 100 | 0 | 0
484 | 558.91 | 0 | 21.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 558.91 | 0 | 0.05921 | 4.461 | 0 | 0 | 161.4744 | 0 | off_peak | 558.91 |  |  | 0 | 0 | 100 | 0 | 0
485 | 601.37 | 0 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 601.37 | 0 | 0.05921 | 4.1179 | 0 | 0 | 161.4744 | 0 | off_peak | 601.37 |  |  | 0 | 0 | 100 | 0 | 0
486 | 706.9 | 0 | 21.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 706.9 | 0 | 0.05921 | 3.7248 | 0 | 0 | 161.4744 | 0 | off_peak | 706.9 |  |  | 0 | 0 | 100 | 0 | 0
487 | 722.34 | 0 | 21.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 722.34 | 0 | 0.05921 | 3.23 | 0 | 0 | 161.4744 | 0 | off_peak | 722.34 |  |  | 0 | 0 | 100 | 0 | 0
488 | 736.57 | 33.6792 | 21.9 | 6.8961 | 6.8961 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 729.6739 | 0 | 0.05921 | 2.9044 | 0 | 0 | 161.4744 | 6.8961 | off_peak | 729.6739 |  |  | 0.94 | 0 | 99.06 | 20.029 | 0
489 | 676.94 | 212.231 | 22.6 | 43.3481 | 43.3481 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 633.5919 | 0 | 0.05921 | 2.706 | 0 | 0 | 161.4744 | 43.3481 | off_peak | 633.5919 |  |  | 6.4 | 0 | 93.6 | 117.2997 | 0
490 | 714.87 | 399.536 | 23.4 | 81.3721 | 72.6457 | 0 | 8.7263 | 8.7263 | 0 | 0 | 0 | 0 | 15.6021 | 642.2243 | 0 | 0.05921 | 2.5847 | 0 | 0 | 169.6372 | 72.6457 | off_peak | 642.2243 | 100 | 0 | 10.16 | 0 | 89.84 | 187.7654 | 0
491 | 728.84 | 551.659 | 24.1 | 112.0729 | 112.0729 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15.6021 | 616.7671 | 0 | 0.05921 | 2.546 | 0 | 0 | 169.6372 | 112.0729 | off_peak | 616.7671 |  |  | 15.38 | 0 | 84.62 | 285.3359 | 0
492 | 764.43 | 489.283 | 24.6 | 99.2225 | 99.2225 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15.6021 | 665.2075 | 0 | 0.05921 | 2.6887 | 0 | 0 | 169.6372 | 99.2225 | off_peak | 665.2075 |  |  | 12.98 | 0 | 87.02 | 266.7749 | 0
493 | 748.63 | 522.396 | 24.9 | 105.8233 | 105.8233 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15.6021 | 642.8067 | 0 | 0.05921 | 2.9122 | 0 | 0 | 169.6372 | 105.8233 | off_peak | 642.8067 |  |  | 14.14 | 0 | 85.86 | 308.1753 | 0
494 | 683.93 | 405.907 | 25.1 | 82.1666 | 82.1666 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15.6021 | 601.7634 | 0 | 0.05921 | 3.2323 | 0 | 0 | 169.6372 | 82.1666 | off_peak | 601.7634 |  |  | 12.01 | 0 | 87.99 | 265.5874 | 0
495 | 688.7 | 566.017 | 25.1 | 114.5772 | 114.5772 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15.6021 | 574.1228 | 0 | 0.05921 | 3.6504 | 0 | 0 | 169.6372 | 114.5772 | off_peak | 574.1228 |  |  | 16.64 | 0 | 83.36 | 418.258 | 0
496 | 680.18 | 418.48 | 24.9 | 84.7727 | 84.7727 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15.6021 | 595.4073 | 0 | 0.05921 | 3.9908 | 0 | 0 | 169.6372 | 84.7727 | off_peak | 595.4073 |  |  | 12.46 | 0 | 87.54 | 338.3126 | 0
497 | 653.49 | 233.788 | 24.4 | 47.4443 | 47.4443 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15.6021 | 606.0457 | 0 | 0.05921 | 4.1916 | 0 | 0 | 169.6372 | 47.4443 | off_peak | 606.0457 |  |  | 7.26 | 0 | 92.74 | 198.8671 | 0
498 | 670.86 | 50.3805 | 23.7 | 10.2498 | 10.2498 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15.6021 | 660.6102 | 0 | 0.05921 | 4.2983 | 0 | 0 | 169.6372 | 10.2498 | off_peak | 660.6102 |  |  | 1.53 | 0 | 98.47 | 44.0563 | 0
499 | 654.67 | 0 | 23.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15.6021 | 654.67 | 0 | 0.05921 | 4.5463 | 0 | 0 | 169.6372 | 0 | off_peak | 654.67 |  |  | 0 | 0 | 100 | 0 | 0
500 | 638.11 | 0 | 23.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15.6021 | 638.11 | 0 | 0.05921 | 4.8164 | 0 | 0 | 169.6372 | 0 | off_peak | 638.11 |  |  | 0 | 0 | 100 | 0 | 0
501 | 647.83 | 0 | 23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15.6021 | 647.83 | 0 | 0.05921 | 5.0705 | 0 | 0 | 169.6372 | 0 | off_peak | 647.83 |  |  | 0 | 0 | 100 | 0 | 0
502 | 568.07 | 0 | 22.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15.6021 | 568.07 | 0 | 0.05921 | 5.2705 | 0 | 0 | 169.6372 | 0 | off_peak | 568.07 |  |  | 0 | 0 | 100 | 0 | 0
503 | 574.38 | 0 | 22.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15.6021 | 574.38 | 0 | 0.05921 | 5.3273 | 0 | 0 | 169.6372 | 0 | off_peak | 574.38 |  |  | 0 | 0 | 100 | 0 | 0
504 | 519.33 | 0 | 22.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15.6021 | 519.33 | 0 | 0.05921 | 5.2583 | 0 | 0 | 169.6372 | 0 | off_peak | 519.33 |  |  | 0 | 0 | 100 | 0 | 0
505 | 567.77 | 0 | 22.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15.6021 | 567.77 | 0 | 0.05921 | 5.3194 | 0 | 0 | 169.6372 | 0 | off_peak | 567.77 |  |  | 0 | 0 | 100 | 0 | 0
506 | 536.42 | 0 | 22.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15.6021 | 536.42 | 0 | 0.05921 | 5.1121 | 0 | 0 | 169.6372 | 0 | off_peak | 536.42 |  |  | 0 | 0 | 100 | 0 | 0
507 | 535.86 | 0 | 22.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15.6021 | 535.86 | 0 | 0.05921 | 4.791 | 0 | 0 | 169.6372 | 0 | off_peak | 535.86 |  |  | 0 | 0 | 100 | 0 | 0
508 | 555.97 | 0 | 22.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15.6021 | 555.97 | 0 | 0.05921 | 4.4048 | 0 | 0 | 169.6372 | 0 | off_peak | 555.97 |  |  | 0 | 0 | 100 | 0 | 0
509 | 563.82 | 0 | 22.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15.6021 | 563.82 | 0 | 0.05921 | 4.0545 | 0 | 0 | 169.6372 | 0 | off_peak | 563.82 |  |  | 0 | 0 | 100 | 0 | 0
510 | 624.34 | 0 | 22.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15.6021 | 624.34 | 0 | 0.05921 | 3.7269 | 0 | 0 | 169.6372 | 0 | off_peak | 624.34 |  |  | 0 | 0 | 100 | 0 | 0
511 | 715.2 | 0 | 22.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15.6021 | 715.2 | 0 | 0.05921 | 3.3351 | 0 | 0 | 169.6372 | 0 | off_peak | 715.2 |  |  | 0 | 0 | 100 | 0 | 0
512 | 673.51 | 33.285 | 23.1 | 6.7863 | 6.7863 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15.6021 | 666.7237 | 0 | 0.05921 | 2.9645 | 0 | 0 | 169.6372 | 6.7863 | off_peak | 666.7237 |  |  | 1.01 | 0 | 98.99 | 20.1178 | 0
513 | 668.22 | 208.824 | 23.9 | 42.4543 | 42.4543 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15.6021 | 625.7657 | 0 | 0.05921 | 2.7476 | 0 | 0 | 169.6372 | 42.4543 | off_peak | 625.7657 |  |  | 6.35 | 0 | 93.65 | 116.6484 | 0
514 | 672.57 | 392.988 | 24.3 | 79.7806 | 79.7806 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15.6021 | 592.7894 | 0 | 0.05921 | 2.6296 | 0 | 0 | 169.6372 | 79.7806 | off_peak | 592.7894 |  |  | 11.86 | 0 | 88.14 | 209.794 | 0
515 | 660.43 | 542.807 | 24.7 | 110.0371 | 110.0371 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15.6021 | 550.3929 | 0 | 0.05921 | 2.5947 | 0 | 0 | 169.6372 | 110.0371 | off_peak | 550.3929 |  |  | 16.66 | 0 | 83.34 | 285.5147 | 0
516 | 669.59 | 260.312 | 24.9 | 52.7322 | 52.7322 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15.6021 | 616.8578 | 0 | 0.05921 | 2.6517 | 0 | 0 | 169.6372 | 52.7322 | off_peak | 616.8578 |  |  | 7.88 | 0 | 92.12 | 139.829 | 0
517 | 623.91 | 420.037 | 25 | 85.0575 | 85.0575 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15.6021 | 538.8525 | 0 | 0.05921 | 2.8479 | 0 | 0 | 169.6372 | 85.0575 | off_peak | 538.8525 |  |  | 13.63 | 0 | 86.37 | 242.2325 | 0
518 | 658.82 | 338.548 | 24.9 | 68.5807 | 56.1817 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 0 | 27.2003 | 602.6383 | 0 | 0.05921 | 3.1358 | 0 | 0 | 181.2353 | 56.1817 | off_peak | 602.6383 | 100 | 0 | 8.53 | 0 | 91.47 | 176.1767 | 0
519 | 657.28 | 561.18 | 24.6 | 113.8026 | 113.8026 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27.2003 | 543.4774 | 0 | 0.05921 | 3.542 | 0 | 0 | 181.2353 | 113.8026 | off_peak | 543.4774 |  |  | 17.31 | 0 | 82.69 | 403.088 | 0
520 | 624.03 | 413.65 | 24.3 | 83.9752 | 71.5763 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 0 | 38.7984 | 552.4537 | 0 | 0.05921 | 3.9365 | 0 | 0 | 192.8335 | 71.5763 | off_peak | 552.4537 | 100 | 0 | 11.47 | 0 | 88.53 | 281.7574 | 0
521 | 601.96 | 228.506 | 23.8 | 46.4724 | 46.4724 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 38.7984 | 555.4876 | 0 | 0.05921 | 4.1587 | 0 | 0 | 192.8335 | 46.4724 | off_peak | 555.4876 |  |  | 7.72 | 0 | 92.28 | 193.2643 | 0
522 | 615.1 | 47.701 | 23.4 | 9.7151 | 9.7151 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 38.7984 | 605.3849 | 0 | 0.05921 | 4.425 | 0 | 0 | 192.8335 | 9.7151 | off_peak | 605.3849 |  |  | 1.58 | 0 | 98.42 | 42.9891 | 0
523 | 567.04 | 0 | 23.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 38.7984 | 567.04 | 0 | 0.05921 | 4.6585 | 0 | 0 | 192.8335 | 0 | off_peak | 567.04 |  |  | 0 | 0 | 100 | 0 | 0
524 | 612.7 | 0 | 23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 38.7984 | 612.7 | 0 | 0.05921 | 4.8911 | 0 | 0 | 192.8335 | 0 | off_peak | 612.7 |  |  | 0 | 0 | 100 | 0 | 0
525 | 571.54 | 0 | 22.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 38.7984 | 571.54 | 0 | 0.05921 | 5.0096 | 0 | 0 | 192.8335 | 0 | off_peak | 571.54 |  |  | 0 | 0 | 100 | 0 | 0
526 | 601.66 | 0 | 22.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 38.7984 | 601.66 | 0 | 0.05921 | 5.2319 | 0 | 0 | 192.8335 | 0 | off_peak | 601.66 |  |  | 0 | 0 | 100 | 0 | 0
527 | 545.01 | 0 | 22.7 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 50.3966 | 557.4089 | 0 | 0.05921 | 5.4259 | 0 | 0 | 192.8335 | 0 | off_peak | 545.01 | 0 | 100 | 0 | 0 | 100 | 0 | 0
528 | 538.46 | 0 | 22.6 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 61.9947 | 550.8589 | 0 | 0.05921 | 5.6984 | 0 | 0 | 192.8335 | 0 | off_peak | 538.46 | 0 | 100 | 0 | 0 | 100 | 0 | 0
529 | 494.26 | 0 | 22.5 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 73.5928 | 506.6589 | 0 | 0.05921 | 5.7551 | 0 | 0 | 192.8335 | 0 | off_peak | 494.26 | 0 | 100 | 0 | 0 | 100 | 0 | 0
530 | 479.95 | 0 | 22.4 | 0 | 0 | 0 | 0 | 0.80079 | 0.80079 | 0 | 0 | 0 | 74.3419 | 480.7508 | 0 | 0.05921 | 5.5712 | 0 | 0 | 192.8335 | 0 | off_peak | 479.95 | 0 | 100 | 0 | 0 | 100 | 0 | 0
531 | 535.86 | 0 | 22.3 | 0 | 0 | 0 | 0 | 0.05172 | 0.05172 | 0 | 0 | 0 | 74.3903 | 535.9117 | 0 | 0.05921 | 5.2204 | 0 | 0 | 192.8335 | 0 | off_peak | 535.86 | 0 | 100 | 0 | 0 | 100 | 0 | 0
532 | 504.7 | 0 | 22.2 | 0 | 0 | 0 | 0 | 0.0033404 | 0.0033404 | 0 | 0 | 0 | 74.3934 | 504.7033 | 0 | 0.05921 | 4.8216 | 0 | 0 | 192.8335 | 0 | off_peak | 504.7 | 0 | 100 | 0 | 0 | 100 | 0 | 0
533 | 527.08 | 0 | 22.1 | 0 | 0 | 0 | 0 | 0.00021574 | 0.00021574 | 0 | 0 | 0 | 74.3936 | 527.0802 | 0 | 0.05921 | 4.3589 | 0 | 0 | 192.8335 | 0 | off_peak | 527.08 | 0 | 100 | 0 | 0 | 100 | 0 | 0
534 | 661.96 | 0 | 22.1 | 0 | 0 | 0 | 0 | 1.3934e-05 | 1.3934e-05 | 0 | 0 | 0 | 74.3936 | 661.96 | 0 | 0.05921 | 3.7793 | 0 | 0 | 192.8335 | 0 | off_peak | 661.96 | 0 | 100 | 0 | 0 | 100 | 0 | 0
535 | 733.26 | 0 | 22.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 733.26 | 0 | 0.088511 | 3.2505 | 0 | 0 | 192.8335 | 0 | on_peak | 733.26 |  |  | 0 | 0 | 100 | 0 | 0
536 | 803.54 | 20.8166 | 22.9 | 4.2472 | 4.2472 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 799.2928 | 0 | 0.088511 | 2.9349 | 0 | 0 | 192.8335 | 4.2472 | on_peak | 799.2928 |  |  | 0.53 | 0 | 99.47 | 12.465 | 0
537 | 842.15 | 201.259 | 23.6 | 40.9604 | 40.9604 | 0 | 0 | 0 | 0 | 62.63 | 62.63 | 0 | 7.4394 | 738.5597 | 0 | 0.088511 | 2.783 | 0 | 0 | 192.8335 | 40.9604 | on_peak | 738.5597 |  |  | 4.86 | 7.44 | 87.7 | 113.9909 | 0
538 | 834.53 | 83.6 | 24 | 16.9899 | 16.9899 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 817.5401 | 0 | 0.088511 | 2.7074 | 0 | 0 | 192.8335 | 16.9899 | on_peak | 817.5401 |  |  | 2.04 | 0 | 97.96 | 45.9978 | 0
539 | 836.39 | 234.027 | 24.3 | 47.5099 | 35.111 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 0 | 19.0375 | 801.279 | 0 | 0.05921 | 2.7601 | 0 | 0 | 204.4316 | 35.111 | off_peak | 801.279 | 100 | 0 | 4.2 | 0 | 95.8 | 96.911 | 0
540 | 808.24 | 330.779 | 24.5 | 67.1033 | 54.7044 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 0 | 30.6357 | 753.5356 | 0 | 0.05921 | 3.1499 | 0 | 0 | 216.0298 | 54.7044 | off_peak | 753.5356 | 100 | 0 | 6.77 | 0 | 93.23 | 172.3137 | 0
541 | 804.67 | 682.141 | 24.4 | 138.4319 | 138.4319 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 42.2338 | 678.637 | 0 | 0.05921 | 3.6802 | 0 | 0 | 216.0298 | 138.4319 | off_peak | 666.2381 | 0 | 100 | 17.2 | 0 | 82.8 | 509.4537 | 0
542 | 828.01 | 453.602 | 24.2 | 92.1189 | 92.1189 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 53.832 | 748.29 | 0 | 0.05921 | 4.0442 | 0 | 0 | 216.0298 | 92.1189 | off_peak | 735.8911 | 0 | 100 | 11.13 | 0 | 88.87 | 372.5451 | 0
543 | 842.81 | 561.265 | 24.1 | 114.0244 | 101.6255 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 0 | 65.4301 | 741.1845 | 0 | 0.05921 | 4.2792 | 0 | 0 | 227.6279 | 101.6255 | off_peak | 741.1845 | 100 | 0 | 12.06 | 0 | 87.94 | 434.8778 | 0
544 | 833.87 | 287.611 | 24.1 | 58.4299 | 49.4664 | 0 | 8.9635 | 8.9635 | 0 | 0 | 0 | 0 | 73.8147 | 784.4036 | 0 | 0.05921 | 4.3251 | 0 | 0 | 236.0126 | 49.4664 | off_peak | 784.4036 | 100 | 0 | 5.93 | 0 | 94.07 | 213.9459 | 0
545 | 806.79 | 149.238 | 23.8 | 30.3512 | 30.3512 | 0 | 0 | 0.57892 | 0.57892 | 0 | 0 | 0 | 74.3563 | 777.0177 | 0 | 0.05921 | 4.3614 | 0 | 0 | 236.0126 | 30.3512 | off_peak | 776.4388 | 0 | 100 | 3.76 | 0 | 96.24 | 132.373 | 0
546 | 814.35 | 50.1184 | 23.5 | 10.2038 | 10.1664 | 0 | 0.03739 | 0.03739 | 0 | 0 | 0 | 0 | 74.3912 | 804.1836 | 0 | 0.05921 | 4.4974 | 0 | 0 | 236.0475 | 10.1664 | off_peak | 804.1836 | 100 | 0 | 1.25 | 0 | 98.75 | 45.7225 | 0
547 | 802.74 | 0 | 23.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3912 | 802.74 | 0 | 0.088511 | 4.4271 | 0 | 0 | 236.0475 | 0 | on_peak | 802.74 |  |  | 0 | 0 | 100 | 0 | 0
548 | 787.24 | 0 | 23.3 | 0 | 0 | 0 | 0 | 0 | 0 | 62.6277 | 62.6277 | 0 | 7.4394 | 724.6123 | 0 | 0.088511 | 4.3725 | 0 | 0 | 236.0475 | 0 | on_peak | 724.6123 |  |  | 0 | 7.96 | 92.04 | 0 | 0
549 | 793.41 | 0 | 23.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 793.41 | 0 | 0.088511 | 4.3908 | 0 | 0 | 236.0475 | 0 | on_peak | 793.41 |  |  | 0 | 0 | 100 | 0 | 0
550 | 721.55 | 0 | 23.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 721.55 | 0 | 0.088511 | 4.5128 | 0 | 0 | 236.0475 | 0 | on_peak | 721.55 |  |  | 0 | 0 | 100 | 0 | 0
551 | 774.75 | 0 | 23.3 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 19.0375 | 787.1489 | 0 | 0.05921 | 4.8025 | 0 | 0 | 236.0475 | 0 | off_peak | 774.75 | 0 | 100 | 0 | 0 | 100 | 0 | 0
552 | 752.31 | 0 | 23.4 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 30.6357 | 764.7089 | 0 | 0.05921 | 5.1003 | 0 | 0 | 236.0475 | 0 | off_peak | 752.31 | 0 | 100 | 0 | 0 | 100 | 0 | 0
553 | 661.1 | 0 | 23.4 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 42.2338 | 673.4989 | 0 | 0.05921 | 5.4834 | 0 | 0 | 236.0475 | 0 | off_peak | 661.1 | 0 | 100 | 0 | 0 | 100 | 0 | 0
554 | 631.79 | 0 | 23.5 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 53.832 | 644.1889 | 0 | 0.05921 | 5.453 | 0 | 0 | 236.0475 | 0 | off_peak | 631.79 | 0 | 100 | 0 | 0 | 100 | 0 | 0
555 | 550.74 | 0 | 23.5 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 65.4301 | 563.1389 | 0 | 0.05921 | 5.1419 | 0 | 0 | 236.0475 | 0 | off_peak | 550.74 | 0 | 100 | 0 | 0 | 100 | 0 | 0
556 | 567.51 | 0 | 23.5 | 0 | 0 | 0 | 0 | 8.9635 | 8.9635 | 0 | 0 | 0 | 73.8147 | 576.4735 | 0 | 0.05921 | 4.671 | 0 | 0 | 236.0475 | 0 | off_peak | 567.51 | 0 | 100 | 0 | 0 | 100 | 0 | 0
557 | 587.18 | 0 | 23.5 | 0 | 0 | 0 | 0 | 0.57892 | 0.57892 | 0 | 0 | 0 | 74.3563 | 587.7589 | 0 | 0.05921 | 4.2276 | 0 | 0 | 236.0475 | 0 | off_peak | 587.18 | 0 | 100 | 0 | 0 | 100 | 0 | 0
558 | 666.89 | 0 | 23.6 | 0 | 0 | 0 | 0 | 0.03739 | 0.03739 | 0 | 0 | 0 | 74.3912 | 666.9274 | 0 | 0.05921 | 3.6415 | 0 | 0 | 236.0475 | 0 | off_peak | 666.89 | 0 | 100 | 0 | 0 | 100 | 0 | 0
559 | 759.83 | 0 | 23.7 | 0 | 0 | 0 | 0 | 0 | 0 | 62.6277 | 62.6277 | 0 | 7.4394 | 697.2023 | 0 | 0.088511 | 3.3091 | 0 | 0 | 236.0475 | 0 | on_peak | 697.2023 |  |  | 0 | 8.24 | 91.76 | 0 | 0
560 | 758.76 | 40.917 | 23.9 | 8.3185 | 8.3185 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 750.4415 | 0 | 0.088511 | 3.116 | 0 | 0 | 236.0475 | 8.3185 | on_peak | 750.4415 |  |  | 1.1 | 0 | 98.9 | 25.92 | 0
561 | 759.64 | 234.158 | 24.2 | 47.5536 | 47.5536 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 712.0864 | 0 | 0.088511 | 3.0168 | 0 | 0 | 236.0475 | 47.5536 | on_peak | 712.0864 |  |  | 6.26 | 0 | 93.74 | 143.4604 | 0
562 | 784.14 | 432.679 | 24.6 | 87.7437 | 87.7437 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 696.3963 | 0 | 0.088511 | 2.98 | 0 | 0 | 236.0475 | 87.7437 | on_peak | 696.3963 |  |  | 11.19 | 0 | 88.81 | 261.479 | 0
563 | 781.87 | 589.579 | 24.7 | 119.5187 | 119.5187 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 19.0375 | 674.7503 | 0 | 0.05921 | 3.0663 | 0 | 0 | 236.0475 | 119.5187 | off_peak | 662.3513 | 0 | 100 | 15.29 | 0 | 84.71 | 366.4841 | 0
564 | 820.46 | 690.989 | 24.3 | 140.2779 | 140.2779 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 30.6357 | 692.5811 | 0 | 0.05921 | 3.4232 | 0 | 0 | 236.0475 | 140.2779 | off_peak | 680.1821 | 0 | 100 | 17.1 | 0 | 82.9 | 480.1964 | 0
565 | 790.73 | 722.667 | 23.5 | 147.1303 | 147.1303 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 42.2338 | 655.9986 | 0 | 0.05921 | 4.1594 | 0 | 0 | 236.0475 | 147.1303 | off_peak | 643.5997 | 0 | 100 | 18.61 | 0 | 81.39 | 611.9666 | 0
566 | 803.54 | 689.176 | 22.6 | 140.7639 | 140.7639 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 53.832 | 675.175 | 0 | 0.05921 | 4.4733 | 0 | 0 | 236.0475 | 140.7639 | off_peak | 662.7761 | 0 | 100 | 17.52 | 0 | 82.48 | 629.6752 | 0
567 | 867.64 | 588.798 | 21.9 | 120.5622 | 120.5622 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 65.4301 | 759.4767 | 0 | 0.05921 | 4.3459 | 0 | 0 | 236.0475 | 120.5622 | off_peak | 747.0778 | 0 | 100 | 13.9 | 0 | 86.1 | 523.947 | 0
568 | 839.61 | 431.904 | 21.5 | 88.5626 | 79.599 | 0 | 8.9635 | 8.9635 | 0 | 0 | 0 | 0 | 73.8147 | 760.011 | 0 | 0.05921 | 3.9733 | 0 | 0 | 244.4322 | 79.599 | off_peak | 760.011 | 100 | 0 | 9.48 | 0 | 90.52 | 316.2738 | 0
569 | 829.13 | 239.803 | 21.2 | 49.2244 | 48.6455 | 0 | 0.57892 | 0.57892 | 0 | 0 | 0 | 0 | 74.3563 | 780.4845 | 0 | 0.05921 | 3.6681 | 0 | 0 | 244.9737 | 48.6455 | off_peak | 780.4845 | 100 | 0 | 5.87 | 0 | 94.13 | 178.4364 | 0
570 | 832.12 | 52.2428 | 20.8 | 10.7391 | 10.7391 | 0 | 0 | 0.03739 | 0.03739 | 0 | 0 | 0 | 74.3912 | 821.4183 | 0 | 0.05921 | 3.5247 | 0 | 0 | 244.9737 | 10.7391 | off_peak | 821.3809 | 0 | 100 | 1.29 | 0 | 98.71 | 37.8526 | 0
571 | 774.5 | 0 | 20.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3912 | 774.5 | 0 | 0.088511 | 3.6078 | 0 | 0 | 244.9737 | 0 | on_peak | 774.5 |  |  | 0 | 0 | 100 | 0 | 0
572 | 782.72 | 0 | 19.7 | 0 | 0 | 0 | 0 | 0 | 0 | 62.6277 | 62.6277 | 0 | 7.4394 | 720.0923 | 0 | 0.088511 | 3.7253 | 0 | 0 | 244.9737 | 0 | on_peak | 720.0923 |  |  | 0 | 8 | 92 | 0 | 0
573 | 779.41 | 0 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 779.41 | 0 | 0.088511 | 3.9635 | 0 | 0 | 244.9737 | 0 | on_peak | 779.41 |  |  | 0 | 0 | 100 | 0 | 0
574 | 726.06 | 0 | 18.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 726.06 | 0 | 0.088511 | 4.2182 | 0 | 0 | 244.9737 | 0 | on_peak | 726.06 |  |  | 0 | 0 | 100 | 0 | 0
575 | 770.23 | 0 | 17.3 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 19.0375 | 782.6289 | 0 | 0.05921 | 4.6331 | 0 | 0 | 244.9737 | 0 | off_peak | 770.23 | 0 | 100 | 0 | 0 | 100 | 0 | 0
576 | 759.4 | 0 | 16.5 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 30.6357 | 771.7989 | 0 | 0.05921 | 5.0767 | 0 | 0 | 244.9737 | 0 | off_peak | 759.4 | 0 | 100 | 0 | 0 | 100 | 0 | 0
577 | 712.7 | 0 | 15.9 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 42.2338 | 725.0989 | 0 | 0.05921 | 5.3998 | 0 | 0 | 244.9737 | 0 | off_peak | 712.7 | 0 | 100 | 0 | 0 | 100 | 0 | 0
578 | 661.23 | 0 | 15.3 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 53.832 | 673.6289 | 0 | 0.05921 | 5.3907 | 0 | 0 | 244.9737 | 0 | off_peak | 661.23 | 0 | 100 | 0 | 0 | 100 | 0 | 0
579 | 565.69 | 0 | 14.9 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 65.4301 | 578.0889 | 0 | 0.05921 | 5.1099 | 0 | 0 | 244.9737 | 0 | off_peak | 565.69 | 0 | 100 | 0 | 0 | 100 | 0 | 0
580 | 593.78 | 0 | 14.4 | 0 | 0 | 0 | 0 | 8.9635 | 8.9635 | 0 | 0 | 0 | 73.8147 | 602.7435 | 0 | 0.05921 | 4.7086 | 0 | 0 | 244.9737 | 0 | off_peak | 593.78 | 0 | 100 | 0 | 0 | 100 | 0 | 0
581 | 581.74 | 0 | 14 | 0 | 0 | 0 | 0 | 0.57892 | 0.57892 | 0 | 0 | 0 | 74.3563 | 582.3189 | 0 | 0.05921 | 4.2593 | 0 | 0 | 244.9737 | 0 | off_peak | 581.74 | 0 | 100 | 0 | 0 | 100 | 0 | 0
582 | 710.05 | 0 | 13.6 | 0 | 0 | 0 | 0 | 0.03739 | 0.03739 | 0 | 0 | 0 | 74.3912 | 710.0874 | 0 | 0.05921 | 3.7441 | 0 | 0 | 244.9737 | 0 | off_peak | 710.05 | 0 | 100 | 0 | 0 | 100 | 0 | 0
583 | 794.34 | 0 | 13.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3912 | 794.34 | 0 | 0.088511 | 3.3127 | 0 | 0 | 244.9737 | 0 | on_peak | 794.34 |  |  | 0 | 0 | 100 | 0 | 0
584 | 788.53 | 43.7419 | 13.7 | 9.2181 | 9.2181 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3912 | 779.3119 | 0 | 0.088511 | 3.0132 | 0 | 0 | 244.9737 | 9.2181 | on_peak | 779.3119 |  |  | 1.17 | 0 | 98.83 | 27.7763 | 0
585 | 793.05 | 240.725 | 14.3 | 50.6245 | 50.6245 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3912 | 742.4255 | 0 | 0.088511 | 2.8175 | 0 | 0 | 244.9737 | 50.6245 | on_peak | 742.4255 |  |  | 6.38 | 0 | 93.62 | 142.6369 | 0
586 | 838.8 | 439.114 | 15.1 | 92.0897 | 92.0897 | 0 | 0 | 0 | 0 | 62.6277 | 62.6277 | 0 | 7.4394 | 684.0826 | 0 | 0.088511 | 2.757 | 0 | 0 | 244.9737 | 92.0897 | on_peak | 684.0826 |  |  | 10.98 | 7.47 | 81.55 | 253.8945 | 0
587 | 805.24 | 597.452 | 16.1 | 124.8604 | 124.8604 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 19.0375 | 692.7786 | 0 | 0.05921 | 2.7693 | 0 | 0 | 244.9737 | 124.8604 | off_peak | 680.3796 | 0 | 100 | 15.51 | 0 | 84.49 | 345.7706 | 0
588 | 864.71 | 702.232 | 17 | 146.2974 | 146.2974 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 30.6357 | 730.8115 | 0 | 0.05921 | 3.0776 | 0 | 0 | 244.9737 | 146.2974 | off_peak | 718.4126 | 0 | 100 | 16.92 | 0 | 83.08 | 450.2434 | 0
589 | 854.39 | 740.417 | 17.7 | 153.8747 | 153.8747 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 42.2338 | 712.9142 | 0 | 0.05921 | 3.6344 | 0 | 0 | 244.9737 | 153.8747 | off_peak | 700.5153 | 0 | 100 | 18.01 | 0 | 81.99 | 559.2454 | 0
590 | 857.77 | 708.128 | 18.2 | 146.9063 | 146.9063 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 53.832 | 723.2627 | 0 | 0.05921 | 3.9819 | 0 | 0 | 244.9737 | 146.9063 | off_peak | 710.8637 | 0 | 100 | 17.13 | 0 | 82.87 | 584.9654 | 0
591 | 910.36 | 612.316 | 18.5 | 126.8954 | 126.8954 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 65.4301 | 795.8635 | 0 | 0.05921 | 4.0261 | 0 | 0 | 244.9737 | 126.8954 | off_peak | 783.4646 | 0 | 100 | 13.94 | 0 | 86.06 | 510.899 | 0
592 | 868.53 | 458.672 | 18.5 | 95.0545 | 95.0545 | 0 | 0 | 8.9635 | 8.9635 | 0 | 0 | 0 | 73.8147 | 782.439 | 0 | 0.05921 | 4.0629 | 0 | 0 | 244.9737 | 95.0545 | off_peak | 773.4755 | 0 | 100 | 10.94 | 0 | 89.06 | 386.1977 | 0
593 | 897.16 | 264.387 | 18.3 | 54.8297 | 54.2508 | 0 | 0.57892 | 0.57892 | 0 | 0 | 0 | 0 | 74.3563 | 842.9092 | 0 | 0.05921 | 4.2257 | 0 | 0 | 245.5152 | 54.2508 | off_peak | 842.9092 | 100 | 0 | 6.05 | 0 | 93.95 | 229.249 | 0
594 | 885.22 | 64.8251 | 18 | 13.4579 | 13.4579 | 0 | 0 | 0.03739 | 0.03739 | 0 | 0 | 0 | 74.3912 | 871.7995 | 0 | 0.05921 | 4.4941 | 0 | 0 | 245.5152 | 13.4579 | off_peak | 871.7621 | 0 | 100 | 1.52 | 0 | 98.48 | 60.4817 | 0
595 | 842.38 | 0 | 17.8 | 0 | 0 | 0 | 0 | 0 | 0 | 62.6277 | 62.6277 | 0 | 7.4394 | 779.7523 | 0 | 0.088511 | 4.6785 | 0 | 0 | 245.5152 | 0 | on_peak | 779.7523 |  |  | 0 | 7.43 | 92.57 | 0 | 0
596 | 765.62 | 0 | 17.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 765.62 | 0 | 0.088511 | 4.8335 | 0 | 0 | 245.5152 | 0 | on_peak | 765.62 |  |  | 0 | 0 | 100 | 0 | 0
597 | 795.78 | 0 | 17.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 795.78 | 0 | 0.088511 | 4.8934 | 0 | 0 | 245.5152 | 0 | on_peak | 795.78 |  |  | 0 | 0 | 100 | 0 | 0
598 | 808.9 | 0 | 17.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 808.9 | 0 | 0.088511 | 5.1471 | 0 | 0 | 245.5152 | 0 | on_peak | 808.9 |  |  | 0 | 0 | 100 | 0 | 0
599 | 789.96 | 0 | 17 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 19.0375 | 802.3589 | 0 | 0.05921 | 5.522 | 0 | 0 | 245.5152 | 0 | off_peak | 789.96 | 0 | 100 | 0 | 0 | 100 | 0 | 0
600 | 803.59 | 0 | 16.7 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 30.6357 | 815.9889 | 0 | 0.05921 | 5.8344 | 0 | 0 | 245.5152 | 0 | off_peak | 803.59 | 0 | 100 | 0 | 0 | 100 | 0 | 0
601 | 759.69 | 0 | 16.5 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 42.2338 | 772.0889 | 0 | 0.05921 | 5.9968 | 0 | 0 | 245.5152 | 0 | off_peak | 759.69 | 0 | 100 | 0 | 0 | 100 | 0 | 0
602 | 667.86 | 0 | 16.4 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 53.832 | 680.2589 | 0 | 0.05921 | 5.8994 | 0 | 0 | 245.5152 | 0 | off_peak | 667.86 | 0 | 100 | 0 | 0 | 100 | 0 | 0
603 | 615.38 | 0 | 16.4 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 65.4301 | 627.7789 | 0 | 0.05921 | 5.5471 | 0 | 0 | 245.5152 | 0 | off_peak | 615.38 | 0 | 100 | 0 | 0 | 100 | 0 | 0
604 | 604.84 | 0 | 16.7 | 0 | 0 | 0 | 0 | 8.9635 | 8.9635 | 0 | 0 | 0 | 73.8147 | 613.8035 | 0 | 0.05921 | 5.0767 | 0 | 0 | 245.5152 | 0 | off_peak | 604.84 | 0 | 100 | 0 | 0 | 100 | 0 | 0
605 | 620.76 | 0 | 17.3 | 0 | 0 | 0 | 0 | 0.57892 | 0.57892 | 0 | 0 | 0 | 74.3563 | 621.3389 | 0 | 0.05921 | 4.5427 | 0 | 0 | 245.5152 | 0 | off_peak | 620.76 | 0 | 100 | 0 | 0 | 100 | 0 | 0
606 | 746.73 | 0 | 18 | 0 | 0 | 0 | 0 | 0.03739 | 0.03739 | 0 | 0 | 0 | 74.3912 | 746.7674 | 0 | 0.05921 | 3.9777 | 0 | 0 | 245.5152 | 0 | off_peak | 746.73 | 0 | 100 | 0 | 0 | 100 | 0 | 0
607 | 795.67 | 0 | 18.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3912 | 795.67 | 0 | 0.088511 | 3.4169 | 0 | 0 | 245.5152 | 0 | on_peak | 795.67 |  |  | 0 | 0 | 100 | 0 | 0
608 | 858.89 | 40.7022 | 19.7 | 8.3995 | 8.3995 | 0 | 0 | 0 | 0 | 52.2864 | 52.2864 | 0 | 18.4947 | 798.2041 | 0 | 0.088511 | 3.0673 | 0 | 0 | 245.5152 | 8.3995 | on_peak | 798.2041 |  |  | 0.98 | 6.09 | 92.93 | 25.764 | 0
609 | 825.26 | 230.927 | 20.6 | 47.5034 | 47.5034 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18.4947 | 777.7566 | 0 | 0.088511 | 2.8843 | 0 | 0 | 245.5152 | 47.5034 | on_peak | 777.7566 |  |  | 5.76 | 0 | 94.24 | 137.0132 | 0
610 | 868.84 | 191.039 | 21.5 | 39.1728 | 39.1728 | 0 | 0 | 0 | 0 | 10.3413 | 10.3413 | 0 | 7.4394 | 819.3258 | 0 | 0.088511 | 2.7939 | 0 | 0 | 245.5152 | 39.1728 | on_peak | 819.3258 |  |  | 4.51 | 1.19 | 94.3 | 109.4452 | 0
611 | 800.85 | 580.841 | 22.3 | 118.7636 | 118.7636 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 19.0375 | 694.4854 | 0 | 0.05921 | 2.8154 | 0 | 0 | 245.5152 | 118.7636 | off_peak | 682.0864 | 0 | 100 | 14.83 | 0 | 85.17 | 334.3686 | 0
612 | 807.81 | 684.273 | 22.6 | 139.7625 | 139.7625 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 30.6357 | 680.4465 | 0 | 0.05921 | 2.8662 | 0 | 0 | 245.5152 | 139.7625 | off_peak | 668.0475 | 0 | 100 | 17.3 | 0 | 82.7 | 400.5868 | 0
613 | 855.3 | 719.863 | 22.8 | 146.9268 | 146.9268 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 42.2338 | 720.7722 | 0 | 0.05921 | 3.7473 | 0 | 0 | 245.5152 | 146.9268 | off_peak | 708.3732 | 0 | 100 | 17.18 | 0 | 82.82 | 550.5803 | 0
614 | 877.63 | 679.663 | 22.8 | 138.7218 | 138.7218 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 53.832 | 751.3071 | 0 | 0.05921 | 4.1058 | 0 | 0 | 245.5152 | 138.7218 | off_peak | 738.9082 | 0 | 100 | 15.81 | 0 | 84.19 | 569.5641 | 0
615 | 893.48 | 581.862 | 22.5 | 118.8875 | 118.8875 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 65.4301 | 786.9914 | 0 | 0.05921 | 4.211 | 0 | 0 | 245.5152 | 118.8875 | off_peak | 774.5925 | 0 | 100 | 13.31 | 0 | 86.69 | 500.6319 | 0
616 | 828.08 | 389.92 | 21.8 | 79.8684 | 70.9049 | 0 | 8.9635 | 8.9635 | 0 | 0 | 0 | 0 | 73.8147 | 757.1751 | 0 | 0.05921 | 4.0882 | 0 | 0 | 253.8998 | 70.9049 | off_peak | 757.1751 | 100 | 0 | 8.56 | 0 | 91.44 | 289.8755 | 0
617 | 836.67 | 245.569 | 20.9 | 50.4617 | 49.8828 | 0 | 0.57892 | 0.57892 | 0 | 0 | 0 | 0 | 74.3563 | 786.7872 | 0 | 0.05921 | 3.9247 | 0 | 0 | 254.4414 | 49.8828 | off_peak | 786.7872 | 100 | 0 | 5.96 | 0 | 94.04 | 195.774 | 0
618 | 856.24 | 46.3538 | 20.1 | 9.5522 | 9.5522 | 0 | 0 | 0.03739 | 0.03739 | 0 | 0 | 0 | 74.3912 | 846.7252 | 0 | 0.05921 | 3.8142 | 0 | 0 | 254.4414 | 9.5522 | off_peak | 846.6878 | 0 | 100 | 1.12 | 0 | 98.88 | 36.434 | 0
619 | 796.58 | 0 | 19.7 | 0 | 0 | 0 | 0 | 0 | 0 | 62.6277 | 62.6277 | 0 | 7.4394 | 733.9523 | 0 | 0.088511 | 3.9099 | 0 | 0 | 254.4414 | 0 | on_peak | 733.9523 |  |  | 0 | 7.86 | 92.14 | 0 | 0
620 | 785.6 | 0 | 18.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 785.6 | 0 | 0.088511 | 3.8976 | 0 | 0 | 254.4414 | 0 | on_peak | 785.6 |  |  | 0 | 0 | 100 | 0 | 0
621 | 795.9 | 0 | 18.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 795.9 | 0 | 0.088511 | 3.8512 | 0 | 0 | 254.4414 | 0 | on_peak | 795.9 |  |  | 0 | 0 | 100 | 0 | 0
622 | 738.15 | 0 | 17.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 738.15 | 0 | 0.088511 | 4.0791 | 0 | 0 | 254.4414 | 0 | on_peak | 738.15 |  |  | 0 | 0 | 100 | 0 | 0
623 | 798.94 | 0 | 17.3 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 19.0375 | 811.3389 | 0 | 0.05921 | 4.4312 | 0 | 0 | 254.4414 | 0 | off_peak | 798.94 | 0 | 100 | 0 | 0 | 100 | 0 | 0
624 | 734.81 | 0 | 16.9 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 30.6357 | 747.2089 | 0 | 0.05921 | 4.9213 | 0 | 0 | 254.4414 | 0 | off_peak | 734.81 | 0 | 100 | 0 | 0 | 100 | 0 | 0
625 | 717.8 | 0 | 16.5 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 42.2338 | 730.1989 | 0 | 0.05921 | 5.2996 | 0 | 0 | 254.4414 | 0 | off_peak | 717.8 | 0 | 100 | 0 | 0 | 100 | 0 | 0
626 | 628.52 | 0 | 16.1 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 53.832 | 640.9189 | 0 | 0.05921 | 5.2184 | 0 | 0 | 254.4414 | 0 | off_peak | 628.52 | 0 | 100 | 0 | 0 | 100 | 0 | 0
627 | 608.31 | 0 | 15.7 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 65.4301 | 620.7089 | 0 | 0.05921 | 4.9924 | 0 | 0 | 254.4414 | 0 | off_peak | 608.31 | 0 | 100 | 0 | 0 | 100 | 0 | 0
628 | 574.54 | 0 | 15.3 | 0 | 0 | 0 | 0 | 8.9635 | 8.9635 | 0 | 0 | 0 | 73.8147 | 583.5035 | 0 | 0.05921 | 4.6506 | 0 | 0 | 254.4414 | 0 | off_peak | 574.54 | 0 | 100 | 0 | 0 | 100 | 0 | 0
629 | 614.26 | 0 | 14.9 | 0 | 0 | 0 | 0 | 0.57892 | 0.57892 | 0 | 0 | 0 | 74.3563 | 614.8389 | 0 | 0.05921 | 4.1978 | 0 | 0 | 254.4414 | 0 | off_peak | 614.26 | 0 | 100 | 0 | 0 | 100 | 0 | 0
630 | 690.99 | 0 | 14.6 | 0 | 0 | 0 | 0 | 0.03739 | 0.03739 | 0 | 0 | 0 | 74.3912 | 691.0274 | 0 | 0.05921 | 3.6209 | 0 | 0 | 254.4414 | 0 | off_peak | 690.99 | 0 | 100 | 0 | 0 | 100 | 0 | 0
631 | 740.32 | 0 | 14.5 | 0 | 0 | 0 | 0 | 0 | 0 | 62.6277 | 62.6277 | 0 | 7.4394 | 677.6923 | 0 | 0.088511 | 3.456 | 0 | 0 | 254.4414 | 0 | on_peak | 677.6923 |  |  | 0 | 8.46 | 91.54 | 0 | 0
632 | 777.63 | 32.1854 | 14.9 | 6.7545 | 6.7545 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 770.8755 | 0 | 0.088511 | 3.2131 | 0 | 0 | 254.4414 | 6.7545 | on_peak | 770.8755 |  |  | 0.87 | 0 | 99.13 | 21.7029 | 0
633 | 807.66 | 169.623 | 15.6 | 35.511 | 35.511 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 772.149 | 0 | 0.088511 | 3.0986 | 0 | 0 | 254.4414 | 35.511 | on_peak | 772.149 |  |  | 4.4 | 0 | 95.6 | 110.0344 | 0
634 | 816.89 | 396.991 | 16.5 | 82.8506 | 82.8506 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 734.0394 | 0 | 0.088511 | 3.1163 | 0 | 0 | 254.4414 | 82.8506 | on_peak | 734.0394 |  |  | 10.14 | 0 | 89.86 | 258.1865 | 0
635 | 786.23 | 568.322 | 17.4 | 118.2339 | 118.2339 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 19.0375 | 680.395 | 0 | 0.05921 | 3.2468 | 0 | 0 | 254.4414 | 118.2339 | off_peak | 667.9961 | 0 | 100 | 15.04 | 0 | 84.96 | 383.8782 | 0
636 | 879.48 | 668.746 | 18.2 | 138.7362 | 138.7362 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 30.6357 | 753.1428 | 0 | 0.05921 | 3.6957 | 0 | 0 | 254.4414 | 138.7362 | off_peak | 740.7438 | 0 | 100 | 15.77 | 0 | 84.23 | 512.729 | 0
637 | 788.27 | 553.191 | 18.9 | 114.4812 | 114.4812 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 42.2338 | 686.1878 | 0 | 0.05921 | 4.5326 | 0 | 0 | 254.4414 | 114.4812 | off_peak | 673.7888 | 0 | 100 | 14.52 | 0 | 85.48 | 518.8965 | 0
638 | 811.93 | 627.417 | 19.4 | 129.6133 | 129.6133 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 53.832 | 694.7156 | 0 | 0.05921 | 4.9686 | 0 | 0 | 254.4414 | 129.6133 | off_peak | 682.3167 | 0 | 100 | 15.96 | 0 | 84.04 | 644.0025 | 0
639 | 811.15 | 585.898 | 19.8 | 120.8654 | 120.8654 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 65.4301 | 702.6836 | 0 | 0.05921 | 4.856 | 0 | 0 | 254.4414 | 120.8654 | off_peak | 690.2846 | 0 | 100 | 14.9 | 0 | 85.1 | 586.9256 | 0
640 | 764.28 | 436.767 | 20 | 90.0373 | 90.0373 | 0 | 0 | 8.9635 | 8.9635 | 0 | 0 | 0 | 73.8147 | 683.2062 | 0 | 0.05921 | 4.1229 | 0 | 0 | 254.4414 | 90.0373 | off_peak | 674.2427 | 0 | 100 | 11.78 | 0 | 88.22 | 371.2119 | 0
641 | 810.57 | 191.414 | 19.6 | 39.5149 | 38.9359 | 0 | 0.57892 | 0.57892 | 0 | 0 | 0 | 0 | 74.3563 | 771.6341 | 0 | 0.05921 | 3.8004 | 0 | 0 | 254.9829 | 38.9359 | off_peak | 771.6341 | 100 | 0 | 4.8 | 0 | 95.2 | 147.9707 | 0
642 | 812.3 | 60.1287 | 19 | 12.4391 | 12.4017 | 0 | 0.03739 | 0.03739 | 0 | 0 | 0 | 0 | 74.3912 | 799.8983 | 0 | 0.05921 | 3.5265 | 0 | 0 | 255.0179 | 12.4017 | off_peak | 799.8983 | 100 | 0 | 1.53 | 0 | 98.47 | 43.734 | 0
643 | 782.66 | 0 | 18.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3912 | 782.66 | 0 | 0.088511 | 3.4104 | 0 | 0 | 255.0179 | 0 | on_peak | 782.66 |  |  | 0 | 0 | 100 | 0 | 0
644 | 770.67 | 0 | 18.2 | 0 | 0 | 0 | 0 | 0 | 0 | 62.6277 | 62.6277 | 0 | 7.4394 | 708.0423 | 0 | 0.088511 | 3.3746 | 62.6277 | 0 | 188.066 | 62.6277 | on_peak | 708.0423 |  |  | 0 | 8.13 | 91.87 | 211.3431 | 0
645 | 771.53 | 0 | 17.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 771.53 | 0 | 0.088511 | 3.3848 | 0 | 0 | 188.066 | 0 | on_peak | 771.53 |  |  | 0 | 0 | 100 | 0 | 0
646 | 715.3 | 0 | 17.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 715.3 | 0 | 0.088511 | 3.5262 | 0 | 0 | 188.066 | 0 | on_peak | 715.3 |  |  | 0 | 0 | 100 | 0 | 0
647 | 755.66 | 0 | 17.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 755.66 | 0 | 0.05921 | 3.9187 | 0 | 0 | 188.066 | 0 | off_peak | 755.66 |  |  | 0 | 0 | 100 | 0 | 0
648 | 724.86 | 0 | 17.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 724.86 | 0 | 0.05921 | 4.5437 | 0 | 0 | 188.066 | 0 | off_peak | 724.86 |  |  | 0 | 0 | 100 | 0 | 0
649 | 705.98 | 0 | 17.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 705.98 | 0 | 0.05921 | 4.936 | 0 | 0 | 188.066 | 0 | off_peak | 705.98 |  |  | 0 | 0 | 100 | 0 | 0
650 | 606.47 | 0 | 17.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 606.47 | 0 | 0.05921 | 4.8391 | 0 | 0 | 188.066 | 0 | off_peak | 606.47 |  |  | 0 | 0 | 100 | 0 | 0
651 | 610.94 | 0 | 17.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 610.94 | 0 | 0.05921 | 4.6296 | 0 | 0 | 188.066 | 0 | off_peak | 610.94 |  |  | 0 | 0 | 100 | 0 | 0
652 | 603.56 | 0 | 16.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 603.56 | 0 | 0.05921 | 4.3002 | 0 | 0 | 188.066 | 0 | off_peak | 603.56 |  |  | 0 | 0 | 100 | 0 | 0
653 | 592.24 | 0 | 15.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 592.24 | 0 | 0.05921 | 4.1246 | 0 | 0 | 188.066 | 0 | off_peak | 592.24 |  |  | 0 | 0 | 100 | 0 | 0
654 | 672.26 | 0 | 14.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 672.26 | 0 | 0.05921 | 4.0339 | 0 | 0 | 188.066 | 0 | off_peak | 672.26 |  |  | 0 | 0 | 100 | 0 | 0
655 | 721.78 | 0 | 14.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 721.78 | 0 | 0.05921 | 3.5199 | 0 | 0 | 188.066 | 0 | off_peak | 721.78 |  |  | 0 | 0 | 100 | 0 | 0
656 | 700.61 | 43.3107 | 14.8 | 9.0925 | 9.0925 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 691.5175 | 0 | 0.05921 | 3.2258 | 0 | 0 | 188.066 | 9.0925 | off_peak | 691.5175 |  |  | 1.3 | 0 | 98.7 | 29.3309 | 0
657 | 773.28 | 235.296 | 15.6 | 49.2598 | 49.2598 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 724.0202 | 0 | 0.05921 | 3.1419 | 0 | 0 | 188.066 | 49.2598 | off_peak | 724.0202 |  |  | 6.37 | 0 | 93.63 | 154.7715 | 0
658 | 741.27 | 430.561 | 16.5 | 89.8566 | 89.8566 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 651.4134 | 0 | 0.05921 | 3.194 | 0 | 0 | 188.066 | 89.8566 | off_peak | 651.4134 |  |  | 12.12 | 0 | 87.88 | 287.0061 | 0
659 | 720.84 | 588.307 | 17.3 | 122.4345 | 122.4345 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 598.4055 | 0 | 0.05921 | 3.2344 | 0 | 0 | 188.066 | 122.4345 | off_peak | 598.4055 |  |  | 16.98 | 0 | 83.02 | 396.0035 | 0
660 | 786.61 | 692.449 | 18 | 143.7545 | 143.7545 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 642.8555 | 0 | 0.05921 | 3.3859 | 0 | 0 | 188.066 | 143.7545 | off_peak | 642.8555 |  |  | 18.28 | 0 | 81.72 | 486.7386 | 0
661 | 682.51 | 728.348 | 18.6 | 150.8887 | 150.8887 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 531.6213 | 0 | 0.05921 | 3.6609 | 0 | 0 | 188.066 | 150.8887 | off_peak | 531.6213 |  |  | 22.11 | 0 | 77.89 | 552.3869 | 0
662 | 696.83 | 691.053 | 19 | 142.9609 | 142.9609 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 553.8691 | 0 | 0.05921 | 4.1884 | 0 | 0 | 188.066 | 142.9609 | off_peak | 553.8691 |  |  | 20.52 | 0 | 79.48 | 598.7797 | 0
663 | 669.36 | 594.819 | 19.2 | 122.9659 | 122.9659 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 546.3941 | 0 | 0.05921 | 4.2093 | 0 | 0 | 188.066 | 122.9659 | off_peak | 546.3941 |  |  | 18.37 | 0 | 81.63 | 517.6024 | 0
664 | 649.41 | 438.275 | 19.2 | 90.6038 | 90.6038 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 558.8062 | 0 | 0.05921 | 4.1116 | 0 | 0 | 188.066 | 90.6038 | off_peak | 558.8062 |  |  | 13.95 | 0 | 86.05 | 372.53 | 0
665 | 676.91 | 247.014 | 18.6 | 51.1728 | 51.1728 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 625.7372 | 0 | 0.05921 | 3.8709 | 0 | 0 | 188.066 | 51.1728 | off_peak | 625.7372 |  |  | 7.56 | 0 | 92.44 | 198.086 | 0
666 | 646.89 | 58.6475 | 17.7 | 12.1882 | 12.1882 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 634.7018 | 0 | 0.05921 | 3.9712 | 0 | 0 | 188.066 | 12.1882 | off_peak | 634.7018 |  |  | 1.88 | 0 | 98.12 | 48.4018 | 0
667 | 601.26 | 0 | 17.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 601.26 | 0 | 0.05921 | 3.8995 | 0 | 0 | 188.066 | 0 | off_peak | 601.26 |  |  | 0 | 0 | 100 | 0 | 0
668 | 603.47 | 0 | 16.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 603.47 | 0 | 0.05921 | 3.7645 | 0 | 0 | 188.066 | 0 | off_peak | 603.47 |  |  | 0 | 0 | 100 | 0 | 0
669 | 517.33 | 0 | 16.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 517.33 | 0 | 0.05921 | 3.8408 | 0 | 0 | 188.066 | 0 | off_peak | 517.33 |  |  | 0 | 0 | 100 | 0 | 0
670 | 555.38 | 0 | 16.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 555.38 | 0 | 0.05921 | 4.0046 | 0 | 0 | 188.066 | 0 | off_peak | 555.38 |  |  | 0 | 0 | 100 | 0 | 0
671 | 534.1 | 0 | 16.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 534.1 | 0 | 0.05921 | 4.1942 | 0 | 0 | 188.066 | 0 | off_peak | 534.1 |  |  | 0 | 0 | 100 | 0 | 0
672 | 553.8 | 0 | 16.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 553.8 | 0 | 0.05921 | 4.4339 | 0 | 0 | 188.066 | 0 | off_peak | 553.8 |  |  | 0 | 0 | 100 | 0 | 0
673 | 524.77 | 0 | 16.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 524.77 | 0 | 0.05921 | 4.6956 | 0 | 0 | 188.066 | 0 | off_peak | 524.77 |  |  | 0 | 0 | 100 | 0 | 0
674 | 513.86 | 0 | 16.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 513.86 | 0 | 0.05921 | 4.5978 | 0 | 0 | 188.066 | 0 | off_peak | 513.86 |  |  | 0 | 0 | 100 | 0 | 0
675 | 553.42 | 0 | 16.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 553.42 | 0 | 0.05921 | 4.4466 | 0 | 0 | 188.066 | 0 | off_peak | 553.42 |  |  | 0 | 0 | 100 | 0 | 0
676 | 519.17 | 0 | 16.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 519.17 | 0 | 0.05921 | 4.1592 | 0 | 0 | 188.066 | 0 | off_peak | 519.17 |  |  | 0 | 0 | 100 | 0 | 0
677 | 548.93 | 0 | 16.8 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 19.0375 | 561.3289 | 0 | 0.05921 | 3.9264 | 0 | 0 | 188.066 | 0 | off_peak | 548.93 | 0 | 100 | 0 | 0 | 100 | 0 | 0
678 | 609.23 | 0 | 16.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19.0375 | 609.23 | 0 | 0.05921 | 3.617 | 0 | 0 | 188.066 | 0 | off_peak | 609.23 |  |  | 0 | 0 | 100 | 0 | 0
679 | 644.46 | 0 | 17.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19.0375 | 644.46 | 0 | 0.05921 | 3.2934 | 0 | 0 | 188.066 | 0 | off_peak | 644.46 |  |  | 0 | 0 | 100 | 0 | 0
680 | 661.46 | 10.45 | 18.3 | 2.1672 | 2.1672 | 0 | 0 | 8.7263 | 8.7263 | 0 | 0 | 0 | 27.2003 | 668.0192 | 0 | 0.05921 | 3.0167 | 0 | 0 | 188.066 | 2.1672 | off_peak | 659.2928 | 0 | 100 | 0.33 | 0 | 99.67 | 6.5376 | 0
681 | 667.15 | 43.7 | 19.3 | 9.0308 | 9.0308 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27.2003 | 658.1192 | 0 | 0.05921 | 2.8622 | 0 | 0 | 188.066 | 9.0308 | off_peak | 658.1192 |  |  | 1.35 | 0 | 98.65 | 25.8478 | 0
682 | 641.94 | 18.05 | 19.9 | 3.7222 | 3.7222 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27.2003 | 638.2178 | 0 | 0.05921 | 2.7651 | 0 | 0 | 188.066 | 3.7222 | off_peak | 638.2178 |  |  | 0.58 | 0 | 99.42 | 10.2925 | 0
683 | 649.16 | 123.692 | 20.4 | 25.4624 | 25.4624 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27.2003 | 623.6976 | 0 | 0.05921 | 2.6944 | 0 | 0 | 188.066 | 25.4624 | off_peak | 623.6976 |  |  | 3.92 | 0 | 96.08 | 68.6072 | 0
684 | 697.99 | 105.45 | 20.6 | 21.6919 | 21.6919 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27.2003 | 676.2981 | 0 | 0.05921 | 2.778 | 0 | 0 | 188.066 | 21.6919 | off_peak | 676.2981 |  |  | 3.11 | 0 | 96.89 | 60.2594 | 0
685 | 668.49 | 84.55 | 20.8 | 17.3803 | 17.3803 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27.2003 | 651.1097 | 0 | 0.05921 | 2.9584 | 0 | 0 | 188.066 | 17.3803 | off_peak | 651.1097 |  |  | 2.6 | 0 | 97.4 | 51.4178 | 0
686 | 640.17 | 107.35 | 20.8 | 22.0671 | 22.0671 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 38.7984 | 630.5019 | 0 | 0.05921 | 3.2344 | 0 | 0 | 188.066 | 22.0671 | off_peak | 618.1029 | 0 | 100 | 3.45 | 0 | 96.55 | 71.3737 | 0
687 | 675.72 | 26.6 | 20.8 | 5.4679 | 5.4679 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 38.7984 | 670.2521 | 0 | 0.05921 | 3.5571 | 0 | 0 | 188.066 | 5.4679 | off_peak | 670.2521 |  |  | 0.81 | 0 | 99.19 | 19.45 | 0
688 | 712.25 | 55.1 | 20.6 | 11.3345 | 11.3345 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 38.7984 | 700.9155 | 0 | 0.05921 | 3.6684 | 0 | 0 | 188.066 | 11.3345 | off_peak | 700.9155 |  |  | 1.59 | 0 | 98.41 | 41.5797 | 0
689 | 673.12 | 45.6 | 20.1 | 9.3969 | 9.3969 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 50.3966 | 676.1221 | 0 | 0.05921 | 3.6639 | 0 | 0 | 188.066 | 9.3969 | off_peak | 663.7231 | 0 | 100 | 1.4 | 0 | 98.6 | 34.4295 | 0
690 | 629.43 | 12.35 | 19.5 | 2.5504 | 2.5504 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50.3966 | 626.8796 | 0 | 0.05921 | 3.708 | 0 | 0 | 188.066 | 2.5504 | off_peak | 626.8796 |  |  | 0.41 | 0 | 99.59 | 9.4567 | 0
691 | 638.06 | 0 | 19.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50.3966 | 638.06 | 0 | 0.05921 | 3.9224 | 0 | 0 | 188.066 | 0 | off_peak | 638.06 |  |  | 0 | 0 | 100 | 0 | 0
692 | 596.08 | 0 | 19.1 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 61.9947 | 608.4789 | 0 | 0.05921 | 4.1668 | 0 | 0 | 188.066 | 0 | off_peak | 596.08 | 0 | 100 | 0 | 0 | 100 | 0 | 0
693 | 596.5 | 0 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 61.9947 | 596.5 | 0 | 0.05921 | 4.5015 | 0 | 0 | 188.066 | 0 | off_peak | 596.5 |  |  | 0 | 0 | 100 | 0 | 0
694 | 552.46 | 0 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 61.9947 | 552.46 | 0 | 0.05921 | 4.7891 | 0 | 0 | 188.066 | 0 | off_peak | 552.46 |  |  | 0 | 0 | 100 | 0 | 0
695 | 548.79 | 0 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 61.9947 | 548.79 | 0 | 0.05921 | 5.1482 | 0 | 0 | 188.066 | 0 | off_peak | 548.79 |  |  | 0 | 0 | 100 | 0 | 0
696 | 543.77 | 0 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 61.9947 | 543.77 | 0 | 0.05921 | 5.3701 | 0 | 0 | 188.066 | 0 | off_peak | 543.77 |  |  | 0 | 0 | 100 | 0 | 0
697 | 548.6 | 0 | 18.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 61.9947 | 548.6 | 0 | 0.05921 | 5.6132 | 0 | 0 | 188.066 | 0 | off_peak | 548.6 |  |  | 0 | 0 | 100 | 0 | 0
698 | 550 | 0 | 18.7 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 73.5928 | 562.3989 | 0 | 0.05921 | 5.4196 | 0 | 0 | 188.066 | 0 | off_peak | 550 | 0 | 100 | 0 | 0 | 100 | 0 | 0
699 | 519.77 | 0 | 18.3 | 0 | 0 | 0 | 0 | 0.80079 | 0.80079 | 0 | 0 | 0 | 74.3419 | 520.5708 | 0 | 0.05921 | 5.1273 | 0 | 0 | 188.066 | 0 | off_peak | 519.77 | 0 | 100 | 0 | 0 | 100 | 0 | 0
700 | 556.48 | 0 | 17.8 | 0 | 0 | 0 | 0 | 0.05172 | 0.05172 | 0 | 0 | 0 | 74.3903 | 556.5317 | 0 | 0.05921 | 4.7845 | 0 | 0 | 188.066 | 0 | off_peak | 556.48 | 0 | 100 | 0 | 0 | 100 | 0 | 0
701 | 539.08 | 0 | 17.4 | 0 | 0 | 0 | 0 | 0.0033404 | 0.0033404 | 0 | 0 | 0 | 74.3934 | 539.0833 | 0 | 0.05921 | 4.4239 | 0 | 0 | 188.066 | 0 | off_peak | 539.08 | 0 | 100 | 0 | 0 | 100 | 0 | 0
702 | 709.57 | 0 | 17.1 | 0 | 0 | 0 | 0 | 0.00021574 | 0.00021574 | 0 | 0 | 0 | 74.3936 | 709.5702 | 0 | 0.05921 | 3.8434 | 0 | 0 | 188.066 | 0 | off_peak | 709.57 | 0 | 100 | 0 | 0 | 100 | 0 | 0
703 | 747.3 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 747.3 | 0 | 0.088511 | 3.3258 | 0 | 0 | 188.066 | 0 | on_peak | 747.3 |  |  | 0 | 0 | 100 | 0 | 0
704 | 775 | 45.9622 | 17.6 | 9.5553 | 9.5553 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 765.4447 | 0 | 0.088511 | 2.9905 | 0 | 0 | 188.066 | 9.5553 | on_peak | 765.4447 |  |  | 1.23 | 0 | 98.77 | 28.5752 | 0
705 | 848.23 | 238.829 | 18.7 | 49.4597 | 49.4597 | 0 | 0 | 0 | 0 | 62.63 | 62.63 | 0 | 7.4394 | 736.1403 | 0 | 0.088511 | 2.7971 | 62.63 | 0 | 121.1117 | 112.0897 | on_peak | 736.1403 |  |  | 5.83 | 7.38 | 86.79 | 313.5272 | 0
706 | 864.42 | 436.096 | 19.8 | 89.9626 | 89.9626 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 774.4574 | 0 | 0.088511 | 2.7 | 0 | 0 | 121.1117 | 89.9626 | on_peak | 774.4574 |  |  | 10.41 | 0 | 89.59 | 242.8963 | 0
707 | 810.85 | 594.134 | 20.8 | 122.1313 | 109.7323 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 0 | 19.0375 | 701.1177 | 0 | 0.05921 | 2.744 | 0 | 0 | 132.7099 | 109.7323 | off_peak | 701.1177 | 100 | 0 | 13.53 | 0 | 86.47 | 301.1002 | 0
708 | 887.87 | 698.189 | 21.2 | 143.3174 | 143.3174 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 30.6357 | 756.9515 | 0 | 0.05921 | 3.0448 | 0 | 0 | 132.7099 | 143.3174 | off_peak | 744.5526 | 0 | 100 | 16.14 | 0 | 83.86 | 436.3657 | 0
709 | 806.66 | 735.636 | 21.5 | 150.8433 | 138.4443 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 0 | 42.2338 | 668.2157 | 0 | 0.05921 | 3.5794 | 0 | 0 | 144.308 | 138.4443 | off_peak | 668.2157 | 100 | 0 | 17.16 | 0 | 82.84 | 495.5446 | 0
710 | 856.41 | 711.567 | 21.7 | 145.8041 | 145.8041 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 53.832 | 723.0048 | 0 | 0.05921 | 3.9404 | 0 | 0 | 144.308 | 145.8041 | off_peak | 710.6059 | 0 | 100 | 17.03 | 0 | 82.97 | 574.53 | 0
711 | 878.56 | 618.044 | 21.9 | 126.5506 | 126.5506 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 65.4301 | 764.4083 | 0 | 0.05921 | 3.9562 | 0 | 0 | 144.308 | 126.5506 | off_peak | 752.0094 | 0 | 100 | 14.4 | 0 | 85.6 | 500.6588 | 0
712 | 848 | 465.277 | 21.9 | 95.2701 | 86.3065 | 0 | 8.9635 | 8.9635 | 0 | 0 | 0 | 0 | 73.8147 | 761.6935 | 0 | 0.05921 | 3.8814 | 0 | 0 | 152.6927 | 86.3065 | off_peak | 761.6935 | 100 | 0 | 10.18 | 0 | 89.82 | 334.992 | 0
713 | 849.68 | 271.54 | 21.5 | 55.6797 | 55.1008 | 0 | 0.57892 | 0.57892 | 0 | 0 | 0 | 0 | 74.3563 | 794.5792 | 0 | 0.05921 | 3.9975 | 0 | 0 | 153.2342 | 55.1008 | off_peak | 794.5792 | 100 | 0 | 6.48 | 0 | 93.52 | 220.2631 | 0
714 | 833.65 | 47.7105 | 21.1 | 9.797 | 9.797 | 0 | 0 | 0.03739 | 0.03739 | 0 | 0 | 0 | 74.3912 | 823.8904 | 0 | 0.05921 | 4.2911 | 0 | 0 | 153.2342 | 9.797 | off_peak | 823.853 | 0 | 100 | 1.18 | 0 | 98.82 | 42.0395 | 0
715 | 784.09 | 0 | 20.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3912 | 784.09 | 0 | 0.088511 | 4.7131 | 0 | 0 | 153.2342 | 0 | on_peak | 784.09 |  |  | 0 | 0 | 100 | 0 | 0
716 | 827.97 | 0 | 20.5 | 0 | 0 | 0 | 0 | 0 | 0 | 62.6277 | 62.6277 | 0 | 7.4394 | 765.3423 | 0 | 0.088511 | 5.0289 | 0 | 0 | 153.2342 | 0 | on_peak | 765.3423 |  |  | 0 | 7.56 | 92.44 | 0 | 0
717 | 762.67 | 0 | 20.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 762.67 | 0 | 0.088511 | 5.4439 | 0 | 0 | 153.2342 | 0 | on_peak | 762.67 |  |  | 0 | 0 | 100 | 0 | 0
718 | 758.9 | 0 | 19.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 758.9 | 0 | 0.088511 | 5.7363 | 0 | 0 | 153.2342 | 0 | on_peak | 758.9 |  |  | 0 | 0 | 100 | 0 | 0
719 | 754.76 | 0 | 19.3 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 19.0375 | 767.1589 | 0 | 0.05921 | 6.0886 | 0 | 0 | 153.2342 | 0 | off_peak | 754.76 | 0 | 100 | 0 | 0 | 100 | 0 | 0
720 | 754.25 | 0 | 18.9 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 30.6357 | 766.6489 | 0 | 0.05921 | 6.3981 | 0 | 0 | 153.2342 | 0 | off_peak | 754.25 | 0 | 100 | 0 | 0 | 100 | 0 | 0
721 | 731.15 | 0 | 18.7 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 42.2338 | 743.5489 | 0 | 0.05921 | 6.3613 | 0 | 0 | 153.2342 | 0 | off_peak | 731.15 | 0 | 100 | 0 | 0 | 100 | 0 | 0
722 | 665.64 | 0 | 18.6 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 53.832 | 678.0389 | 0 | 0.05921 | 6.1868 | 0 | 0 | 153.2342 | 0 | off_peak | 665.64 | 0 | 100 | 0 | 0 | 100 | 0 | 0
723 | 603.05 | 0 | 18.6 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 65.4301 | 615.4489 | 0 | 0.05921 | 5.6277 | 0 | 0 | 153.2342 | 0 | off_peak | 603.05 | 0 | 100 | 0 | 0 | 100 | 0 | 0
724 | 636.06 | 0 | 18.6 | 0 | 0 | 0 | 0 | 8.9635 | 8.9635 | 0 | 0 | 0 | 73.8147 | 645.0235 | 0 | 0.05921 | 5.1071 | 0 | 0 | 153.2342 | 0 | off_peak | 636.06 | 0 | 100 | 0 | 0 | 100 | 0 | 0
725 | 575.32 | 0 | 18.4 | 0 | 0 | 0 | 0 | 0.57892 | 0.57892 | 0 | 0 | 0 | 74.3563 | 575.8989 | 0 | 0.05921 | 4.6093 | 0 | 0 | 153.2342 | 0 | off_peak | 575.32 | 0 | 100 | 0 | 0 | 100 | 0 | 0
726 | 699.23 | 0 | 18.2 | 0 | 0 | 0 | 0 | 0.03739 | 0.03739 | 0 | 0 | 0 | 74.3912 | 699.2674 | 0 | 0.05921 | 3.9939 | 0 | 0 | 153.2342 | 0 | off_peak | 699.23 | 0 | 100 | 0 | 0 | 100 | 0 | 0
727 | 767.07 | 0 | 18.3 | 0 | 0 | 0 | 0 | 0 | 0 | 62.6277 | 62.6277 | 0 | 7.4394 | 704.4423 | 0 | 0.088511 | 3.4381 | 0 | 0 | 153.2342 | 0 | on_peak | 704.4423 |  |  | 0 | 8.16 | 91.84 | 0 | 0
728 | 789.63 | 49.0117 | 19.2 | 10.1321 | 10.1321 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 779.4979 | 0 | 0.088511 | 3.0609 | 0 | 0 | 153.2342 | 10.1321 | on_peak | 779.4979 |  |  | 1.28 | 0 | 98.72 | 31.013 | 0
729 | 802.02 | 246.12 | 20.3 | 50.6826 | 50.6826 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 751.3374 | 0 | 0.088511 | 2.8201 | 0 | 0 | 153.2342 | 50.6826 | on_peak | 751.3374 |  |  | 6.32 | 0 | 93.68 | 142.9306 | 0
730 | 832.24 | 445.514 | 21.1 | 91.4832 | 91.4832 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 740.7568 | 0 | 0.088511 | 2.6964 | 0 | 0 | 153.2342 | 91.4832 | on_peak | 740.7568 |  |  | 10.99 | 0 | 89.01 | 246.6797 | 0
731 | 767.92 | 606.039 | 21.7 | 124.1808 | 124.1808 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 19.0375 | 656.1381 | 0 | 0.05921 | 2.7177 | 0 | 0 | 153.2342 | 124.1808 | off_peak | 643.7392 | 0 | 100 | 16.17 | 0 | 83.83 | 337.4856 | 0
732 | 874.97 | 711.695 | 22 | 145.6747 | 145.6747 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 30.6357 | 741.6942 | 0 | 0.05921 | 2.9813 | 0 | 0 | 153.2342 | 145.6747 | off_peak | 729.2953 | 0 | 100 | 16.65 | 0 | 83.35 | 434.2929 | 0
733 | 806.9 | 749.764 | 22.1 | 153.4123 | 153.4123 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 42.2338 | 665.8867 | 0 | 0.05921 | 3.5551 | 0 | 0 | 153.2342 | 153.4123 | off_peak | 653.4877 | 0 | 100 | 19.01 | 0 | 80.99 | 545.4002 | 0
734 | 854.18 | 718.594 | 22.1 | 147.0345 | 134.6355 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 0 | 53.832 | 719.5445 | 0 | 0.05921 | 3.8133 | 0 | 0 | 164.8323 | 134.6355 | off_peak | 719.5445 | 100 | 0 | 15.76 | 0 | 84.24 | 513.4008 | 0
735 | 901.73 | 622.671 | 21.9 | 127.4981 | 127.4981 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 65.4301 | 786.6309 | 0 | 0.05921 | 3.9021 | 0 | 0 | 164.8323 | 127.4981 | off_peak | 774.2319 | 0 | 100 | 14.14 | 0 | 85.86 | 497.5147 | 0
736 | 890.06 | 470.533 | 21.5 | 96.4835 | 96.4835 | 0 | 0 | 8.9635 | 8.9635 | 0 | 0 | 0 | 73.8147 | 802.54 | 0 | 0.05921 | 4.0193 | 0 | 0 | 164.8323 | 96.4835 | off_peak | 793.5765 | 0 | 100 | 10.84 | 0 | 89.16 | 387.8006 | 0
737 | 915.26 | 276.684 | 21 | 56.8353 | 56.2564 | 0 | 0.57892 | 0.57892 | 0 | 0 | 0 | 0 | 74.3563 | 859.0036 | 0 | 0.05921 | 4.1319 | 0 | 0 | 165.3739 | 56.2564 | off_peak | 859.0036 | 100 | 0 | 6.15 | 0 | 93.85 | 232.4463 | 0
738 | 876.66 | 76.2664 | 20.5 | 15.6941 | 15.6941 | 0 | 0 | 0.03739 | 0.03739 | 0 | 0 | 0 | 74.3912 | 861.0033 | 0 | 0.05921 | 4.3452 | 0 | 0 | 165.3739 | 15.6941 | off_peak | 860.9659 | 0 | 100 | 1.79 | 0 | 98.21 | 68.1944 | 0
739 | 797.45 | 0 | 20.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3912 | 797.45 | 0 | 0.088511 | 4.5515 | 0 | 0 | 165.3739 | 0 | on_peak | 797.45 |  |  | 0 | 0 | 100 | 0 | 0
740 | 833.13 | 0 | 20.5 | 0 | 0 | 0 | 0 | 0 | 0 | 13.8042 | 13.8042 | 0 | 59.634 | 819.3258 | 0 | 0.088511 | 4.8609 | 0 | 0 | 165.3739 | 0 | on_peak | 819.3258 |  |  | 0 | 1.66 | 98.34 | 0 | 0
741 | 809.69 | 0 | 20.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 59.634 | 809.69 | 0 | 0.088511 | 5.0328 | 0 | 0 | 165.3739 | 0 | on_peak | 809.69 |  |  | 0 | 0 | 100 | 0 | 0
742 | 757.78 | 0 | 19.9 | 0 | 0 | 0 | 0 | 0 | 0 | 48.8236 | 48.8236 | 0 | 7.4394 | 708.9564 | 0 | 0.088511 | 5.2989 | 0 | 0 | 165.3739 | 0 | on_peak | 708.9564 |  |  | 0 | 6.44 | 93.56 | 0 | 0
743 | 756.29 | 0 | 19.5 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 19.0375 | 768.6889 | 0 | 0.05921 | 5.7331 | 0 | 0 | 165.3739 | 0 | off_peak | 756.29 | 0 | 100 | 0 | 0 | 100 | 0 | 0
744 | 759.02 | 0 | 18.9 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 30.6357 | 771.4189 | 0 | 0.05921 | 6.0745 | 0 | 0 | 165.3739 | 0 | off_peak | 759.02 | 0 | 100 | 0 | 0 | 100 | 0 | 0
745 | 706.88 | 0 | 18.3 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 42.2338 | 719.2789 | 0 | 0.05921 | 6.2358 | 0 | 0 | 165.3739 | 0 | off_peak | 706.88 | 0 | 100 | 0 | 0 | 100 | 0 | 0
746 | 643.47 | 0 | 17.8 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 53.832 | 655.8689 | 0 | 0.05921 | 6.0561 | 0 | 0 | 165.3739 | 0 | off_peak | 643.47 | 0 | 100 | 0 | 0 | 100 | 0 | 0
747 | 642.1 | 0 | 17.2 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 65.4301 | 654.4989 | 0 | 0.05921 | 5.6381 | 0 | 0 | 165.3739 | 0 | off_peak | 642.1 | 0 | 100 | 0 | 0 | 100 | 0 | 0
748 | 595.31 | 0 | 16.8 | 0 | 0 | 0 | 0 | 8.9635 | 8.9635 | 0 | 0 | 0 | 73.8147 | 604.2735 | 0 | 0.05921 | 5.0961 | 0 | 0 | 165.3739 | 0 | off_peak | 595.31 | 0 | 100 | 0 | 0 | 100 | 0 | 0
749 | 603.34 | 0 | 16.6 | 0 | 0 | 0 | 0 | 0.57892 | 0.57892 | 0 | 0 | 0 | 74.3563 | 603.9189 | 0 | 0.05921 | 4.5552 | 0 | 0 | 165.3739 | 0 | off_peak | 603.34 | 0 | 100 | 0 | 0 | 100 | 0 | 0
750 | 719.14 | 0 | 16.5 | 0 | 0 | 0 | 0 | 0.03739 | 0.03739 | 0 | 0 | 0 | 74.3912 | 719.1774 | 0 | 0.05921 | 4.028 | 0 | 0 | 165.3739 | 0 | off_peak | 719.14 | 0 | 100 | 0 | 0 | 100 | 0 | 0
751 | 734.39 | 0 | 16.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3912 | 734.39 | 0 | 0.088511 | 3.4262 | 0 | 0 | 165.3739 | 0 | on_peak | 734.39 |  |  | 0 | 0 | 100 | 0 | 0
752 | 786.83 | 51.896 | 17 | 10.8116 | 10.8116 | 0 | 0 | 0 | 0 | 62.6277 | 62.6277 | 0 | 7.4394 | 713.3907 | 0 | 0.088511 | 3.0407 | 0 | 0 | 165.3739 | 10.8116 | on_peak | 713.3907 |  |  | 1.37 | 7.96 | 90.67 | 32.8747 | 0
753 | 777.86 | 245.72 | 18 | 51.0122 | 51.0122 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 726.8478 | 0 | 0.088511 | 2.7961 | 0 | 0 | 165.3739 | 51.0122 | on_peak | 726.8478 |  |  | 6.56 | 0 | 93.44 | 142.6368 | 0
754 | 773.04 | 183.438 | 19.3 | 37.9084 | 37.9084 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 735.1316 | 0 | 0.088511 | 2.6594 | 0 | 0 | 165.3739 | 37.9084 | on_peak | 735.1316 |  |  | 4.9 | 0 | 95.1 | 100.8141 | 0
755 | 766.94 | 448.85 | 20.5 | 92.3646 | 92.3646 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 19.0375 | 686.9744 | 0 | 0.05921 | 2.6956 | 0 | 0 | 165.3739 | 92.3646 | off_peak | 674.5754 | 0 | 100 | 12.04 | 0 | 87.96 | 248.9758 | 0
756 | 813.69 | 401.502 | 21.3 | 82.3871 | 69.9882 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 0 | 30.6357 | 743.7018 | 0 | 0.05921 | 2.9816 | 0 | 0 | 176.972 | 69.9882 | off_peak | 743.7018 | 100 | 0 | 8.6 | 0 | 91.4 | 208.6753 | 0
757 | 814.02 | 582.631 | 21.8 | 119.3419 | 119.3419 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 42.2338 | 707.077 | 0 | 0.05921 | 3.5551 | 0 | 0 | 176.972 | 119.3419 | off_peak | 694.6781 | 0 | 100 | 14.66 | 0 | 85.34 | 424.2784 | 0
758 | 801.02 | 594.791 | 22 | 121.746 | 121.746 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 53.832 | 691.673 | 0 | 0.05921 | 3.8686 | 0 | 0 | 176.972 | 121.746 | off_peak | 679.274 | 0 | 100 | 15.2 | 0 | 84.8 | 470.9894 | 0
759 | 864.33 | 595.657 | 22 | 121.9232 | 121.9232 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 65.4301 | 754.8057 | 0 | 0.05921 | 3.8841 | 0 | 0 | 176.972 | 121.9232 | off_peak | 742.4068 | 0 | 100 | 14.11 | 0 | 85.89 | 473.5577 | 0
760 | 858.26 | 382.882 | 21.8 | 78.4268 | 78.4268 | 0 | 0 | 8.9635 | 8.9635 | 0 | 0 | 0 | 73.8147 | 788.7968 | 0 | 0.05921 | 3.8974 | 0 | 0 | 176.972 | 78.4268 | off_peak | 779.8332 | 0 | 100 | 9.14 | 0 | 90.86 | 305.6604 | 0
761 | 816.78 | 270.735 | 21.2 | 55.5738 | 55.5738 | 0 | 0 | 0.57892 | 0.57892 | 0 | 0 | 0 | 74.3563 | 761.7851 | 0 | 0.05921 | 4.0465 | 0 | 0 | 176.972 | 55.5738 | off_peak | 761.2062 | 0 | 100 | 6.8 | 0 | 93.2 | 224.8811 | 0
762 | 831.8 | 77.8842 | 20.5 | 16.027 | 16.027 | 0 | 0 | 0.03739 | 0.03739 | 0 | 0 | 0 | 74.3912 | 815.8103 | 0 | 0.05921 | 4.362 | 0 | 0 | 176.972 | 16.027 | off_peak | 815.773 | 0 | 100 | 1.93 | 0 | 98.07 | 69.9106 | 0
763 | 771.31 | 0 | 20.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3912 | 771.31 | 0 | 0.088511 | 4.6223 | 0 | 0 | 176.972 | 0 | on_peak | 771.31 |  |  | 0 | 0 | 100 | 0 | 0
764 | 782.52 | 0 | 19.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3912 | 782.52 | 0 | 0.088511 | 4.9385 | 0 | 0 | 176.972 | 0 | on_peak | 782.52 |  |  | 0 | 0 | 100 | 0 | 0
765 | 799.92 | 0 | 19.5 | 0 | 0 | 0 | 0 | 0 | 0 | 62.6277 | 62.6277 | 0 | 7.4394 | 737.2923 | 0 | 0.088511 | 5.202 | 0 | 0 | 176.972 | 0 | on_peak | 737.2923 |  |  | 0 | 7.83 | 92.17 | 0 | 0
766 | 701.57 | 0 | 19.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 701.57 | 0 | 0.088511 | 5.4827 | 0 | 0 | 176.972 | 0 | on_peak | 701.57 |  |  | 0 | 0 | 100 | 0 | 0
767 | 770.82 | 0 | 19.2 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 19.0375 | 783.2189 | 0 | 0.05921 | 5.9759 | 0 | 0 | 176.972 | 0 | off_peak | 770.82 | 0 | 100 | 0 | 0 | 100 | 0 | 0
768 | 732.78 | 0 | 19 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 30.6357 | 745.1789 | 0 | 0.05921 | 6.2184 | 0 | 0 | 176.972 | 0 | off_peak | 732.78 | 0 | 100 | 0 | 0 | 100 | 0 | 0
769 | 683.58 | 0 | 18.9 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 42.2338 | 695.9789 | 0 | 0.05921 | 6.3389 | 0 | 0 | 176.972 | 0 | off_peak | 683.58 | 0 | 100 | 0 | 0 | 100 | 0 | 0
770 | 620.71 | 0 | 18.7 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 53.832 | 633.1089 | 0 | 0.05921 | 6.2279 | 0 | 0 | 176.972 | 0 | off_peak | 620.71 | 0 | 100 | 0 | 0 | 100 | 0 | 0
771 | 570.63 | 0 | 18.4 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 65.4301 | 583.0289 | 0 | 0.05921 | 5.7243 | 0 | 0 | 176.972 | 0 | off_peak | 570.63 | 0 | 100 | 0 | 0 | 100 | 0 | 0
772 | 583.48 | 0 | 18.2 | 0 | 0 | 0 | 0 | 8.9635 | 8.9635 | 0 | 0 | 0 | 73.8147 | 592.4435 | 0 | 0.05921 | 5.2157 | 0 | 0 | 176.972 | 0 | off_peak | 583.48 | 0 | 100 | 0 | 0 | 100 | 0 | 0
773 | 581.35 | 0 | 17.9 | 0 | 0 | 0 | 0 | 0.57892 | 0.57892 | 0 | 0 | 0 | 74.3563 | 581.9289 | 0 | 0.05921 | 4.6321 | 0 | 0 | 176.972 | 0 | off_peak | 581.35 | 0 | 100 | 0 | 0 | 100 | 0 | 0
774 | 677.84 | 0 | 17.8 | 0 | 0 | 0 | 0 | 0.03739 | 0.03739 | 0 | 0 | 0 | 74.3912 | 677.8774 | 0 | 0.05921 | 3.9375 | 0 | 0 | 176.972 | 0 | off_peak | 677.84 | 0 | 100 | 0 | 0 | 100 | 0 | 0
775 | 755.84 | 0 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 62.6277 | 62.6277 | 0 | 7.4394 | 693.2123 | 0 | 0.088511 | 3.4715 | 0 | 0 | 176.972 | 0 | on_peak | 693.2123 |  |  | 0 | 8.29 | 91.71 | 0 | 0
776 | 798.77 | 50.2217 | 18.9 | 10.3932 | 10.3932 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 788.3768 | 0 | 0.088511 | 3.0963 | 0 | 0 | 176.972 | 10.3932 | on_peak | 788.3768 |  |  | 1.3 | 0 | 98.7 | 32.1802 | 0
777 | 754.5 | 199.353 | 20 | 41.0956 | 41.0956 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 713.4044 | 0 | 0.088511 | 2.8684 | 0 | 0 | 176.972 | 41.0956 | on_peak | 713.4044 |  |  | 5.45 | 0 | 94.55 | 117.8801 | 0
778 | 787.62 | 416.852 | 20.9 | 85.6585 | 85.6585 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 701.9615 | 0 | 0.088511 | 2.7631 | 0 | 0 | 176.972 | 85.6585 | on_peak | 701.9615 |  |  | 10.88 | 0 | 89.12 | 236.6854 | 0
779 | 768.43 | 395.98 | 21.6 | 81.1674 | 81.1674 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 19.0375 | 699.6615 | 0 | 0.05921 | 2.7768 | 0 | 0 | 176.972 | 81.1674 | off_peak | 687.2626 | 0 | 100 | 10.56 | 0 | 89.44 | 225.3873 | 0
780 | 837.15 | 546.962 | 21.9 | 111.9959 | 111.9959 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 30.6357 | 737.5531 | 0 | 0.05921 | 3.0569 | 0 | 0 | 176.972 | 111.9959 | off_peak | 725.1541 | 0 | 100 | 13.38 | 0 | 86.62 | 342.3571 | 0
781 | 806.58 | 543.638 | 22.1 | 111.236 | 111.236 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 42.2338 | 707.7429 | 0 | 0.05921 | 3.5575 | 0 | 0 | 176.972 | 111.236 | off_peak | 695.344 | 0 | 100 | 13.79 | 0 | 86.21 | 395.7219 | 0
782 | 823.06 | 604.122 | 22.2 | 123.5678 | 123.5678 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 53.832 | 711.8911 | 0 | 0.05921 | 3.9284 | 0 | 0 | 176.972 | 123.5678 | off_peak | 699.4922 | 0 | 100 | 15.01 | 0 | 84.99 | 485.4294 | 0
783 | 947.24 | 383.239 | 22.1 | 78.4161 | 78.4161 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 65.4301 | 881.2228 | 0 | 0.05921 | 3.9897 | 0 | 0 | 176.972 | 78.4161 | off_peak | 868.8239 | 0 | 100 | 8.28 | 0 | 91.72 | 312.8537 | 0
784 | 849.13 | 291.823 | 21.9 | 59.7536 | 59.7536 | 0 | 0 | 8.9635 | 8.9635 | 0 | 0 | 0 | 73.8147 | 798.3399 | 0 | 0.05921 | 3.9289 | 0 | 0 | 176.972 | 59.7536 | off_peak | 789.3764 | 0 | 100 | 7.04 | 0 | 92.96 | 234.7653 | 0
785 | 872.44 | 189.874 | 21.4 | 38.9478 | 38.9478 | 0 | 0 | 0.57892 | 0.57892 | 0 | 0 | 0 | 74.3563 | 834.0711 | 0 | 0.05921 | 4.0003 | 0 | 0 | 176.972 | 38.9478 | off_peak | 833.4922 | 0 | 100 | 4.46 | 0 | 95.54 | 155.804 | 0
786 | 865.97 | 68.0082 | 20.8 | 13.9799 | 13.9799 | 0 | 0 | 0.03739 | 0.03739 | 0 | 0 | 0 | 74.3912 | 852.0275 | 0 | 0.05921 | 4.2816 | 0 | 0 | 176.972 | 13.9799 | off_peak | 851.9901 | 0 | 100 | 1.61 | 0 | 98.39 | 59.8562 | 0
787 | 786.47 | 0 | 20.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3912 | 786.47 | 0 | 0.088511 | 4.662 | 0 | 0 | 176.972 | 0 | on_peak | 786.47 |  |  | 0 | 0 | 100 | 0 | 0
788 | 861.73 | 0 | 20.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3912 | 861.73 | 0 | 0.088511 | 5.0084 | 0 | 0 | 176.972 | 0 | on_peak | 861.73 |  |  | 0 | 0 | 100 | 0 | 0
789 | 813.37 | 0 | 20.3 | 0 | 0 | 0 | 0 | 0 | 0 | 62.6277 | 62.6277 | 0 | 7.4394 | 750.7423 | 0 | 0.088511 | 5.2514 | 0 | 0 | 176.972 | 0 | on_peak | 750.7423 |  |  | 0 | 7.7 | 92.3 | 0 | 0
790 | 763.94 | 0 | 20.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 763.94 | 0 | 0.088511 | 5.5529 | 0 | 0 | 176.972 | 0 | on_peak | 763.94 |  |  | 0 | 0 | 100 | 0 | 0
791 | 794.19 | 0 | 20.2 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 19.0375 | 806.5889 | 0 | 0.05921 | 5.999 | 0 | 0 | 176.972 | 0 | off_peak | 794.19 | 0 | 100 | 0 | 0 | 100 | 0 | 0
792 | 768.99 | 0 | 20.1 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 30.6357 | 781.3889 | 0 | 0.05921 | 6.3001 | 0 | 0 | 176.972 | 0 | off_peak | 768.99 | 0 | 100 | 0 | 0 | 100 | 0 | 0
793 | 715.39 | 0 | 20.1 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 42.2338 | 727.7889 | 0 | 0.05921 | 6.4211 | 0 | 0 | 176.972 | 0 | off_peak | 715.39 | 0 | 100 | 0 | 0 | 100 | 0 | 0
794 | 662.38 | 0 | 20 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 53.832 | 674.7789 | 0 | 0.05921 | 6.2438 | 0 | 0 | 176.972 | 0 | off_peak | 662.38 | 0 | 100 | 0 | 0 | 100 | 0 | 0
795 | 606.7 | 0 | 19.6 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 65.4301 | 619.0989 | 0 | 0.05921 | 5.7598 | 0 | 0 | 176.972 | 0 | off_peak | 606.7 | 0 | 100 | 0 | 0 | 100 | 0 | 0
796 | 620.23 | 0 | 19 | 0 | 0 | 0 | 0 | 8.9635 | 8.9635 | 0 | 0 | 0 | 73.8147 | 629.1935 | 0 | 0.05921 | 5.3135 | 0 | 0 | 176.972 | 0 | off_peak | 620.23 | 0 | 100 | 0 | 0 | 100 | 0 | 0
797 | 632.79 | 0 | 18.4 | 0 | 0 | 0 | 0 | 0.57892 | 0.57892 | 0 | 0 | 0 | 74.3563 | 633.3689 | 0 | 0.05921 | 4.6988 | 0 | 0 | 176.972 | 0 | off_peak | 632.79 | 0 | 100 | 0 | 0 | 100 | 0 | 0
798 | 689.82 | 0 | 17.7 | 0 | 0 | 0 | 0 | 0.03739 | 0.03739 | 0 | 0 | 0 | 74.3912 | 689.8574 | 0 | 0.05921 | 3.9933 | 0 | 0 | 176.972 | 0 | off_peak | 689.82 | 0 | 100 | 0 | 0 | 100 | 0 | 0
799 | 719 | 0 | 17.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3912 | 719 | 0 | 0.088511 | 3.6013 | 0 | 0 | 176.972 | 0 | on_peak | 719 |  |  | 0 | 0 | 100 | 0 | 0
800 | 767 | 40.2803 | 17.4 | 8.3799 | 8.3799 | 0 | 0 | 0 | 0 | 62.6277 | 62.6277 | 0 | 7.4394 | 695.9923 | 0 | 0.088511 | 3.2746 | 0 | 0 | 176.972 | 8.3799 | on_peak | 695.9923 |  |  | 1.09 | 8.17 | 90.74 | 27.441 | 0
801 | 809.33 | 63.765 | 18.1 | 13.2332 | 13.2332 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 796.0968 | 0 | 0.088511 | 3.0166 | 0 | 0 | 176.972 | 13.2332 | on_peak | 796.0968 |  |  | 1.64 | 0 | 98.36 | 39.9194 | 0
802 | 839.23 | 33.25 | 19.3 | 6.8713 | 6.8713 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 832.3587 | 0 | 0.088511 | 2.8956 | 0 | 0 | 176.972 | 6.8713 | on_peak | 832.3587 |  |  | 0.82 | 0 | 99.18 | 19.8964 | 0
803 | 834.27 | 93.1 | 20.6 | 19.1514 | 19.1514 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 19.0375 | 827.5176 | 0 | 0.05921 | 2.9348 | 0 | 0 | 176.972 | 19.1514 | off_peak | 815.1186 | 0 | 100 | 2.3 | 0 | 97.7 | 56.2048 | 0
804 | 885.14 | 177.65 | 21.4 | 36.4403 | 36.4403 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 30.6357 | 861.0986 | 0 | 0.05921 | 3.2074 | 0 | 0 | 176.972 | 36.4403 | off_peak | 848.6997 | 0 | 100 | 4.12 | 0 | 95.88 | 116.8787 | 0
805 | 812.45 | 307.601 | 21.9 | 62.9843 | 62.9843 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 42.2338 | 761.8646 | 0 | 0.05921 | 3.7498 | 0 | 0 | 176.972 | 62.9843 | off_peak | 749.4657 | 0 | 100 | 7.75 | 0 | 92.25 | 236.1761 | 0
806 | 783.74 | 349.778 | 22.2 | 71.544 | 59.1451 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 0 | 53.832 | 724.5949 | 0 | 0.05921 | 4.1002 | 0 | 0 | 188.5702 | 59.1451 | off_peak | 724.5949 | 100 | 0 | 7.55 | 0 | 92.45 | 242.508 | 0
807 | 821.51 | 152.95 | 22.2 | 31.2846 | 31.2846 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 65.4301 | 802.6244 | 0 | 0.05921 | 4.3541 | 0 | 0 | 188.5702 | 31.2846 | off_peak | 790.2254 | 0 | 100 | 3.81 | 0 | 96.19 | 136.2169 | 0
808 | 795.45 | 75.05 | 22 | 15.3618 | 15.3618 | 0 | 0 | 8.9635 | 8.9635 | 0 | 0 | 0 | 73.8147 | 789.0518 | 0 | 0.05921 | 4.5444 | 0 | 0 | 188.5702 | 15.3618 | off_peak | 780.0882 | 0 | 100 | 1.93 | 0 | 98.07 | 69.8093 | 0
809 | 793.29 | 143.136 | 21.3 | 29.3711 | 29.3711 | 0 | 0 | 0.57892 | 0.57892 | 0 | 0 | 0 | 74.3563 | 764.4978 | 0 | 0.05921 | 4.5263 | 0 | 0 | 188.5702 | 29.3711 | off_peak | 763.9189 | 0 | 100 | 3.7 | 0 | 96.3 | 132.9428 | 0
810 | 768.62 | 69.4012 | 20.4 | 14.2865 | 14.2865 | 0 | 0 | 0.03739 | 0.03739 | 0 | 0 | 0 | 74.3912 | 754.3709 | 0 | 0.05921 | 4.6932 | 0 | 0 | 188.5702 | 14.2865 | off_peak | 754.3335 | 0 | 100 | 1.86 | 0 | 98.14 | 67.0491 | 0
811 | 760.19 | 0 | 20.1 | 0 | 0 | 0 | 0 | 0 | 0 | 62.6277 | 62.6277 | 0 | 7.4394 | 697.5623 | 0 | 0.088511 | 4.8955 | 0 | 0 | 188.5702 | 0 | on_peak | 697.5623 |  |  | 0 | 8.24 | 91.76 | 0 | 0
812 | 729.21 | 0 | 19.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 729.21 | 0 | 0.088511 | 5.0994 | 0 | 0 | 188.5702 | 0 | on_peak | 729.21 |  |  | 0 | 0 | 100 | 0 | 0
813 | 693.72 | 0 | 19.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 693.72 | 0 | 0.088511 | 5.3727 | 0 | 0 | 188.5702 | 0 | on_peak | 693.72 |  |  | 0 | 0 | 100 | 0 | 0
814 | 695.78 | 0 | 19.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 695.78 | 0 | 0.088511 | 5.5618 | 0 | 0 | 188.5702 | 0 | on_peak | 695.78 |  |  | 0 | 0 | 100 | 0 | 0
815 | 724.2 | 0 | 18.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 724.2 | 0 | 0.05921 | 5.6175 | 0 | 0 | 188.5702 | 0 | off_peak | 724.2 |  |  | 0 | 0 | 100 | 0 | 0
816 | 698.66 | 0 | 18.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 698.66 | 0 | 0.05921 | 5.8373 | 0 | 0 | 188.5702 | 0 | off_peak | 698.66 |  |  | 0 | 0 | 100 | 0 | 0
817 | 614.29 | 0 | 17.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 614.29 | 0 | 0.05921 | 5.7661 | 0 | 0 | 188.5702 | 0 | off_peak | 614.29 |  |  | 0 | 0 | 100 | 0 | 0
818 | 554.97 | 0 | 17.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 554.97 | 0 | 0.05921 | 5.5105 | 0 | 0 | 188.5702 | 0 | off_peak | 554.97 |  |  | 0 | 0 | 100 | 0 | 0
819 | 555.14 | 0 | 16.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 555.14 | 0 | 0.05921 | 5.1068 | 0 | 0 | 188.5702 | 0 | off_peak | 555.14 |  |  | 0 | 0 | 100 | 0 | 0
820 | 533.34 | 0 | 16.3 | 0 | 0 | 0 | 0 | 8.7263 | 8.7263 | 0 | 0 | 0 | 15.6021 | 542.0663 | 0 | 0.05921 | 4.8104 | 0 | 0 | 188.5702 | 0 | off_peak | 533.34 | 0 | 100 | 0 | 0 | 100 | 0 | 0
821 | 529.5 | 0 | 15.9 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 27.2003 | 541.8989 | 0 | 0.05921 | 4.4784 | 0 | 0 | 188.5702 | 0 | off_peak | 529.5 | 0 | 100 | 0 | 0 | 100 | 0 | 0
822 | 604.41 | 0 | 15.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27.2003 | 604.41 | 0 | 0.05921 | 4.0069 | 0 | 0 | 188.5702 | 0 | off_peak | 604.41 |  |  | 0 | 0 | 100 | 0 | 0
823 | 681.99 | 0 | 15.6 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 38.7984 | 694.3889 | 0 | 0.05921 | 3.5743 | 0 | 0 | 188.5702 | 0 | off_peak | 681.99 | 0 | 100 | 0 | 0 | 100 | 0 | 0
824 | 811.58 | 44.4295 | 16.2 | 9.282 | 9.282 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 50.3966 | 814.6969 | 0 | 0.05921 | 3.3033 | 0 | 0 | 188.5702 | 9.282 | off_peak | 802.298 | 0 | 100 | 1.14 | 0 | 98.86 | 30.6612 | 0
825 | 792.97 | 216.455 | 17.2 | 45.0629 | 32.664 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 0 | 61.9947 | 760.306 | 0 | 0.05921 | 3.1065 | 0 | 0 | 200.1683 | 32.664 | off_peak | 760.306 | 100 | 0 | 4.12 | 0 | 95.88 | 101.4702 | 0
826 | 811.91 | 431.93 | 18.4 | 89.544 | 89.544 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 61.9947 | 722.366 | 0 | 0.05921 | 3.0123 | 0 | 0 | 200.1683 | 89.544 | off_peak | 722.366 |  |  | 11.03 | 0 | 88.97 | 269.7341 | 0
827 | 805.33 | 584.659 | 19.7 | 120.6524 | 120.6524 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 61.9947 | 684.6776 | 0 | 0.05921 | 3.0395 | 0 | 0 | 200.1683 | 120.6524 | off_peak | 684.6776 |  |  | 14.98 | 0 | 85.02 | 366.7221 | 0
828 | 811.89 | 686.857 | 20.7 | 141.2416 | 141.2416 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 61.9947 | 670.6484 | 0 | 0.05921 | 3.1561 | 0 | 0 | 200.1683 | 141.2416 | off_peak | 670.6484 |  |  | 17.4 | 0 | 82.6 | 445.7781 | 0
829 | 775.32 | 706.569 | 21.4 | 144.9345 | 144.9345 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 61.9947 | 630.3855 | 0 | 0.05921 | 3.4637 | 0 | 0 | 200.1683 | 144.9345 | off_peak | 630.3855 |  |  | 18.69 | 0 | 81.31 | 502.0113 | 0
830 | 756.45 | 472.472 | 21.9 | 96.7433 | 84.3444 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 0 | 73.5928 | 672.1056 | 0 | 0.05921 | 3.9078 | 0 | 0 | 211.7664 | 84.3444 | off_peak | 672.1056 | 100 | 0 | 11.15 | 0 | 88.85 | 329.6051 | 0
831 | 709.99 | 464.419 | 22.1 | 95.0267 | 95.0267 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 73.5928 | 614.9633 | 0 | 0.05921 | 3.9574 | 0 | 0 | 211.7664 | 95.0267 | off_peak | 614.9633 |  |  | 13.38 | 0 | 86.62 | 376.0576 | 0
832 | 606.17 | 273.029 | 22.1 | 55.8656 | 55.8656 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 73.5928 | 550.3044 | 0 | 0.05921 | 3.7826 | 0 | 0 | 211.7664 | 55.8656 | off_peak | 550.3044 |  |  | 9.22 | 0 | 90.78 | 211.3145 | 0
833 | 623.32 | 204.135 | 21.5 | 41.8582 | 41.8582 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 73.5928 | 581.4618 | 0 | 0.05921 | 3.6709 | 0 | 0 | 211.7664 | 41.8582 | off_peak | 581.4618 |  |  | 6.72 | 0 | 93.28 | 153.6558 | 0
834 | 560.71 | 58.8526 | 20.8 | 12.0978 | 11.2971 | 0 | 0.80079 | 0.80079 | 0 | 0 | 0 | 0 | 74.3419 | 549.4129 | 0 | 0.05921 | 3.757 | 0 | 0 | 212.5155 | 11.2971 | off_peak | 549.4129 | 100 | 0 | 2.01 | 0 | 97.99 | 42.4433 | 0
835 | 566.52 | 0 | 20.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3419 | 566.52 | 0 | 0.05921 | 3.7244 | 0 | 0 | 212.5155 | 0 | off_peak | 566.52 |  |  | 0 | 0 | 100 | 0 | 0
836 | 541.41 | 0 | 20.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3419 | 541.41 | 0 | 0.05921 | 3.6201 | 0 | 0 | 212.5155 | 0 | off_peak | 541.41 |  |  | 0 | 0 | 100 | 0 | 0
837 | 507.26 | 0 | 20.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3419 | 507.26 | 0 | 0.05921 | 3.6263 | 0 | 0 | 212.5155 | 0 | off_peak | 507.26 |  |  | 0 | 0 | 100 | 0 | 0
838 | 509.91 | 0 | 20.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3419 | 509.91 | 0 | 0.05921 | 3.7877 | 0 | 0 | 212.5155 | 0 | off_peak | 509.91 |  |  | 0 | 0 | 100 | 0 | 0
839 | 478.19 | 0 | 20.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3419 | 478.19 | 0 | 0.05921 | 3.8821 | 0 | 0 | 212.5155 | 0 | off_peak | 478.19 |  |  | 0 | 0 | 100 | 0 | 0
840 | 479.47 | 0 | 20.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3419 | 479.47 | 0 | 0.05921 | 4.3683 | 0 | 0 | 212.5155 | 0 | off_peak | 479.47 |  |  | 0 | 0 | 100 | 0 | 0
841 | 483.24 | 0 | 20.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3419 | 483.24 | 0 | 0.05921 | 4.5858 | 0 | 0 | 212.5155 | 0 | off_peak | 483.24 |  |  | 0 | 0 | 100 | 0 | 0
842 | 483.02 | 0 | 19.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3419 | 483.02 | 0 | 0.05921 | 4.5374 | 0 | 0 | 212.5155 | 0 | off_peak | 483.02 |  |  | 0 | 0 | 100 | 0 | 0
843 | 455.08 | 0 | 19.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3419 | 455.08 | 0 | 0.05921 | 4.3521 | 0 | 0 | 212.5155 | 0 | off_peak | 455.08 |  |  | 0 | 0 | 100 | 0 | 0
844 | 479.94 | 0 | 19.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3419 | 479.94 | 0 | 0.05921 | 4.1617 | 0 | 0 | 212.5155 | 0 | off_peak | 479.94 |  |  | 0 | 0 | 100 | 0 | 0
845 | 509.84 | 0 | 19.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3419 | 509.84 | 0 | 0.05921 | 3.9502 | 0 | 0 | 212.5155 | 0 | off_peak | 509.84 |  |  | 0 | 0 | 100 | 0 | 0
846 | 633.48 | 0 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3419 | 633.48 | 0 | 0.05921 | 3.6557 | 0 | 0 | 212.5155 | 0 | off_peak | 633.48 |  |  | 0 | 0 | 100 | 0 | 0
847 | 725.53 | 0 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3419 | 725.53 | 0 | 0.05921 | 3.2936 | 0 | 0 | 212.5155 | 0 | off_peak | 725.53 |  |  | 0 | 0 | 100 | 0 | 0
848 | 721.56 | 44.0446 | 19.7 | 9.0892 | 9.0892 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3419 | 712.4708 | 0 | 0.05921 | 3.0046 | 0 | 0 | 212.5155 | 9.0892 | off_peak | 712.4708 |  |  | 1.26 | 0 | 98.74 | 27.3099 | 0
849 | 738.17 | 232.118 | 20.8 | 47.7146 | 47.7146 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3419 | 690.4554 | 0 | 0.05921 | 2.8157 | 0 | 0 | 212.5155 | 47.7146 | off_peak | 690.4554 |  |  | 6.46 | 0 | 93.54 | 134.35 | 0
850 | 725.86 | 421.069 | 21.9 | 86.218 | 86.218 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3419 | 639.642 | 0 | 0.05921 | 2.732 | 0 | 0 | 212.5155 | 86.218 | off_peak | 639.642 |  |  | 11.88 | 0 | 88.12 | 235.5438 | 0
851 | 689.97 | 521.73 | 22.7 | 106.5251 | 106.5251 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3419 | 583.4449 | 0 | 0.05921 | 2.7003 | 0 | 0 | 212.5155 | 106.5251 | off_peak | 583.4449 |  |  | 15.44 | 0 | 84.56 | 287.6503 | 0
852 | 719.79 | 678.963 | 23.2 | 138.3809 | 138.3809 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3419 | 581.4091 | 0 | 0.05921 | 2.7905 | 0 | 0 | 212.5155 | 138.3809 | off_peak | 581.4091 |  |  | 19.23 | 0 | 80.77 | 386.1551 | 0
853 | 651.77 | 679.356 | 23.5 | 138.3125 | 138.3125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3419 | 513.4575 | 0 | 0.05921 | 2.9782 | 0 | 0 | 212.5155 | 138.3125 | off_peak | 513.4575 |  |  | 21.22 | 0 | 78.78 | 411.9263 | 0
854 | 682.65 | 561.42 | 23.7 | 114.2196 | 114.2196 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3419 | 568.4304 | 0 | 0.05921 | 3.276 | 0 | 0 | 212.5155 | 114.2196 | off_peak | 568.4304 |  |  | 16.73 | 0 | 83.27 | 374.1823 | 0
855 | 698.96 | 598.416 | 23.8 | 121.7027 | 121.7027 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3419 | 577.2573 | 0 | 0.05921 | 3.6748 | 0 | 0 | 212.5155 | 121.7027 | off_peak | 577.2573 |  |  | 17.41 | 0 | 82.59 | 447.2312 | 0
856 | 659.02 | 451.607 | 23.8 | 91.8455 | 91.8455 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3419 | 567.1745 | 0 | 0.05921 | 3.9982 | 0 | 0 | 212.5155 | 91.8455 | off_peak | 567.1745 |  |  | 13.94 | 0 | 86.06 | 367.2204 | 0
857 | 655.85 | 259.653 | 23.3 | 52.9015 | 52.9015 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3419 | 602.9485 | 0 | 0.05921 | 4.063 | 0 | 0 | 212.5155 | 52.9015 | off_peak | 602.9485 |  |  | 8.07 | 0 | 91.93 | 214.9369 | 0
858 | 617 | 53.9248 | 22.6 | 11.0141 | 11.0141 | 0 | 0 | 0.05172 | 0.05172 | 0 | 0 | 0 | 74.3903 | 606.0376 | 0 | 0.05921 | 3.9215 | 0 | 0 | 212.5155 | 11.0141 | off_peak | 605.9859 | 0 | 100 | 1.79 | 0 | 98.21 | 43.1917 | 0
859 | 577.44 | 0 | 22.3 | 0 | 0 | 0 | 0 | 0.0033404 | 0.0033404 | 0 | 0 | 0 | 74.3934 | 577.4433 | 0 | 0.05921 | 3.9591 | 0 | 0 | 212.5155 | 0 | off_peak | 577.44 | 0 | 100 | 0 | 0 | 100 | 0 | 0
860 | 581.11 | 0 | 21.9 | 0 | 0 | 0 | 0 | 0.00021574 | 0.00021574 | 0 | 0 | 0 | 74.3936 | 581.1102 | 0 | 0.05921 | 4.1491 | 0 | 0 | 212.5155 | 0 | off_peak | 581.11 | 0 | 100 | 0 | 0 | 100 | 0 | 0
861 | 549.36 | 0 | 21.7 | 0 | 0 | 0 | 0 | 1.4896e-05 | 1.4896e-05 | 0 | 0 | 0 | 74.3936 | 549.36 | 0 | 0.05921 | 4.363 | 0 | 0 | 212.5155 | 0 | off_peak | 549.36 | 0 | 100 | 0 | 0 | 100 | 0 | 0
862 | 539.75 | 0 | 21.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 539.75 | 0 | 0.05921 | 4.3536 | 0 | 0 | 212.5155 | 0 | off_peak | 539.75 |  |  | 0 | 0 | 100 | 0 | 0
863 | 559.92 | 0 | 21.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 559.92 | 0 | 0.05921 | 4.5217 | 0 | 0 | 212.5155 | 0 | off_peak | 559.92 |  |  | 0 | 0 | 100 | 0 | 0
864 | 546.53 | 0 | 21.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 546.53 | 0 | 0.05921 | 4.8587 | 0 | 0 | 212.5155 | 0 | off_peak | 546.53 |  |  | 0 | 0 | 100 | 0 | 0
865 | 550.88 | 0 | 21.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 550.88 | 0 | 0.05921 | 5.105 | 0 | 0 | 212.5155 | 0 | off_peak | 550.88 |  |  | 0 | 0 | 100 | 0 | 0
866 | 528.21 | 0 | 21.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 528.21 | 0 | 0.05921 | 5.1079 | 0 | 0 | 212.5155 | 0 | off_peak | 528.21 |  |  | 0 | 0 | 100 | 0 | 0
867 | 538.36 | 0 | 21.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 538.36 | 0 | 0.05921 | 4.8069 | 0 | 0 | 212.5155 | 0 | off_peak | 538.36 |  |  | 0 | 0 | 100 | 0 | 0
868 | 553.13 | 0 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 553.13 | 0 | 0.05921 | 4.4686 | 0 | 0 | 212.5155 | 0 | off_peak | 553.13 |  |  | 0 | 0 | 100 | 0 | 0
869 | 556.1 | 0 | 20.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 556.1 | 0 | 0.05921 | 3.9939 | 0 | 0 | 212.5155 | 0 | off_peak | 556.1 |  |  | 0 | 0 | 100 | 0 | 0
870 | 670.37 | 0 | 20.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 670.37 | 0 | 0.05921 | 3.5001 | 0 | 0 | 212.5155 | 0 | off_peak | 670.37 |  |  | 0 | 0 | 100 | 0 | 0
871 | 703.96 | 0 | 20.8 | 0 | 0 | 0 | 0 | 0 | 0 | 62.63 | 62.63 | 0 | 7.4394 | 641.33 | 0 | 0.088511 | 3.0041 | 0 | 0 | 212.5155 | 0 | on_peak | 641.33 |  |  | 0 | 8.9 | 91.1 | 0 | 0
872 | 780.33 | 53.396 | 21.5 | 10.9489 | 10.9489 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 769.3811 | 0 | 0.088511 | 2.7644 | 0 | 0 | 212.5155 | 10.9489 | on_peak | 769.3811 |  |  | 1.4 | 0 | 98.6 | 30.2673 | 0
873 | 803.24 | 238.161 | 22.5 | 48.6617 | 48.6617 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 754.5783 | 0 | 0.088511 | 2.5479 | 0 | 0 | 212.5155 | 48.6617 | on_peak | 754.5783 |  |  | 6.06 | 0 | 93.94 | 123.9827 | 0
874 | 834.74 | 376.899 | 23.5 | 76.7342 | 76.7342 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 758.0058 | 0 | 0.088511 | 2.507 | 0 | 0 | 212.5155 | 76.7342 | on_peak | 758.0058 |  |  | 9.19 | 0 | 90.81 | 192.3743 | 0
875 | 829.43 | 275.252 | 24 | 55.9392 | 55.9392 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 19.0375 | 785.8898 | 0 | 0.05921 | 2.6187 | 0 | 0 | 212.5155 | 55.9392 | off_peak | 773.4908 | 0 | 100 | 6.74 | 0 | 93.26 | 146.489 | 0
876 | 872.13 | 257.242 | 24.4 | 52.204 | 52.204 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 30.6357 | 832.3249 | 0 | 0.05921 | 2.9885 | 0 | 0 | 212.5155 | 52.204 | off_peak | 819.926 | 0 | 100 | 5.99 | 0 | 94.01 | 156.0118 | 0
877 | 837.88 | 171.95 | 24.6 | 34.87 | 34.87 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 42.2338 | 815.4089 | 0 | 0.05921 | 3.6003 | 0 | 0 | 212.5155 | 34.87 | off_peak | 803.01 | 0 | 100 | 4.16 | 0 | 95.84 | 125.5414 | 0
878 | 870.9 | 193.712 | 24.7 | 39.269 | 39.269 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 53.832 | 844.0299 | 0 | 0.05921 | 3.9983 | 0 | 0 | 212.5155 | 39.269 | off_peak | 831.631 | 0 | 100 | 4.51 | 0 | 95.49 | 157.0084 | 0
879 | 865.94 | 152.95 | 24.7 | 31.0058 | 31.0058 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 65.4301 | 847.3331 | 0 | 0.05921 | 3.7826 | 0 | 0 | 212.5155 | 31.0058 | off_peak | 834.9342 | 0 | 100 | 3.58 | 0 | 96.42 | 117.2823 | 0
880 | 868.87 | 313.392 | 24.5 | 63.5761 | 63.5761 | 0 | 0 | 8.9635 | 8.9635 | 0 | 0 | 0 | 73.8147 | 814.2574 | 0 | 0.05921 | 3.431 | 0 | 0 | 212.5155 | 63.5761 | off_peak | 805.2939 | 0 | 100 | 7.32 | 0 | 92.68 | 218.1308 | 0
881 | 862.05 | 233.182 | 24 | 47.3893 | 47.3893 | 0 | 0 | 0.57892 | 0.57892 | 0 | 0 | 0 | 74.3563 | 815.2396 | 0 | 0.05921 | 3.2823 | 0 | 0 | 212.5155 | 47.3893 | off_peak | 814.6607 | 0 | 100 | 5.5 | 0 | 94.5 | 155.5448 | 0
882 | 811 | 84.0306 | 23.3 | 17.1203 | 17.1203 | 0 | 0 | 0.03739 | 0.03739 | 0 | 0 | 0 | 74.3912 | 793.9171 | 0 | 0.05921 | 3.2819 | 0 | 0 | 212.5155 | 17.1203 | off_peak | 793.8797 | 0 | 100 | 2.11 | 0 | 97.89 | 56.1871 | 0
883 | 785.66 | 0 | 23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3912 | 785.66 | 0 | 0.088511 | 3.4289 | 0 | 0 | 212.5155 | 0 | on_peak | 785.66 |  |  | 0 | 0 | 100 | 0 | 0
884 | 787.98 | 0 | 22.6 | 0 | 0 | 0 | 0 | 0 | 0 | 62.6277 | 62.6277 | 0 | 7.4394 | 725.3523 | 0 | 0.088511 | 3.5026 | 62.6277 | 0 | 145.5637 | 62.6277 | on_peak | 725.3523 |  |  | 0 | 7.95 | 92.05 | 219.359 | 0
885 | 770.12 | 0 | 22.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 770.12 | 0 | 0.088511 | 3.5807 | 0 | 0 | 145.5637 | 0 | on_peak | 770.12 |  |  | 0 | 0 | 100 | 0 | 0
886 | 754.06 | 0 | 22.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 754.06 | 0 | 0.088511 | 3.93 | 0 | 0 | 145.5637 | 0 | on_peak | 754.06 |  |  | 0 | 0 | 100 | 0 | 0
887 | 787.15 | 0 | 22.1 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 19.0375 | 799.5489 | 0 | 0.05921 | 4.4081 | 0 | 0 | 145.5637 | 0 | off_peak | 787.15 | 0 | 100 | 0 | 0 | 100 | 0 | 0
888 | 744.47 | 0 | 21.9 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 30.6357 | 756.8689 | 0 | 0.05921 | 5.0598 | 0 | 0 | 145.5637 | 0 | off_peak | 744.47 | 0 | 100 | 0 | 0 | 100 | 0 | 0
889 | 730.07 | 0 | 21.8 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 42.2338 | 742.4689 | 0 | 0.05921 | 5.4545 | 0 | 0 | 145.5637 | 0 | off_peak | 730.07 | 0 | 100 | 0 | 0 | 100 | 0 | 0
890 | 627.71 | 0 | 21.8 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 53.832 | 640.1089 | 0 | 0.05921 | 5.4065 | 0 | 0 | 145.5637 | 0 | off_peak | 627.71 | 0 | 100 | 0 | 0 | 100 | 0 | 0
891 | 618.58 | 0 | 21.7 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 65.4301 | 630.9789 | 0 | 0.05921 | 5.0752 | 0 | 0 | 145.5637 | 0 | off_peak | 618.58 | 0 | 100 | 0 | 0 | 100 | 0 | 0
892 | 574.87 | 0 | 21.6 | 0 | 0 | 0 | 0 | 8.9635 | 8.9635 | 0 | 0 | 0 | 73.8147 | 583.8335 | 0 | 0.05921 | 4.6169 | 0 | 0 | 145.5637 | 0 | off_peak | 574.87 | 0 | 100 | 0 | 0 | 100 | 0 | 0
893 | 602.88 | 0 | 21.6 | 0 | 0 | 0 | 0 | 0.57892 | 0.57892 | 0 | 0 | 0 | 74.3563 | 603.4589 | 0 | 0.05921 | 4.1116 | 0 | 0 | 145.5637 | 0 | off_peak | 602.88 | 0 | 100 | 0 | 0 | 100 | 0 | 0
894 | 702.73 | 0 | 21.6 | 0 | 0 | 0 | 0 | 0.03739 | 0.03739 | 0 | 0 | 0 | 74.3912 | 702.7674 | 0 | 0.05921 | 3.5113 | 0 | 0 | 145.5637 | 0 | off_peak | 702.73 | 0 | 100 | 0 | 0 | 100 | 0 | 0
895 | 816.77 | 0 | 21.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3912 | 816.77 | 0 | 0.088511 | 2.9714 | 0 | 0 | 145.5637 | 0 | on_peak | 816.77 |  |  | 0 | 0 | 100 | 0 | 0
896 | 835.04 | 55.8625 | 22.6 | 11.4099 | 11.4099 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3912 | 823.6301 | 0 | 0.088511 | 2.7505 | 0 | 0 | 145.5637 | 11.4099 | on_peak | 823.6301 |  |  | 1.37 | 0 | 98.63 | 31.3829 | 0
897 | 879.65 | 195.362 | 23.4 | 39.7887 | 39.7887 | 0 | 0 | 0 | 0 | 62.6277 | 62.6277 | 0 | 7.4394 | 777.2336 | 0 | 0.088511 | 2.6141 | 0 | 0 | 145.5637 | 39.7887 | on_peak | 777.2336 |  |  | 4.52 | 7.12 | 88.36 | 104.0104 | 0
898 | 886.82 | 132.377 | 23.8 | 26.9221 | 26.9221 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 859.8979 | 0 | 0.088511 | 2.5656 | 0 | 0 | 145.5637 | 26.9221 | on_peak | 859.8979 |  |  | 3.04 | 0 | 96.96 | 69.0703 | 0
899 | 862.12 | 236.418 | 24.2 | 48.0125 | 48.0125 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 19.0375 | 826.5064 | 0 | 0.05921 | 2.6773 | 0 | 0 | 145.5637 | 48.0125 | off_peak | 814.1075 | 0 | 100 | 5.57 | 0 | 94.43 | 128.5442 | 0
900 | 897.07 | 326.977 | 24.5 | 66.332 | 66.332 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 30.6357 | 843.1369 | 0 | 0.05921 | 2.9652 | 0 | 0 | 145.5637 | 66.332 | off_peak | 830.738 | 0 | 100 | 7.39 | 0 | 92.61 | 196.688 | 0
901 | 884.46 | 681.619 | 24.6 | 138.2266 | 138.2266 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 42.2338 | 758.6323 | 0 | 0.05921 | 3.587 | 0 | 0 | 145.5637 | 138.2266 | off_peak | 746.2334 | 0 | 100 | 15.63 | 0 | 84.37 | 495.8216 | 0
902 | 861.46 | 698.791 | 24.8 | 141.6071 | 141.6071 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 53.832 | 732.2519 | 0 | 0.05921 | 3.9318 | 0 | 0 | 145.5637 | 141.6071 | off_peak | 719.8529 | 0 | 100 | 16.44 | 0 | 83.56 | 556.7669 | 0
903 | 893.08 | 585.146 | 24.8 | 118.5774 | 106.1784 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 0 | 65.4301 | 786.9016 | 0 | 0.05921 | 3.7767 | 0 | 0 | 157.1618 | 106.1784 | off_peak | 786.9016 | 100 | 0 | 11.89 | 0 | 88.11 | 401.0079 | 0
904 | 831.29 | 455.589 | 24.8 | 92.3232 | 92.3232 | 0 | 0 | 8.9635 | 8.9635 | 0 | 0 | 0 | 73.8147 | 747.9303 | 0 | 0.05921 | 3.2653 | 0 | 0 | 157.1618 | 92.3232 | off_peak | 738.9668 | 0 | 100 | 11.11 | 0 | 88.89 | 301.4591 | 0
905 | 831.39 | 245.026 | 24.3 | 49.7428 | 49.7428 | 0 | 0 | 0.57892 | 0.57892 | 0 | 0 | 0 | 74.3563 | 782.2261 | 0 | 0.05921 | 3.1092 | 0 | 0 | 157.1618 | 49.7428 | off_peak | 781.6472 | 0 | 100 | 5.98 | 0 | 94.02 | 154.6598 | 0
906 | 855.68 | 87.5828 | 23.7 | 17.8185 | 17.8185 | 0 | 0 | 0.03739 | 0.03739 | 0 | 0 | 0 | 74.3912 | 837.8989 | 0 | 0.05921 | 3.1025 | 0 | 0 | 157.1618 | 17.8185 | off_peak | 837.8615 | 0 | 100 | 2.08 | 0 | 97.92 | 55.2818 | 0
907 | 783.68 | 0 | 23.3 | 0 | 0 | 0 | 0 | 0 | 0 | 62.6277 | 62.6277 | 0 | 7.4394 | 721.0523 | 0 | 0.088511 | 3.3014 | 0 | 0 | 157.1618 | 0 | on_peak | 721.0523 |  |  | 0 | 7.99 | 92.01 | 0 | 0
908 | 798.97 | 0 | 23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 798.97 | 0 | 0.088511 | 3.455 | 0 | 0 | 157.1618 | 0 | on_peak | 798.97 |  |  | 0 | 0 | 100 | 0 | 0
909 | 786.92 | 0 | 22.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 786.92 | 0 | 0.088511 | 3.6557 | 0 | 0 | 157.1618 | 0 | on_peak | 786.92 |  |  | 0 | 0 | 100 | 0 | 0
910 | 741.8 | 0 | 22.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 741.8 | 0 | 0.088511 | 3.9832 | 0 | 0 | 157.1618 | 0 | on_peak | 741.8 |  |  | 0 | 0 | 100 | 0 | 0
911 | 788.52 | 0 | 22.4 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 19.0375 | 800.9189 | 0 | 0.05921 | 4.3682 | 0 | 0 | 157.1618 | 0 | off_peak | 788.52 | 0 | 100 | 0 | 0 | 100 | 0 | 0
912 | 777.92 | 0 | 22.3 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 30.6357 | 790.3189 | 0 | 0.05921 | 4.9268 | 0 | 0 | 157.1618 | 0 | off_peak | 777.92 | 0 | 100 | 0 | 0 | 100 | 0 | 0
913 | 728.89 | 0 | 22.1 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 42.2338 | 741.2889 | 0 | 0.05921 | 5.1964 | 0 | 0 | 157.1618 | 0 | off_peak | 728.89 | 0 | 100 | 0 | 0 | 100 | 0 | 0
914 | 650.92 | 0 | 22 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 53.832 | 663.3189 | 0 | 0.05921 | 5.1512 | 0 | 0 | 157.1618 | 0 | off_peak | 650.92 | 0 | 100 | 0 | 0 | 100 | 0 | 0
915 | 568.13 | 0 | 21.8 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 65.4301 | 580.5289 | 0 | 0.05921 | 4.9242 | 0 | 0 | 157.1618 | 0 | off_peak | 568.13 | 0 | 100 | 0 | 0 | 100 | 0 | 0
916 | 586.59 | 0 | 21.7 | 0 | 0 | 0 | 0 | 8.9635 | 8.9635 | 0 | 0 | 0 | 73.8147 | 595.5535 | 0 | 0.05921 | 4.518 | 0 | 0 | 157.1618 | 0 | off_peak | 586.59 | 0 | 100 | 0 | 0 | 100 | 0 | 0
917 | 614.23 | 0 | 21.6 | 0 | 0 | 0 | 0 | 0.57892 | 0.57892 | 0 | 0 | 0 | 74.3563 | 614.8089 | 0 | 0.05921 | 12.2935 | 0 | 0 | 157.1618 | 0 | off_peak | 614.23 | 0 | 100 | 0 | 0 | 100 | 0 | 0
918 | 697.39 | 0 | 21.6 | 0 | 0 | 0 | 0 | 0.03739 | 0.03739 | 0 | 0 | 0 | 74.3912 | 697.4274 | 0 | 0.05921 | 11.9587 | 0 | 0 | 157.1618 | 0 | off_peak | 697.39 | 0 | 100 | 0 | 0 | 100 | 0 | 0
919 | 755.29 | 0 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3912 | 755.29 | 0 | 0.088511 | 3.0071 | 0 | 0 | 157.1618 | 0 | on_peak | 755.29 |  |  | 0 | 0 | 100 | 0 | 0
920 | 809.44 | 61.9544 | 22.8 | 12.6451 | 12.6451 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3912 | 796.7949 | 0 | 0.088511 | 2.75 | 0 | 0 | 157.1618 | 12.6451 | on_peak | 796.7949 |  |  | 1.56 | 0 | 98.44 | 34.7741 | 0
921 | 830.4 | 256.553 | 23.7 | 52.1951 | 52.1951 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3912 | 778.2049 | 0 | 0.088511 | 2.571 | 0 | 0 | 157.1618 | 52.1951 | on_peak | 778.2049 |  |  | 6.29 | 0 | 93.71 | 134.1946 | 0
922 | 836.11 | 451.295 | 24.5 | 91.5517 | 91.5517 | 0 | 0 | 0 | 0 | 62.6277 | 62.6277 | 0 | 7.4394 | 681.9305 | 0 | 0.088511 | 2.4885 | 0 | 0 | 157.1618 | 91.5517 | on_peak | 681.9305 |  |  | 10.95 | 7.49 | 81.56 | 227.8275 | 0
923 | 789.08 | 599.55 | 25.2 | 121.3215 | 121.3215 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 19.0375 | 680.1575 | 0 | 0.05921 | 2.5218 | 0 | 0 | 157.1618 | 121.3215 | off_peak | 667.7585 | 0 | 100 | 15.38 | 0 | 84.62 | 305.9476 | 0
924 | 888.36 | 712.999 | 25.7 | 144.0185 | 144.0185 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 30.6357 | 756.7405 | 0 | 0.05921 | 2.8492 | 0 | 0 | 157.1618 | 144.0185 | off_peak | 744.3415 | 0 | 100 | 16.21 | 0 | 83.79 | 410.332 | 0
925 | 827.72 | 742.828 | 26 | 149.8811 | 149.8811 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 42.2338 | 690.2378 | 0 | 0.05921 | 3.401 | 0 | 0 | 157.1618 | 149.8811 | off_peak | 677.8389 | 0 | 100 | 18.11 | 0 | 81.89 | 509.7468 | 0
926 | 870.51 | 724.495 | 26.2 | 146.0764 | 146.0764 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 53.832 | 736.8325 | 0 | 0.05921 | 3.7096 | 0 | 0 | 157.1618 | 146.0764 | off_peak | 724.4336 | 0 | 100 | 16.78 | 0 | 83.22 | 541.887 | 0
927 | 889.63 | 630.582 | 26.3 | 127.0953 | 127.0953 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 65.4301 | 774.9337 | 0 | 0.05921 | 3.5506 | 0 | 0 | 157.1618 | 127.0953 | off_peak | 762.5347 | 0 | 100 | 14.29 | 0 | 85.71 | 451.2666 | 0
928 | 871.21 | 481.144 | 26.2 | 97.0108 | 97.0108 | 0 | 0 | 8.9635 | 8.9635 | 0 | 0 | 0 | 73.8147 | 783.1628 | 0 | 0.05921 | 3.2438 | 0 | 0 | 157.1618 | 97.0108 | off_peak | 774.1992 | 0 | 100 | 11.14 | 0 | 88.86 | 314.6861 | 0
929 | 863.54 | 290.715 | 25.8 | 58.7002 | 58.7002 | 0 | 0 | 0.57892 | 0.57892 | 0 | 0 | 0 | 74.3563 | 805.4187 | 0 | 0.05921 | 3.2048 | 0 | 0 | 157.1618 | 58.7002 | off_peak | 804.8398 | 0 | 100 | 6.8 | 0 | 93.2 | 188.1251 | 0
930 | 866.25 | 91.8892 | 25.1 | 18.6009 | 18.6009 | 0 | 0 | 0.03739 | 0.03739 | 0 | 0 | 0 | 74.3912 | 847.6865 | 0 | 0.05921 | 3.2975 | 0 | 0 | 157.1618 | 18.6009 | off_peak | 847.6491 | 0 | 100 | 2.15 | 0 | 97.85 | 61.3363 | 0
931 | 816.2 | 0 | 24.7 | 0 | 0 | 0 | 0 | 0 | 0 | 62.6277 | 62.6277 | 0 | 7.4394 | 753.5723 | 0 | 0.088511 | 3.5113 | 0 | 0 | 157.1618 | 0 | on_peak | 753.5723 |  |  | 0 | 7.67 | 92.33 | 0 | 0
932 | 813.09 | 0 | 24.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 813.09 | 0 | 0.088511 | 3.7752 | 0 | 0 | 157.1618 | 0 | on_peak | 813.09 |  |  | 0 | 0 | 100 | 0 | 0
933 | 797.7 | 0 | 23.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 797.7 | 0 | 0.088511 | 4.0737 | 0 | 0 | 157.1618 | 0 | on_peak | 797.7 |  |  | 0 | 0 | 100 | 0 | 0
934 | 780.3 | 0 | 22.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 780.3 | 0 | 0.088511 | 4.309 | 0 | 0 | 157.1618 | 0 | on_peak | 780.3 |  |  | 0 | 0 | 100 | 0 | 0
935 | 818.98 | 0 | 22.1 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 19.0375 | 831.3789 | 0 | 0.05921 | 4.7748 | 0 | 0 | 157.1618 | 0 | off_peak | 818.98 | 0 | 100 | 0 | 0 | 100 | 0 | 0
936 | 776.05 | 0 | 21.5 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 30.6357 | 788.4489 | 0 | 0.05921 | 5.2197 | 0 | 0 | 157.1618 | 0 | off_peak | 776.05 | 0 | 100 | 0 | 0 | 100 | 0 | 0
937 | 766.23 | 0 | 21 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 42.2338 | 778.6289 | 0 | 0.05921 | 5.4373 | 0 | 0 | 157.1618 | 0 | off_peak | 766.23 | 0 | 100 | 0 | 0 | 100 | 0 | 0
938 | 689.91 | 0 | 20.7 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 53.832 | 702.3089 | 0 | 0.05921 | 5.3795 | 0 | 0 | 157.1618 | 0 | off_peak | 689.91 | 0 | 100 | 0 | 0 | 100 | 0 | 0
939 | 573.26 | 0 | 20.6 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 65.4301 | 585.6589 | 0 | 0.05921 | 5.0135 | 0 | 0 | 157.1618 | 0 | off_peak | 573.26 | 0 | 100 | 0 | 0 | 100 | 0 | 0
940 | 573.41 | 0 | 20.6 | 0 | 0 | 0 | 0 | 8.9635 | 8.9635 | 0 | 0 | 0 | 73.8147 | 582.3735 | 0 | 0.05921 | 4.7688 | 0 | 0 | 157.1618 | 0 | off_peak | 573.41 | 0 | 100 | 0 | 0 | 100 | 0 | 0
941 | 607.17 | 0 | 20.8 | 0 | 0 | 0 | 0 | 0.57892 | 0.57892 | 0 | 0 | 0 | 74.3563 | 607.7489 | 0 | 0.05921 | 4.2307 | 0 | 0 | 157.1618 | 0 | off_peak | 607.17 | 0 | 100 | 0 | 0 | 100 | 0 | 0
942 | 702.58 | 0 | 21 | 0 | 0 | 0 | 0 | 0.03739 | 0.03739 | 0 | 0 | 0 | 74.3912 | 702.6174 | 0 | 0.05921 | 3.659 | 0 | 0 | 157.1618 | 0 | off_peak | 702.58 | 0 | 100 | 0 | 0 | 100 | 0 | 0
943 | 852.41 | 0 | 21.4 | 0 | 0 | 0 | 0 | 0 | 0 | 62.6277 | 62.6277 | 0 | 7.4394 | 789.7823 | 0 | 0.088511 | 3.1136 | 0 | 0 | 157.1618 | 0 | on_peak | 789.7823 |  |  | 0 | 7.35 | 92.65 | 0 | 0
944 | 819.55 | 61.5273 | 22.3 | 12.5804 | 12.5804 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 806.9696 | 0 | 0.088511 | 2.8287 | 0 | 0 | 157.1618 | 12.5804 | on_peak | 806.9696 |  |  | 1.54 | 0 | 98.46 | 35.5868 | 0
945 | 864.82 | 253.686 | 23.1 | 51.7228 | 51.7228 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 813.0972 | 0 | 0.088511 | 2.6465 | 0 | 0 | 157.1618 | 51.7228 | on_peak | 813.0972 |  |  | 5.98 | 0 | 94.02 | 136.8861 | 0
946 | 837.1 | 449.08 | 23.8 | 91.3316 | 91.3316 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 745.7684 | 0 | 0.088511 | 2.5624 | 0 | 0 | 157.1618 | 91.3316 | on_peak | 745.7684 |  |  | 10.91 | 0 | 89.09 | 234.0247 | 0
947 | 855.69 | 595.423 | 24.4 | 120.8336 | 120.8336 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 19.0375 | 747.2553 | 0 | 0.05921 | 2.5923 | 0 | 0 | 157.1618 | 120.8336 | off_peak | 734.8564 | 0 | 100 | 14.12 | 0 | 85.88 | 313.234 | 0
948 | 886.27 | 632.218 | 24.7 | 128.1624 | 128.1624 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 30.6357 | 770.5065 | 0 | 0.05921 | 2.932 | 0 | 0 | 157.1618 | 128.1624 | off_peak | 758.1076 | 0 | 100 | 14.46 | 0 | 85.54 | 375.7703 | 0
949 | 817.97 | 624.489 | 24.8 | 126.5501 | 126.5501 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 42.2338 | 703.8189 | 0 | 0.05921 | 3.4999 | 0 | 0 | 157.1618 | 126.5501 | off_peak | 691.4199 | 0 | 100 | 15.47 | 0 | 84.53 | 442.9156 | 0
950 | 876.25 | 688.706 | 24.7 | 139.6136 | 139.6136 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 53.832 | 749.0354 | 0 | 0.05921 | 3.8426 | 0 | 0 | 157.1618 | 139.6136 | off_peak | 736.6364 | 0 | 100 | 15.93 | 0 | 84.07 | 536.4761 | 0
951 | 944.88 | 625.196 | 24.5 | 126.8301 | 126.8301 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 65.4301 | 830.4489 | 0 | 0.05921 | 3.7688 | 0 | 0 | 157.1618 | 126.8301 | off_peak | 818.0499 | 0 | 100 | 13.42 | 0 | 86.58 | 478.0029 | 0
952 | 884.55 | 484.756 | 24.1 | 98.4811 | 98.4811 | 0 | 0 | 8.9635 | 8.9635 | 0 | 0 | 0 | 73.8147 | 795.0324 | 0 | 0.05921 | 3.7085 | 0 | 0 | 157.1618 | 98.4811 | off_peak | 786.0689 | 0 | 100 | 11.13 | 0 | 88.87 | 365.221 | 0
953 | 914.41 | 276.391 | 23.6 | 56.2513 | 56.2513 | 0 | 0 | 0.57892 | 0.57892 | 0 | 0 | 0 | 74.3563 | 858.7377 | 0 | 0.05921 | 3.7886 | 0 | 0 | 157.1618 | 56.2513 | off_peak | 858.1587 | 0 | 100 | 6.15 | 0 | 93.85 | 213.1137 | 0
954 | 866.78 | 93.8254 | 23 | 19.1364 | 19.1364 | 0 | 0 | 0.03739 | 0.03739 | 0 | 0 | 0 | 74.3912 | 847.6809 | 0 | 0.05921 | 4.1058 | 0 | 0 | 157.1618 | 19.1364 | off_peak | 847.6436 | 0 | 100 | 2.21 | 0 | 97.79 | 78.5713 | 0
955 | 863.62 | 0 | 22.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3912 | 863.62 | 0 | 0.088511 | 4.4899 | 0 | 0 | 157.1618 | 0 | on_peak | 863.62 |  |  | 0 | 0 | 100 | 0 | 0
956 | 865.39 | 0 | 22.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3912 | 865.39 | 0 | 0.088511 | 4.7808 | 0 | 0 | 157.1618 | 0 | on_peak | 865.39 |  |  | 0 | 0 | 100 | 0 | 0
957 | 838.14 | 0 | 22.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3912 | 838.14 | 0 | 0.088511 | 4.9776 | 0 | 0 | 157.1618 | 0 | on_peak | 838.14 |  |  | 0 | 0 | 100 | 0 | 0
958 | 797.02 | 0 | 22.2 | 0 | 0 | 0 | 0 | 0 | 0 | 62.6277 | 62.6277 | 0 | 7.4394 | 734.3923 | 0 | 0.088511 | 5.2517 | 0 | 0 | 157.1618 | 0 | on_peak | 734.3923 |  |  | 0 | 7.86 | 92.14 | 0 | 0
959 | 839.79 | 0 | 22.1 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 19.0375 | 852.1889 | 0 | 0.05921 | 5.6845 | 0 | 0 | 157.1618 | 0 | off_peak | 839.79 | 0 | 100 | 0 | 0 | 100 | 0 | 0
960 | 790.73 | 0 | 21.9 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 30.6357 | 803.1289 | 0 | 0.05921 | 5.8442 | 0 | 0 | 157.1618 | 0 | off_peak | 790.73 | 0 | 100 | 0 | 0 | 100 | 0 | 0
961 | 817.45 | 0 | 21.8 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 42.2338 | 829.8489 | 0 | 0.05921 | 5.9092 | 0 | 0 | 157.1618 | 0 | off_peak | 817.45 | 0 | 100 | 0 | 0 | 100 | 0 | 0
962 | 677 | 0 | 21.7 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 53.832 | 689.3989 | 0 | 0.05921 | 5.8353 | 0 | 0 | 157.1618 | 0 | off_peak | 677 | 0 | 100 | 0 | 0 | 100 | 0 | 0
963 | 610.19 | 0 | 21.6 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 65.4301 | 622.5889 | 0 | 0.05921 | 5.4627 | 0 | 0 | 157.1618 | 0 | off_peak | 610.19 | 0 | 100 | 0 | 0 | 100 | 0 | 0
964 | 631.31 | 0 | 21.5 | 0 | 0 | 0 | 0 | 8.9635 | 8.9635 | 0 | 0 | 0 | 73.8147 | 640.2735 | 0 | 0.05921 | 5.1601 | 0 | 0 | 157.1618 | 0 | off_peak | 631.31 | 0 | 100 | 0 | 0 | 100 | 0 | 0
965 | 626.74 | 0 | 21.5 | 0 | 0 | 0 | 0 | 0.57892 | 0.57892 | 0 | 0 | 0 | 74.3563 | 627.3189 | 0 | 0.05921 | 4.6295 | 0 | 0 | 157.1618 | 0 | off_peak | 626.74 | 0 | 100 | 0 | 0 | 100 | 0 | 0
966 | 726.8 | 0 | 21.4 | 0 | 0 | 0 | 0 | 0.03739 | 0.03739 | 0 | 0 | 0 | 74.3912 | 726.8374 | 0 | 0.05921 | 3.9984 | 0 | 0 | 157.1618 | 0 | off_peak | 726.8 | 0 | 100 | 0 | 0 | 100 | 0 | 0
967 | 779.84 | 0 | 21.7 | 0 | 0 | 0 | 0 | 0 | 0 | 62.6277 | 62.6277 | 0 | 7.4394 | 717.2123 | 0 | 0.088511 | 3.5279 | 0 | 0 | 157.1618 | 0 | on_peak | 717.2123 |  |  | 0 | 8.03 | 91.97 | 0 | 0
968 | 814.58 | 64.452 | 22.4 | 13.1737 | 13.1737 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 801.4063 | 0 | 0.088511 | 3.152 | 0 | 0 | 157.1618 | 13.1737 | on_peak | 801.4063 |  |  | 1.62 | 0 | 98.38 | 41.5233 | 0
969 | 818 | 255.019 | 23 | 52.0132 | 52.0132 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 765.9868 | 0 | 0.088511 | 2.9032 | 0 | 0 | 157.1618 | 52.0132 | on_peak | 765.9868 |  |  | 6.36 | 0 | 93.64 | 151.006 | 0
970 | 845.38 | 340.053 | 23.3 | 69.2822 | 69.2822 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 776.0978 | 0 | 0.088511 | 2.7637 | 0 | 0 | 157.1618 | 69.2822 | on_peak | 776.0978 |  |  | 8.2 | 0 | 91.8 | 191.4743 | 0
971 | 873.47 | 495.091 | 23.6 | 100.7612 | 100.7612 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 19.0375 | 785.1077 | 0 | 0.05921 | 2.7813 | 0 | 0 | 157.1618 | 100.7612 | off_peak | 772.7088 | 0 | 100 | 11.54 | 0 | 88.46 | 280.245 | 0
972 | 916.21 | 425.917 | 23.8 | 86.6208 | 86.6208 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 30.6357 | 841.9882 | 0 | 0.05921 | 3.0369 | 0 | 0 | 157.1618 | 86.6208 | off_peak | 829.5892 | 0 | 100 | 9.45 | 0 | 90.55 | 263.0609 | 0
973 | 886.06 | 667.568 | 23.9 | 135.7178 | 135.7178 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 42.2338 | 762.7411 | 0 | 0.05921 | 3.5568 | 0 | 0 | 157.1618 | 135.7178 | off_peak | 750.3422 | 0 | 100 | 15.32 | 0 | 84.68 | 482.7173 | 0
974 | 939.49 | 640.695 | 23.9 | 130.2545 | 130.2545 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 53.832 | 821.6344 | 0 | 0.05921 | 3.9014 | 0 | 0 | 157.1618 | 130.2545 | off_peak | 809.2355 | 0 | 100 | 13.86 | 0 | 86.14 | 508.1714 | 0
975 | 956.04 | 556.813 | 23.8 | 113.2417 | 113.2417 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 65.4301 | 855.1972 | 0 | 0.05921 | 3.9816 | 0 | 0 | 157.1618 | 113.2417 | off_peak | 842.7983 | 0 | 100 | 11.84 | 0 | 88.16 | 450.8882 | 0
976 | 936.21 | 335.495 | 23.5 | 68.3046 | 68.3046 | 0 | 0 | 8.9635 | 8.9635 | 0 | 0 | 0 | 73.8147 | 876.8689 | 0 | 0.05921 | 4.0877 | 0 | 0 | 157.1618 | 68.3046 | off_peak | 867.9054 | 0 | 100 | 7.3 | 0 | 92.7 | 279.2099 | 0
977 | 922.76 | 277.854 | 23.1 | 56.6503 | 56.6503 | 0 | 0 | 0.57892 | 0.57892 | 0 | 0 | 0 | 74.3563 | 866.6886 | 0 | 0.05921 | 4.3219 | 0 | 0 | 157.1618 | 56.6503 | off_peak | 866.1097 | 0 | 100 | 6.14 | 0 | 93.86 | 244.8374 | 0
978 | 929.14 | 96.1262 | 22.8 | 19.6197 | 19.6197 | 0 | 0 | 0.03739 | 0.03739 | 0 | 0 | 0 | 74.3912 | 909.5577 | 0 | 0.05921 | 4.5704 | 0 | 0 | 157.1618 | 19.6197 | off_peak | 909.5203 | 0 | 100 | 2.11 | 0 | 97.89 | 89.6691 | 0
979 | 900.59 | 0 | 22.6 | 0 | 0 | 0 | 0 | 0 | 0 | 22.7759 | 22.7759 | 0 | 50.0428 | 877.8141 | 0 | 0.088511 | 4.8065 | 0 | 0 | 157.1618 | 0 | on_peak | 877.8141 |  |  | 0 | 2.53 | 97.47 | 0 | 0
980 | 902.37 | 0 | 22.5 | 0 | 0 | 0 | 0 | 0 | 0 | 24.5559 | 24.5559 | 0 | 23.7914 | 877.8141 | 0 | 0.088511 | 5.2167 | 0 | 0 | 157.1618 | 0 | on_peak | 877.8141 |  |  | 0 | 2.72 | 97.28 | 0 | 0
981 | 893.11 | 0 | 22.4 | 0 | 0 | 0 | 0 | 0 | 0 | 15.2959 | 15.2959 | 0 | 7.4394 | 877.8141 | 0 | 0.088511 | 5.6789 | 0 | 0 | 157.1618 | 0 | on_peak | 877.8141 |  |  | 0 | 1.71 | 98.29 | 0 | 0
982 | 858.5 | 0 | 22.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 858.5 | 0 | 0.088511 | 5.9645 | 0 | 0 | 157.1618 | 0 | on_peak | 858.5 |  |  | 0 | 0 | 100 | 0 | 0
983 | 842.12 | 0 | 22.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 842.12 | 0 | 0.05921 | 6.1351 | 0 | 0 | 157.1618 | 0 | off_peak | 842.12 |  |  | 0 | 0 | 100 | 0 | 0
984 | 859.88 | 0 | 21.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 859.88 | 0 | 0.05921 | 6.2342 | 0 | 0 | 157.1618 | 0 | off_peak | 859.88 |  |  | 0 | 0 | 100 | 0 | 0
985 | 800.45 | 0 | 21.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 800.45 | 0 | 0.05921 | 6.1814 | 0 | 0 | 157.1618 | 0 | off_peak | 800.45 |  |  | 0 | 0 | 100 | 0 | 0
986 | 687.42 | 0 | 21.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 687.42 | 0 | 0.05921 | 5.8417 | 0 | 0 | 157.1618 | 0 | off_peak | 687.42 |  |  | 0 | 0 | 100 | 0 | 0
987 | 664.44 | 0 | 21.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 664.44 | 0 | 0.05921 | 5.448 | 0 | 0 | 157.1618 | 0 | off_peak | 664.44 |  |  | 0 | 0 | 100 | 0 | 0
988 | 661.38 | 0 | 21.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 661.38 | 0 | 0.05921 | 4.9546 | 0 | 0 | 157.1618 | 0 | off_peak | 661.38 |  |  | 0 | 0 | 100 | 0 | 0
989 | 694.5 | 0 | 21.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 694.5 | 0 | 0.05921 | 4.5388 | 0 | 0 | 157.1618 | 0 | off_peak | 694.5 |  |  | 0 | 0 | 100 | 0 | 0
990 | 783.43 | 0 | 21.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 783.43 | 0 | 0.05921 | 4.0703 | 0 | 0 | 157.1618 | 0 | off_peak | 783.43 |  |  | 0 | 0 | 100 | 0 | 0
991 | 848.33 | 0 | 21.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 848.33 | 0 | 0.05921 | 3.6269 | 0 | 0 | 157.1618 | 0 | off_peak | 848.33 |  |  | 0 | 0 | 100 | 0 | 0
992 | 804.41 | 61.9107 | 22.7 | 12.6407 | 12.6407 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 791.7693 | 0 | 0.05921 | 3.2595 | 0 | 0 | 157.1618 | 12.6407 | off_peak | 791.7693 |  |  | 1.57 | 0 | 98.43 | 41.2029 | 0
993 | 792.68 | 173.32 | 23.4 | 35.2995 | 35.2995 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 19.0375 | 769.7795 | 0 | 0.05921 | 2.9814 | 0 | 0 | 157.1618 | 35.2995 | off_peak | 757.3805 | 0 | 100 | 4.45 | 0 | 95.55 | 105.2413 | 0
994 | 748.07 | 348.6 | 23.9 | 70.871 | 70.871 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19.0375 | 677.199 | 0 | 0.05921 | 2.8385 | 0 | 0 | 157.1618 | 70.871 | off_peak | 677.199 |  |  | 9.47 | 0 | 90.53 | 201.1678 | 0
995 | 765.96 | 436.589 | 24.3 | 88.6321 | 88.6321 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19.0375 | 677.3279 | 0 | 0.05921 | 2.776 | 0 | 0 | 157.1618 | 88.6321 | off_peak | 677.3279 |  |  | 11.57 | 0 | 88.43 | 246.0446 | 0
996 | 794.42 | 360.349 | 24.5 | 73.102 | 73.102 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19.0375 | 721.318 | 0 | 0.05921 | 2.8564 | 0 | 0 | 157.1618 | 73.102 | off_peak | 721.318 |  |  | 9.2 | 0 | 90.8 | 208.8087 | 0
997 | 777.69 | 647.387 | 24.7 | 131.2375 | 131.2375 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19.0375 | 646.4525 | 0 | 0.05921 | 3.0662 | 0 | 0 | 157.1618 | 131.2375 | off_peak | 646.4525 |  |  | 16.88 | 0 | 83.12 | 402.3984 | 0
998 | 787.9 | 560.852 | 24.8 | 113.6543 | 113.6543 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19.0375 | 674.2457 | 0 | 0.05921 | 3.3615 | 0 | 0 | 157.1618 | 113.6543 | off_peak | 674.2457 |  |  | 14.42 | 0 | 85.58 | 382.0517 | 0
999 | 733.47 | 342.61 | 24.7 | 69.4535 | 69.4535 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19.0375 | 664.0165 | 0 | 0.05921 | 3.7989 | 0 | 0 | 157.1618 | 69.4535 | off_peak | 664.0165 |  |  | 9.47 | 0 | 90.53 | 263.8497 | 0
1000 | 737.62 | 311.139 | 24.5 | 63.1191 | 63.1191 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19.0375 | 674.5009 | 0 | 0.05921 | 4.1966 | 0 | 0 | 157.1618 | 63.1191 | off_peak | 674.5009 |  |  | 8.56 | 0 | 91.44 | 264.8868 | 0
1001 | 729.8 | 263.935 | 24.1 | 53.62 | 53.62 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19.0375 | 676.18 | 0 | 0.05921 | 4.589 | 0 | 0 | 157.1618 | 53.62 | off_peak | 676.18 |  |  | 7.35 | 0 | 92.65 | 246.0608 | 0
1002 | 659.51 | 92.6034 | 23.5 | 18.8535 | 18.8535 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19.0375 | 640.6565 | 0 | 0.05921 | 4.9279 | 0 | 0 | 157.1618 | 18.8535 | off_peak | 640.6565 |  |  | 2.86 | 0 | 97.14 | 92.9085 | 0
1003 | 633.22 | 0 | 23.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19.0375 | 633.22 | 0 | 0.05921 | 5.2089 | 0 | 0 | 157.1618 | 0 | off_peak | 633.22 |  |  | 0 | 0 | 100 | 0 | 0
1004 | 612.91 | 0 | 23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19.0375 | 612.91 | 0 | 0.05921 | 5.5203 | 0 | 0 | 157.1618 | 0 | off_peak | 612.91 |  |  | 0 | 0 | 100 | 0 | 0
1005 | 631.27 | 0 | 22.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19.0375 | 631.27 | 0 | 0.05921 | 5.7024 | 0 | 0 | 157.1618 | 0 | off_peak | 631.27 |  |  | 0 | 0 | 100 | 0 | 0
1006 | 626.65 | 0 | 22.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19.0375 | 626.65 | 0 | 0.05921 | 5.8325 | 0 | 0 | 157.1618 | 0 | off_peak | 626.65 |  |  | 0 | 0 | 100 | 0 | 0
1007 | 583.94 | 0 | 22.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19.0375 | 583.94 | 0 | 0.05921 | 6.11 | 0 | 0 | 157.1618 | 0 | off_peak | 583.94 |  |  | 0 | 0 | 100 | 0 | 0
1008 | 629.35 | 0 | 22.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19.0375 | 629.35 | 0 | 0.05921 | 6.0581 | 0 | 0 | 157.1618 | 0 | off_peak | 629.35 |  |  | 0 | 0 | 100 | 0 | 0
1009 | 573.35 | 0 | 22.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19.0375 | 573.35 | 0 | 0.05921 | 5.9712 | 0 | 0 | 157.1618 | 0 | off_peak | 573.35 |  |  | 0 | 0 | 100 | 0 | 0
1010 | 599.15 | 0 | 22.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19.0375 | 599.15 | 0 | 0.05921 | 5.9081 | 0 | 0 | 157.1618 | 0 | off_peak | 599.15 |  |  | 0 | 0 | 100 | 0 | 0
1011 | 606.22 | 0 | 22.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19.0375 | 606.22 | 0 | 0.05921 | 5.5384 | 0 | 0 | 157.1618 | 0 | off_peak | 606.22 |  |  | 0 | 0 | 100 | 0 | 0
1012 | 576.55 | 0 | 22.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19.0375 | 576.55 | 0 | 0.05921 | 5.1019 | 0 | 0 | 157.1618 | 0 | off_peak | 576.55 |  |  | 0 | 0 | 100 | 0 | 0
1013 | 634.16 | 0 | 22.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19.0375 | 634.16 | 0 | 0.05921 | 4.7399 | 0 | 0 | 157.1618 | 0 | off_peak | 634.16 |  |  | 0 | 0 | 100 | 0 | 0
1014 | 663.36 | 0 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19.0375 | 663.36 | 0 | 0.05921 | 4.2993 | 0 | 0 | 157.1618 | 0 | off_peak | 663.36 |  |  | 0 | 0 | 100 | 0 | 0
1015 | 707.07 | 0 | 22.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19.0375 | 707.07 | 0 | 0.05921 | 3.8948 | 0 | 0 | 157.1618 | 0 | off_peak | 707.07 |  |  | 0 | 0 | 100 | 0 | 0
1016 | 731.91 | 67.4486 | 23.4 | 13.737 | 13.737 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19.0375 | 718.173 | 0 | 0.05921 | 3.5363 | 0 | 0 | 157.1618 | 13.737 | off_peak | 718.173 |  |  | 1.88 | 0 | 98.12 | 48.5788 | 0
1017 | 749.85 | 265.992 | 24.2 | 54.0185 | 54.0185 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19.0375 | 695.8315 | 0 | 0.05921 | 3.2406 | 0 | 0 | 157.1618 | 54.0185 | off_peak | 695.8315 |  |  | 7.2 | 0 | 92.8 | 175.0523 | 0
1018 | 732.83 | 464.045 | 24.8 | 94.0368 | 94.0368 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19.0375 | 638.7932 | 0 | 0.05921 | 3.0169 | 0 | 0 | 157.1618 | 94.0368 | off_peak | 638.7932 |  |  | 12.83 | 0 | 87.17 | 283.6968 | 0
1019 | 719.27 | 612.793 | 25.3 | 123.9566 | 123.9566 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19.0375 | 595.3134 | 0 | 0.05921 | 2.9149 | 0 | 0 | 157.1618 | 123.9566 | off_peak | 595.3134 |  |  | 17.23 | 0 | 82.77 | 361.3193 | 0
1020 | 703.21 | 664.851 | 25.6 | 134.3415 | 134.3415 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19.0375 | 568.8685 | 0 | 0.05921 | 2.9055 | 0 | 0 | 157.1618 | 134.3415 | off_peak | 568.8685 |  |  | 19.1 | 0 | 80.9 | 390.323 | 0
1021 | 736.46 | 598.834 | 25.8 | 120.9146 | 120.9146 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19.0375 | 615.5454 | 0 | 0.05921 | 2.9918 | 0 | 0 | 157.1618 | 120.9146 | off_peak | 615.5454 |  |  | 16.42 | 0 | 83.58 | 361.7557 | 0
1022 | 627.79 | 711.849 | 26 | 143.6305 | 143.6305 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19.0375 | 484.1595 | 0 | 0.05921 | 3.24 | 0 | 0 | 157.1618 | 143.6305 | off_peak | 484.1595 |  |  | 22.88 | 0 | 77.12 | 465.3677 | 0
1023 | 692.05 | 643.827 | 26 | 129.9056 | 129.9056 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19.0375 | 562.1444 | 0 | 0.05921 | 3.4752 | 0 | 0 | 157.1618 | 129.9056 | off_peak | 562.1444 |  |  | 18.77 | 0 | 81.23 | 451.4464 | 0
1024 | 625.02 | 491.334 | 25.9 | 99.1728 | 99.1728 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19.0375 | 525.8472 | 0 | 0.05921 | 3.6233 | 0 | 0 | 157.1618 | 99.1728 | off_peak | 525.8472 |  |  | 15.87 | 0 | 84.13 | 359.3361 | 0
1025 | 620.1 | 298.519 | 25.4 | 60.363 | 60.363 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19.0375 | 559.737 | 0 | 0.05921 | 3.8571 | 0 | 0 | 157.1618 | 60.363 | off_peak | 559.737 |  |  | 9.73 | 0 | 90.27 | 232.8291 | 0
1026 | 601.83 | 97.1824 | 24.8 | 19.6936 | 19.6936 | 0 | 0 | 8.7263 | 8.7263 | 0 | 0 | 0 | 27.2003 | 590.8627 | 0 | 0.05921 | 3.9069 | 0 | 0 | 157.1618 | 19.6936 | off_peak | 582.1364 | 0 | 100 | 3.27 | 0 | 96.73 | 76.9407 | 0
1027 | 562.92 | 0 | 24.4 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 38.7984 | 575.3189 | 0 | 0.05921 | 3.7848 | 0 | 0 | 157.1618 | 0 | off_peak | 562.92 | 0 | 100 | 0 | 0 | 100 | 0 | 0
1028 | 557.13 | 0 | 23.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 38.7984 | 557.13 | 0 | 0.05921 | 3.7468 | 0 | 0 | 157.1618 | 0 | off_peak | 557.13 |  |  | 0 | 0 | 100 | 0 | 0
1029 | 557.89 | 0 | 23.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 38.7984 | 557.89 | 0 | 0.05921 | 3.7434 | 0 | 0 | 157.1618 | 0 | off_peak | 557.89 |  |  | 0 | 0 | 100 | 0 | 0
1030 | 520.15 | 0 | 23.2 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 50.3966 | 532.5489 | 0 | 0.05921 | 3.7348 | 0 | 0 | 157.1618 | 0 | off_peak | 520.15 | 0 | 100 | 0 | 0 | 100 | 0 | 0
1031 | 556.63 | 0 | 23 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 61.9947 | 569.0289 | 0 | 0.05921 | 4.0092 | 0 | 0 | 157.1618 | 0 | off_peak | 556.63 | 0 | 100 | 0 | 0 | 100 | 0 | 0
1032 | 535.61 | 0 | 23 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 73.5928 | 548.0089 | 0 | 0.05921 | 4.5225 | 0 | 0 | 157.1618 | 0 | off_peak | 535.61 | 0 | 100 | 0 | 0 | 100 | 0 | 0
1033 | 538.08 | 0 | 23 | 0 | 0 | 0 | 0 | 0.80079 | 0.80079 | 0 | 0 | 0 | 74.3419 | 538.8808 | 0 | 0.05921 | 4.7741 | 0 | 0 | 157.1618 | 0 | off_peak | 538.08 | 0 | 100 | 0 | 0 | 100 | 0 | 0
1034 | 541.98 | 0 | 23.1 | 0 | 0 | 0 | 0 | 0.05172 | 0.05172 | 0 | 0 | 0 | 74.3903 | 542.0317 | 0 | 0.05921 | 4.5159 | 0 | 0 | 157.1618 | 0 | off_peak | 541.98 | 0 | 100 | 0 | 0 | 100 | 0 | 0
1035 | 520.83 | 0 | 23.1 | 0 | 0 | 0 | 0 | 0.0033404 | 0.0033404 | 0 | 0 | 0 | 74.3934 | 520.8333 | 0 | 0.05921 | 4.1653 | 0 | 0 | 157.1618 | 0 | off_peak | 520.83 | 0 | 100 | 0 | 0 | 100 | 0 | 0
1036 | 541.37 | 0 | 23.1 | 0 | 0 | 0 | 0 | 0.00021574 | 0.00021574 | 0 | 0 | 0 | 74.3936 | 541.3702 | 0 | 0.05921 | 3.9645 | 0 | 0 | 157.1618 | 0 | off_peak | 541.37 | 0 | 100 | 0 | 0 | 100 | 0 | 0
1037 | 553.73 | 0 | 23.2 | 0 | 0 | 0 | 0 | 1.3934e-05 | 1.3934e-05 | 0 | 0 | 0 | 74.3936 | 553.73 | 0 | 0.05921 | 3.7457 | 0 | 0 | 157.1618 | 0 | off_peak | 553.73 | 0 | 100 | 0 | 0 | 100 | 0 | 0
1038 | 650.29 | 0 | 23.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 650.29 | 0 | 0.05921 | 3.4019 | 0 | 0 | 157.1618 | 0 | off_peak | 650.29 |  |  | 0 | 0 | 100 | 0 | 0
1039 | 737.21 | 0 | 23.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 737.21 | 0 | 0.088511 | 2.9156 | 0 | 0 | 157.1618 | 0 | on_peak | 737.21 |  |  | 0 | 0 | 100 | 0 | 0
1040 | 751.08 | 69.6742 | 24.3 | 14.1446 | 14.1446 | 0 | 0 | 0 | 0 | 62.63 | 62.63 | 0 | 7.4394 | 674.3054 | 0 | 0.088511 | 2.6406 | 0 | 0 | 157.1618 | 14.1446 | on_peak | 674.3054 |  |  | 1.88 | 8.34 | 89.78 | 37.35 | 0
1041 | 826.73 | 267.795 | 25 | 54.2285 | 54.2285 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 772.5015 | 0 | 0.088511 | 2.5151 | 0 | 0 | 157.1618 | 54.2285 | on_peak | 772.5015 |  |  | 6.56 | 0 | 93.44 | 136.3895 | 0
1042 | 798.2 | 465.581 | 25.5 | 94.1104 | 94.1104 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 704.0896 | 0 | 0.088511 | 2.4984 | 0 | 0 | 157.1618 | 94.1104 | on_peak | 704.0896 |  |  | 11.79 | 0 | 88.21 | 235.1261 | 0
1043 | 806.95 | 567.959 | 26 | 114.5977 | 114.5977 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 19.0375 | 704.7513 | 0 | 0.05921 | 2.6828 | 0 | 0 | 157.1618 | 114.5977 | off_peak | 692.3523 | 0 | 100 | 14.2 | 0 | 85.8 | 307.4432 | 0
1044 | 855.47 | 702.509 | 26.3 | 141.5923 | 141.5923 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 30.6357 | 726.2766 | 0 | 0.05921 | 2.9947 | 0 | 0 | 157.1618 | 141.5923 | off_peak | 713.8777 | 0 | 100 | 16.55 | 0 | 83.45 | 424.0221 | 0
1045 | 775.69 | 756.558 | 26.5 | 152.3757 | 152.3757 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 42.2338 | 635.7132 | 0 | 0.05921 | 3.6245 | 0 | 0 | 157.1618 | 152.3757 | off_peak | 623.3143 | 0 | 100 | 19.64 | 0 | 80.36 | 552.2791 | 0
1046 | 833.69 | 690.177 | 26.5 | 139.0061 | 139.0061 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 53.832 | 707.0828 | 0 | 0.05921 | 4.0021 | 0 | 0 | 157.1618 | 139.0061 | off_peak | 694.6839 | 0 | 100 | 16.67 | 0 | 83.33 | 556.3187 | 0
1047 | 873.67 | 621.074 | 26.4 | 125.1336 | 125.1336 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 65.4301 | 760.9353 | 0 | 0.05921 | 3.6843 | 0 | 0 | 157.1618 | 125.1336 | off_peak | 748.5364 | 0 | 100 | 14.32 | 0 | 85.68 | 461.024 | 0
1048 | 809.3 | 459.834 | 26.2 | 92.7141 | 83.7506 | 0 | 8.9635 | 8.9635 | 0 | 0 | 0 | 0 | 73.8147 | 725.5494 | 0 | 0.05921 | 3.1924 | 0 | 0 | 165.5464 | 83.7506 | off_peak | 725.5494 | 100 | 0 | 10.35 | 0 | 89.65 | 267.3636 | 0
1049 | 841.83 | 256.802 | 25.8 | 51.8526 | 51.8526 | 0 | 0 | 0.57892 | 0.57892 | 0 | 0 | 0 | 74.3563 | 790.5563 | 0 | 0.05921 | 2.8563 | 0 | 0 | 165.5464 | 51.8526 | off_peak | 789.9774 | 0 | 100 | 6.16 | 0 | 93.84 | 148.1073 | 0
1050 | 847.54 | 81.2215 | 25.2 | 16.4355 | 16.4355 | 0 | 0 | 0.03739 | 0.03739 | 0 | 0 | 0 | 74.3912 | 831.1419 | 0 | 0.05921 | 2.7386 | 0 | 0 | 165.5464 | 16.4355 | off_peak | 831.1045 | 0 | 100 | 1.94 | 0 | 98.06 | 45.01 | 0
1051 | 804.81 | 0 | 24.8 | 0 | 0 | 0 | 0 | 0 | 0 | 62.6277 | 62.6277 | 0 | 7.4394 | 742.1823 | 0 | 0.088511 | 2.6804 | 0 | 0 | 165.5464 | 0 | on_peak | 742.1823 |  |  | 0 | 7.78 | 92.22 | 0 | 0
1052 | 801.36 | 0 | 24.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 801.36 | 0 | 0.088511 | 2.5969 | 0 | 0 | 165.5464 | 0 | on_peak | 801.36 |  |  | 0 | 0 | 100 | 0 | 0
1053 | 776.37 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 776.37 | 0 | 0.088511 | 2.6465 | 0 | 0 | 165.5464 | 0 | on_peak | 776.37 |  |  | 0 | 0 | 100 | 0 | 0
1054 | 744.5 | 0 | 23.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 744.5 | 0 | 0.088511 | 2.8954 | 0 | 0 | 165.5464 | 0 | on_peak | 744.5 |  |  | 0 | 0 | 100 | 0 | 0
1055 | 739.7 | 0 | 23.7 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 19.0375 | 752.0989 | 0 | 0.05921 | 3.3822 | 0 | 0 | 165.5464 | 0 | off_peak | 739.7 | 0 | 100 | 0 | 0 | 100 | 0 | 0
1056 | 722.19 | 0 | 23.5 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 30.6357 | 734.5889 | 0 | 0.05921 | 4.1278 | 0 | 0 | 165.5464 | 0 | off_peak | 722.19 | 0 | 100 | 0 | 0 | 100 | 0 | 0
1057 | 723.49 | 0 | 23.5 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 42.2338 | 735.8889 | 0 | 0.05921 | 4.589 | 0 | 0 | 165.5464 | 0 | off_peak | 723.49 | 0 | 100 | 0 | 0 | 100 | 0 | 0
1058 | 630.14 | 0 | 23.5 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 53.832 | 642.5389 | 0 | 0.05921 | 4.627 | 0 | 0 | 165.5464 | 0 | off_peak | 630.14 | 0 | 100 | 0 | 0 | 100 | 0 | 0
1059 | 559.48 | 0 | 23.4 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 65.4301 | 571.8789 | 0 | 0.05921 | 4.3748 | 0 | 0 | 165.5464 | 0 | off_peak | 559.48 | 0 | 100 | 0 | 0 | 100 | 0 | 0
1060 | 589.59 | 0 | 23.4 | 0 | 0 | 0 | 0 | 8.9635 | 8.9635 | 0 | 0 | 0 | 73.8147 | 598.5535 | 0 | 0.05921 | 4.1014 | 0 | 0 | 165.5464 | 0 | off_peak | 589.59 | 0 | 100 | 0 | 0 | 100 | 0 | 0
1061 | 596.07 | 0 | 23.4 | 0 | 0 | 0 | 0 | 0.57892 | 0.57892 | 0 | 0 | 0 | 74.3563 | 596.6489 | 0 | 0.05921 | 3.6588 | 0 | 0 | 165.5464 | 0 | off_peak | 596.07 | 0 | 100 | 0 | 0 | 100 | 0 | 0
1062 | 659.39 | 0 | 23.6 | 0 | 0 | 0 | 0 | 0.03739 | 0.03739 | 0 | 0 | 0 | 74.3912 | 659.4274 | 0 | 0.05921 | 3.1684 | 0 | 0 | 165.5464 | 0 | off_peak | 659.39 | 0 | 100 | 0 | 0 | 100 | 0 | 0
1063 | 729.4 | 0 | 23.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3912 | 729.4 | 0 | 0.088511 | 2.7606 | 0 | 0 | 165.5464 | 0 | on_peak | 729.4 |  |  | 0 | 0 | 100 | 0 | 0
1064 | 773.91 | 66.2581 | 24.3 | 13.4511 | 13.4511 | 0 | 0 | 0 | 0 | 62.6277 | 62.6277 | 0 | 7.4394 | 697.8312 | 0 | 0.088511 | 2.5325 | 0 | 0 | 165.5464 | 13.4511 | on_peak | 697.8312 |  |  | 1.74 | 8.09 | 90.17 | 34.0651 | 0
1065 | 866.43 | 244.907 | 25 | 49.5937 | 49.5937 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 816.8363 | 0 | 0.088511 | 2.4404 | 0 | 0 | 165.5464 | 49.5937 | on_peak | 816.8363 |  |  | 5.72 | 0 | 94.28 | 121.0297 | 0
1066 | 852.26 | 466.577 | 25.8 | 94.2097 | 94.2097 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 758.0503 | 0 | 0.088511 | 2.4485 | 0 | 0 | 165.5464 | 94.2097 | on_peak | 758.0503 |  |  | 11.05 | 0 | 88.95 | 230.6682 | 0
1067 | 819.35 | 636.13 | 26.3 | 128.2135 | 128.2135 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 19.0375 | 703.5355 | 0 | 0.05921 | 2.7159 | 0 | 0 | 165.5464 | 128.2135 | off_peak | 691.1365 | 0 | 100 | 15.65 | 0 | 84.35 | 348.2136 | 0
1068 | 878.67 | 736.303 | 26.7 | 148.1889 | 148.1889 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 30.6357 | 742.8801 | 0 | 0.05921 | 3.0489 | 0 | 0 | 165.5464 | 148.1889 | off_peak | 730.4811 | 0 | 100 | 16.87 | 0 | 83.13 | 451.8184 | 0
1069 | 810.29 | 757.069 | 26.8 | 152.313 | 152.313 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 42.2338 | 670.3759 | 0 | 0.05921 | 3.8455 | 0 | 0 | 165.5464 | 152.313 | off_peak | 657.977 | 0 | 100 | 18.8 | 0 | 81.2 | 585.7212 | 0
1070 | 856.17 | 750.831 | 26.7 | 151.1128 | 151.1128 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 53.832 | 717.4562 | 0 | 0.05921 | 4.1688 | 0 | 0 | 165.5464 | 151.1128 | off_peak | 705.0572 | 0 | 100 | 17.65 | 0 | 82.35 | 629.966 | 0
1071 | 897.5 | 653.529 | 26.4 | 131.6726 | 131.6726 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 65.4301 | 778.2263 | 0 | 0.05921 | 3.7452 | 0 | 0 | 165.5464 | 131.6726 | off_peak | 765.8274 | 0 | 100 | 14.67 | 0 | 85.33 | 493.1398 | 0
1072 | 867.7 | 499.634 | 25.9 | 100.8481 | 100.8481 | 0 | 0 | 8.9635 | 8.9635 | 0 | 0 | 0 | 73.8147 | 775.8155 | 0 | 0.05921 | 3.2554 | 0 | 0 | 165.5464 | 100.8481 | off_peak | 766.8519 | 0 | 100 | 11.62 | 0 | 88.38 | 328.3046 | 0
1073 | 838.91 | 306.145 | 25.3 | 61.9274 | 61.9274 | 0 | 0 | 0.57892 | 0.57892 | 0 | 0 | 0 | 74.3563 | 777.5615 | 0 | 0.05921 | 2.8145 | 0 | 0 | 165.5464 | 61.9274 | off_peak | 776.9826 | 0 | 100 | 7.38 | 0 | 92.62 | 174.2937 | 0
1074 | 849.94 | 102.44 | 24.6 | 20.774 | 20.774 | 0 | 0 | 0.03739 | 0.03739 | 0 | 0 | 0 | 74.3912 | 829.2034 | 0 | 0.05921 | 2.6262 | 0 | 0 | 165.5464 | 20.774 | off_peak | 829.166 | 0 | 100 | 2.44 | 0 | 97.56 | 54.5561 | 0
1075 | 815.23 | 0 | 24.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3912 | 815.23 | 0 | 0.088511 | 2.5694 | 0 | 0 | 165.5464 | 0 | on_peak | 815.23 |  |  | 0 | 0 | 100 | 0 | 0
1076 | 817.57 | 0 | 23.6 | 0 | 0 | 0 | 0 | 0 | 0 | 62.6277 | 62.6277 | 0 | 7.4394 | 754.9423 | 0 | 0.088511 | 2.6313 | 0 | 0 | 165.5464 | 0 | on_peak | 754.9423 |  |  | 0 | 7.66 | 92.34 | 0 | 0
1077 | 779.57 | 0 | 23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 779.57 | 0 | 0.088511 | 2.7403 | 0 | 0 | 165.5464 | 0 | on_peak | 779.57 |  |  | 0 | 0 | 100 | 0 | 0
1078 | 777.5 | 0 | 22.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 777.5 | 0 | 0.088511 | 3.0864 | 0 | 0 | 165.5464 | 0 | on_peak | 777.5 |  |  | 0 | 0 | 100 | 0 | 0
1079 | 780.95 | 0 | 21.6 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 19.0375 | 793.3489 | 0 | 0.05921 | 3.6528 | 0 | 0 | 165.5464 | 0 | off_peak | 780.95 | 0 | 100 | 0 | 0 | 100 | 0 | 0
1080 | 800.62 | 0 | 21.1 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 30.6357 | 813.0189 | 0 | 0.05921 | 4.3917 | 0 | 0 | 165.5464 | 0 | off_peak | 800.62 | 0 | 100 | 0 | 0 | 100 | 0 | 0
1081 | 731.36 | 0 | 20.6 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 42.2338 | 743.7589 | 0 | 0.05921 | 4.8413 | 0 | 0 | 165.5464 | 0 | off_peak | 731.36 | 0 | 100 | 0 | 0 | 100 | 0 | 0
1082 | 652.19 | 0 | 20.3 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 53.832 | 664.5889 | 0 | 0.05921 | 4.7887 | 0 | 0 | 165.5464 | 0 | off_peak | 652.19 | 0 | 100 | 0 | 0 | 100 | 0 | 0
1083 | 590.45 | 0 | 20 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 65.4301 | 602.8489 | 0 | 0.05921 | 4.503 | 0 | 0 | 165.5464 | 0 | off_peak | 590.45 | 0 | 100 | 0 | 0 | 100 | 0 | 0
1084 | 573.39 | 0 | 20.1 | 0 | 0 | 0 | 0 | 8.9635 | 8.9635 | 0 | 0 | 0 | 73.8147 | 582.3535 | 0 | 0.05921 | 4.1264 | 0 | 0 | 165.5464 | 0 | off_peak | 573.39 | 0 | 100 | 0 | 0 | 100 | 0 | 0
1085 | 622.11 | 0 | 20.4 | 0 | 0 | 0 | 0 | 0.57892 | 0.57892 | 0 | 0 | 0 | 74.3563 | 622.6889 | 0 | 0.05921 | 3.6776 | 0 | 0 | 165.5464 | 0 | off_peak | 622.11 | 0 | 100 | 0 | 0 | 100 | 0 | 0
1086 | 682.44 | 0 | 20.6 | 0 | 0 | 0 | 0 | 0.03739 | 0.03739 | 0 | 0 | 0 | 74.3912 | 682.4774 | 0 | 0.05921 | 3.2032 | 0 | 0 | 165.5464 | 0 | off_peak | 682.44 | 0 | 100 | 0 | 0 | 100 | 0 | 0
1087 | 811.84 | 0 | 20.9 | 0 | 0 | 0 | 0 | 0 | 0 | 62.6277 | 62.6277 | 0 | 7.4394 | 749.2123 | 0 | 0.088511 | 2.8304 | 0 | 0 | 165.5464 | 0 | on_peak | 749.2123 |  |  | 0 | 7.71 | 92.29 | 0 | 0
1088 | 841.7 | 77.9964 | 21.4 | 15.999 | 15.999 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 825.701 | 0 | 0.088511 | 2.5587 | 0 | 0 | 165.5464 | 15.999 | on_peak | 825.701 |  |  | 1.9 | 0 | 98.1 | 40.9358 | 0
1089 | 899.87 | 284.648 | 22 | 58.2637 | 58.2637 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 841.6063 | 0 | 0.088511 | 2.4249 | 0 | 0 | 165.5464 | 58.2637 | on_peak | 841.6063 |  |  | 6.47 | 0 | 93.53 | 141.2838 | 0
1090 | 839.64 | 431.159 | 22.5 | 88.0955 | 88.0955 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 751.5445 | 0 | 0.088511 | 2.4052 | 0 | 0 | 165.5464 | 88.0955 | on_peak | 751.5445 |  |  | 10.49 | 0 | 89.51 | 211.8858 | 0
1091 | 814.04 | 602.808 | 22.8 | 123.0354 | 123.0354 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 19.0375 | 703.4035 | 0 | 0.05921 | 2.501 | 0 | 0 | 165.5464 | 123.0354 | off_peak | 691.0046 | 0 | 100 | 15.11 | 0 | 84.89 | 307.7156 | 0
1092 | 859.04 | 758.319 | 23 | 154.6652 | 154.6652 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 30.6357 | 716.7737 | 0 | 0.05921 | 2.7942 | 0 | 0 | 165.5464 | 154.6652 | off_peak | 704.3748 | 0 | 100 | 18 | 0 | 82 | 432.1721 | 0
1093 | 844.16 | 799.556 | 22.9 | 163.1341 | 150.7352 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 0 | 42.2338 | 693.4248 | 0 | 0.05921 | 3.3831 | 0 | 0 | 177.1446 | 150.7352 | off_peak | 693.4248 | 100 | 0 | 17.86 | 0 | 82.14 | 509.9528 | 0
1094 | 880.34 | 770.068 | 22.7 | 157.2299 | 157.2299 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 53.832 | 735.509 | 0 | 0.05921 | 3.7148 | 0 | 0 | 177.1446 | 157.2299 | off_peak | 723.1101 | 0 | 100 | 17.86 | 0 | 82.14 | 584.0821 | 0
1095 | 919.93 | 671.534 | 22.5 | 137.2095 | 137.2095 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 65.4301 | 795.1194 | 0 | 0.05921 | 3.4672 | 0 | 0 | 177.1446 | 137.2095 | off_peak | 782.7205 | 0 | 100 | 14.92 | 0 | 85.08 | 475.7262 | 0
1096 | 896.95 | 517.54 | 22.1 | 105.896 | 105.896 | 0 | 0 | 8.9635 | 8.9635 | 0 | 0 | 0 | 73.8147 | 800.0176 | 0 | 0.05921 | 3.1948 | 0 | 0 | 177.1446 | 105.896 | off_peak | 791.054 | 0 | 100 | 11.81 | 0 | 88.19 | 338.3172 | 0
1097 | 875.24 | 320.468 | 21.6 | 65.6891 | 65.6891 | 0 | 0 | 0.57892 | 0.57892 | 0 | 0 | 0 | 74.3563 | 810.1298 | 0 | 0.05921 | 3.3503 | 0 | 0 | 177.1446 | 65.6891 | off_peak | 809.5509 | 0 | 100 | 7.51 | 0 | 92.49 | 220.077 | 0
1098 | 857.11 | 111.473 | 21 | 22.8983 | 22.8983 | 0 | 0 | 0.03739 | 0.03739 | 0 | 0 | 0 | 74.3912 | 834.2491 | 0 | 0.05921 | 3.5522 | 0 | 0 | 177.1446 | 22.8983 | off_peak | 834.2117 | 0 | 100 | 2.67 | 0 | 97.33 | 81.3384 | 0
1099 | 826.14 | 0 | 20.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3912 | 826.14 | 0 | 0.088511 | 3.7395 | 0 | 0 | 177.1446 | 0 | on_peak | 826.14 |  |  | 0 | 0 | 100 | 0 | 0
1100 | 860.97 | 0 | 20.4 | 0 | 0 | 0 | 0 | 0 | 0 | 62.6277 | 62.6277 | 0 | 7.4394 | 798.3423 | 0 | 0.088511 | 3.9014 | 0 | 0 | 177.1446 | 0 | on_peak | 798.3423 |  |  | 0 | 7.27 | 92.73 | 0 | 0
1101 | 809.95 | 0 | 20.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 809.95 | 0 | 0.088511 | 4.0427 | 0 | 0 | 177.1446 | 0 | on_peak | 809.95 |  |  | 0 | 0 | 100 | 0 | 0
1102 | 778.73 | 0 | 20.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 778.73 | 0 | 0.088511 | 4.3561 | 0 | 0 | 177.1446 | 0 | on_peak | 778.73 |  |  | 0 | 0 | 100 | 0 | 0
1103 | 761.33 | 0 | 20 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 19.0375 | 773.7289 | 0 | 0.05921 | 4.7057 | 0 | 0 | 177.1446 | 0 | off_peak | 761.33 | 0 | 100 | 0 | 0 | 100 | 0 | 0
1104 | 798.99 | 0 | 19.9 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 30.6357 | 811.3889 | 0 | 0.05921 | 5.1907 | 0 | 0 | 177.1446 | 0 | off_peak | 798.99 | 0 | 100 | 0 | 0 | 100 | 0 | 0
1105 | 751.91 | 0 | 19.8 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 42.2338 | 764.3089 | 0 | 0.05921 | 5.4946 | 0 | 0 | 177.1446 | 0 | off_peak | 751.91 | 0 | 100 | 0 | 0 | 100 | 0 | 0
1106 | 652.49 | 0 | 19.7 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 53.832 | 664.8889 | 0 | 0.05921 | 5.4392 | 0 | 0 | 177.1446 | 0 | off_peak | 652.49 | 0 | 100 | 0 | 0 | 100 | 0 | 0
1107 | 611.66 | 0 | 19.7 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 65.4301 | 624.0589 | 0 | 0.05921 | 5.1191 | 0 | 0 | 177.1446 | 0 | off_peak | 611.66 | 0 | 100 | 0 | 0 | 100 | 0 | 0
1108 | 574.88 | 0 | 19.7 | 0 | 0 | 0 | 0 | 8.9635 | 8.9635 | 0 | 0 | 0 | 73.8147 | 583.8435 | 0 | 0.05921 | 4.6913 | 0 | 0 | 177.1446 | 0 | off_peak | 574.88 | 0 | 100 | 0 | 0 | 100 | 0 | 0
1109 | 622.8 | 0 | 19.6 | 0 | 0 | 0 | 0 | 0.57892 | 0.57892 | 0 | 0 | 0 | 74.3563 | 623.3789 | 0 | 0.05921 | 4.2043 | 0 | 0 | 177.1446 | 0 | off_peak | 622.8 | 0 | 100 | 0 | 0 | 100 | 0 | 0
1110 | 680.97 | 0 | 19.5 | 0 | 0 | 0 | 0 | 0.03739 | 0.03739 | 0 | 0 | 0 | 74.3912 | 681.0074 | 0 | 0.05921 | 3.6399 | 0 | 0 | 177.1446 | 0 | off_peak | 680.97 | 0 | 100 | 0 | 0 | 100 | 0 | 0
1111 | 796.03 | 0 | 19.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3912 | 796.03 | 0 | 0.088511 | 3.1644 | 0 | 0 | 177.1446 | 0 | on_peak | 796.03 |  |  | 0 | 0 | 100 | 0 | 0
1112 | 838.18 | 82.9223 | 19.7 | 17.1122 | 17.1122 | 0 | 0 | 0 | 0 | 62.6277 | 62.6277 | 0 | 7.4394 | 758.4401 | 0 | 0.088511 | 2.8091 | 0 | 0 | 177.1446 | 17.1122 | on_peak | 758.4401 |  |  | 2.04 | 7.47 | 90.49 | 48.0705 | 0
1113 | 842.8 | 293.814 | 19.7 | 60.6325 | 60.6325 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 782.1675 | 0 | 0.088511 | 2.6256 | 0 | 0 | 177.1446 | 60.6325 | on_peak | 782.1675 |  |  | 7.19 | 0 | 92.81 | 159.1962 | 0
1114 | 857.32 | 499.394 | 19.7 | 103.0568 | 103.0568 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 754.2632 | 0 | 0.088511 | 2.5373 | 0 | 0 | 177.1446 | 103.0568 | on_peak | 754.2632 |  |  | 12.02 | 0 | 87.98 | 261.4897 | 0
1115 | 853.29 | 666.32 | 20.1 | 137.31 | 124.911 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 0 | 19.0375 | 728.379 | 0 | 0.05921 | 2.5903 | 0 | 0 | 188.7427 | 124.911 | off_peak | 728.379 | 100 | 0 | 14.64 | 0 | 85.36 | 323.5565 | 0
1116 | 899.97 | 773.363 | 20.5 | 159.143 | 159.143 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 30.6357 | 753.2259 | 0 | 0.05921 | 2.9089 | 0 | 0 | 188.7427 | 159.143 | off_peak | 740.827 | 0 | 100 | 17.68 | 0 | 82.32 | 462.9368 | 0
1117 | 848.23 | 814.373 | 20.8 | 167.404 | 167.404 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 42.2338 | 693.225 | 0 | 0.05921 | 3.5216 | 0 | 0 | 188.7427 | 167.404 | off_peak | 680.826 | 0 | 100 | 19.74 | 0 | 80.26 | 589.5296 | 0
1118 | 883.39 | 783.155 | 21.4 | 160.6442 | 160.6442 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 53.832 | 735.1447 | 0 | 0.05921 | 3.8392 | 0 | 0 | 188.7427 | 160.6442 | off_peak | 722.7458 | 0 | 100 | 18.18 | 0 | 81.82 | 616.7373 | 0
1119 | 890.97 | 685.369 | 21.9 | 140.3361 | 140.3361 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 65.4301 | 763.0329 | 0 | 0.05921 | 3.8174 | 0 | 0 | 188.7427 | 140.3361 | off_peak | 750.6339 | 0 | 100 | 15.75 | 0 | 84.25 | 535.7194 | 0
1120 | 902.45 | 528.606 | 22 | 108.1988 | 108.1988 | 0 | 0 | 8.9635 | 8.9635 | 0 | 0 | 0 | 73.8147 | 803.2148 | 0 | 0.05921 | 3.8921 | 0 | 0 | 188.7427 | 108.1988 | off_peak | 794.2512 | 0 | 100 | 11.99 | 0 | 88.01 | 421.1182 | 0
1121 | 895.35 | 326.552 | 21.3 | 67.0076 | 67.0076 | 0 | 0 | 0.57892 | 0.57892 | 0 | 0 | 0 | 74.3563 | 828.9213 | 0 | 0.05921 | 4.0611 | 0 | 0 | 188.7427 | 67.0076 | off_peak | 828.3424 | 0 | 100 | 7.48 | 0 | 92.52 | 272.1271 | 0
1122 | 905.6 | 116.812 | 20.2 | 24.0632 | 24.0632 | 0 | 0 | 0.03739 | 0.03739 | 0 | 0 | 0 | 74.3912 | 881.5742 | 0 | 0.05921 | 4.2751 | 0 | 0 | 188.7427 | 24.0632 | off_peak | 881.5368 | 0 | 100 | 2.66 | 0 | 97.34 | 102.8715 | 0
1123 | 839.12 | 0 | 19.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3912 | 839.12 | 0 | 0.088511 | 4.5608 | 0 | 0 | 188.7427 | 0 | on_peak | 839.12 |  |  | 0 | 0 | 100 | 0 | 0
1124 | 871.39 | 0 | 18.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3912 | 871.39 | 0 | 0.088511 | 4.8627 | 0 | 0 | 188.7427 | 0 | on_peak | 871.39 |  |  | 0 | 0 | 100 | 0 | 0
1125 | 877.86 | 0 | 17.5 | 0 | 0 | 0 | 0 | 0 | 0 | 62.6277 | 62.6277 | 0 | 7.4394 | 815.2323 | 0 | 0.088511 | 5.0883 | 0 | 0 | 188.7427 | 0 | on_peak | 815.2323 |  |  | 0 | 7.13 | 92.87 | 0 | 0
1126 | 799.13 | 0 | 16.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 799.13 | 0 | 0.088511 | 5.2612 | 0 | 0 | 188.7427 | 0 | on_peak | 799.13 |  |  | 0 | 0 | 100 | 0 | 0
1127 | 810.5 | 0 | 15.8 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 19.0375 | 822.8989 | 0 | 0.05921 | 5.6345 | 0 | 0 | 188.7427 | 0 | off_peak | 810.5 | 0 | 100 | 0 | 0 | 100 | 0 | 0
1128 | 837.08 | 0 | 15.1 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 30.6357 | 849.4789 | 0 | 0.05921 | 5.9444 | 0 | 0 | 188.7427 | 0 | off_peak | 837.08 | 0 | 100 | 0 | 0 | 100 | 0 | 0
1129 | 777.01 | 0 | 14.7 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 42.2338 | 789.4089 | 0 | 0.05921 | 6.0334 | 0 | 0 | 188.7427 | 0 | off_peak | 777.01 | 0 | 100 | 0 | 0 | 100 | 0 | 0
1130 | 680.42 | 0 | 14.4 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 53.832 | 692.8189 | 0 | 0.05921 | 5.8865 | 0 | 0 | 188.7427 | 0 | off_peak | 680.42 | 0 | 100 | 0 | 0 | 100 | 0 | 0
1131 | 672.14 | 0 | 14.1 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 65.4301 | 684.5389 | 0 | 0.05921 | 5.5007 | 0 | 0 | 188.7427 | 0 | off_peak | 672.14 | 0 | 100 | 0 | 0 | 100 | 0 | 0
1132 | 608.39 | 0 | 13.6 | 0 | 0 | 0 | 0 | 8.9635 | 8.9635 | 0 | 0 | 0 | 73.8147 | 617.3535 | 0 | 0.05921 | 5.1746 | 0 | 0 | 188.7427 | 0 | off_peak | 608.39 | 0 | 100 | 0 | 0 | 100 | 0 | 0
1133 | 680.26 | 0 | 12.8 | 0 | 0 | 0 | 0 | 0.57892 | 0.57892 | 0 | 0 | 0 | 74.3563 | 680.8389 | 0 | 0.05921 | 4.6757 | 0 | 0 | 188.7427 | 0 | off_peak | 680.26 | 0 | 100 | 0 | 0 | 100 | 0 | 0
1134 | 728.95 | 0 | 11.9 | 0 | 0 | 0 | 0 | 0.03739 | 0.03739 | 0 | 0 | 0 | 74.3912 | 728.9874 | 0 | 0.05921 | 4.072 | 0 | 0 | 188.7427 | 0 | off_peak | 728.95 | 0 | 100 | 0 | 0 | 100 | 0 | 0
1135 | 825.66 | 0 | 11.2 | 0 | 0 | 0 | 0 | 0 | 0 | 62.6277 | 62.6277 | 0 | 7.4394 | 763.0323 | 0 | 0.088511 | 3.724 | 0 | 0 | 188.7427 | 0 | on_peak | 763.0323 |  |  | 0 | 7.59 | 92.41 | 0 | 0
1136 | 877.66 | 87.9749 | 11 | 18.7128 | 18.7128 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 858.9472 | 0 | 0.088511 | 3.4424 | 0 | 0 | 188.7427 | 18.7128 | on_peak | 858.9472 |  |  | 2.13 | 0 | 97.87 | 64.416 | 0
1137 | 867.3 | 300.651 | 11.3 | 63.8845 | 63.8845 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 803.4155 | 0 | 0.088511 | 3.2649 | 0 | 0 | 188.7427 | 63.8845 | on_peak | 803.4155 |  |  | 7.37 | 0 | 92.63 | 208.5749 | 0
1138 | 896.2 | 502.084 | 12 | 106.4303 | 106.4303 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 789.7697 | 0 | 0.088511 | 3.1712 | 0 | 0 | 188.7427 | 106.4303 | on_peak | 789.7697 |  |  | 11.88 | 0 | 88.12 | 337.5123 | 0
1139 | 880.11 | 664.901 | 12.8 | 140.5559 | 128.157 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 0 | 19.0375 | 751.953 | 0 | 0.05921 | 3.1921 | 0 | 0 | 200.3409 | 128.157 | off_peak | 751.953 | 100 | 0 | 14.56 | 0 | 85.44 | 409.0943 | 0
1140 | 925.11 | 727.243 | 13.6 | 153.3105 | 153.3105 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 30.6357 | 784.1984 | 0 | 0.05921 | 3.4238 | 0 | 0 | 200.3409 | 153.3105 | off_peak | 771.7995 | 0 | 100 | 16.57 | 0 | 83.43 | 524.9034 | 0
1141 | 919.06 | 757.013 | 14.3 | 159.2001 | 159.2001 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 42.2338 | 772.2589 | 0 | 0.05921 | 3.9515 | 0 | 0 | 200.3409 | 159.2001 | off_peak | 759.8599 | 0 | 100 | 17.32 | 0 | 82.68 | 629.0812 | 0
1142 | 952 | 703.108 | 14.8 | 147.6075 | 135.2086 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 0 | 53.832 | 816.7914 | 0 | 0.05921 | 4.2778 | 0 | 0 | 211.939 | 135.2086 | off_peak | 816.7914 | 100 | 0 | 14.2 | 0 | 85.8 | 578.392 | 0
1143 | 960.21 | 643.956 | 15.1 | 135.0486 | 135.0486 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 65.4301 | 837.5604 | 0 | 0.05921 | 4.4766 | 0 | 0 | 211.939 | 135.0486 | off_peak | 825.1614 | 0 | 100 | 14.06 | 0 | 85.94 | 604.5526 | 0
1144 | 838.14 | 508.298 | 15.2 | 106.5617 | 106.5617 | 0 | 0 | 8.9635 | 8.9635 | 0 | 0 | 0 | 73.8147 | 740.5418 | 0 | 0.05921 | 4.5869 | 0 | 0 | 211.939 | 106.5617 | off_peak | 731.5783 | 0 | 100 | 12.71 | 0 | 87.29 | 488.7857 | 0
1145 | 914.41 | 326.299 | 14.9 | 68.4781 | 68.4781 | 0 | 0 | 0.57892 | 0.57892 | 0 | 0 | 0 | 74.3563 | 846.5109 | 0 | 0.05921 | 4.7635 | 0 | 0 | 211.939 | 68.4781 | off_peak | 845.9319 | 0 | 100 | 7.49 | 0 | 92.51 | 326.1921 | 0
1146 | 901.95 | 115.994 | 14.2 | 24.402 | 24.402 | 0 | 0 | 0.03739 | 0.03739 | 0 | 0 | 0 | 74.3912 | 877.5854 | 0 | 0.05921 | 4.9988 | 0 | 0 | 211.939 | 24.402 | off_peak | 877.548 | 0 | 100 | 2.71 | 0 | 97.29 | 121.9809 | 0
1147 | 838.77 | 0 | 13.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3912 | 838.77 | 0 | 0.088511 | 5.1696 | 0 | 0 | 211.939 | 0 | on_peak | 838.77 |  |  | 0 | 0 | 100 | 0 | 0
1148 | 870.49 | 0 | 13.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3912 | 870.49 | 0 | 0.088511 | 5.3128 | 0 | 0 | 211.939 | 0 | on_peak | 870.49 |  |  | 0 | 0 | 100 | 0 | 0
1149 | 872.93 | 0 | 13.1 | 0 | 0 | 0 | 0 | 0 | 0 | 62.6277 | 62.6277 | 0 | 7.4394 | 810.3023 | 0 | 0.088511 | 5.4298 | 62.6277 | 0 | 144.9872 | 62.6277 | on_peak | 810.3023 |  |  | 0 | 7.17 | 92.83 | 340.0531 | 0
1150 | 824.6 | 0 | 13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 824.6 | 0 | 0.088511 | 5.5681 | 0 | 0 | 144.9872 | 0 | on_peak | 824.6 |  |  | 0 | 0 | 100 | 0 | 0
1151 | 853.23 | 0 | 12.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 853.23 | 0 | 0.05921 | 5.8165 | 0 | 0 | 144.9872 | 0 | off_peak | 853.23 |  |  | 0 | 0 | 100 | 0 | 0
1152 | 832.12 | 0 | 12.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 832.12 | 0 | 0.05921 | 6.0861 | 0 | 0 | 144.9872 | 0 | off_peak | 832.12 |  |  | 0 | 0 | 100 | 0 | 0
1153 | 777.37 | 0 | 12.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 777.37 | 0 | 0.05921 | 6.2374 | 0 | 0 | 144.9872 | 0 | off_peak | 777.37 |  |  | 0 | 0 | 100 | 0 | 0
1154 | 713.3 | 0 | 13.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 713.3 | 0 | 0.05921 | 6.0483 | 0 | 0 | 144.9872 | 0 | off_peak | 713.3 |  |  | 0 | 0 | 100 | 0 | 0
1155 | 624.09 | 0 | 13.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 624.09 | 0 | 0.05921 | 5.6912 | 0 | 0 | 144.9872 | 0 | off_peak | 624.09 |  |  | 0 | 0 | 100 | 0 | 0
1156 | 651.37 | 0 | 13.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 651.37 | 0 | 0.05921 | 5.3516 | 0 | 0 | 144.9872 | 0 | off_peak | 651.37 |  |  | 0 | 0 | 100 | 0 | 0
1157 | 645.21 | 0 | 13.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 645.21 | 0 | 0.05921 | 4.974 | 0 | 0 | 144.9872 | 0 | off_peak | 645.21 |  |  | 0 | 0 | 100 | 0 | 0
1158 | 727.23 | 0 | 14.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 727.23 | 0 | 0.05921 | 4.3642 | 0 | 0 | 144.9872 | 0 | off_peak | 727.23 |  |  | 0 | 0 | 100 | 0 | 0
1159 | 789.71 | 0 | 14.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 789.71 | 0 | 0.05921 | 4.0932 | 0 | 0 | 144.9872 | 0 | off_peak | 789.71 |  |  | 0 | 0 | 100 | 0 | 0
1160 | 800.65 | 82.8796 | 16.2 | 17.3148 | 17.3148 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 783.3352 | 0 | 0.05921 | 3.7198 | 0 | 0 | 144.9872 | 17.3148 | off_peak | 783.3352 |  |  | 2.16 | 0 | 97.84 | 64.4084 | 0
1161 | 803.81 | 285.71 | 17.4 | 59.4392 | 59.4392 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 744.3708 | 0 | 0.05921 | 3.4741 | 0 | 0 | 144.9872 | 59.4392 | off_peak | 744.3708 |  |  | 7.39 | 0 | 92.61 | 206.4986 | 0
1162 | 811.18 | 486.369 | 18.4 | 100.8298 | 100.8298 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 710.3502 | 0 | 0.05921 | 3.3678 | 0 | 0 | 144.9872 | 100.8298 | off_peak | 710.3502 |  |  | 12.43 | 0 | 87.57 | 339.5697 | 0
1163 | 769.19 | 570.868 | 19.1 | 118.0561 | 118.0561 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 651.1339 | 0 | 0.05921 | 3.3436 | 0 | 0 | 144.9872 | 118.0561 | off_peak | 651.1339 |  |  | 15.35 | 0 | 84.65 | 394.7382 | 0
1164 | 800.69 | 711.486 | 19.5 | 146.9286 | 146.9286 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 653.7614 | 0 | 0.05921 | 3.4543 | 0 | 0 | 144.9872 | 146.9286 | off_peak | 653.7614 |  |  | 18.35 | 0 | 81.65 | 507.5326 | 0
1165 | 732.92 | 797.257 | 19.8 | 164.4668 | 164.4668 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 568.4532 | 0 | 0.05921 | 3.693 | 0 | 0 | 144.9872 | 164.4668 | off_peak | 568.4532 |  |  | 22.44 | 0 | 77.56 | 607.3717 | 0
1166 | 718.54 | 769.957 | 20 | 158.7228 | 158.7228 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 559.8172 | 0 | 0.05921 | 4.0085 | 0 | 0 | 144.9872 | 158.7228 | off_peak | 559.8172 |  |  | 22.09 | 0 | 77.91 | 636.2406 | 0
1167 | 706.04 | 675.201 | 20.1 | 139.1401 | 139.1401 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 566.8999 | 0 | 0.05921 | 4.2051 | 0 | 0 | 144.9872 | 139.1401 | off_peak | 566.8999 |  |  | 19.71 | 0 | 80.29 | 585.0973 | 0
1168 | 675.48 | 522.099 | 20.1 | 107.59 | 107.59 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 567.89 | 0 | 0.05921 | 4.3083 | 0 | 0 | 144.9872 | 107.59 | off_peak | 567.89 |  |  | 15.93 | 0 | 84.07 | 463.532 | 0
1169 | 689.31 | 324.854 | 19.8 | 67.0144 | 67.0144 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 622.2956 | 0 | 0.05921 | 4.2178 | 0 | 0 | 144.9872 | 67.0144 | off_peak | 622.2956 |  |  | 9.72 | 0 | 90.28 | 282.6522 | 0
1170 | 675.82 | 116.636 | 19.3 | 24.1034 | 24.1034 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 651.7166 | 0 | 0.05921 | 4.1443 | 0 | 0 | 144.9872 | 24.1034 | off_peak | 651.7166 |  |  | 3.57 | 0 | 96.43 | 99.8922 | 0
1171 | 609.87 | 0 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 609.87 | 0 | 0.05921 | 4.159 | 0 | 0 | 144.9872 | 0 | off_peak | 609.87 |  |  | 0 | 0 | 100 | 0 | 0
1172 | 593.96 | 0 | 19.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 593.96 | 0 | 0.05921 | 4.2426 | 0 | 0 | 144.9872 | 0 | off_peak | 593.96 |  |  | 0 | 0 | 100 | 0 | 0
1173 | 559.84 | 0 | 19.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 559.84 | 0 | 0.05921 | 4.2636 | 0 | 0 | 144.9872 | 0 | off_peak | 559.84 |  |  | 0 | 0 | 100 | 0 | 0
1174 | 549.36 | 0 | 19.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 549.36 | 0 | 0.05921 | 4.4082 | 0 | 0 | 144.9872 | 0 | off_peak | 549.36 |  |  | 0 | 0 | 100 | 0 | 0
1175 | 562.63 | 0 | 19.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 562.63 | 0 | 0.05921 | 4.7421 | 0 | 0 | 144.9872 | 0 | off_peak | 562.63 |  |  | 0 | 0 | 100 | 0 | 0
1176 | 565.25 | 0 | 19.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 565.25 | 0 | 0.05921 | 5.1498 | 0 | 0 | 144.9872 | 0 | off_peak | 565.25 |  |  | 0 | 0 | 100 | 0 | 0
1177 | 565.88 | 0 | 19.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 565.88 | 0 | 0.05921 | 5.5359 | 0 | 0 | 144.9872 | 0 | off_peak | 565.88 |  |  | 0 | 0 | 100 | 0 | 0
1178 | 539.98 | 0 | 19.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 539.98 | 0 | 0.05921 | 5.4502 | 0 | 0 | 144.9872 | 0 | off_peak | 539.98 |  |  | 0 | 0 | 100 | 0 | 0
1179 | 539.91 | 0 | 19.8 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 19.0375 | 552.3089 | 0 | 0.05921 | 5.2377 | 0 | 0 | 144.9872 | 0 | off_peak | 539.91 | 0 | 100 | 0 | 0 | 100 | 0 | 0
1180 | 579.23 | 0 | 19.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19.0375 | 579.23 | 0 | 0.05921 | 4.9413 | 0 | 0 | 144.9872 | 0 | off_peak | 579.23 |  |  | 0 | 0 | 100 | 0 | 0
1181 | 543.97 | 0 | 19.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19.0375 | 543.97 | 0 | 0.05921 | 4.6337 | 0 | 0 | 144.9872 | 0 | off_peak | 543.97 |  |  | 0 | 0 | 100 | 0 | 0
1182 | 659.89 | 0 | 19.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19.0375 | 659.89 | 0 | 0.05921 | 4.2052 | 0 | 0 | 144.9872 | 0 | off_peak | 659.89 |  |  | 0 | 0 | 100 | 0 | 0
1183 | 700.05 | 0 | 20.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19.0375 | 700.05 | 0 | 0.05921 | 3.8653 | 0 | 0 | 144.9872 | 0 | off_peak | 700.05 |  |  | 0 | 0 | 100 | 0 | 0
1184 | 699.77 | 84.1199 | 21.2 | 17.2673 | 17.2673 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 30.6357 | 694.9016 | 0 | 0.05921 | 3.5362 | 0 | 0 | 144.9872 | 17.2673 | off_peak | 682.5027 | 0 | 100 | 2.47 | 0 | 97.53 | 61.0612 | 0
1185 | 720.49 | 105.961 | 22 | 21.6888 | 21.6888 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30.6357 | 698.8012 | 0 | 0.05921 | 3.3099 | 0 | 0 | 144.9872 | 21.6888 | off_peak | 698.8012 |  |  | 3.01 | 0 | 96.99 | 71.7881 | 0
1186 | 747.38 | 114.5 | 22.4 | 23.4033 | 23.4033 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30.6357 | 723.9767 | 0 | 0.05921 | 3.1356 | 0 | 0 | 144.9872 | 23.4033 | off_peak | 723.9767 |  |  | 3.13 | 0 | 96.87 | 73.3831 | 0
1187 | 736.04 | 124.45 | 22.8 | 25.4007 | 13.0018 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 0 | 42.2338 | 723.0382 | 0 | 0.05921 | 3.08 | 0 | 0 | 156.5853 | 13.0018 | off_peak | 723.0382 | 100 | 0 | 1.77 | 0 | 98.23 | 40.0456 | 0
1188 | 733.62 | 374.268 | 23 | 76.335 | 63.936 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 0 | 53.832 | 669.684 | 0 | 0.05921 | 3.161 | 0 | 0 | 168.1835 | 63.936 | off_peak | 669.684 | 100 | 0 | 8.72 | 0 | 91.28 | 202.099 | 0
1189 | 713.01 | 458.078 | 23 | 93.4287 | 93.4287 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 53.832 | 619.5813 | 0 | 0.05921 | 3.3516 | 0 | 0 | 168.1835 | 93.4287 | off_peak | 619.5813 |  |  | 13.1 | 0 | 86.9 | 313.1361 | 0
1190 | 736.02 | 457.837 | 23 | 93.3795 | 93.3795 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 53.832 | 642.6405 | 0 | 0.05921 | 3.6885 | 0 | 0 | 168.1835 | 93.3795 | off_peak | 642.6405 |  |  | 12.69 | 0 | 87.31 | 344.432 | 0
1191 | 705.43 | 651.638 | 22.9 | 132.9543 | 132.9543 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 53.832 | 572.4757 | 0 | 0.05921 | 3.9442 | 0 | 0 | 168.1835 | 132.9543 | off_peak | 572.4757 |  |  | 18.85 | 0 | 81.15 | 524.4014 | 0
1192 | 719.21 | 401.364 | 22.9 | 81.8907 | 81.8907 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 53.832 | 637.3193 | 0 | 0.05921 | 4.0932 | 0 | 0 | 168.1835 | 81.8907 | off_peak | 637.3193 |  |  | 11.39 | 0 | 88.61 | 335.1958 | 0
1193 | 704.44 | 98.5688 | 22.6 | 20.1326 | 7.7337 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 0 | 65.4301 | 696.7063 | 0 | 0.05921 | 4.2827 | 0 | 0 | 179.7816 | 7.7337 | off_peak | 696.7063 | 100 | 0 | 1.1 | 0 | 98.9 | 33.1212 | 0
1194 | 620.38 | 112.83 | 22.2 | 23.0784 | 23.0784 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 65.4301 | 597.3016 | 0 | 0.05921 | 4.636 | 0 | 0 | 179.7816 | 23.0784 | off_peak | 597.3016 |  |  | 3.72 | 0 | 96.28 | 106.9923 | 0
1195 | 570.14 | 0 | 21.9 | 0 | 0 | 0 | 0 | 8.9635 | 8.9635 | 0 | 0 | 0 | 73.8147 | 579.1035 | 0 | 0.05921 | 5.0404 | 0 | 0 | 179.7816 | 0 | off_peak | 570.14 | 0 | 100 | 0 | 0 | 100 | 0 | 0
1196 | 562.55 | 0 | 21.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 73.8147 | 562.55 | 0 | 0.05921 | 5.2746 | 0 | 0 | 179.7816 | 0 | off_peak | 562.55 |  |  | 0 | 0 | 100 | 0 | 0
1197 | 564.1 | 0 | 21.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 73.8147 | 564.1 | 0 | 0.05921 | 5.4022 | 0 | 0 | 179.7816 | 0 | off_peak | 564.1 |  |  | 0 | 0 | 100 | 0 | 0
1198 | 556.93 | 0 | 21.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 73.8147 | 556.93 | 0 | 0.05921 | 5.7099 | 0 | 0 | 179.7816 | 0 | off_peak | 556.93 |  |  | 0 | 0 | 100 | 0 | 0
1199 | 567.59 | 0 | 21.4 | 0 | 0 | 0 | 0 | 0.57892 | 0.57892 | 0 | 0 | 0 | 74.3563 | 568.1689 | 0 | 0.05921 | 6.0021 | 0 | 0 | 179.7816 | 0 | off_peak | 567.59 | 0 | 100 | 0 | 0 | 100 | 0 | 0
1200 | 548.54 | 0 | 21.4 | 0 | 0 | 0 | 0 | 0.03739 | 0.03739 | 0 | 0 | 0 | 74.3912 | 548.5774 | 0 | 0.05921 | 6.1875 | 0 | 0 | 179.7816 | 0 | off_peak | 548.54 | 0 | 100 | 0 | 0 | 100 | 0 | 0
1201 | 537.9 | 0 | 21.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3912 | 537.9 | 0 | 0.05921 | 6.2892 | 0 | 0 | 179.7816 | 0 | off_peak | 537.9 |  |  | 0 | 0 | 100 | 0 | 0
1202 | 558.16 | 0 | 21.1 | 0 | 0 | 0 | 0 | 0.0024148 | 0.0024148 | 0 | 0 | 0 | 74.3935 | 558.1624 | 0 | 0.05921 | 6.1471 | 0 | 0 | 179.7816 | 0 | off_peak | 558.16 | 0 | 100 | 0 | 0 | 100 | 0 | 0
1203 | 546.92 | 0 | 21 | 0 | 0 | 0 | 0 | 0.00015596 | 0.00015596 | 0 | 0 | 0 | 74.3936 | 546.9202 | 0 | 0.05921 | 5.8651 | 0 | 0 | 179.7816 | 0 | off_peak | 546.92 | 0 | 100 | 0 | 0 | 100 | 0 | 0
1204 | 529.83 | 0 | 20.8 | 0 | 0 | 0 | 0 | 1.0769e-05 | 1.0769e-05 | 0 | 0 | 0 | 74.3936 | 529.83 | 0 | 0.05921 | 5.4619 | 0 | 0 | 179.7816 | 0 | off_peak | 529.83 | 0 | 100 | 0 | 0 | 100 | 0 | 0
1205 | 588.99 | 0 | 20.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 588.99 | 0 | 0.05921 | 4.9539 | 0 | 0 | 179.7816 | 0 | off_peak | 588.99 |  |  | 0 | 0 | 100 | 0 | 0
1206 | 707.97 | 0 | 20.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 707.97 | 0 | 0.05921 | 4.3864 | 0 | 0 | 179.7816 | 0 | off_peak | 707.97 |  |  | 0 | 0 | 100 | 0 | 0
1207 | 737.23 | 0 | 20.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 737.23 | 0 | 0.088511 | 3.8394 | 0 | 0 | 179.7816 | 0 | on_peak | 737.23 |  |  | 0 | 0 | 100 | 0 | 0
1208 | 782.42 | 84.3471 | 20.9 | 17.3324 | 17.3324 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 765.0876 | 0 | 0.088511 | 3.5187 | 0 | 0 | 179.7816 | 17.3324 | on_peak | 765.0876 |  |  | 2.22 | 0 | 97.78 | 60.9872 | 0
1209 | 821.96 | 287.703 | 21.7 | 58.952 | 58.952 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 763.008 | 0 | 0.088511 | 3.2956 | 0 | 0 | 179.7816 | 58.952 | on_peak | 763.008 |  |  | 7.17 | 0 | 92.83 | 194.2812 | 0
1210 | 810.66 | 414.707 | 22.5 | 84.734 | 84.734 | 0 | 0 | 0 | 0 | 62.63 | 62.63 | 0 | 7.4394 | 663.296 | 0 | 0.088511 | 3.1594 | 0 | 0 | 179.7816 | 84.734 | on_peak | 663.296 |  |  | 10.45 | 7.73 | 81.82 | 267.7118 | 0
1211 | 808.52 | 458.175 | 23.2 | 93.3817 | 93.3817 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 19.0375 | 727.5373 | 0 | 0.05921 | 3.1657 | 0 | 0 | 179.7816 | 93.3817 | off_peak | 715.1383 | 0 | 100 | 11.55 | 0 | 88.45 | 295.6223 | 0
1212 | 889.36 | 649.976 | 23.7 | 132.2361 | 132.2361 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 30.6357 | 769.5228 | 0 | 0.05921 | 3.3805 | 0 | 0 | 179.7816 | 132.2361 | off_peak | 757.1239 | 0 | 100 | 14.87 | 0 | 85.13 | 447.0288 | 0
1213 | 843.24 | 681.145 | 24 | 138.4284 | 138.4284 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 42.2338 | 717.2105 | 0 | 0.05921 | 3.7623 | 0 | 0 | 179.7816 | 138.4284 | off_peak | 704.8116 | 0 | 100 | 16.42 | 0 | 83.58 | 520.803 | 0
1214 | 891.36 | 636.873 | 24.3 | 129.2918 | 129.2918 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 53.832 | 774.4672 | 0 | 0.05921 | 4.0651 | 0 | 0 | 179.7816 | 129.2918 | off_peak | 762.0682 | 0 | 100 | 14.51 | 0 | 85.49 | 525.5895 | 0
1215 | 879.67 | 580.407 | 24.3 | 117.8286 | 117.8286 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 65.4301 | 774.2403 | 0 | 0.05921 | 4.1897 | 0 | 0 | 179.7816 | 117.8286 | off_peak | 761.8414 | 0 | 100 | 13.39 | 0 | 86.61 | 493.6704 | 0
1216 | 879.53 | 515.532 | 24.1 | 104.7335 | 104.7335 | 0 | 0 | 8.9635 | 8.9635 | 0 | 0 | 0 | 73.8147 | 783.7601 | 0 | 0.05921 | 4.338 | 0 | 0 | 179.7816 | 104.7335 | off_peak | 774.7965 | 0 | 100 | 11.91 | 0 | 88.09 | 454.3301 | 0
1217 | 891.73 | 317.667 | 23.6 | 64.6518 | 64.6518 | 0 | 0 | 0.57892 | 0.57892 | 0 | 0 | 0 | 74.3563 | 827.6571 | 0 | 0.05921 | 4.4323 | 0 | 0 | 179.7816 | 64.6518 | off_peak | 827.0782 | 0 | 100 | 7.25 | 0 | 92.75 | 286.5538 | 0
1218 | 858.81 | 111.849 | 22.9 | 22.8207 | 22.8207 | 0 | 0 | 0.03739 | 0.03739 | 0 | 0 | 0 | 74.3912 | 836.0267 | 0 | 0.05921 | 4.6881 | 0 | 0 | 179.7816 | 22.8207 | off_peak | 835.9893 | 0 | 100 | 2.66 | 0 | 97.34 | 106.9858 | 0
1219 | 846.23 | 0 | 22.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3912 | 846.23 | 0 | 0.088511 | 5.0777 | 0 | 0 | 179.7816 | 0 | on_peak | 846.23 |  |  | 0 | 0 | 100 | 0 | 0
1220 | 854.3 | 0 | 22.2 | 0 | 0 | 0 | 0 | 0 | 0 | 62.6277 | 62.6277 | 0 | 7.4394 | 791.6723 | 0 | 0.088511 | 5.4337 | 0 | 0 | 179.7816 | 0 | on_peak | 791.6723 |  |  | 0 | 7.33 | 92.67 | 0 | 0
1221 | 820.06 | 0 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 820.06 | 0 | 0.088511 | 5.6612 | 0 | 0 | 179.7816 | 0 | on_peak | 820.06 |  |  | 0 | 0 | 100 | 0 | 0
1222 | 794.03 | 0 | 21.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 794.03 | 0 | 0.088511 | 5.9001 | 0 | 0 | 179.7816 | 0 | on_peak | 794.03 |  |  | 0 | 0 | 100 | 0 | 0
1223 | 810.02 | 0 | 21.7 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 19.0375 | 822.4189 | 0 | 0.05921 | 6.2244 | 0 | 0 | 179.7816 | 0 | off_peak | 810.02 | 0 | 100 | 0 | 0 | 100 | 0 | 0
1224 | 818.68 | 0 | 21.6 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 30.6357 | 831.0789 | 0 | 0.05921 | 6.6813 | 0 | 0 | 179.7816 | 0 | off_peak | 818.68 | 0 | 100 | 0 | 0 | 100 | 0 | 0
1225 | 756 | 0 | 21.5 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 42.2338 | 768.3989 | 0 | 0.05921 | 6.7907 | 0 | 0 | 179.7816 | 0 | off_peak | 756 | 0 | 100 | 0 | 0 | 100 | 0 | 0
1226 | 666.36 | 0 | 21.4 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 53.832 | 678.7589 | 0 | 0.05921 | 6.684 | 0 | 0 | 179.7816 | 0 | off_peak | 666.36 | 0 | 100 | 0 | 0 | 100 | 0 | 0
1227 | 623.76 | 0 | 21.4 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 65.4301 | 636.1589 | 0 | 0.05921 | 6.1995 | 0 | 0 | 179.7816 | 0 | off_peak | 623.76 | 0 | 100 | 0 | 0 | 100 | 0 | 0
1228 | 594.88 | 0 | 21.4 | 0 | 0 | 0 | 0 | 8.9635 | 8.9635 | 0 | 0 | 0 | 73.8147 | 603.8435 | 0 | 0.05921 | 5.8234 | 0 | 0 | 179.7816 | 0 | off_peak | 594.88 | 0 | 100 | 0 | 0 | 100 | 0 | 0
1229 | 599.54 | 0 | 21.4 | 0 | 0 | 0 | 0 | 0.57892 | 0.57892 | 0 | 0 | 0 | 74.3563 | 600.1189 | 0 | 0.05921 | 5.2347 | 0 | 0 | 179.7816 | 0 | off_peak | 599.54 | 0 | 100 | 0 | 0 | 100 | 0 | 0
1230 | 715.14 | 0 | 21.4 | 0 | 0 | 0 | 0 | 0.03739 | 0.03739 | 0 | 0 | 0 | 74.3912 | 715.1774 | 0 | 0.05921 | 4.5398 | 0 | 0 | 179.7816 | 0 | off_peak | 715.14 | 0 | 100 | 0 | 0 | 100 | 0 | 0
1231 | 812.24 | 0 | 21.9 | 0 | 0 | 0 | 0 | 0 | 0 | 62.6277 | 62.6277 | 0 | 7.4394 | 749.6123 | 0 | 0.088511 | 4.016 | 0 | 0 | 179.7816 | 0 | on_peak | 749.6123 |  |  | 0 | 7.71 | 92.29 | 0 | 0
1232 | 791.04 | 84.0958 | 22.9 | 17.1581 | 17.1581 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 773.8819 | 0 | 0.088511 | 3.5727 | 0 | 0 | 179.7816 | 17.1581 | on_peak | 773.8819 |  |  | 2.17 | 0 | 97.83 | 61.301 | 0
1233 | 846.66 | 289.001 | 23.7 | 58.7966 | 58.7966 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 787.8634 | 0 | 0.088511 | 3.3035 | 0 | 0 | 179.7816 | 58.7966 | on_peak | 787.8634 |  |  | 6.94 | 0 | 93.06 | 194.2359 | 0
1234 | 858.28 | 489.782 | 24.2 | 99.4665 | 99.4665 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 758.8135 | 0 | 0.088511 | 3.164 | 0 | 0 | 179.7816 | 99.4665 | on_peak | 758.8135 |  |  | 11.59 | 0 | 88.41 | 314.7086 | 0
1235 | 843.26 | 617.932 | 24.6 | 125.3114 | 125.3114 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 19.0375 | 730.3475 | 0 | 0.05921 | 3.1735 | 0 | 0 | 179.7816 | 125.3114 | off_peak | 717.9486 | 0 | 100 | 14.86 | 0 | 85.14 | 397.6742 | 0
1236 | 895.57 | 570.158 | 24.9 | 115.4986 | 115.4986 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 30.6357 | 792.4704 | 0 | 0.05921 | 3.473 | 0 | 0 | 179.7816 | 115.4986 | off_peak | 780.0714 | 0 | 100 | 12.9 | 0 | 87.1 | 401.1233 | 0
1237 | 884.48 | 613.746 | 25 | 124.2836 | 124.2836 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 42.2338 | 772.5954 | 0 | 0.05921 | 4.0317 | 0 | 0 | 179.7816 | 124.2836 | off_peak | 760.1964 | 0 | 100 | 14.05 | 0 | 85.95 | 501.0757 | 0
1238 | 896.42 | 698.899 | 25.1 | 141.4761 | 141.4761 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 53.832 | 767.3428 | 0 | 0.05921 | 4.2887 | 0 | 0 | 179.7816 | 141.4761 | off_peak | 754.9439 | 0 | 100 | 15.78 | 0 | 84.22 | 606.7499 | 0
1239 | 926.63 | 590.818 | 25 | 119.6406 | 119.6406 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 65.4301 | 819.3883 | 0 | 0.05921 | 4.444 | 0 | 0 | 179.7816 | 119.6406 | off_peak | 806.9894 | 0 | 100 | 12.91 | 0 | 87.09 | 531.6865 | 0
1240 | 950.18 | 515.34 | 24.8 | 104.4315 | 104.4315 | 0 | 0 | 8.9635 | 8.9635 | 0 | 0 | 0 | 73.8147 | 854.7121 | 0 | 0.05921 | 4.531 | 0 | 0 | 179.7816 | 104.4315 | off_peak | 845.7485 | 0 | 100 | 10.99 | 0 | 89.01 | 473.1828 | 0
1241 | 890.5 | 314.068 | 24.4 | 63.7361 | 63.7361 | 0 | 0 | 0.57892 | 0.57892 | 0 | 0 | 0 | 74.3563 | 827.3428 | 0 | 0.05921 | 4.6146 | 0 | 0 | 179.7816 | 63.7361 | off_peak | 826.7639 | 0 | 100 | 7.16 | 0 | 92.84 | 294.1167 | 0
1242 | 899.97 | 117.592 | 23.7 | 23.9238 | 23.9238 | 0 | 0 | 0.03739 | 0.03739 | 0 | 0 | 0 | 74.3912 | 876.0836 | 0 | 0.05921 | 4.7401 | 0 | 0 | 179.7816 | 23.9238 | off_peak | 876.0462 | 0 | 100 | 2.66 | 0 | 97.34 | 113.4014 | 0
1243 | 843.47 | 0 | 23.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3912 | 843.47 | 0 | 0.088511 | 5.0829 | 0 | 0 | 179.7816 | 0 | on_peak | 843.47 |  |  | 0 | 0 | 100 | 0 | 0
1244 | 847.14 | 0 | 22.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3912 | 847.14 | 0 | 0.088511 | 5.4119 | 0 | 0 | 179.7816 | 0 | on_peak | 847.14 |  |  | 0 | 0 | 100 | 0 | 0
1245 | 906.59 | 0 | 22.8 | 0 | 0 | 0 | 0 | 0 | 0 | 62.6277 | 62.6277 | 0 | 7.4394 | 843.9623 | 0 | 0.088511 | 5.7462 | 0 | 0 | 179.7816 | 0 | on_peak | 843.9623 |  |  | 0 | 6.91 | 93.09 | 0 | 0
1246 | 813.74 | 0 | 22.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 813.74 | 0 | 0.088511 | 6.0652 | 0 | 0 | 179.7816 | 0 | on_peak | 813.74 |  |  | 0 | 0 | 100 | 0 | 0
1247 | 828.36 | 0 | 22.6 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 19.0375 | 840.7589 | 0 | 0.05921 | 6.5167 | 0 | 0 | 179.7816 | 0 | off_peak | 828.36 | 0 | 100 | 0 | 0 | 100 | 0 | 0
1248 | 874.32 | 0 | 22.5 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 30.6357 | 886.7189 | 0 | 0.05921 | 6.9448 | 0 | 0 | 179.7816 | 0 | off_peak | 874.32 | 0 | 100 | 0 | 0 | 100 | 0 | 0
1249 | 733.02 | 0 | 22.4 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 42.2338 | 745.4189 | 0 | 0.05921 | 7.1038 | 0 | 0 | 179.7816 | 0 | off_peak | 733.02 | 0 | 100 | 0 | 0 | 100 | 0 | 0
1250 | 696 | 0 | 22.3 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 53.832 | 708.3989 | 0 | 0.05921 | 6.9614 | 0 | 0 | 179.7816 | 0 | off_peak | 696 | 0 | 100 | 0 | 0 | 100 | 0 | 0
1251 | 618.96 | 0 | 22.3 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 65.4301 | 631.3589 | 0 | 0.05921 | 6.4484 | 0 | 0 | 179.7816 | 0 | off_peak | 618.96 | 0 | 100 | 0 | 0 | 100 | 0 | 0
1252 | 609.62 | 0 | 22.4 | 0 | 0 | 0 | 0 | 8.9635 | 8.9635 | 0 | 0 | 0 | 73.8147 | 618.5835 | 0 | 0.05921 | 5.8439 | 0 | 0 | 179.7816 | 0 | off_peak | 609.62 | 0 | 100 | 0 | 0 | 100 | 0 | 0
1253 | 646.75 | 0 | 22.4 | 0 | 0 | 0 | 0 | 0.57892 | 0.57892 | 0 | 0 | 0 | 74.3563 | 647.3289 | 0 | 0.05921 | 5.2164 | 0 | 0 | 179.7816 | 0 | off_peak | 646.75 | 0 | 100 | 0 | 0 | 100 | 0 | 0
1254 | 698.18 | 0 | 22.5 | 0 | 0 | 0 | 0 | 0.03739 | 0.03739 | 0 | 0 | 0 | 74.3912 | 698.2174 | 0 | 0.05921 | 4.564 | 0 | 0 | 179.7816 | 0 | off_peak | 698.18 | 0 | 100 | 0 | 0 | 100 | 0 | 0
1255 | 796.1 | 0 | 23 | 0 | 0 | 0 | 0 | 0 | 0 | 62.6277 | 62.6277 | 0 | 7.4394 | 733.4723 | 0 | 0.088511 | 3.9193 | 0 | 0 | 179.7816 | 0 | on_peak | 733.4723 |  |  | 0 | 7.87 | 92.13 | 0 | 0
1256 | 839.7 | 86.0723 | 23.8 | 17.5049 | 17.5049 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 822.1951 | 0 | 0.088511 | 3.5114 | 0 | 0 | 179.7816 | 17.5049 | on_peak | 822.1951 |  |  | 2.08 | 0 | 97.92 | 61.4669 | 0
1257 | 847.73 | 290.018 | 24.4 | 58.8555 | 58.8555 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 788.8745 | 0 | 0.088511 | 3.2875 | 0 | 0 | 179.7816 | 58.8555 | on_peak | 788.8745 |  |  | 6.94 | 0 | 93.06 | 193.49 | 0
1258 | 859.82 | 488.463 | 24.9 | 98.9494 | 98.9494 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 760.8706 | 0 | 0.088511 | 3.1319 | 0 | 0 | 179.7816 | 98.9494 | on_peak | 760.8706 |  |  | 11.51 | 0 | 88.49 | 309.8982 | 0
1259 | 858.96 | 629.715 | 25.2 | 127.4255 | 115.0265 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 0 | 19.0375 | 743.9335 | 0 | 0.05921 | 3.1382 | 0 | 0 | 191.3797 | 115.0265 | off_peak | 743.9335 | 100 | 0 | 13.39 | 0 | 86.61 | 360.9719 | 0
1260 | 941.17 | 656.828 | 25.5 | 132.7683 | 132.7683 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 30.6357 | 820.8007 | 0 | 0.05921 | 3.0918 | 0 | 0 | 191.3797 | 132.7683 | off_peak | 808.4017 | 0 | 100 | 14.11 | 0 | 85.89 | 410.4951 | 0
1261 | 845.41 | 610.664 | 25.6 | 123.3924 | 123.3924 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 42.2338 | 734.4166 | 0 | 0.05921 | 3.937 | 0 | 0 | 191.3797 | 123.3924 | off_peak | 722.0176 | 0 | 100 | 14.6 | 0 | 85.4 | 485.7925 | 0
1262 | 901.05 | 523.975 | 25.7 | 105.8376 | 105.8376 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 53.832 | 807.6114 | 0 | 0.05921 | 4.2366 | 0 | 0 | 191.3797 | 105.8376 | off_peak | 795.2124 | 0 | 100 | 11.75 | 0 | 88.25 | 448.3878 | 0
1263 | 949.87 | 459.157 | 25.7 | 92.745 | 92.745 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 65.4301 | 869.524 | 0 | 0.05921 | 4.279 | 0 | 0 | 191.3797 | 92.745 | off_peak | 857.125 | 0 | 100 | 9.76 | 0 | 90.24 | 396.8512 | 0
1264 | 925.36 | 523.977 | 25.5 | 105.9144 | 96.9508 | 0 | 8.9635 | 8.9635 | 0 | 0 | 0 | 0 | 73.8147 | 828.4092 | 0 | 0.05921 | 4.3335 | 0 | 0 | 199.7644 | 96.9508 | off_peak | 828.4092 | 100 | 0 | 10.48 | 0 | 89.52 | 420.1335 | 0
1265 | 965.85 | 329.216 | 25.2 | 66.6182 | 66.6182 | 0 | 0 | 0.57892 | 0.57892 | 0 | 0 | 0 | 74.3563 | 899.8107 | 0 | 0.05921 | 4.5301 | 0 | 0 | 199.7644 | 66.6182 | off_peak | 899.2318 | 0 | 100 | 6.9 | 0 | 93.1 | 301.7854 | 0
1266 | 908.69 | 121.063 | 24.6 | 24.5506 | 24.5506 | 0 | 0 | 0.03739 | 0.03739 | 0 | 0 | 0 | 74.3912 | 884.1768 | 0 | 0.05921 | 4.8975 | 0 | 0 | 199.7644 | 24.5506 | off_peak | 884.1394 | 0 | 100 | 2.7 | 0 | 97.3 | 120.237 | 0
1267 | 865.94 | 0 | 24.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3912 | 865.94 | 0 | 0.088511 | 5.3406 | 0 | 0 | 199.7644 | 0 | on_peak | 865.94 |  |  | 0 | 0 | 100 | 0 | 0
1268 | 902.62 | 0 | 23.8 | 0 | 0 | 0 | 0 | 0 | 0 | 60.6718 | 60.6718 | 0 | 9.5303 | 841.9482 | 0 | 0.088511 | 5.7237 | 0 | 0 | 199.7644 | 0 | on_peak | 841.9482 |  |  | 0 | 6.72 | 93.28 | 0 | 0
1269 | 879.77 | 0 | 23.7 | 0 | 0 | 0 | 0 | 0 | 0 | 1.9559 | 1.9559 | 0 | 7.4394 | 877.8141 | 0 | 0.088511 | 6.0668 | 0 | 0 | 199.7644 | 0 | on_peak | 877.8141 |  |  | 0 | 0.22 | 99.78 | 0 | 0
1270 | 814.88 | 0 | 23.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 814.88 | 0 | 0.088511 | 6.3216 | 0 | 0 | 199.7644 | 0 | on_peak | 814.88 |  |  | 0 | 0 | 100 | 0 | 0
1271 | 877.3 | 0 | 23.5 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 19.0375 | 889.6989 | 0 | 0.05921 | 6.7311 | 0 | 0 | 199.7644 | 0 | off_peak | 877.3 | 0 | 100 | 0 | 0 | 100 | 0 | 0
1272 | 814.65 | 0 | 23.4 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 30.6357 | 827.0489 | 0 | 0.05921 | 7.1733 | 0 | 0 | 199.7644 | 0 | off_peak | 814.65 | 0 | 100 | 0 | 0 | 100 | 0 | 0
1273 | 779.18 | 0 | 23.2 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 42.2338 | 791.5789 | 0 | 0.05921 | 7.2198 | 0 | 0 | 199.7644 | 0 | off_peak | 779.18 | 0 | 100 | 0 | 0 | 100 | 0 | 0
1274 | 691.77 | 0 | 23.1 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 53.832 | 704.1689 | 0 | 0.05921 | 7.0403 | 0 | 0 | 199.7644 | 0 | off_peak | 691.77 | 0 | 100 | 0 | 0 | 100 | 0 | 0
1275 | 650.03 | 0 | 22.9 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 65.4301 | 662.4289 | 0 | 0.05921 | 6.6079 | 0 | 0 | 199.7644 | 0 | off_peak | 650.03 | 0 | 100 | 0 | 0 | 100 | 0 | 0
1276 | 628.17 | 0 | 22.9 | 0 | 0 | 0 | 0 | 8.9635 | 8.9635 | 0 | 0 | 0 | 73.8147 | 637.1335 | 0 | 0.05921 | 6.0261 | 0 | 0 | 199.7644 | 0 | off_peak | 628.17 | 0 | 100 | 0 | 0 | 100 | 0 | 0
1277 | 665.28 | 0 | 22.9 | 0 | 0 | 0 | 0 | 0.57892 | 0.57892 | 0 | 0 | 0 | 74.3563 | 665.8589 | 0 | 0.05921 | 5.4472 | 0 | 0 | 199.7644 | 0 | off_peak | 665.28 | 0 | 100 | 0 | 0 | 100 | 0 | 0
1278 | 737.66 | 0 | 22.9 | 0 | 0 | 0 | 0 | 0.03739 | 0.03739 | 0 | 0 | 0 | 74.3912 | 737.6974 | 0 | 0.05921 | 4.7747 | 0 | 0 | 199.7644 | 0 | off_peak | 737.66 | 0 | 100 | 0 | 0 | 100 | 0 | 0
1279 | 812.31 | 0 | 23.4 | 0 | 0 | 0 | 0 | 0 | 0 | 62.6277 | 62.6277 | 0 | 7.4394 | 749.6823 | 0 | 0.088511 | 4.2256 | 0 | 0 | 199.7644 | 0 | on_peak | 749.6823 |  |  | 0 | 7.71 | 92.29 | 0 | 0
1280 | 817.99 | 94.3593 | 24.2 | 19.1628 | 19.1628 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 798.8272 | 0 | 0.088511 | 3.8035 | 0 | 0 | 199.7644 | 19.1628 | on_peak | 798.8272 |  |  | 2.34 | 0 | 97.66 | 72.8853 | 0
1281 | 855.69 | 253.8 | 24.9 | 51.413 | 51.413 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 804.277 | 0 | 0.088511 | 3.5865 | 0 | 0 | 199.7644 | 51.413 | on_peak | 804.277 |  |  | 6.01 | 0 | 93.99 | 184.3913 | 0
1282 | 874.53 | 498.245 | 25.4 | 100.7493 | 100.7493 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 773.7807 | 0 | 0.088511 | 3.441 | 0 | 0 | 199.7644 | 100.7493 | on_peak | 773.7807 |  |  | 11.52 | 0 | 88.48 | 346.6828 | 0
1283 | 835.08 | 668.357 | 25.8 | 134.9525 | 134.9525 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 19.0375 | 712.5264 | 0 | 0.05921 | 3.4186 | 0 | 0 | 199.7644 | 134.9525 | off_peak | 700.1275 | 0 | 100 | 16.16 | 0 | 83.84 | 461.3456 | 0
1284 | 961.88 | 669.598 | 26.2 | 135.0078 | 135.0078 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 30.6357 | 839.2711 | 0 | 0.05921 | 3.6487 | 0 | 0 | 199.7644 | 135.0078 | off_peak | 826.8722 | 0 | 100 | 14.04 | 0 | 85.96 | 492.6038 | 0
1285 | 908.96 | 809.228 | 26.3 | 163.1018 | 163.1018 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 42.2338 | 758.2572 | 0 | 0.05921 | 4.1507 | 0 | 0 | 199.7644 | 163.1018 | off_peak | 745.8582 | 0 | 100 | 17.94 | 0 | 82.06 | 676.9786 | 0
1286 | 908.75 | 740.343 | 26.4 | 149.1639 | 136.7649 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 0 | 53.832 | 771.9851 | 0 | 0.05921 | 4.5366 | 0 | 0 | 211.3625 | 136.7649 | off_peak | 771.9851 | 100 | 0 | 15.05 | 0 | 84.95 | 620.4467 | 0
1287 | 979.68 | 426.386 | 26.3 | 85.9391 | 85.9391 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 65.4301 | 906.1399 | 0 | 0.05921 | 4.6069 | 0 | 0 | 211.3625 | 85.9391 | off_peak | 893.7409 | 0 | 100 | 8.77 | 0 | 91.23 | 395.9149 | 0
1288 | 895.22 | 356.58 | 26.1 | 71.9215 | 71.9215 | 0 | 0 | 8.9635 | 8.9635 | 0 | 0 | 0 | 73.8147 | 832.262 | 0 | 0.05921 | 4.7762 | 0 | 0 | 211.3625 | 71.9215 | off_peak | 823.2985 | 0 | 100 | 8.03 | 0 | 91.97 | 343.5145 | 0
1289 | 902.81 | 272.261 | 25.8 | 54.9741 | 54.9741 | 0 | 0 | 0.57892 | 0.57892 | 0 | 0 | 0 | 74.3563 | 848.4148 | 0 | 0.05921 | 5.16 | 0 | 0 | 211.3625 | 54.9741 | off_peak | 847.8359 | 0 | 100 | 6.09 | 0 | 93.91 | 283.6658 | 0
1290 | 910.42 | 122.554 | 25.2 | 24.7993 | 24.7993 | 0 | 0 | 0.03739 | 0.03739 | 0 | 0 | 0 | 74.3912 | 885.6581 | 0 | 0.05921 | 5.5262 | 0 | 0 | 211.3625 | 24.7993 | off_peak | 885.6207 | 0 | 100 | 2.72 | 0 | 97.28 | 137.0448 | 0
1291 | 824.63 | 0 | 24.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3912 | 824.63 | 0 | 0.088511 | 5.9399 | 0 | 0 | 211.3625 | 0 | on_peak | 824.63 |  |  | 0 | 0 | 100 | 0 | 0
1292 | 865.53 | 0 | 24.3 | 0 | 0 | 0 | 0 | 0 | 0 | 62.6277 | 62.6277 | 0 | 7.4394 | 802.9023 | 0 | 0.088511 | 6.2467 | 0 | 0 | 211.3625 | 0 | on_peak | 802.9023 |  |  | 0 | 7.24 | 92.76 | 0 | 0
1293 | 836.31 | 0 | 24.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 836.31 | 0 | 0.088511 | 6.641 | 0 | 0 | 211.3625 | 0 | on_peak | 836.31 |  |  | 0 | 0 | 100 | 0 | 0
1294 | 792.52 | 0 | 23.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 792.52 | 0 | 0.088511 | 7.05 | 0 | 0 | 211.3625 | 0 | on_peak | 792.52 |  |  | 0 | 0 | 100 | 0 | 0
1295 | 811.96 | 0 | 23.7 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 19.0375 | 824.3589 | 0 | 0.05921 | 7.3613 | 0 | 0 | 211.3625 | 0 | off_peak | 811.96 | 0 | 100 | 0 | 0 | 100 | 0 | 0
1296 | 831.95 | 0 | 23.6 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 30.6357 | 844.3489 | 0 | 0.05921 | 7.4896 | 0 | 0 | 211.3625 | 0 | off_peak | 831.95 | 0 | 100 | 0 | 0 | 100 | 0 | 0
1297 | 745.59 | 0 | 23.4 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 42.2338 | 757.9889 | 0 | 0.05921 | 7.4209 | 0 | 0 | 211.3625 | 0 | off_peak | 745.59 | 0 | 100 | 0 | 0 | 100 | 0 | 0
1298 | 679.3 | 0 | 23.3 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 53.832 | 691.6989 | 0 | 0.05921 | 7.3328 | 0 | 0 | 211.3625 | 0 | off_peak | 679.3 | 0 | 100 | 0 | 0 | 100 | 0 | 0
1299 | 604.27 | 0 | 23.2 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 65.4301 | 616.6689 | 0 | 0.05921 | 6.7743 | 0 | 0 | 211.3625 | 0 | off_peak | 604.27 | 0 | 100 | 0 | 0 | 100 | 0 | 0
1300 | 618.26 | 0 | 23 | 0 | 0 | 0 | 0 | 8.9635 | 8.9635 | 0 | 0 | 0 | 73.8147 | 627.2235 | 0 | 0.05921 | 6.1063 | 0 | 0 | 211.3625 | 0 | off_peak | 618.26 | 0 | 100 | 0 | 0 | 100 | 0 | 0
1301 | 582.23 | 0 | 23 | 0 | 0 | 0 | 0 | 0.57892 | 0.57892 | 0 | 0 | 0 | 74.3563 | 582.8089 | 0 | 0.05921 | 5.5827 | 0 | 0 | 211.3625 | 0 | off_peak | 582.23 | 0 | 100 | 0 | 0 | 100 | 0 | 0
1302 | 686.15 | 0 | 22.9 | 0 | 0 | 0 | 0 | 0.03739 | 0.03739 | 0 | 0 | 0 | 74.3912 | 686.1874 | 0 | 0.05921 | 4.8015 | 0 | 0 | 211.3625 | 0 | off_peak | 686.15 | 0 | 100 | 0 | 0 | 100 | 0 | 0
1303 | 787.85 | 0 | 23.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3912 | 787.85 | 0 | 0.088511 | 4.2305 | 0 | 0 | 211.3625 | 0 | on_peak | 787.85 |  |  | 0 | 0 | 100 | 0 | 0
1304 | 851.25 | 99.4476 | 24.2 | 20.1961 | 20.1961 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3912 | 831.0539 | 0 | 0.088511 | 3.8057 | 0 | 0 | 211.3625 | 20.1961 | on_peak | 831.0539 |  |  | 2.37 | 0 | 97.63 | 76.8599 | 0
1305 | 893.43 | 310.409 | 25 | 62.8578 | 62.8578 | 0 | 0 | 0 | 0 | 62.6277 | 62.6277 | 0 | 7.4394 | 767.9444 | 0 | 0.088511 | 3.5205 | 0 | 0 | 211.3625 | 62.8578 | on_peak | 767.9444 |  |  | 7.04 | 7.01 | 85.95 | 221.293 | 0
1306 | 917.77 | 478.162 | 25.8 | 96.5489 | 96.5489 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 821.2211 | 0 | 0.088511 | 3.3651 | 0 | 0 | 211.3625 | 96.5489 | on_peak | 821.2211 |  |  | 10.52 | 0 | 89.48 | 324.8934 | 0
1307 | 874.61 | 552.021 | 26.4 | 111.2209 | 111.2209 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 19.0375 | 775.7881 | 0 | 0.05921 | 3.3545 | 0 | 0 | 211.3625 | 111.2209 | off_peak | 763.3891 | 0 | 100 | 12.72 | 0 | 87.28 | 373.0877 | 0
1308 | 1002.35 | 660.915 | 26.9 | 132.9199 | 132.9199 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 30.6357 | 881.8291 | 0 | 0.05921 | 3.5627 | 0 | 0 | 211.3625 | 132.9199 | off_peak | 869.4301 | 0 | 100 | 13.26 | 0 | 86.74 | 473.5531 | 0
1309 | 871.01 | 704.699 | 27.2 | 141.5714 | 141.5714 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 42.2338 | 741.8376 | 0 | 0.05921 | 4.0388 | 0 | 0 | 211.3625 | 141.5714 | off_peak | 729.4386 | 0 | 100 | 16.25 | 0 | 83.75 | 571.7772 | 0
1310 | 979.68 | 605.774 | 27.4 | 121.6094 | 121.6094 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 53.832 | 870.4696 | 0 | 0.05921 | 4.4716 | 0 | 0 | 211.3625 | 121.6094 | off_peak | 858.0706 | 0 | 100 | 12.41 | 0 | 87.59 | 543.7829 | 0
1311 | 1021.2 | 683.486 | 27.5 | 137.1603 | 137.1603 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 65.4301 | 896.4387 | 0 | 0.05921 | 4.5786 | 0 | 0 | 211.3625 | 137.1603 | off_peak | 884.0397 | 0 | 100 | 13.43 | 0 | 86.57 | 628.0059 | 0
1312 | 938.33 | 485.764 | 27.4 | 97.5173 | 97.5173 | 0 | 0 | 8.9635 | 8.9635 | 0 | 0 | 0 | 73.8147 | 849.7762 | 0 | 0.05921 | 4.6403 | 0 | 0 | 211.3625 | 97.5173 | off_peak | 840.8127 | 0 | 100 | 10.39 | 0 | 89.61 | 452.5099 | 0
1313 | 952.68 | 338.268 | 27 | 68.0061 | 68.0061 | 0 | 0 | 0.57892 | 0.57892 | 0 | 0 | 0 | 74.3563 | 885.2528 | 0 | 0.05921 | 4.8437 | 0 | 0 | 211.3625 | 68.0061 | off_peak | 884.6739 | 0 | 100 | 7.14 | 0 | 92.86 | 329.4008 | 0
1314 | 893.53 | 126.877 | 26.3 | 25.5724 | 25.5724 | 0 | 0 | 0.03739 | 0.03739 | 0 | 0 | 0 | 74.3912 | 867.995 | 0 | 0.05921 | 5.3749 | 0 | 0 | 211.3625 | 25.5724 | off_peak | 867.9576 | 0 | 100 | 2.86 | 0 | 97.14 | 137.4495 | 0
1315 | 868.4 | 0 | 25.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3912 | 868.4 | 0 | 0.088511 | 5.8319 | 0 | 0 | 211.3625 | 0 | on_peak | 868.4 |  |  | 0 | 0 | 100 | 0 | 0
1316 | 896.19 | 0 | 25.2 | 0 | 0 | 0 | 0 | 0 | 0 | 62.6277 | 62.6277 | 0 | 7.4394 | 833.5623 | 0 | 0.088511 | 6.206 | 0 | 0 | 211.3625 | 0 | on_peak | 833.5623 |  |  | 0 | 6.99 | 93.01 | 0 | 0
1317 | 813.03 | 0 | 24.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 813.03 | 0 | 0.088511 | 6.7031 | 0 | 0 | 211.3625 | 0 | on_peak | 813.03 |  |  | 0 | 0 | 100 | 0 | 0
1318 | 809.76 | 0 | 24.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 809.76 | 0 | 0.088511 | 6.9753 | 0 | 0 | 211.3625 | 0 | on_peak | 809.76 |  |  | 0 | 0 | 100 | 0 | 0
1319 | 851.24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 851.24 | 0 | 0.05921 | 7.2501 | 0 | 0 | 211.3625 | 0 | off_peak | 851.24 |  |  | 0 | 0 | 100 | 0 | 0
1320 | 786.42 | 0 | 23.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 786.42 | 0 | 0.05921 | 7.4019 | 0 | 0 | 211.3625 | 0 | off_peak | 786.42 |  |  | 0 | 0 | 100 | 0 | 0
1321 | 785.94 | 0 | 23.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 785.94 | 0 | 0.05921 | 7.3454 | 0 | 0 | 211.3625 | 0 | off_peak | 785.94 |  |  | 0 | 0 | 100 | 0 | 0
1322 | 683.68 | 0 | 23.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 683.68 | 0 | 0.05921 | 7.0736 | 0 | 0 | 211.3625 | 0 | off_peak | 683.68 |  |  | 0 | 0 | 100 | 0 | 0
1323 | 671.34 | 0 | 23.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 671.34 | 0 | 0.05921 | 6.4155 | 0 | 0 | 211.3625 | 0 | off_peak | 671.34 |  |  | 0 | 0 | 100 | 0 | 0
1324 | 683.15 | 0 | 23.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 683.15 | 0 | 0.05921 | 5.8487 | 0 | 0 | 211.3625 | 0 | off_peak | 683.15 |  |  | 0 | 0 | 100 | 0 | 0
1325 | 688.84 | 0 | 23.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 688.84 | 0 | 0.05921 | 5.3848 | 0 | 0 | 211.3625 | 0 | off_peak | 688.84 |  |  | 0 | 0 | 100 | 0 | 0
1326 | 782.05 | 0 | 23.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 782.05 | 0 | 0.05921 | 4.7556 | 0 | 0 | 211.3625 | 0 | off_peak | 782.05 |  |  | 0 | 0 | 100 | 0 | 0
1327 | 773.98 | 0 | 23.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 773.98 | 0 | 0.05921 | 4.1928 | 0 | 0 | 211.3625 | 0 | off_peak | 773.98 |  |  | 0 | 0 | 100 | 0 | 0
1328 | 820.85 | 102.683 | 24.7 | 20.8158 | 20.8158 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 800.0342 | 0 | 0.05921 | 3.7835 | 0 | 0 | 211.3625 | 20.8158 | off_peak | 800.0342 |  |  | 2.54 | 0 | 97.46 | 78.7568 | 0
1329 | 878.55 | 260.099 | 25.5 | 52.5752 | 52.5752 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 825.9748 | 0 | 0.05921 | 3.4869 | 0 | 0 | 211.3625 | 52.5752 | off_peak | 825.9748 |  |  | 5.98 | 0 | 94.02 | 183.3271 | 0
1330 | 852.11 | 476.95 | 26 | 96.2347 | 96.2347 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 755.8753 | 0 | 0.05921 | 3.2928 | 0 | 0 | 211.3625 | 96.2347 | off_peak | 755.8753 |  |  | 11.29 | 0 | 88.71 | 316.8811 | 0
1331 | 845.48 | 367.929 | 26.4 | 74.1301 | 74.1301 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 771.3499 | 0 | 0.05921 | 3.1929 | 0 | 0 | 211.3625 | 74.1301 | off_peak | 771.3499 |  |  | 8.77 | 0 | 91.23 | 236.6893 | 0
1332 | 926.17 | 788.221 | 26.8 | 158.5804 | 158.5804 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 767.5896 | 0 | 0.05921 | 3.2076 | 0 | 0 | 211.3625 | 158.5804 | off_peak | 767.5896 |  |  | 17.12 | 0 | 82.88 | 508.6625 | 0
1333 | 821.78 | 798.657 | 26.9 | 160.6218 | 160.6218 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 661.1582 | 0 | 0.05921 | 3.3693 | 0 | 0 | 211.3625 | 160.6218 | off_peak | 661.1582 |  |  | 19.55 | 0 | 80.45 | 541.1757 | 0
1334 | 834.13 | 796.58 | 27 | 160.146 | 160.146 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 673.984 | 0 | 0.05921 | 3.7438 | 0 | 0 | 211.3625 | 160.146 | off_peak | 673.984 |  |  | 19.2 | 0 | 80.8 | 599.5539 | 0
1335 | 764.41 | 677.839 | 27 | 136.2741 | 136.2741 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 628.1359 | 0 | 0.05921 | 4.1606 | 0 | 0 | 211.3625 | 136.2741 | off_peak | 628.1359 |  |  | 17.83 | 0 | 82.17 | 566.9868 | 0
1336 | 777.33 | 544.052 | 26.8 | 109.4566 | 109.4566 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 667.8734 | 0 | 0.05921 | 4.4845 | 0 | 0 | 211.3625 | 109.4566 | off_peak | 667.8734 |  |  | 14.08 | 0 | 85.92 | 490.859 | 0
1337 | 793.52 | 345.212 | 26.4 | 69.5531 | 69.5531 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 723.9669 | 0 | 0.05921 | 4.8106 | 0 | 0 | 211.3625 | 69.5531 | off_peak | 723.9669 |  |  | 8.77 | 0 | 91.23 | 334.5899 | 0
1338 | 728.87 | 131.66 | 25.7 | 26.594 | 26.594 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 702.276 | 0 | 0.05921 | 5.2791 | 0 | 0 | 211.3625 | 26.594 | off_peak | 702.276 |  |  | 3.65 | 0 | 96.35 | 140.3911 | 0
1339 | 686.95 | 0 | 25.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 686.95 | 0 | 0.05921 | 5.5543 | 0 | 0 | 211.3625 | 0 | off_peak | 686.95 |  |  | 0 | 0 | 100 | 0 | 0
1340 | 677.14 | 0 | 24.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 677.14 | 0 | 0.05921 | 5.9 | 0 | 0 | 211.3625 | 0 | off_peak | 677.14 |  |  | 0 | 0 | 100 | 0 | 0
1341 | 632.6 | 0 | 24.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 632.6 | 0 | 0.05921 | 6.1607 | 0 | 0 | 211.3625 | 0 | off_peak | 632.6 |  |  | 0 | 0 | 100 | 0 | 0
1342 | 632.63 | 0 | 24.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 632.63 | 0 | 0.05921 | 6.4375 | 0 | 0 | 211.3625 | 0 | off_peak | 632.63 |  |  | 0 | 0 | 100 | 0 | 0
1343 | 613.82 | 0 | 24.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 613.82 | 0 | 0.05921 | 6.7212 | 0 | 0 | 211.3625 | 0 | off_peak | 613.82 |  |  | 0 | 0 | 100 | 0 | 0
1344 | 622.37 | 0 | 24.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 622.37 | 0 | 0.05921 | 6.9964 | 0 | 0 | 211.3625 | 0 | off_peak | 622.37 |  |  | 0 | 0 | 100 | 0 | 0
1345 | 624.01 | 0 | 24.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 624.01 | 0 | 0.05921 | 6.8431 | 0 | 0 | 211.3625 | 0 | off_peak | 624.01 |  |  | 0 | 0 | 100 | 0 | 0
1346 | 603.95 | 0 | 24.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 603.95 | 0 | 0.05921 | 6.4869 | 0 | 0 | 211.3625 | 0 | off_peak | 603.95 |  |  | 0 | 0 | 100 | 0 | 0
1347 | 608.53 | 0 | 24.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 608.53 | 0 | 0.05921 | 5.9803 | 0 | 0 | 211.3625 | 0 | off_peak | 608.53 |  |  | 0 | 0 | 100 | 0 | 0
1348 | 606.28 | 0 | 24.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 606.28 | 0 | 0.05921 | 5.5065 | 0 | 0 | 211.3625 | 0 | off_peak | 606.28 |  |  | 0 | 0 | 100 | 0 | 0
1349 | 632.87 | 0 | 24.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 632.87 | 0 | 0.05921 | 5.0524 | 0 | 0 | 211.3625 | 0 | off_peak | 632.87 |  |  | 0 | 0 | 100 | 0 | 0
1350 | 687.47 | 0 | 24.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 687.47 | 0 | 0.05921 | 4.4626 | 0 | 0 | 211.3625 | 0 | off_peak | 687.47 |  |  | 0 | 0 | 100 | 0 | 0
1351 | 775.47 | 0 | 24.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 775.47 | 0 | 0.05921 | 3.9825 | 0 | 0 | 211.3625 | 0 | off_peak | 775.47 |  |  | 0 | 0 | 100 | 0 | 0
1352 | 802.57 | 102.221 | 25.4 | 20.6699 | 20.6699 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 781.9001 | 0 | 0.05921 | 3.6424 | 0 | 0 | 211.3625 | 20.6699 | off_peak | 781.9001 |  |  | 2.58 | 0 | 97.42 | 75.2881 | 0
1353 | 773.56 | 297.899 | 26 | 60.1074 | 60.1074 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 713.4526 | 0 | 0.05921 | 3.3508 | 0 | 0 | 211.3625 | 60.1074 | off_peak | 713.4526 |  |  | 7.77 | 0 | 92.23 | 201.4074 | 0
1354 | 755.49 | 497.454 | 26.5 | 100.1905 | 100.1905 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 655.2995 | 0 | 0.05921 | 3.157 | 0 | 0 | 211.3625 | 100.1905 | off_peak | 655.2995 |  |  | 13.26 | 0 | 86.74 | 316.3014 | 0
1355 | 756.31 | 675.192 | 26.8 | 135.8404 | 135.8404 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 620.4696 | 0 | 0.05921 | 3.0704 | 0 | 0 | 211.3625 | 135.8404 | off_peak | 620.4696 |  |  | 17.96 | 0 | 82.04 | 417.0879 | 0
1356 | 736.01 | 781.789 | 27 | 157.1724 | 157.1724 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 578.8376 | 0 | 0.05921 | 3.027 | 0 | 0 | 211.3625 | 157.1724 | off_peak | 578.8376 |  |  | 21.35 | 0 | 78.65 | 475.7679 | 0
1357 | 725.18 | 707.536 | 27.2 | 142.1413 | 142.1413 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 583.0387 | 0 | 0.05921 | 3.1041 | 0 | 0 | 211.3625 | 142.1413 | off_peak | 583.0387 |  |  | 19.6 | 0 | 80.4 | 441.2176 | 0
1358 | 746.1 | 300.174 | 27.3 | 60.2819 | 60.2819 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 685.8181 | 0 | 0.05921 | 3.4637 | 0 | 0 | 211.3625 | 60.2819 | off_peak | 685.8181 |  |  | 8.08 | 0 | 91.92 | 208.801 | 0
1359 | 732.31 | 263.149 | 27.2 | 52.8656 | 52.8656 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 19.0375 | 691.8433 | 0 | 0.05921 | 3.7666 | 0 | 0 | 211.3625 | 52.8656 | off_peak | 679.4444 | 0 | 100 | 7.22 | 0 | 92.78 | 199.1225 | 0
1360 | 733.57 | 295.771 | 27.1 | 59.4408 | 59.4408 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 30.6357 | 686.5281 | 0 | 0.05921 | 3.8312 | 0 | 0 | 211.3625 | 59.4408 | off_peak | 674.1292 | 0 | 100 | 8.1 | 0 | 91.9 | 227.7319 | 0
1361 | 705.62 | 261.578 | 26.8 | 52.6263 | 52.6263 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30.6357 | 652.9937 | 0 | 0.05921 | 4.1179 | 0 | 0 | 211.3625 | 52.6263 | off_peak | 652.9937 |  |  | 7.46 | 0 | 92.54 | 216.7095 | 0
1362 | 701.94 | 130.806 | 26.3 | 26.3643 | 26.3643 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30.6357 | 675.5757 | 0 | 0.05921 | 4.5536 | 0 | 0 | 211.3625 | 26.3643 | off_peak | 675.5757 |  |  | 3.76 | 0 | 96.24 | 120.0528 | 0
1363 | 677.93 | 0 | 26.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30.6357 | 677.93 | 0 | 0.05921 | 5.0703 | 0 | 0 | 211.3625 | 0 | off_peak | 677.93 |  |  | 0 | 0 | 100 | 0 | 0
1364 | 616.98 | 0 | 25.5 | 0 | 0 | 0 | 0 | 8.7263 | 8.7263 | 0 | 0 | 0 | 38.7984 | 625.7063 | 0 | 0.05921 | 5.5436 | 0 | 0 | 211.3625 | 0 | off_peak | 616.98 | 0 | 100 | 0 | 0 | 100 | 0 | 0
1365 | 608.36 | 0 | 25.3 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 50.3966 | 620.7589 | 0 | 0.05921 | 5.827 | 0 | 0 | 211.3625 | 0 | off_peak | 608.36 | 0 | 100 | 0 | 0 | 100 | 0 | 0
1366 | 616.42 | 0 | 25.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50.3966 | 616.42 | 0 | 0.05921 | 6.2219 | 0 | 0 | 211.3625 | 0 | off_peak | 616.42 |  |  | 0 | 0 | 100 | 0 | 0
1367 | 589.33 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50.3966 | 589.33 | 0 | 0.05921 | 6.5499 | 0 | 0 | 211.3625 | 0 | off_peak | 589.33 |  |  | 0 | 0 | 100 | 0 | 0
1368 | 585.97 | 0 | 24.8 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 61.9947 | 598.3689 | 0 | 0.05921 | 6.8449 | 0 | 0 | 211.3625 | 0 | off_peak | 585.97 | 0 | 100 | 0 | 0 | 100 | 0 | 0
1369 | 599.52 | 0 | 24.7 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 73.5928 | 611.9189 | 0 | 0.05921 | 6.8674 | 0 | 0 | 211.3625 | 0 | off_peak | 599.52 | 0 | 100 | 0 | 0 | 100 | 0 | 0
1370 | 560.84 | 0 | 24.6 | 0 | 0 | 0 | 0 | 0.80079 | 0.80079 | 0 | 0 | 0 | 74.3419 | 561.6408 | 0 | 0.05921 | 6.6445 | 0 | 0 | 211.3625 | 0 | off_peak | 560.84 | 0 | 100 | 0 | 0 | 100 | 0 | 0
1371 | 588.03 | 0 | 24.4 | 0 | 0 | 0 | 0 | 0.05172 | 0.05172 | 0 | 0 | 0 | 74.3903 | 588.0817 | 0 | 0.05921 | 6.1792 | 0 | 0 | 211.3625 | 0 | off_peak | 588.03 | 0 | 100 | 0 | 0 | 100 | 0 | 0
1372 | 583.1 | 0 | 24.2 | 0 | 0 | 0 | 0 | 0.0033404 | 0.0033404 | 0 | 0 | 0 | 74.3934 | 583.1033 | 0 | 0.05921 | 5.6738 | 0 | 0 | 211.3625 | 0 | off_peak | 583.1 | 0 | 100 | 0 | 0 | 100 | 0 | 0
1373 | 595.64 | 0 | 24 | 0 | 0 | 0 | 0 | 0.00021574 | 0.00021574 | 0 | 0 | 0 | 74.3936 | 595.6402 | 0 | 0.05921 | 5.1035 | 0 | 0 | 211.3625 | 0 | off_peak | 595.64 | 0 | 100 | 0 | 0 | 100 | 0 | 0
1374 | 713.09 | 0 | 23.7 | 0 | 0 | 0 | 0 | 1.3934e-05 | 1.3934e-05 | 0 | 0 | 0 | 74.3936 | 713.09 | 0 | 0.05921 | 4.4306 | 0 | 0 | 211.3625 | 0 | off_peak | 713.09 | 0 | 100 | 0 | 0 | 100 | 0 | 0
1375 | 755.34 | 0 | 23.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 755.34 | 0 | 0.088511 | 3.8078 | 0 | 0 | 211.3625 | 0 | on_peak | 755.34 |  |  | 0 | 0 | 100 | 0 | 0
1376 | 831.29 | 102.762 | 23.6 | 20.9142 | 20.9142 | 0 | 0 | 0 | 0 | 60.257 | 60.257 | 0 | 9.9762 | 750.1189 | 0 | 0.088511 | 3.4227 | 0 | 0 | 211.3625 | 20.9142 | on_peak | 750.1189 |  |  | 2.52 | 7.25 | 90.24 | 71.5836 | 0
1377 | 819.82 | 308.991 | 23.9 | 62.8185 | 62.8185 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9.9762 | 757.0015 | 0 | 0.088511 | 3.195 | 0 | 0 | 211.3625 | 62.8185 | on_peak | 757.0015 |  |  | 7.66 | 0 | 92.34 | 200.7027 | 0
1378 | 888.87 | 507.343 | 24.4 | 102.9589 | 102.9589 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9.9762 | 785.9111 | 0 | 0.088511 | 3.0452 | 0 | 0 | 211.3625 | 102.9589 | on_peak | 785.9111 |  |  | 11.58 | 0 | 88.42 | 313.5255 | 0
1379 | 832.08 | 665.987 | 24.8 | 134.9595 | 134.9595 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 21.5744 | 709.5195 | 0 | 0.05921 | 3.0611 | 0 | 0 | 211.3625 | 134.9595 | off_peak | 697.1205 | 0 | 100 | 16.22 | 0 | 83.78 | 413.1207 | 0
1380 | 923.63 | 693.208 | 25.4 | 140.1725 | 140.1725 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 33.1725 | 795.8565 | 0 | 0.05921 | 3.255 | 0 | 0 | 211.3625 | 140.1725 | off_peak | 783.4575 | 0 | 100 | 15.18 | 0 | 84.82 | 456.2658 | 0
1381 | 886.8 | 645.376 | 26 | 130.2182 | 130.2182 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 44.7707 | 768.9808 | 0 | 0.05921 | 3.7803 | 0 | 0 | 211.3625 | 130.2182 | off_peak | 756.5818 | 0 | 100 | 14.68 | 0 | 85.32 | 492.2629 | 0
1382 | 920.39 | 250.143 | 26.1 | 50.4534 | 50.4534 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 56.3688 | 882.3356 | 0 | 0.05921 | 4.1305 | 0 | 0 | 211.3625 | 50.4534 | off_peak | 869.9366 | 0 | 100 | 5.48 | 0 | 94.52 | 208.3958 | 0
1383 | 948.3 | 133.186 | 26 | 26.8731 | 26.8731 | 0 | 0 | 0 | 0 | 11.8693 | 11.8693 | 0 | 43.6801 | 909.5577 | 0 | 0.05921 | 4.1484 | 11.8693 | 0 | 198.6737 | 38.7423 | off_peak | 909.5577 |  |  | 2.83 | 1.25 | 95.91 | 160.718 | 0
1384 | 938.88 | 324.071 | 25.7 | 65.459 | 53.0601 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 0 | 55.2782 | 885.8199 | 0 | 0.05921 | 4.0743 | 0 | 0 | 210.2719 | 53.0601 | off_peak | 885.8199 | 100 | 0 | 5.65 | 0 | 94.35 | 216.1812 | 0
1385 | 922 | 221.503 | 25.2 | 44.8221 | 44.8221 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 66.8764 | 889.5769 | 0 | 0.05921 | 4.3082 | 0 | 0 | 210.2719 | 44.8221 | off_peak | 877.1779 | 0 | 100 | 4.86 | 0 | 95.14 | 193.104 | 0
1386 | 927.07 | 123.381 | 24.5 | 25.0296 | 25.0296 | 0 | 0 | 7.5173 | 7.5173 | 0 | 0 | 0 | 73.9081 | 909.5577 | 0 | 0.05921 | 4.5724 | 0 | 0 | 210.2719 | 25.0296 | off_peak | 902.0404 | 0 | 100 | 2.7 | 0 | 97.3 | 114.4458 | 0
1387 | 868.11 | 0 | 24.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 73.9081 | 868.11 | 0 | 0.088511 | 4.906 | 0 | 0 | 210.2719 | 0 | on_peak | 868.11 |  |  | 0 | 0 | 100 | 0 | 0
1388 | 888.47 | 0 | 23 | 0 | 0 | 0 | 0 | 0 | 0 | 62.1758 | 62.1758 | 0 | 7.4394 | 826.2942 | 0 | 0.088511 | 5.3476 | 0 | 0 | 210.2719 | 0 | on_peak | 826.2942 |  |  | 0 | 7 | 93 | 0 | 0
1389 | 860 | 0 | 22.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 860 | 0 | 0.088511 | 5.639 | 0 | 0 | 210.2719 | 0 | on_peak | 860 |  |  | 0 | 0 | 100 | 0 | 0
1390 | 799.79 | 0 | 22.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 799.79 | 0 | 0.088511 | 6.0175 | 0 | 0 | 210.2719 | 0 | on_peak | 799.79 |  |  | 0 | 0 | 100 | 0 | 0
1391 | 822.63 | 0 | 21.8 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 19.0375 | 835.0289 | 0 | 0.05921 | 6.6068 | 0 | 0 | 210.2719 | 0 | off_peak | 822.63 | 0 | 100 | 0 | 0 | 100 | 0 | 0
1392 | 829.46 | 0 | 21.4 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 30.6357 | 841.8589 | 0 | 0.05921 | 7.0196 | 0 | 0 | 210.2719 | 0 | off_peak | 829.46 | 0 | 100 | 0 | 0 | 100 | 0 | 0
1393 | 774.9 | 0 | 21 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 42.2338 | 787.2989 | 0 | 0.05921 | 7.1517 | 0 | 0 | 210.2719 | 0 | off_peak | 774.9 | 0 | 100 | 0 | 0 | 100 | 0 | 0
1394 | 711.22 | 0 | 20.6 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 53.832 | 723.6189 | 0 | 0.05921 | 6.9959 | 0 | 0 | 210.2719 | 0 | off_peak | 711.22 | 0 | 100 | 0 | 0 | 100 | 0 | 0
1395 | 670.63 | 0 | 20.3 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 65.4301 | 683.0289 | 0 | 0.05921 | 6.4852 | 0 | 0 | 210.2719 | 0 | off_peak | 670.63 | 0 | 100 | 0 | 0 | 100 | 0 | 0
1396 | 632.88 | 0 | 19.9 | 0 | 0 | 0 | 0 | 8.9635 | 8.9635 | 0 | 0 | 0 | 73.8147 | 641.8435 | 0 | 0.05921 | 5.856 | 0 | 0 | 210.2719 | 0 | off_peak | 632.88 | 0 | 100 | 0 | 0 | 100 | 0 | 0
1397 | 654.57 | 0 | 19.4 | 0 | 0 | 0 | 0 | 0.57892 | 0.57892 | 0 | 0 | 0 | 74.3563 | 655.1489 | 0 | 0.05921 | 5.2165 | 0 | 0 | 210.2719 | 0 | off_peak | 654.57 | 0 | 100 | 0 | 0 | 100 | 0 | 0
1398 | 717.71 | 0 | 18.8 | 0 | 0 | 0 | 0 | 0.03739 | 0.03739 | 0 | 0 | 0 | 74.3912 | 717.7474 | 0 | 0.05921 | 4.4304 | 0 | 0 | 210.2719 | 0 | off_peak | 717.71 | 0 | 100 | 0 | 0 | 100 | 0 | 0
1399 | 818.87 | 0 | 18.3 | 0 | 0 | 0 | 0 | 0 | 0 | 62.6277 | 62.6277 | 0 | 7.4394 | 756.2423 | 0 | 0.088511 | 3.8234 | 0 | 0 | 210.2719 | 0 | on_peak | 756.2423 |  |  | 0 | 7.65 | 92.35 | 0 | 0
1400 | 847.26 | 111.317 | 18.3 | 23.0854 | 23.0854 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 824.1746 | 0 | 0.088511 | 3.4166 | 0 | 0 | 210.2719 | 23.0854 | on_peak | 824.1746 |  |  | 2.72 | 0 | 97.28 | 78.8745 | 0
1401 | 836.9 | 324.246 | 18.8 | 67.1253 | 67.1253 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 769.7747 | 0 | 0.088511 | 3.1612 | 0 | 0 | 210.2719 | 67.1253 | on_peak | 769.7747 |  |  | 8.02 | 0 | 91.98 | 212.195 | 0
1402 | 852.74 | 474.924 | 19.6 | 98.0417 | 98.0417 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 754.6983 | 0 | 0.088511 | 3.0134 | 0 | 0 | 210.2719 | 98.0417 | on_peak | 754.6983 |  |  | 11.5 | 0 | 88.5 | 295.4398 | 0
1403 | 856.44 | 503.199 | 20.5 | 103.5485 | 103.5485 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 19.0375 | 765.2904 | 0 | 0.05921 | 3.0027 | 0 | 0 | 210.2719 | 103.5485 | off_peak | 752.8915 | 0 | 100 | 12.09 | 0 | 87.91 | 310.9239 | 0
1404 | 927.29 | 728.04 | 21.4 | 149.3388 | 149.3388 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 30.6357 | 790.3502 | 0 | 0.05921 | 3.2754 | 0 | 0 | 210.2719 | 149.3388 | off_peak | 777.9512 | 0 | 100 | 16.1 | 0 | 83.9 | 489.1403 | 0
1405 | 842.69 | 778.276 | 22.1 | 159.2462 | 159.2462 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 42.2338 | 695.8427 | 0 | 0.05921 | 3.7871 | 0 | 0 | 210.2719 | 159.2462 | off_peak | 683.4438 | 0 | 100 | 18.9 | 0 | 81.1 | 603.0885 | 0
1406 | 892.97 | 453.462 | 22.6 | 92.6194 | 92.6194 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 53.832 | 812.7495 | 0 | 0.05921 | 4.0594 | 0 | 0 | 210.2719 | 92.6194 | off_peak | 800.3506 | 0 | 100 | 10.37 | 0 | 89.63 | 375.9755 | 0
1407 | 935.72 | 614.154 | 22.9 | 125.3064 | 112.9075 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 0 | 65.4301 | 822.8125 | 0 | 0.05921 | 4.0405 | 0 | 0 | 221.87 | 112.9075 | off_peak | 822.8125 | 100 | 0 | 12.07 | 0 | 87.93 | 456.2018 | 0
1408 | 905.34 | 531.081 | 22.9 | 108.3569 | 108.3569 | 0 | 0 | 8.9635 | 8.9635 | 0 | 0 | 0 | 73.8147 | 805.9466 | 0 | 0.05921 | 4.1207 | 0 | 0 | 221.87 | 108.3569 | off_peak | 796.9831 | 0 | 100 | 11.97 | 0 | 88.03 | 446.5046 | 0
1409 | 872.27 | 335.242 | 22.6 | 68.473 | 68.473 | 0 | 0 | 0.57892 | 0.57892 | 0 | 0 | 0 | 74.3563 | 804.3759 | 0 | 0.05921 | 4.3433 | 0 | 0 | 221.87 | 68.473 | off_peak | 803.797 | 0 | 100 | 7.85 | 0 | 92.15 | 297.3993 | 0
1410 | 875.28 | 127.149 | 22.1 | 26.0165 | 25.9791 | 0 | 0.03739 | 0.03739 | 0 | 0 | 0 | 0 | 74.3912 | 849.3009 | 0 | 0.05921 | 4.5761 | 0 | 0 | 221.905 | 25.9791 | off_peak | 849.3009 | 100 | 0 | 2.97 | 0 | 97.03 | 118.8841 | 0
1411 | 854.19 | 0 | 21.8 | 0 | 0 | 0 | 0 | 0 | 0 | 62.6277 | 62.6277 | 0 | 7.4394 | 791.5623 | 0 | 0.088511 | 4.9169 | 0 | 0 | 221.905 | 0 | on_peak | 791.5623 |  |  | 0 | 7.33 | 92.67 | 0 | 0
1412 | 811.54 | 0 | 19.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 811.54 | 0 | 0.088511 | 5.3114 | 0 | 0 | 221.905 | 0 | on_peak | 811.54 |  |  | 0 | 0 | 100 | 0 | 0
1413 | 832.98 | 0 | 19.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 832.98 | 0 | 0.088511 | 5.6638 | 0 | 0 | 221.905 | 0 | on_peak | 832.98 |  |  | 0 | 0 | 100 | 0 | 0
1414 | 788.17 | 0 | 19.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 788.17 | 0 | 0.088511 | 6.1068 | 0 | 0 | 221.905 | 0 | on_peak | 788.17 |  |  | 0 | 0 | 100 | 0 | 0
1415 | 772.49 | 0 | 19.7 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 19.0375 | 784.8889 | 0 | 0.05921 | 6.6083 | 0 | 0 | 221.905 | 0 | off_peak | 772.49 | 0 | 100 | 0 | 0 | 100 | 0 | 0
1416 | 746.25 | 0 | 19.7 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 30.6357 | 758.6489 | 0 | 0.05921 | 7.0374 | 0 | 0 | 221.905 | 0 | off_peak | 746.25 | 0 | 100 | 0 | 0 | 100 | 0 | 0
1417 | 748.27 | 0 | 19.7 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 42.2338 | 760.6689 | 0 | 0.05921 | 7.0852 | 0 | 0 | 221.905 | 0 | off_peak | 748.27 | 0 | 100 | 0 | 0 | 100 | 0 | 0
1418 | 688.11 | 0 | 19.7 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 53.832 | 700.5089 | 0 | 0.05921 | 6.8778 | 0 | 0 | 221.905 | 0 | off_peak | 688.11 | 0 | 100 | 0 | 0 | 100 | 0 | 0
1419 | 634.99 | 0 | 19.9 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 65.4301 | 647.3889 | 0 | 0.05921 | 6.3242 | 0 | 0 | 221.905 | 0 | off_peak | 634.99 | 0 | 100 | 0 | 0 | 100 | 0 | 0
1420 | 650.15 | 0 | 20.2 | 0 | 0 | 0 | 0 | 8.9635 | 8.9635 | 0 | 0 | 0 | 73.8147 | 659.1135 | 0 | 0.05921 | 5.7774 | 0 | 0 | 221.905 | 0 | off_peak | 650.15 | 0 | 100 | 0 | 0 | 100 | 0 | 0
1421 | 629.36 | 0 | 20.4 | 0 | 0 | 0 | 0 | 0.57892 | 0.57892 | 0 | 0 | 0 | 74.3563 | 629.9389 | 0 | 0.05921 | 5.1032 | 0 | 0 | 221.905 | 0 | off_peak | 629.36 | 0 | 100 | 0 | 0 | 100 | 0 | 0
1422 | 640.49 | 0 | 20.5 | 0 | 0 | 0 | 0 | 0.03739 | 0.03739 | 0 | 0 | 0 | 74.3912 | 640.5274 | 0 | 0.05921 | 4.4549 | 0 | 0 | 221.905 | 0 | off_peak | 640.49 | 0 | 100 | 0 | 0 | 100 | 0 | 0
1423 | 702.84 | 0 | 20.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3912 | 702.84 | 0 | 0.088511 | 3.8026 | 0 | 0 | 221.905 | 0 | on_peak | 702.84 |  |  | 0 | 0 | 100 | 0 | 0
1424 | 666.85 | 121.903 | 21.3 | 25.0142 | 25.0142 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3912 | 641.8358 | 0 | 0.088511 | 3.37 | 0 | 0 | 221.905 | 25.0142 | on_peak | 641.8358 |  |  | 3.75 | 0 | 96.25 | 84.2972 | 0
1425 | 703.1 | 344.872 | 22 | 70.5908 | 70.5908 | 0 | 0 | 0 | 0 | 62.6277 | 62.6277 | 0 | 7.4394 | 569.8815 | 0 | 0.088511 | 3.1166 | 0 | 0 | 221.905 | 70.5908 | on_peak | 569.8815 |  |  | 10.04 | 8.91 | 81.05 | 220.0002 | 0
1426 | 756.28 | 557.356 | 22.6 | 113.8397 | 113.8397 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 642.4403 | 0 | 0.088511 | 2.9987 | 0 | 0 | 221.905 | 113.8397 | on_peak | 642.4403 |  |  | 15.05 | 0 | 84.95 | 341.3674 | 0
1427 | 713.31 | 727.11 | 23.3 | 148.1409 | 148.1409 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 19.0375 | 577.5681 | 0 | 0.05921 | 2.9754 | 0 | 0 | 221.905 | 148.1409 | off_peak | 565.1691 | 0 | 100 | 20.77 | 0 | 79.23 | 440.7754 | 0
1428 | 705.26 | 833.79 | 23.7 | 169.6327 | 169.6327 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 30.6357 | 548.0263 | 0 | 0.05921 | 3.1882 | 0 | 0 | 221.905 | 169.6327 | off_peak | 535.6273 | 0 | 100 | 24.05 | 0 | 75.95 | 540.8166 | 0
1429 | 774.07 | 872.585 | 24 | 177.3346 | 164.9356 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 0 | 42.2338 | 609.1344 | 0 | 0.05921 | 3.7054 | 0 | 0 | 233.5032 | 164.9356 | off_peak | 609.1344 | 100 | 0 | 21.31 | 0 | 78.69 | 611.1538 | 0
1430 | 755.58 | 837.045 | 24.2 | 169.9898 | 169.9898 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 53.832 | 597.9892 | 0 | 0.05921 | 3.9528 | 0 | 0 | 233.5032 | 169.9898 | off_peak | 585.5902 | 0 | 100 | 22.5 | 0 | 77.5 | 671.9353 | 0
1431 | 765.93 | 735.965 | 24.3 | 149.4085 | 149.4085 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 65.4301 | 628.9205 | 0 | 0.05921 | 4.0232 | 0 | 0 | 233.5032 | 149.4085 | off_peak | 616.5215 | 0 | 100 | 19.51 | 0 | 80.49 | 601.1047 | 0
1432 | 769.76 | 571.107 | 24.2 | 115.9822 | 107.0187 | 0 | 8.9635 | 8.9635 | 0 | 0 | 0 | 0 | 73.8147 | 662.7413 | 0 | 0.05921 | 4.1304 | 0 | 0 | 241.8878 | 107.0187 | off_peak | 662.7413 | 100 | 0 | 13.9 | 0 | 86.1 | 442.0261 | 0
1433 | 730.21 | 365.194 | 23.7 | 74.2979 | 74.2979 | 0 | 0 | 0.57892 | 0.57892 | 0 | 0 | 0 | 74.3563 | 656.491 | 0 | 0.05921 | 4.221 | 0 | 0 | 241.8878 | 74.2979 | off_peak | 655.9121 | 0 | 100 | 10.17 | 0 | 89.83 | 313.6136 | 0
1434 | 755.78 | 143.915 | 22.9 | 29.3631 | 29.3631 | 0 | 0 | 0.03739 | 0.03739 | 0 | 0 | 0 | 74.3912 | 726.4543 | 0 | 0.05921 | 4.3959 | 0 | 0 | 241.8878 | 29.3631 | off_peak | 726.4169 | 0 | 100 | 3.89 | 0 | 96.11 | 129.0759 | 0
1435 | 746.64 | 0 | 22.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3912 | 746.64 | 0 | 0.088511 | 4.8205 | 0 | 0 | 241.8878 | 0 | on_peak | 746.64 |  |  | 0 | 0 | 100 | 0 | 0
1436 | 733.02 | 0 | 21.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3912 | 733.02 | 0 | 0.088511 | 5.2553 | 0 | 0 | 241.8878 | 0 | on_peak | 733.02 |  |  | 0 | 0 | 100 | 0 | 0
1437 | 762.21 | 0 | 21.3 | 0 | 0 | 0 | 0 | 0 | 0 | 62.6277 | 62.6277 | 0 | 7.4394 | 699.5823 | 0 | 0.088511 | 5.7523 | 0 | 0 | 241.8878 | 0 | on_peak | 699.5823 |  |  | 0 | 8.22 | 91.78 | 0 | 0
1438 | 729.21 | 0 | 21.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 729.21 | 0 | 0.088511 | 6.0576 | 0 | 0 | 241.8878 | 0 | on_peak | 729.21 |  |  | 0 | 0 | 100 | 0 | 0
1439 | 781.38 | 0 | 20.9 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 19.0375 | 793.7789 | 0 | 0.05921 | 6.4253 | 0 | 0 | 241.8878 | 0 | off_peak | 781.38 | 0 | 100 | 0 | 0 | 100 | 0 | 0
1440 | 703.65 | 0 | 20.8 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 30.6357 | 716.0489 | 0 | 0.05921 | 6.7028 | 0 | 0 | 241.8878 | 0 | off_peak | 703.65 | 0 | 100 | 0 | 0 | 100 | 0 | 0
1441 | 672.74 | 0 | 20.7 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 42.2338 | 685.1389 | 0 | 0.05921 | 6.7376 | 0 | 0 | 241.8878 | 0 | off_peak | 672.74 | 0 | 100 | 0 | 0 | 100 | 0 | 0
1442 | 651.88 | 0 | 20.7 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 53.832 | 664.2789 | 0 | 0.05921 | 6.5502 | 0 | 0 | 241.8878 | 0 | off_peak | 651.88 | 0 | 100 | 0 | 0 | 100 | 0 | 0
1443 | 592.88 | 0 | 20.7 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 65.4301 | 605.2789 | 0 | 0.05921 | 6.0355 | 0 | 0 | 241.8878 | 0 | off_peak | 592.88 | 0 | 100 | 0 | 0 | 100 | 0 | 0
1444 | 579.02 | 0 | 20.7 | 0 | 0 | 0 | 0 | 8.9635 | 8.9635 | 0 | 0 | 0 | 73.8147 | 587.9835 | 0 | 0.05921 | 5.4871 | 0 | 0 | 241.8878 | 0 | off_peak | 579.02 | 0 | 100 | 0 | 0 | 100 | 0 | 0
1445 | 584.93 | 0 | 20.8 | 0 | 0 | 0 | 0 | 0.57892 | 0.57892 | 0 | 0 | 0 | 74.3563 | 585.5089 | 0 | 0.05921 | 4.8915 | 0 | 0 | 241.8878 | 0 | off_peak | 584.93 | 0 | 100 | 0 | 0 | 100 | 0 | 0
1446 | 655.33 | 0 | 20.9 | 0 | 0 | 0 | 0 | 0.03739 | 0.03739 | 0 | 0 | 0 | 74.3912 | 655.3674 | 0 | 0.05921 | 4.2701 | 0 | 0 | 241.8878 | 0 | off_peak | 655.33 | 0 | 100 | 0 | 0 | 100 | 0 | 0
1447 | 741.6 | 0 | 21.2 | 0 | 0 | 0 | 0 | 0 | 0 | 62.6277 | 62.6277 | 0 | 7.4394 | 678.9723 | 0 | 0.088511 | 3.7579 | 62.6277 | 0 | 174.9359 | 62.6277 | on_peak | 678.9723 |  |  | 0 | 8.44 | 91.56 | 235.3465 | 0
1448 | 785.16 | 123.351 | 22 | 25.2483 | 25.2483 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 759.9117 | 0 | 0.088511 | 3.3794 | 0 | 0 | 174.9359 | 25.2483 | on_peak | 759.9117 |  |  | 3.22 | 0 | 96.78 | 85.3249 | 0
1449 | 813.45 | 344.232 | 22.7 | 70.2842 | 70.2842 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 743.1658 | 0 | 0.088511 | 3.1516 | 0 | 0 | 174.9359 | 70.2842 | on_peak | 743.1658 |  |  | 8.64 | 0 | 91.36 | 221.5081 | 0
1450 | 897.96 | 550.988 | 23.2 | 112.2981 | 112.2981 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 785.6619 | 0 | 0.088511 | 3.0186 | 0 | 0 | 174.9359 | 112.2981 | on_peak | 785.6619 |  |  | 12.51 | 0 | 87.49 | 338.9885 | 0
1451 | 901.86 | 714.126 | 23.7 | 145.2873 | 145.2873 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 19.0375 | 768.9716 | 0 | 0.05921 | 3.0041 | 0 | 0 | 174.9359 | 145.2873 | off_peak | 756.5727 | 0 | 100 | 16.11 | 0 | 83.89 | 436.4609 | 0
1452 | 901.3 | 814.186 | 24.2 | 165.3475 | 165.3475 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 30.6357 | 748.3514 | 0 | 0.05921 | 3.1868 | 0 | 0 | 174.9359 | 165.3475 | off_peak | 735.9525 | 0 | 100 | 18.35 | 0 | 81.65 | 526.9349 | 0
1453 | 895.21 | 810.726 | 24.5 | 164.4675 | 164.4675 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 42.2338 | 743.1414 | 0 | 0.05921 | 3.6476 | 0 | 0 | 174.9359 | 164.4675 | off_peak | 730.7425 | 0 | 100 | 18.37 | 0 | 81.63 | 599.9178 | 0
1454 | 917.29 | 826.905 | 24.8 | 167.5688 | 167.5688 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 53.832 | 762.1201 | 0 | 0.05921 | 3.9678 | 0 | 0 | 174.9359 | 167.5688 | off_peak | 749.7212 | 0 | 100 | 18.27 | 0 | 81.73 | 664.8737 | 0
1455 | 936.11 | 725.633 | 25.1 | 146.8878 | 146.8878 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 65.4301 | 801.6212 | 0 | 0.05921 | 3.9464 | 0 | 0 | 174.9359 | 146.8878 | off_peak | 789.2222 | 0 | 100 | 15.69 | 0 | 84.31 | 579.6738 | 0
1456 | 925.84 | 565.271 | 25.1 | 114.4262 | 114.4262 | 0 | 0 | 8.9635 | 8.9635 | 0 | 0 | 0 | 73.8147 | 820.3774 | 0 | 0.05921 | 4.0322 | 0 | 0 | 174.9359 | 114.4262 | off_peak | 811.4138 | 0 | 100 | 12.36 | 0 | 87.64 | 461.3899 | 0
1457 | 894.16 | 360.78 | 24.7 | 73.1369 | 73.1369 | 0 | 0 | 0.57892 | 0.57892 | 0 | 0 | 0 | 74.3563 | 821.6021 | 0 | 0.05921 | 4.2273 | 0 | 0 | 174.9359 | 73.1369 | off_peak | 821.0231 | 0 | 100 | 8.18 | 0 | 91.82 | 309.1706 | 0
1458 | 923.09 | 140.951 | 24.1 | 28.6351 | 28.6351 | 0 | 0 | 0.03739 | 0.03739 | 0 | 0 | 0 | 74.3912 | 894.4923 | 0 | 0.05921 | 4.5793 | 0 | 0 | 174.9359 | 28.6351 | off_peak | 894.4549 | 0 | 100 | 3.1 | 0 | 96.9 | 131.1286 | 0
1459 | 876.35 | 0 | 23.7 | 0 | 0 | 0 | 0 | 0 | 0 | 9.7484 | 9.7484 | 0 | 63.9698 | 866.6016 | 0 | 0.088511 | 4.9478 | 0 | 0 | 174.9359 | 0 | on_peak | 866.6016 |  |  | 0 | 1.11 | 98.89 | 0 | 0
1460 | 881.78 | 0 | 22.8 | 0 | 0 | 0 | 0 | 0 | 0 | 15.1784 | 15.1784 | 0 | 47.7434 | 866.6016 | 0 | 0.088511 | 5.3899 | 0 | 0 | 174.9359 | 0 | on_peak | 866.6016 |  |  | 0 | 1.72 | 98.28 | 0 | 0
1461 | 874.56 | 0 | 22.4 | 0 | 0 | 0 | 0 | 0 | 0 | 7.9584 | 7.9584 | 0 | 39.2356 | 866.6016 | 0 | 0.088511 | 5.5981 | 0 | 0 | 174.9359 | 0 | on_peak | 866.6016 |  |  | 0 | 0.91 | 99.09 | 0 | 0
1462 | 782.41 | 0 | 22.1 | 0 | 0 | 0 | 0 | 0 | 0 | 29.7426 | 29.7426 | 0 | 7.4394 | 752.6674 | 0 | 0.088511 | 6.0385 | 0 | 0 | 174.9359 | 0 | on_peak | 752.6674 |  |  | 0 | 3.8 | 96.2 | 0 | 0
1463 | 813.76 | 0 | 21.9 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 19.0375 | 826.1589 | 0 | 0.05921 | 6.3769 | 0 | 0 | 174.9359 | 0 | off_peak | 813.76 | 0 | 100 | 0 | 0 | 100 | 0 | 0
1464 | 812.72 | 0 | 21.7 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 30.6357 | 825.1189 | 0 | 0.05921 | 6.652 | 0 | 0 | 174.9359 | 0 | off_peak | 812.72 | 0 | 100 | 0 | 0 | 100 | 0 | 0
1465 | 766.73 | 0 | 21.5 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 42.2338 | 779.1289 | 0 | 0.05921 | 6.7059 | 0 | 0 | 174.9359 | 0 | off_peak | 766.73 | 0 | 100 | 0 | 0 | 100 | 0 | 0
1466 | 680.62 | 0 | 21.2 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 53.832 | 693.0189 | 0 | 0.05921 | 6.5523 | 0 | 0 | 174.9359 | 0 | off_peak | 680.62 | 0 | 100 | 0 | 0 | 100 | 0 | 0
1467 | 628.31 | 0 | 21 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 65.4301 | 640.7089 | 0 | 0.05921 | 6.1067 | 0 | 0 | 174.9359 | 0 | off_peak | 628.31 | 0 | 100 | 0 | 0 | 100 | 0 | 0
1468 | 629.73 | 0 | 20.8 | 0 | 0 | 0 | 0 | 8.9635 | 8.9635 | 0 | 0 | 0 | 73.8147 | 638.6935 | 0 | 0.05921 | 5.5947 | 0 | 0 | 174.9359 | 0 | off_peak | 629.73 | 0 | 100 | 0 | 0 | 100 | 0 | 0
1469 | 662.4 | 0 | 20.6 | 0 | 0 | 0 | 0 | 0.57892 | 0.57892 | 0 | 0 | 0 | 74.3563 | 662.9789 | 0 | 0.05921 | 5.0661 | 0 | 0 | 174.9359 | 0 | off_peak | 662.4 | 0 | 100 | 0 | 0 | 100 | 0 | 0
1470 | 740.47 | 0 | 20.5 | 0 | 0 | 0 | 0 | 0.03739 | 0.03739 | 0 | 0 | 0 | 74.3912 | 740.5074 | 0 | 0.05921 | 4.3599 | 0 | 0 | 174.9359 | 0 | off_peak | 740.47 | 0 | 100 | 0 | 0 | 100 | 0 | 0
1471 | 817.39 | 0 | 20.8 | 0 | 0 | 0 | 0 | 0 | 0 | 62.6277 | 62.6277 | 0 | 7.4394 | 754.7623 | 0 | 0.088511 | 3.8556 | 62.6277 | 0 | 107.9841 | 62.6277 | on_peak | 754.7623 |  |  | 0 | 7.66 | 92.34 | 241.469 | 0
1472 | 823.86 | 118.669 | 21.5 | 24.3333 | 24.3333 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 799.5267 | 0 | 0.088511 | 3.4967 | 0 | 0 | 107.9841 | 24.3333 | on_peak | 799.5267 |  |  | 2.95 | 0 | 97.05 | 85.085 | 0
1473 | 890.22 | 337.185 | 22.4 | 68.9191 | 68.9191 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 821.3009 | 0 | 0.088511 | 3.3247 | 0 | 0 | 107.9841 | 68.9191 | on_peak | 821.3009 |  |  | 7.74 | 0 | 92.26 | 229.1348 | 0
1474 | 896.62 | 537.365 | 23.5 | 109.404 | 109.404 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 787.216 | 0 | 0.088511 | 3.2164 | 0 | 0 | 107.9841 | 109.404 | on_peak | 787.216 |  |  | 12.2 | 0 | 87.8 | 351.8871 | 0
1475 | 875.24 | 639.929 | 24.4 | 129.8655 | 129.8655 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 19.0375 | 757.7734 | 0 | 0.05921 | 3.2148 | 0 | 0 | 107.9841 | 129.8655 | off_peak | 745.3745 | 0 | 100 | 14.84 | 0 | 85.16 | 417.493 | 0
1476 | 956.11 | 796.46 | 25.1 | 161.2251 | 161.2251 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 30.6357 | 807.2839 | 0 | 0.05921 | 3.4719 | 0 | 0 | 107.9841 | 161.2251 | off_peak | 794.8849 | 0 | 100 | 16.86 | 0 | 83.14 | 559.7592 | 0
1477 | 917.8 | 820.181 | 25.5 | 165.7877 | 165.7877 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 42.2338 | 764.4112 | 0 | 0.05921 | 3.9582 | 0 | 0 | 107.9841 | 165.7877 | off_peak | 752.0123 | 0 | 100 | 18.06 | 0 | 81.94 | 656.2234 | 0
1478 | 937.32 | 809.001 | 25.8 | 163.3509 | 163.3509 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 53.832 | 786.368 | 0 | 0.05921 | 4.3001 | 0 | 0 | 107.9841 | 163.3509 | off_peak | 773.9691 | 0 | 100 | 17.43 | 0 | 82.57 | 702.4181 | 0
1479 | 967.02 | 709.126 | 25.9 | 143.1328 | 143.1328 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 65.4301 | 836.2862 | 0 | 0.05921 | 4.4189 | 0 | 0 | 107.9841 | 143.1328 | off_peak | 823.8872 | 0 | 100 | 14.8 | 0 | 85.2 | 632.4945 | 0
1480 | 891.99 | 550.774 | 25.8 | 111.2105 | 111.2105 | 0 | 0 | 8.9635 | 8.9635 | 0 | 0 | 0 | 73.8147 | 789.743 | 0 | 0.05921 | 4.6948 | 0 | 0 | 107.9841 | 111.2105 | off_peak | 780.7795 | 0 | 100 | 12.47 | 0 | 87.53 | 522.1161 | 0
1481 | 888.07 | 347.632 | 25.4 | 70.2941 | 70.2941 | 0 | 0 | 0.57892 | 0.57892 | 0 | 0 | 0 | 74.3563 | 818.3548 | 0 | 0.05921 | 4.934 | 0 | 0 | 107.9841 | 70.2941 | off_peak | 817.7759 | 0 | 100 | 7.92 | 0 | 92.08 | 346.8284 | 0
1482 | 858.23 | 133.233 | 24.7 | 27.0088 | 27.0088 | 0 | 0 | 0.03739 | 0.03739 | 0 | 0 | 0 | 74.3912 | 831.2586 | 0 | 0.05921 | 5.3129 | 0 | 0 | 107.9841 | 27.0088 | off_peak | 831.2212 | 0 | 100 | 3.15 | 0 | 96.85 | 143.4953 | 0
1483 | 800.28 | 0 | 24.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3912 | 800.28 | 0 | 0.088511 | 5.6352 | 0 | 0 | 107.9841 | 0 | on_peak | 800.28 |  |  | 0 | 0 | 100 | 0 | 0
1484 | 822.33 | 0 | 23.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3912 | 822.33 | 0 | 0.088511 | 5.9797 | 0 | 0 | 107.9841 | 0 | on_peak | 822.33 |  |  | 0 | 0 | 100 | 0 | 0
1485 | 815.89 | 0 | 22.9 | 0 | 0 | 0 | 0 | 0 | 0 | 62.6277 | 62.6277 | 0 | 7.4394 | 753.2623 | 0 | 0.088511 | 6.2317 | 0 | 0 | 107.9841 | 0 | on_peak | 753.2623 |  |  | 0 | 7.68 | 92.32 | 0 | 0
1486 | 819.59 | 0 | 22.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 819.59 | 0 | 0.088511 | 6.6077 | 0 | 0 | 107.9841 | 0 | on_peak | 819.59 |  |  | 0 | 0 | 100 | 0 | 0
1487 | 841.36 | 0 | 21.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 841.36 | 0 | 0.05921 | 7.046 | 0 | 0 | 107.9841 | 0 | off_peak | 841.36 |  |  | 0 | 0 | 100 | 0 | 0
1488 | 804.13 | 0 | 21.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 804.13 | 0 | 0.05921 | 7.1208 | 0 | 0 | 107.9841 | 0 | off_peak | 804.13 |  |  | 0 | 0 | 100 | 0 | 0
1489 | 770.26 | 0 | 20.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 770.26 | 0 | 0.05921 | 6.9421 | 0 | 0 | 107.9841 | 0 | off_peak | 770.26 |  |  | 0 | 0 | 100 | 0 | 0
1490 | 622.6 | 0 | 20.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 622.6 | 0 | 0.05921 | 6.7109 | 0 | 0 | 107.9841 | 0 | off_peak | 622.6 |  |  | 0 | 0 | 100 | 0 | 0
1491 | 626.57 | 0 | 19.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 626.57 | 0 | 0.05921 | 6.2206 | 0 | 0 | 107.9841 | 0 | off_peak | 626.57 |  |  | 0 | 0 | 100 | 0 | 0
1492 | 651.89 | 0 | 19.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 651.89 | 0 | 0.05921 | 5.9 | 0 | 0 | 107.9841 | 0 | off_peak | 651.89 |  |  | 0 | 0 | 100 | 0 | 0
1493 | 635.49 | 0 | 19.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 635.49 | 0 | 0.05921 | 5.4219 | 0 | 0 | 107.9841 | 0 | off_peak | 635.49 |  |  | 0 | 0 | 100 | 0 | 0
1494 | 722.06 | 0 | 19.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 722.06 | 0 | 0.05921 | 4.8382 | 0 | 0 | 107.9841 | 0 | off_peak | 722.06 |  |  | 0 | 0 | 100 | 0 | 0
1495 | 821.8 | 0 | 19.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 821.8 | 0 | 0.05921 | 4.3942 | 0 | 0 | 107.9841 | 0 | off_peak | 821.8 |  |  | 0 | 0 | 100 | 0 | 0
1496 | 836.02 | 109.383 | 20.8 | 22.485 | 22.485 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 813.535 | 0 | 0.05921 | 3.9787 | 0 | 0 | 107.9841 | 22.485 | off_peak | 813.535 |  |  | 2.69 | 0 | 97.31 | 89.4601 | 0
1497 | 862.61 | 316.576 | 22.1 | 64.7759 | 64.7759 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 797.8341 | 0 | 0.05921 | 3.7146 | 0 | 0 | 107.9841 | 64.7759 | off_peak | 797.8341 |  |  | 7.51 | 0 | 92.49 | 240.6168 | 0
1498 | 838.49 | 497.322 | 23.2 | 101.3603 | 101.3603 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 737.1297 | 0 | 0.05921 | 3.5601 | 0 | 0 | 107.9841 | 101.3603 | off_peak | 737.1297 |  |  | 12.09 | 0 | 87.91 | 360.8544 | 0
1499 | 813.94 | 629.862 | 23.9 | 128.0521 | 128.0521 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 685.8879 | 0 | 0.05921 | 3.4664 | 0 | 0 | 107.9841 | 128.0521 | off_peak | 685.8879 |  |  | 15.73 | 0 | 84.27 | 443.8796 | 0
1500 | 859.78 | 552.104 | 24.3 | 112.0828 | 112.0828 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 747.6972 | 0 | 0.05921 | 3.5431 | 0 | 0 | 107.9841 | 112.0828 | off_peak | 747.6972 |  |  | 13.04 | 0 | 86.96 | 397.115 | 0
1501 | 769.61 | 511.919 | 24.5 | 103.8502 | 103.8502 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 665.7598 | 0 | 0.05921 | 3.6523 | 0 | 0 | 107.9841 | 103.8502 | off_peak | 665.7598 |  |  | 13.49 | 0 | 86.51 | 379.292 | 0
1502 | 818.28 | 335.567 | 24.5 | 68.0746 | 68.0746 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 750.2054 | 0 | 0.05921 | 3.937 | 0 | 0 | 107.9841 | 68.0746 | off_peak | 750.2054 |  |  | 8.32 | 0 | 91.68 | 268.0073 | 0
1503 | 783.54 | 410.181 | 24.4 | 83.2411 | 83.2411 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 700.2989 | 0 | 0.05921 | 4.2703 | 0 | 0 | 107.9841 | 83.2411 | off_peak | 700.2989 |  |  | 10.62 | 0 | 89.38 | 355.4624 | 0
1504 | 798.08 | 385.808 | 24.1 | 78.3792 | 78.3792 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 719.7008 | 0 | 0.05921 | 4.555 | 0 | 0 | 107.9841 | 78.3792 | off_peak | 719.7008 |  |  | 9.82 | 0 | 90.18 | 357.0155 | 0
1505 | 778.68 | 340.495 | 23.5 | 69.3226 | 69.3226 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 709.3574 | 0 | 0.05921 | 4.9319 | 0 | 0 | 107.9841 | 69.3226 | off_peak | 709.3574 |  |  | 8.9 | 0 | 91.1 | 341.8931 | 0
1506 | 693.62 | 131.166 | 22.8 | 26.7715 | 26.7715 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 666.8485 | 0 | 0.05921 | 5.319 | 0 | 0 | 107.9841 | 26.7715 | off_peak | 666.8485 |  |  | 3.86 | 0 | 96.14 | 142.3974 | 0
1507 | 644.82 | 0 | 22.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 644.82 | 0 | 0.05921 | 5.8117 | 0 | 0 | 107.9841 | 0 | off_peak | 644.82 |  |  | 0 | 0 | 100 | 0 | 0
1508 | 635.93 | 0 | 21.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 635.93 | 0 | 0.05921 | 6.0737 | 0 | 0 | 107.9841 | 0 | off_peak | 635.93 |  |  | 0 | 0 | 100 | 0 | 0
1509 | 633.27 | 0 | 21.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 633.27 | 0 | 0.05921 | 6.2439 | 0 | 0 | 107.9841 | 0 | off_peak | 633.27 |  |  | 0 | 0 | 100 | 0 | 0
1510 | 625.73 | 0 | 21.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 625.73 | 0 | 0.05921 | 6.5394 | 0 | 0 | 107.9841 | 0 | off_peak | 625.73 |  |  | 0 | 0 | 100 | 0 | 0
1511 | 628.85 | 0 | 20.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 628.85 | 0 | 0.05921 | 6.8449 | 0 | 0 | 107.9841 | 0 | off_peak | 628.85 |  |  | 0 | 0 | 100 | 0 | 0
1512 | 602.12 | 0 | 20.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 602.12 | 0 | 0.05921 | 7.1165 | 0 | 0 | 107.9841 | 0 | off_peak | 602.12 |  |  | 0 | 0 | 100 | 0 | 0
1513 | 600.9 | 0 | 20.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 600.9 | 0 | 0.05921 | 7.0401 | 0 | 0 | 107.9841 | 0 | off_peak | 600.9 |  |  | 0 | 0 | 100 | 0 | 0
1514 | 607.49 | 0 | 20.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 607.49 | 0 | 0.05921 | 6.7525 | 0 | 0 | 107.9841 | 0 | off_peak | 607.49 |  |  | 0 | 0 | 100 | 0 | 0
1515 | 600.52 | 0 | 19.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 600.52 | 0 | 0.05921 | 6.1938 | 0 | 0 | 107.9841 | 0 | off_peak | 600.52 |  |  | 0 | 0 | 100 | 0 | 0
1516 | 594.82 | 0 | 19.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 594.82 | 0 | 0.05921 | 5.6683 | 0 | 0 | 107.9841 | 0 | off_peak | 594.82 |  |  | 0 | 0 | 100 | 0 | 0
1517 | 615.06 | 0 | 19.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 615.06 | 0 | 0.05921 | 5.119 | 0 | 0 | 107.9841 | 0 | off_peak | 615.06 |  |  | 0 | 0 | 100 | 0 | 0
1518 | 678.88 | 0 | 19.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 678.88 | 0 | 0.05921 | 4.491 | 0 | 0 | 107.9841 | 0 | off_peak | 678.88 |  |  | 0 | 0 | 100 | 0 | 0
1519 | 714.73 | 0 | 20.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 714.73 | 0 | 0.05921 | 4.0188 | 0 | 0 | 107.9841 | 0 | off_peak | 714.73 |  |  | 0 | 0 | 100 | 0 | 0
1520 | 787.43 | 131.139 | 20.9 | 26.9476 | 26.9476 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 760.4824 | 0 | 0.05921 | 3.5803 | 0 | 0 | 107.9841 | 26.9476 | off_peak | 760.4824 |  |  | 3.42 | 0 | 96.58 | 96.4798 | 0
1521 | 784.57 | 352.395 | 21.4 | 72.2848 | 72.2848 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 712.2852 | 0 | 0.05921 | 3.2894 | 0 | 0 | 107.9841 | 72.2848 | off_peak | 712.2852 |  |  | 9.21 | 0 | 90.79 | 237.7763 | 0
1522 | 745.48 | 560.871 | 21.9 | 114.8439 | 114.8439 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 630.6361 | 0 | 0.05921 | 3.1053 | 0 | 0 | 107.9841 | 114.8439 | off_peak | 630.6361 |  |  | 15.41 | 0 | 84.59 | 356.6217 | 0
1523 | 769.49 | 724.385 | 22.3 | 148.1138 | 148.1138 | 0 | 0 | 8.7263 | 8.7263 | 0 | 0 | 0 | 15.6021 | 630.1026 | 0 | 0.05921 | 3.0166 | 0 | 0 | 107.9841 | 148.1138 | off_peak | 621.3762 | 0 | 100 | 19.25 | 0 | 80.75 | 446.7971 | 0
1524 | 768.02 | 831.787 | 22.6 | 169.8922 | 157.4932 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 0 | 27.2003 | 610.5268 | 0 | 0.05921 | 3.0507 | 0 | 0 | 119.5822 | 157.4932 | off_peak | 610.5268 | 100 | 0 | 20.51 | 0 | 79.49 | 480.4675 | 0
1525 | 729.54 | 861.533 | 22.7 | 175.905 | 163.506 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 0 | 38.7984 | 566.034 | 0 | 0.05921 | 3.1235 | 0 | 0 | 131.1804 | 163.506 | off_peak | 566.034 | 100 | 0 | 22.41 | 0 | 77.59 | 510.7038 | 0
1526 | 752.52 | 697.244 | 22.8 | 142.3101 | 142.3101 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 38.7984 | 610.2099 | 0 | 0.05921 | 3.276 | 0 | 0 | 131.1804 | 142.3101 | off_peak | 610.2099 |  |  | 18.91 | 0 | 81.09 | 466.213 | 0
1527 | 757.16 | 638.403 | 22.9 | 130.2539 | 130.2539 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 38.7984 | 626.9061 | 0 | 0.05921 | 3.5175 | 0 | 0 | 131.1804 | 130.2539 | off_peak | 626.9061 |  |  | 17.2 | 0 | 82.8 | 458.1645 | 0
1528 | 768.13 | 566.699 | 22.8 | 115.6654 | 115.6654 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 50.3966 | 664.8635 | 0 | 0.05921 | 3.9474 | 0 | 0 | 131.1804 | 115.6654 | off_peak | 652.4646 | 0 | 100 | 15.06 | 0 | 84.94 | 456.5811 | 0
1529 | 738.37 | 361.969 | 22.5 | 73.9584 | 73.9584 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50.3966 | 664.4116 | 0 | 0.05921 | 4.475 | 0 | 0 | 131.1804 | 73.9584 | off_peak | 664.4116 |  |  | 10.02 | 0 | 89.98 | 330.964 | 0
1530 | 679.18 | 143.318 | 21.8 | 29.3562 | 29.3562 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50.3966 | 649.8238 | 0 | 0.05921 | 5.1013 | 0 | 0 | 131.1804 | 29.3562 | off_peak | 649.8238 |  |  | 4.32 | 0 | 95.68 | 149.7551 | 0
1531 | 628.39 | 0 | 21.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50.3966 | 628.39 | 0 | 0.05921 | 5.5948 | 0 | 0 | 131.1804 | 0 | off_peak | 628.39 |  |  | 0 | 0 | 100 | 0 | 0
1532 | 624.91 | 0 | 20.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50.3966 | 624.91 | 0 | 0.05921 | 6.1393 | 0 | 0 | 131.1804 | 0 | off_peak | 624.91 |  |  | 0 | 0 | 100 | 0 | 0
1533 | 608.09 | 0 | 20.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50.3966 | 608.09 | 0 | 0.05921 | 6.5073 | 0 | 0 | 131.1804 | 0 | off_peak | 608.09 |  |  | 0 | 0 | 100 | 0 | 0
1534 | 625.32 | 0 | 20.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50.3966 | 625.32 | 0 | 0.05921 | 6.6784 | 0 | 0 | 131.1804 | 0 | off_peak | 625.32 |  |  | 0 | 0 | 100 | 0 | 0
1535 | 575.64 | 0 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50.3966 | 575.64 | 0 | 0.05921 | 6.9471 | 0 | 0 | 131.1804 | 0 | off_peak | 575.64 |  |  | 0 | 0 | 100 | 0 | 0
1536 | 604.73 | 0 | 19.9 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 61.9947 | 617.1289 | 0 | 0.05921 | 7.1828 | 0 | 0 | 131.1804 | 0 | off_peak | 604.73 | 0 | 100 | 0 | 0 | 100 | 0 | 0
1537 | 593.29 | 0 | 19.8 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 73.5928 | 605.6889 | 0 | 0.05921 | 7.1842 | 0 | 0 | 131.1804 | 0 | off_peak | 593.29 | 0 | 100 | 0 | 0 | 100 | 0 | 0
1538 | 628.41 | 0 | 19.8 | 0 | 0 | 0 | 0 | 0.80079 | 0.80079 | 0 | 0 | 0 | 74.3419 | 629.2108 | 0 | 0.05921 | 7.0341 | 0 | 0 | 131.1804 | 0 | off_peak | 628.41 | 0 | 100 | 0 | 0 | 100 | 0 | 0
1539 | 564.06 | 0 | 19.8 | 0 | 0 | 0 | 0 | 0.05172 | 0.05172 | 0 | 0 | 0 | 74.3903 | 564.1117 | 0 | 0.05921 | 6.5189 | 0 | 0 | 131.1804 | 0 | off_peak | 564.06 | 0 | 100 | 0 | 0 | 100 | 0 | 0
1540 | 589.92 | 0 | 19.8 | 0 | 0 | 0 | 0 | 0.0033404 | 0.0033404 | 0 | 0 | 0 | 74.3934 | 589.9233 | 0 | 0.05921 | 5.908 | 0 | 0 | 131.1804 | 0 | off_peak | 589.92 | 0 | 100 | 0 | 0 | 100 | 0 | 0
1541 | 618.85 | 0 | 19.9 | 0 | 0 | 0 | 0 | 0.00021574 | 0.00021574 | 0 | 0 | 0 | 74.3936 | 618.8502 | 0 | 0.05921 | 5.2501 | 0 | 0 | 131.1804 | 0 | off_peak | 618.85 | 0 | 100 | 0 | 0 | 100 | 0 | 0
1542 | 701.29 | 0 | 20 | 0 | 0 | 0 | 0 | 1.3934e-05 | 1.3934e-05 | 0 | 0 | 0 | 74.3936 | 701.29 | 0 | 0.05921 | 4.6472 | 0 | 0 | 131.1804 | 0 | off_peak | 701.29 | 0 | 100 | 0 | 0 | 100 | 0 | 0
1543 | 768.23 | 0 | 20.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 768.23 | 0 | 0.088511 | 4.0957 | 0 | 0 | 131.1804 | 0 | on_peak | 768.23 |  |  | 0 | 0 | 100 | 0 | 0
1544 | 817.53 | 121.366 | 21 | 24.9305 | 24.9305 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 792.5995 | 0 | 0.088511 | 3.6569 | 0 | 0 | 131.1804 | 24.9305 | on_peak | 792.5995 |  |  | 3.05 | 0 | 96.95 | 91.1674 | 0
1545 | 874.51 | 326.529 | 21.6 | 66.9315 | 66.9315 | 0 | 0 | 0 | 0 | 62.63 | 62.63 | 0 | 7.4394 | 744.9486 | 0 | 0.088511 | 3.4022 | 0 | 0 | 131.1804 | 66.9315 | on_peak | 744.9486 |  |  | 7.65 | 7.16 | 85.18 | 227.7116 | 0
1546 | 865.3 | 525.579 | 22.2 | 107.5026 | 107.5026 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 757.7974 | 0 | 0.088511 | 3.2685 | 0 | 0 | 131.1804 | 107.5026 | on_peak | 757.7974 |  |  | 12.42 | 0 | 87.58 | 351.3704 | 0
1547 | 868.72 | 689.746 | 22.8 | 140.7798 | 140.7798 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 19.0375 | 740.3392 | 0 | 0.05921 | 3.2607 | 0 | 0 | 131.1804 | 140.7798 | off_peak | 727.9402 | 0 | 100 | 16.21 | 0 | 83.79 | 459.0442 | 0
1548 | 889.16 | 793.827 | 23.4 | 161.6759 | 161.6759 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 30.6357 | 739.8831 | 0 | 0.05921 | 3.485 | 0 | 0 | 131.1804 | 161.6759 | off_peak | 727.4841 | 0 | 100 | 18.18 | 0 | 81.82 | 563.4337 | 0
1549 | 914 | 678.663 | 23.9 | 137.9735 | 137.9735 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 42.2338 | 788.4255 | 0 | 0.05921 | 3.9846 | 0 | 0 | 131.1804 | 137.9735 | off_peak | 776.0265 | 0 | 100 | 15.1 | 0 | 84.9 | 549.7634 | 0
1550 | 961.73 | 782.336 | 24.2 | 158.8793 | 158.8793 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 53.832 | 815.2496 | 0 | 0.05921 | 4.2268 | 0 | 0 | 131.1804 | 158.8793 | off_peak | 802.8507 | 0 | 100 | 16.52 | 0 | 83.48 | 671.5539 | 0
1551 | 958.72 | 601.169 | 24.5 | 121.9558 | 121.9558 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 65.4301 | 849.1631 | 0 | 0.05921 | 4.3199 | 0 | 0 | 131.1804 | 121.9558 | off_peak | 836.7642 | 0 | 100 | 12.72 | 0 | 87.28 | 526.8356 | 0
1552 | 916.76 | 239.886 | 24.4 | 48.6818 | 48.6818 | 0 | 0 | 8.9635 | 8.9635 | 0 | 0 | 0 | 73.8147 | 877.0417 | 0 | 0.05921 | 4.4941 | 0 | 0 | 131.1804 | 48.6818 | off_peak | 868.0782 | 0 | 100 | 5.31 | 0 | 94.69 | 218.7808 | 0
1553 | 873.44 | 196.455 | 24 | 39.9254 | 39.3464 | 0 | 0.57892 | 0.57892 | 0 | 0 | 0 | 0 | 74.3563 | 834.0936 | 0 | 0.05921 | 4.8086 | 0 | 0 | 131.7219 | 39.3464 | off_peak | 834.0936 | 100 | 0 | 4.5 | 0 | 95.5 | 189.2023 | 0
1554 | 880.47 | 126.087 | 23.1 | 25.7073 | 25.7073 | 0 | 0 | 0.03739 | 0.03739 | 0 | 0 | 0 | 74.3912 | 854.8001 | 0 | 0.05921 | 5.3054 | 0 | 0 | 131.7219 | 25.7073 | off_peak | 854.7627 | 0 | 100 | 2.92 | 0 | 97.08 | 136.3865 | 0
1555 | 841.11 | 0 | 22.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3912 | 841.11 | 0 | 0.088511 | 5.9979 | 0 | 0 | 131.7219 | 0 | on_peak | 841.11 |  |  | 0 | 0 | 100 | 0 | 0
1556 | 863.38 | 0 | 21.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3912 | 863.38 | 0 | 0.088511 | 6.4712 | 0 | 0 | 131.7219 | 0 | on_peak | 863.38 |  |  | 0 | 0 | 100 | 0 | 0
1557 | 849.65 | 0 | 20.8 | 0 | 0 | 0 | 0 | 0 | 0 | 62.6277 | 62.6277 | 0 | 7.4394 | 787.0223 | 0 | 0.088511 | 6.7817 | 0 | 0 | 131.7219 | 0 | on_peak | 787.0223 |  |  | 0 | 7.37 | 92.63 | 0 | 0
1558 | 834.2 | 0 | 20.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 834.2 | 0 | 0.088511 | 7.01 | 0 | 0 | 131.7219 | 0 | on_peak | 834.2 |  |  | 0 | 0 | 100 | 0 | 0
1559 | 870.11 | 0 | 19.7 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 19.0375 | 882.5089 | 0 | 0.05921 | 7.214 | 0 | 0 | 131.7219 | 0 | off_peak | 870.11 | 0 | 100 | 0 | 0 | 100 | 0 | 0
1560 | 854.74 | 0 | 19.3 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 30.6357 | 867.1389 | 0 | 0.05921 | 7.5789 | 0 | 0 | 131.7219 | 0 | off_peak | 854.74 | 0 | 100 | 0 | 0 | 100 | 0 | 0
1561 | 789.14 | 0 | 19.1 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 42.2338 | 801.5389 | 0 | 0.05921 | 7.5353 | 0 | 0 | 131.7219 | 0 | off_peak | 789.14 | 0 | 100 | 0 | 0 | 100 | 0 | 0
1562 | 713.04 | 0 | 19 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 53.832 | 725.4389 | 0 | 0.05921 | 7.3773 | 0 | 0 | 131.7219 | 0 | off_peak | 713.04 | 0 | 100 | 0 | 0 | 100 | 0 | 0
1563 | 642.46 | 0 | 18.9 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 65.4301 | 654.8589 | 0 | 0.05921 | 6.9058 | 0 | 0 | 131.7219 | 0 | off_peak | 642.46 | 0 | 100 | 0 | 0 | 100 | 0 | 0
1564 | 662.03 | 0 | 18.9 | 0 | 0 | 0 | 0 | 8.9635 | 8.9635 | 0 | 0 | 0 | 73.8147 | 670.9935 | 0 | 0.05921 | 6.3894 | 0 | 0 | 131.7219 | 0 | off_peak | 662.03 | 0 | 100 | 0 | 0 | 100 | 0 | 0
1565 | 689.73 | 0 | 19 | 0 | 0 | 0 | 0 | 0.57892 | 0.57892 | 0 | 0 | 0 | 74.3563 | 690.3089 | 0 | 0.05921 | 5.6393 | 0 | 0 | 131.7219 | 0 | off_peak | 689.73 | 0 | 100 | 0 | 0 | 100 | 0 | 0
1566 | 778.76 | 0 | 19.1 | 0 | 0 | 0 | 0 | 0.03739 | 0.03739 | 0 | 0 | 0 | 74.3912 | 778.7974 | 0 | 0.05921 | 4.9295 | 0 | 0 | 131.7219 | 0 | off_peak | 778.76 | 0 | 100 | 0 | 0 | 100 | 0 | 0
1567 | 817.95 | 0 | 19.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3912 | 817.95 | 0 | 0.088511 | 4.3135 | 0 | 0 | 131.7219 | 0 | on_peak | 817.95 |  |  | 0 | 0 | 100 | 0 | 0
1568 | 853.03 | 121.944 | 20.2 | 25.1204 | 25.1204 | 0 | 0 | 0 | 0 | 50.2435 | 50.2435 | 0 | 20.6786 | 777.6661 | 0 | 0.088511 | 3.8104 | 0 | 0 | 131.7219 | 25.1204 | on_peak | 777.6661 |  |  | 2.94 | 5.89 | 91.17 | 95.7191 | 0
1569 | 851.77 | 332.37 | 21 | 68.2741 | 68.2741 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20.6786 | 783.4959 | 0 | 0.088511 | 3.5209 | 0 | 0 | 131.7219 | 68.2741 | on_peak | 783.4959 |  |  | 8.02 | 0 | 91.98 | 240.3858 | 0
1570 | 946.35 | 535.886 | 21.9 | 109.728 | 109.728 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20.6786 | 836.622 | 0 | 0.088511 | 3.3516 | 0 | 0 | 131.7219 | 109.728 | on_peak | 836.622 |  |  | 11.59 | 0 | 88.41 | 367.7619 | 0
1571 | 884.8 | 701 | 22.7 | 143.1279 | 130.7289 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 0 | 32.2768 | 754.0711 | 0 | 0.05921 | 3.3102 | 0 | 0 | 143.32 | 130.7289 | off_peak | 754.0711 | 100 | 0 | 14.77 | 0 | 85.23 | 432.7421 | 0
1572 | 945.24 | 803.422 | 23.2 | 163.7472 | 163.7472 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 43.8749 | 793.8917 | 0 | 0.05921 | 3.4948 | 0 | 0 | 143.32 | 163.7472 | off_peak | 781.4928 | 0 | 100 | 17.32 | 0 | 82.68 | 572.2684 | 0
1573 | 917.54 | 824.986 | 23.6 | 167.9016 | 167.9016 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 55.4731 | 762.0373 | 0 | 0.05921 | 4.0141 | 0 | 0 | 143.32 | 167.9016 | off_peak | 749.6384 | 0 | 100 | 18.3 | 0 | 81.7 | 673.9679 | 0
1574 | 960.4 | 222.47 | 23.7 | 45.261 | 45.261 | 0 | 0 | 0 | 0 | 2.5319 | 2.5319 | 0 | 52.7664 | 912.6071 | 0 | 0.05921 | 4.1926 | 0 | 0 | 143.32 | 45.261 | off_peak | 912.6071 |  |  | 4.71 | 0.26 | 95.02 | 189.7599 | 0
1575 | 1007.46 | 478.011 | 23.6 | 97.2851 | 97.2851 | 0 | 0 | 2.4322 | 2.4322 | 0 | 0 | 0 | 55.0414 | 912.6071 | 0 | 0.05921 | 4.2086 | 0 | 0 | 143.32 | 97.2851 | off_peak | 910.1749 | 0 | 100 | 9.66 | 0 | 90.34 | 409.4315 | 0
1576 | 961.08 | 217.448 | 23.3 | 44.3027 | 44.3027 | 0 | 0 | 0 | 0 | 4.1702 | 4.1702 | 0 | 50.5833 | 912.6071 | 0 | 0.05921 | 4.3333 | 0 | 0 | 143.32 | 44.3027 | off_peak | 912.6071 |  |  | 4.61 | 0.43 | 94.96 | 191.9776 | 0
1577 | 933.65 | 162.695 | 22.5 | 33.2422 | 21.0429 | 0 | 12.1993 | 12.1993 | 0 | 0 | 0 | 0 | 61.9947 | 912.6071 | 0 | 0.05921 | 4.7043 | 0 | 0 | 154.7315 | 21.0429 | off_peak | 912.6071 | 100 | 0 | 2.25 | 0 | 97.75 | 98.9913 | 0
1578 | 910.67 | 137.678 | 21.3 | 28.2512 | 28.2512 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 73.5928 | 894.8178 | 0 | 0.05921 | 5.272 | 0 | 0 | 154.7315 | 28.2512 | off_peak | 882.4188 | 0 | 100 | 3.1 | 0 | 96.9 | 148.9402 | 0
1579 | 850.74 | 0 | 20.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 73.5928 | 850.74 | 0 | 0.088511 | 5.9706 | 0 | 0 | 154.7315 | 0 | on_peak | 850.74 |  |  | 0 | 0 | 100 | 0 | 0
1580 | 860.87 | 0 | 19.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 73.5928 | 860.87 | 0 | 0.088511 | 6.45 | 0 | 0 | 154.7315 | 0 | on_peak | 860.87 |  |  | 0 | 0 | 100 | 0 | 0
1581 | 902.29 | 0 | 18.9 | 0 | 0 | 0 | 0 | 0 | 0 | 61.8809 | 61.8809 | 0 | 7.4394 | 840.4091 | 0 | 0.088511 | 6.5479 | 0 | 0 | 154.7315 | 0 | on_peak | 840.4091 |  |  | 0 | 6.86 | 93.14 | 0 | 0
1582 | 824.93 | 0 | 18.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 824.93 | 0 | 0.088511 | 6.7727 | 0 | 0 | 154.7315 | 0 | on_peak | 824.93 |  |  | 0 | 0 | 100 | 0 | 0
1583 | 839.5 | 0 | 18.2 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 19.0375 | 851.8989 | 0 | 0.05921 | 7.1364 | 0 | 0 | 154.7315 | 0 | off_peak | 839.5 | 0 | 100 | 0 | 0 | 100 | 0 | 0
1584 | 866.04 | 0 | 18.1 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 30.6357 | 878.4389 | 0 | 0.05921 | 7.408 | 0 | 0 | 154.7315 | 0 | off_peak | 866.04 | 0 | 100 | 0 | 0 | 100 | 0 | 0
1585 | 763.96 | 0 | 18 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 42.2338 | 776.3589 | 0 | 0.05921 | 7.4565 | 0 | 0 | 154.7315 | 0 | off_peak | 763.96 | 0 | 100 | 0 | 0 | 100 | 0 | 0
1586 | 710.74 | 0 | 17.9 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 53.832 | 723.1389 | 0 | 0.05921 | 7.4033 | 0 | 0 | 154.7315 | 0 | off_peak | 710.74 | 0 | 100 | 0 | 0 | 100 | 0 | 0
1587 | 639.39 | 0 | 17.8 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 65.4301 | 651.7889 | 0 | 0.05921 | 6.9024 | 0 | 0 | 154.7315 | 0 | off_peak | 639.39 | 0 | 100 | 0 | 0 | 100 | 0 | 0
1588 | 646.66 | 0 | 17.8 | 0 | 0 | 0 | 0 | 8.9635 | 8.9635 | 0 | 0 | 0 | 73.8147 | 655.6235 | 0 | 0.05921 | 6.2487 | 0 | 0 | 154.7315 | 0 | off_peak | 646.66 | 0 | 100 | 0 | 0 | 100 | 0 | 0
1589 | 661.21 | 0 | 17.7 | 0 | 0 | 0 | 0 | 0.57892 | 0.57892 | 0 | 0 | 0 | 74.3563 | 661.7889 | 0 | 0.05921 | 5.5756 | 0 | 0 | 154.7315 | 0 | off_peak | 661.21 | 0 | 100 | 0 | 0 | 100 | 0 | 0
1590 | 759.93 | 0 | 17.7 | 0 | 0 | 0 | 0 | 0.03739 | 0.03739 | 0 | 0 | 0 | 74.3912 | 759.9674 | 0 | 0.05921 | 4.8197 | 0 | 0 | 154.7315 | 0 | off_peak | 759.93 | 0 | 100 | 0 | 0 | 100 | 0 | 0
1591 | 820.03 | 0 | 18.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3912 | 820.03 | 0 | 0.088511 | 4.3223 | 0 | 0 | 154.7315 | 0 | on_peak | 820.03 |  |  | 0 | 0 | 100 | 0 | 0
1592 | 862.43 | 131.278 | 19.2 | 27.1389 | 27.1389 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3912 | 835.2911 | 0 | 0.088511 | 3.9271 | 0 | 0 | 154.7315 | 27.1389 | on_peak | 835.2911 |  |  | 3.15 | 0 | 96.85 | 106.5769 | 0
1593 | 871.57 | 345.356 | 19.9 | 71.2186 | 71.2186 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3912 | 800.3514 | 0 | 0.088511 | 3.6937 | 0 | 0 | 154.7315 | 71.2186 | on_peak | 800.3514 |  |  | 8.17 | 0 | 91.83 | 263.0589 | 0
1594 | 902.71 | 545.154 | 20.4 | 112.2218 | 112.2218 | 0 | 0 | 0 | 0 | 62.6277 | 62.6277 | 0 | 7.4394 | 727.8605 | 0 | 0.088511 | 3.5284 | 0 | 0 | 154.7315 | 112.2218 | on_peak | 727.8605 |  |  | 12.43 | 6.94 | 80.63 | 395.9602 | 0
1595 | 831.62 | 703.762 | 20.9 | 144.6153 | 144.6153 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 19.0375 | 699.4037 | 0 | 0.05921 | 3.4746 | 0 | 0 | 154.7315 | 144.6153 | off_peak | 687.0047 | 0 | 100 | 17.39 | 0 | 82.61 | 502.486 | 0
1596 | 899.99 | 805.362 | 21.2 | 165.3168 | 165.3168 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 30.6357 | 747.0721 | 0 | 0.05921 | 3.6777 | 0 | 0 | 154.7315 | 165.3168 | off_peak | 734.6732 | 0 | 100 | 18.37 | 0 | 81.63 | 607.9813 | 0
1597 | 862.46 | 825.413 | 21.4 | 169.3123 | 169.3123 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 42.2338 | 705.5466 | 0 | 0.05921 | 4.1268 | 0 | 0 | 154.7315 | 169.3123 | off_peak | 693.1477 | 0 | 100 | 19.63 | 0 | 80.37 | 698.7244 | 0
1598 | 898.67 | 301.524 | 21.4 | 61.8499 | 61.8499 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 53.832 | 849.219 | 0 | 0.05921 | 4.309 | 0 | 0 | 154.7315 | 61.8499 | off_peak | 836.8201 | 0 | 100 | 6.88 | 0 | 93.12 | 266.514 | 0
1599 | 945.6 | 662.037 | 21.3 | 135.8482 | 135.8482 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 65.4301 | 822.1507 | 0 | 0.05921 | 4.3437 | 0 | 0 | 154.7315 | 135.8482 | off_peak | 809.7518 | 0 | 100 | 14.37 | 0 | 85.63 | 590.0786 | 0
1600 | 939.44 | 519.612 | 21.1 | 106.6987 | 106.6987 | 0 | 0 | 8.9635 | 8.9635 | 0 | 0 | 0 | 73.8147 | 841.7048 | 0 | 0.05921 | 4.3181 | 0 | 0 | 154.7315 | 106.6987 | off_peak | 832.7413 | 0 | 100 | 11.36 | 0 | 88.64 | 460.7366 | 0
1601 | 909.03 | 112.14 | 20.7 | 23.0599 | 23.0599 | 0 | 0 | 0.57892 | 0.57892 | 0 | 0 | 0 | 74.3563 | 886.549 | 0 | 0.05921 | 4.5296 | 0 | 0 | 154.7315 | 23.0599 | off_peak | 885.9701 | 0 | 100 | 2.54 | 0 | 97.46 | 104.4526 | 0
1602 | 857.04 | 13.3 | 20 | 2.7417 | 2.7417 | 0 | 0 | 0.03739 | 0.03739 | 0 | 0 | 0 | 74.3912 | 854.3357 | 0 | 0.05921 | 5.0606 | 0 | 0 | 154.7315 | 2.7417 | off_peak | 854.2983 | 0 | 100 | 0.32 | 0 | 99.68 | 13.8749 | 0
1603 | 783.61 | 0 | 19.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3912 | 783.61 | 0 | 0.088511 | 5.6701 | 0 | 0 | 154.7315 | 0 | on_peak | 783.61 |  |  | 0 | 0 | 100 | 0 | 0
1604 | 868.84 | 0 | 19.4 | 0 | 0 | 0 | 0 | 0 | 0 | 62.6277 | 62.6277 | 0 | 7.4394 | 806.2123 | 0 | 0.088511 | 6.1068 | 0 | 0 | 154.7315 | 0 | on_peak | 806.2123 |  |  | 0 | 7.21 | 92.79 | 0 | 0
1605 | 796.95 | 0 | 19.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 796.95 | 0 | 0.088511 | 6.3458 | 0 | 0 | 154.7315 | 0 | on_peak | 796.95 |  |  | 0 | 0 | 100 | 0 | 0
1606 | 787.06 | 0 | 19.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 787.06 | 0 | 0.088511 | 6.5311 | 0 | 0 | 154.7315 | 0 | on_peak | 787.06 |  |  | 0 | 0 | 100 | 0 | 0
1607 | 809.66 | 0 | 19.1 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 19.0375 | 822.0589 | 0 | 0.05921 | 6.7853 | 0 | 0 | 154.7315 | 0 | off_peak | 809.66 | 0 | 100 | 0 | 0 | 100 | 0 | 0
1608 | 804.49 | 0 | 19.1 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 30.6357 | 816.8889 | 0 | 0.05921 | 6.9129 | 0 | 0 | 154.7315 | 0 | off_peak | 804.49 | 0 | 100 | 0 | 0 | 100 | 0 | 0
1609 | 761.61 | 0 | 19 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 42.2338 | 774.0089 | 0 | 0.05921 | 7.1005 | 0 | 0 | 154.7315 | 0 | off_peak | 761.61 | 0 | 100 | 0 | 0 | 100 | 0 | 0
1610 | 694.39 | 0 | 18.9 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 53.832 | 706.7889 | 0 | 0.05921 | 6.9686 | 0 | 0 | 154.7315 | 0 | off_peak | 694.39 | 0 | 100 | 0 | 0 | 100 | 0 | 0
1611 | 618.26 | 0 | 18.9 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 65.4301 | 630.6589 | 0 | 0.05921 | 6.495 | 0 | 0 | 154.7315 | 0 | off_peak | 618.26 | 0 | 100 | 0 | 0 | 100 | 0 | 0
1612 | 647.41 | 0 | 18.9 | 0 | 0 | 0 | 0 | 8.9635 | 8.9635 | 0 | 0 | 0 | 73.8147 | 656.3735 | 0 | 0.05921 | 5.9723 | 0 | 0 | 154.7315 | 0 | off_peak | 647.41 | 0 | 100 | 0 | 0 | 100 | 0 | 0
1613 | 663.04 | 0 | 19 | 0 | 0 | 0 | 0 | 0.57892 | 0.57892 | 0 | 0 | 0 | 74.3563 | 663.6189 | 0 | 0.05921 | 5.3483 | 0 | 0 | 154.7315 | 0 | off_peak | 663.04 | 0 | 100 | 0 | 0 | 100 | 0 | 0
1614 | 717.43 | 0 | 19.1 | 0 | 0 | 0 | 0 | 0.03739 | 0.03739 | 0 | 0 | 0 | 74.3912 | 717.4674 | 0 | 0.05921 | 4.7336 | 0 | 0 | 154.7315 | 0 | off_peak | 717.43 | 0 | 100 | 0 | 0 | 100 | 0 | 0
1615 | 806.83 | 0 | 19.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3912 | 806.83 | 0 | 0.088511 | 4.1324 | 0 | 0 | 154.7315 | 0 | on_peak | 806.83 |  |  | 0 | 0 | 100 | 0 | 0
1616 | 850.83 | 130.449 | 20.6 | 26.8344 | 26.8344 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3912 | 823.9956 | 0 | 0.088511 | 3.7184 | 0 | 0 | 154.7315 | 26.8344 | on_peak | 823.9956 |  |  | 3.15 | 0 | 96.85 | 99.7818 | 0
1617 | 924.91 | 342.773 | 21.1 | 70.3861 | 70.3861 | 0 | 0 | 0 | 0 | 62.6277 | 62.6277 | 0 | 7.4394 | 791.8962 | 0 | 0.088511 | 3.4467 | 0 | 0 | 154.7315 | 70.3861 | on_peak | 791.8962 |  |  | 7.61 | 6.77 | 85.62 | 242.5976 | 0
1618 | 866.09 | 545.426 | 21.5 | 111.8404 | 111.8404 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 754.2496 | 0 | 0.088511 | 3.28 | 0 | 0 | 154.7315 | 111.8404 | on_peak | 754.2496 |  |  | 12.91 | 0 | 87.09 | 366.8359 | 0
1619 | 875.4 | 704.444 | 21.8 | 144.2932 | 144.2932 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 19.0375 | 743.5057 | 0 | 0.05921 | 3.2215 | 0 | 0 | 154.7315 | 144.2932 | off_peak | 731.1068 | 0 | 100 | 16.48 | 0 | 83.52 | 464.837 | 0
1620 | 955.34 | 747.84 | 22.2 | 152.9641 | 152.9641 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 30.6357 | 814.7748 | 0 | 0.05921 | 3.404 | 0 | 0 | 154.7315 | 152.9641 | off_peak | 802.3759 | 0 | 100 | 16.01 | 0 | 83.99 | 520.6874 | 0
1621 | 834.64 | 705.849 | 22.5 | 144.2208 | 144.2208 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 42.2338 | 702.8181 | 0 | 0.05921 | 3.8509 | 0 | 0 | 154.7315 | 144.2208 | off_peak | 690.4192 | 0 | 100 | 17.28 | 0 | 82.72 | 555.3869 | 0
1622 | 885.71 | 590.027 | 22.7 | 120.4698 | 120.4698 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 53.832 | 777.6392 | 0 | 0.05921 | 4.0942 | 0 | 0 | 154.7315 | 120.4698 | off_peak | 765.2402 | 0 | 100 | 13.6 | 0 | 86.4 | 493.2266 | 0
1623 | 925.03 | 596.304 | 22.8 | 121.7079 | 109.309 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 0 | 65.4301 | 815.721 | 0 | 0.05921 | 4.1803 | 0 | 0 | 166.3296 | 109.309 | off_peak | 815.721 | 100 | 0 | 11.82 | 0 | 88.18 | 456.9413 | 0
1624 | 882.58 | 531.198 | 22.8 | 108.4195 | 108.4195 | 0 | 0 | 8.9635 | 8.9635 | 0 | 0 | 0 | 73.8147 | 783.124 | 0 | 0.05921 | 4.1584 | 0 | 0 | 166.3296 | 108.4195 | off_peak | 774.1605 | 0 | 100 | 12.28 | 0 | 87.72 | 450.8504 | 0
1625 | 896.12 | 362.444 | 22.6 | 74.029 | 74.029 | 0 | 0 | 0.57892 | 0.57892 | 0 | 0 | 0 | 74.3563 | 822.6699 | 0 | 0.05921 | 4.3484 | 0 | 0 | 166.3296 | 74.029 | off_peak | 822.091 | 0 | 100 | 8.26 | 0 | 91.74 | 321.9094 | 0
1626 | 852.81 | 147.025 | 22.3 | 30.062 | 30.062 | 0 | 0 | 0.03739 | 0.03739 | 0 | 0 | 0 | 74.3912 | 822.7854 | 0 | 0.05921 | 4.6081 | 0 | 0 | 166.3296 | 30.062 | off_peak | 822.748 | 0 | 100 | 3.53 | 0 | 96.47 | 138.5272 | 0
1627 | 820.4 | 0 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3912 | 820.4 | 0 | 0.088511 | 4.8911 | 0 | 0 | 166.3296 | 0 | on_peak | 820.4 |  |  | 0 | 0 | 100 | 0 | 0
1628 | 802.77 | 0 | 21.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3912 | 802.77 | 0 | 0.088511 | 5.1157 | 0 | 0 | 166.3296 | 0 | on_peak | 802.77 |  |  | 0 | 0 | 100 | 0 | 0
1629 | 822.8 | 0 | 21.9 | 0 | 0 | 0 | 0 | 0 | 0 | 62.6277 | 62.6277 | 0 | 7.4394 | 760.1723 | 0 | 0.088511 | 5.3783 | 62.6277 | 0 | 99.3777 | 62.6277 | on_peak | 760.1723 |  |  | 0 | 7.61 | 92.39 | 336.8308 | 0
1630 | 775.04 | 0 | 21.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 775.04 | 0 | 0.088511 | 5.6217 | 0 | 0 | 99.3777 | 0 | on_peak | 775.04 |  |  | 0 | 0 | 100 | 0 | 0
1631 | 791.19 | 0 | 22 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 19.0375 | 803.5889 | 0 | 0.05921 | 5.9141 | 0 | 0 | 99.3777 | 0 | off_peak | 791.19 | 0 | 100 | 0 | 0 | 100 | 0 | 0
1632 | 791.45 | 0 | 22 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 30.6357 | 803.8489 | 0 | 0.05921 | 6.185 | 0 | 0 | 99.3777 | 0 | off_peak | 791.45 | 0 | 100 | 0 | 0 | 100 | 0 | 0
1633 | 753.23 | 0 | 22 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 42.2338 | 765.6289 | 0 | 0.05921 | 6.2909 | 0 | 0 | 99.3777 | 0 | off_peak | 753.23 | 0 | 100 | 0 | 0 | 100 | 0 | 0
1634 | 673.8 | 0 | 22 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 53.832 | 686.1989 | 0 | 0.05921 | 6.2805 | 0 | 0 | 99.3777 | 0 | off_peak | 673.8 | 0 | 100 | 0 | 0 | 100 | 0 | 0
1635 | 627.83 | 0 | 21.9 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 65.4301 | 640.2289 | 0 | 0.05921 | 5.8817 | 0 | 0 | 99.3777 | 0 | off_peak | 627.83 | 0 | 100 | 0 | 0 | 100 | 0 | 0
1636 | 609.69 | 0 | 21.9 | 0 | 0 | 0 | 0 | 8.9635 | 8.9635 | 0 | 0 | 0 | 73.8147 | 618.6535 | 0 | 0.05921 | 5.3257 | 0 | 0 | 99.3777 | 0 | off_peak | 609.69 | 0 | 100 | 0 | 0 | 100 | 0 | 0
1637 | 616.44 | 0 | 21.9 | 0 | 0 | 0 | 0 | 0.57892 | 0.57892 | 0 | 0 | 0 | 74.3563 | 617.0189 | 0 | 0.05921 | 4.6981 | 0 | 0 | 99.3777 | 0 | off_peak | 616.44 | 0 | 100 | 0 | 0 | 100 | 0 | 0
1638 | 720.55 | 0 | 22 | 0 | 0 | 0 | 0 | 0.03739 | 0.03739 | 0 | 0 | 0 | 74.3912 | 720.5874 | 0 | 0.05921 | 4.0773 | 0 | 0 | 99.3777 | 0 | off_peak | 720.55 | 0 | 100 | 0 | 0 | 100 | 0 | 0
1639 | 700.75 | 0 | 22.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3912 | 700.75 | 0 | 0.088511 | 3.4941 | 0 | 0 | 99.3777 | 0 | on_peak | 700.75 |  |  | 0 | 0 | 100 | 0 | 0
1640 | 821.19 | 141.506 | 23.1 | 28.851 | 28.851 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3912 | 792.339 | 0 | 0.088511 | 3.1426 | 0 | 0 | 99.3777 | 28.851 | on_peak | 792.339 |  |  | 3.51 | 0 | 96.49 | 90.6669 | 0
1641 | 904.74 | 358.603 | 23.6 | 72.9831 | 72.9831 | 0 | 0 | 0 | 0 | 62.6277 | 62.6277 | 0 | 7.4394 | 769.1292 | 0 | 0.088511 | 2.9245 | 0 | 0 | 99.3777 | 72.9831 | on_peak | 769.1292 |  |  | 8.07 | 6.92 | 85.01 | 213.4415 | 0
1642 | 856.59 | 563.383 | 24 | 114.4958 | 114.4958 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 742.0942 | 0 | 0.088511 | 2.8043 | 0 | 0 | 99.3777 | 114.4958 | on_peak | 742.0942 |  |  | 13.37 | 0 | 86.63 | 321.0749 | 0
1643 | 831.89 | 726.019 | 24.3 | 147.3893 | 147.3893 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 19.0375 | 696.8996 | 0 | 0.05921 | 2.8017 | 0 | 0 | 99.3777 | 147.3893 | off_peak | 684.5007 | 0 | 100 | 17.72 | 0 | 82.28 | 412.9475 | 0
1644 | 971.3 | 811.624 | 24.6 | 164.5905 | 164.5905 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 30.6357 | 819.1084 | 0 | 0.05921 | 3.0177 | 0 | 0 | 99.3777 | 164.5905 | off_peak | 806.7095 | 0 | 100 | 16.95 | 0 | 83.05 | 496.6905 | 0
1645 | 866.97 | 840.38 | 24.8 | 170.2995 | 157.9005 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 0 | 42.2338 | 709.0695 | 0 | 0.05921 | 3.4465 | 0 | 0 | 110.9759 | 157.9005 | off_peak | 709.0695 | 100 | 0 | 18.21 | 0 | 81.79 | 544.2066 | 0
1646 | 908.29 | 785.158 | 24.9 | 159.0517 | 159.0517 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 53.832 | 761.6372 | 0 | 0.05921 | 3.7963 | 0 | 0 | 110.9759 | 159.0517 | off_peak | 749.2383 | 0 | 100 | 17.51 | 0 | 82.49 | 603.8126 | 0
1647 | 979.62 | 707.691 | 24.9 | 143.359 | 143.359 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 65.4301 | 848.6599 | 0 | 0.05921 | 3.8906 | 0 | 0 | 110.9759 | 143.359 | off_peak | 836.261 | 0 | 100 | 14.63 | 0 | 85.37 | 557.7537 | 0
1648 | 902.92 | 564.301 | 24.8 | 114.3532 | 114.3532 | 0 | 0 | 8.9635 | 8.9635 | 0 | 0 | 0 | 73.8147 | 797.5303 | 0 | 0.05921 | 3.9886 | 0 | 0 | 110.9759 | 114.3532 | off_peak | 788.5668 | 0 | 100 | 12.66 | 0 | 87.34 | 456.1115 | 0
1649 | 910.16 | 363.586 | 24.5 | 73.7587 | 73.7587 | 0 | 0 | 0.57892 | 0.57892 | 0 | 0 | 0 | 74.3563 | 836.9802 | 0 | 0.05921 | 4.0516 | 0 | 0 | 110.9759 | 73.7587 | off_peak | 836.4013 | 0 | 100 | 8.1 | 0 | 91.9 | 298.8401 | 0
1650 | 889.51 | 148.271 | 23.9 | 30.1438 | 30.1438 | 0 | 0 | 0.03739 | 0.03739 | 0 | 0 | 0 | 74.3912 | 859.4036 | 0 | 0.05921 | 4.3486 | 0 | 0 | 110.9759 | 30.1438 | off_peak | 859.3662 | 0 | 100 | 3.39 | 0 | 96.61 | 131.0821 | 0
1651 | 838.1 | 0 | 23.5 | 0 | 0 | 0 | 0 | 0 | 0 | 62.6277 | 62.6277 | 0 | 7.4394 | 775.4723 | 0 | 0.088511 | 4.8109 | 0 | 0 | 110.9759 | 0 | on_peak | 775.4723 |  |  | 0 | 7.47 | 92.53 | 0 | 0
1652 | 816.47 | 0 | 23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 816.47 | 0 | 0.088511 | 5.2899 | 0 | 0 | 110.9759 | 0 | on_peak | 816.47 |  |  | 0 | 0 | 100 | 0 | 0
1653 | 815.59 | 0 | 22.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 815.59 | 0 | 0.088511 | 5.7059 | 0 | 0 | 110.9759 | 0 | on_peak | 815.59 |  |  | 0 | 0 | 100 | 0 | 0
1654 | 811.11 | 0 | 22.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 811.11 | 0 | 0.088511 | 6.0024 | 0 | 0 | 110.9759 | 0 | on_peak | 811.11 |  |  | 0 | 0 | 100 | 0 | 0
1655 | 817.83 | 0 | 22.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 817.83 | 0 | 0.05921 | 6.2294 | 0 | 0 | 110.9759 | 0 | off_peak | 817.83 |  |  | 0 | 0 | 100 | 0 | 0
1656 | 775.92 | 0 | 22.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 775.92 | 0 | 0.05921 | 6.4163 | 0 | 0 | 110.9759 | 0 | off_peak | 775.92 |  |  | 0 | 0 | 100 | 0 | 0
1657 | 726.6 | 0 | 22.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 726.6 | 0 | 0.05921 | 6.3439 | 0 | 0 | 110.9759 | 0 | off_peak | 726.6 |  |  | 0 | 0 | 100 | 0 | 0
1658 | 652.88 | 0 | 22.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 652.88 | 0 | 0.05921 | 6.1672 | 0 | 0 | 110.9759 | 0 | off_peak | 652.88 |  |  | 0 | 0 | 100 | 0 | 0
1659 | 637.87 | 0 | 21.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 637.87 | 0 | 0.05921 | 5.7224 | 0 | 0 | 110.9759 | 0 | off_peak | 637.87 |  |  | 0 | 0 | 100 | 0 | 0
1660 | 617.87 | 0 | 21.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 617.87 | 0 | 0.05921 | 5.2905 | 0 | 0 | 110.9759 | 0 | off_peak | 617.87 |  |  | 0 | 0 | 100 | 0 | 0
1661 | 595.1 | 0 | 21.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 595.1 | 0 | 0.05921 | 4.8198 | 0 | 0 | 110.9759 | 0 | off_peak | 595.1 |  |  | 0 | 0 | 100 | 0 | 0
1662 | 710.12 | 0 | 21.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 710.12 | 0 | 0.05921 | 4.2305 | 0 | 0 | 110.9759 | 0 | off_peak | 710.12 |  |  | 0 | 0 | 100 | 0 | 0
1663 | 795.12 | 0 | 22.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 795.12 | 0 | 0.05921 | 3.7718 | 0 | 0 | 110.9759 | 0 | off_peak | 795.12 |  |  | 0 | 0 | 100 | 0 | 0
1664 | 798.51 | 120.494 | 23.3 | 24.5494 | 24.5494 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 773.9606 | 0 | 0.05921 | 3.4334 | 0 | 0 | 110.9759 | 24.5494 | off_peak | 773.9606 |  |  | 3.07 | 0 | 96.93 | 84.2882 | 0
1665 | 815.53 | 352.399 | 23.8 | 71.6691 | 71.6691 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 743.8609 | 0 | 0.05921 | 3.1857 | 0 | 0 | 110.9759 | 71.6691 | off_peak | 743.8609 |  |  | 8.79 | 0 | 91.21 | 228.3166 | 0
1666 | 767.42 | 556.442 | 24.2 | 113.004 | 113.004 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 654.416 | 0 | 0.05921 | 3.0588 | 0 | 0 | 110.9759 | 113.004 | off_peak | 654.416 |  |  | 14.73 | 0 | 85.27 | 345.6551 | 0
1667 | 807.79 | 719.766 | 24.6 | 145.9625 | 145.9625 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 19.0375 | 674.2264 | 0 | 0.05921 | 3.0181 | 0 | 0 | 110.9759 | 145.9625 | off_peak | 661.8275 | 0 | 100 | 18.07 | 0 | 81.93 | 440.5317 | 0
1668 | 813.29 | 825.589 | 24.8 | 167.3021 | 167.3021 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19.0375 | 645.9879 | 0 | 0.05921 | 3.1159 | 0 | 0 | 110.9759 | 167.3021 | off_peak | 645.9879 |  |  | 20.57 | 0 | 79.43 | 521.3038 | 0
1669 | 771.98 | 774.649 | 24.9 | 156.9229 | 156.9229 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19.0375 | 615.0571 | 0 | 0.05921 | 3.3147 | 0 | 0 | 110.9759 | 156.9229 | off_peak | 615.0571 |  |  | 20.33 | 0 | 79.67 | 520.1595 | 0
1670 | 764.29 | 728.786 | 24.9 | 147.6323 | 147.6323 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19.0375 | 616.6577 | 0 | 0.05921 | 3.4789 | 0 | 0 | 110.9759 | 147.6323 | off_peak | 616.6577 |  |  | 19.32 | 0 | 80.68 | 513.5997 | 0
1671 | 739.16 | 576.36 | 24.9 | 116.7549 | 116.7549 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19.0375 | 622.4051 | 0 | 0.05921 | 3.5742 | 0 | 0 | 110.9759 | 116.7549 | off_peak | 622.4051 |  |  | 15.8 | 0 | 84.2 | 417.3012 | 0
1672 | 730.79 | 91.6785 | 24.7 | 18.5849 | 18.5849 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19.0375 | 712.2051 | 0 | 0.05921 | 3.8966 | 0 | 0 | 110.9759 | 18.5849 | off_peak | 712.2051 |  |  | 2.54 | 0 | 97.46 | 72.4176 | 0
1673 | 737.46 | 106.918 | 24.4 | 21.6977 | 21.6977 | 0 | 0 | 8.7263 | 8.7263 | 0 | 0 | 0 | 27.2003 | 724.4887 | 0 | 0.05921 | 4.1359 | 0 | 0 | 110.9759 | 21.6977 | off_peak | 715.7623 | 0 | 100 | 2.94 | 0 | 97.06 | 89.7399 | 0
1674 | 693.37 | 55.1531 | 23.8 | 11.2168 | 11.2168 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 38.7984 | 694.5522 | 0 | 0.05921 | 4.5182 | 0 | 0 | 110.9759 | 11.2168 | off_peak | 682.1532 | 0 | 100 | 1.62 | 0 | 98.38 | 50.6792 | 0
1675 | 609.23 | 0 | 23.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 38.7984 | 609.23 | 0 | 0.05921 | 4.712 | 0 | 0 | 110.9759 | 0 | off_peak | 609.23 |  |  | 0 | 0 | 100 | 0 | 0
1676 | 585.48 | 0 | 23.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 38.7984 | 585.48 | 0 | 0.05921 | 4.9902 | 0 | 0 | 110.9759 | 0 | off_peak | 585.48 |  |  | 0 | 0 | 100 | 0 | 0
1677 | 600.76 | 0 | 23.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 38.7984 | 600.76 | 0 | 0.05921 | 5.2632 | 0 | 0 | 110.9759 | 0 | off_peak | 600.76 |  |  | 0 | 0 | 100 | 0 | 0
1678 | 596.59 | 0 | 23.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 38.7984 | 596.59 | 0 | 0.05921 | 5.416 | 0 | 0 | 110.9759 | 0 | off_peak | 596.59 |  |  | 0 | 0 | 100 | 0 | 0
1679 | 591.45 | 0 | 22.9 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 50.3966 | 603.8489 | 0 | 0.05921 | 5.6911 | 0 | 0 | 110.9759 | 0 | off_peak | 591.45 | 0 | 100 | 0 | 0 | 100 | 0 | 0
1680 | 609.21 | 0 | 22.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50.3966 | 609.21 | 0 | 0.05921 | 6.0691 | 0 | 0 | 110.9759 | 0 | off_peak | 609.21 |  |  | 0 | 0 | 100 | 0 | 0
1681 | 578.31 | 0 | 22.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50.3966 | 578.31 | 0 | 0.05921 | 6.1458 | 0 | 0 | 110.9759 | 0 | off_peak | 578.31 |  |  | 0 | 0 | 100 | 0 | 0
1682 | 574.63 | 0 | 22.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50.3966 | 574.63 | 0 | 0.05921 | 5.9744 | 0 | 0 | 110.9759 | 0 | off_peak | 574.63 |  |  | 0 | 0 | 100 | 0 | 0
1683 | 574.63 | 0 | 22.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50.3966 | 574.63 | 0 | 0.05921 | 5.5937 | 0 | 0 | 110.9759 | 0 | off_peak | 574.63 |  |  | 0 | 0 | 100 | 0 | 0
1684 | 574.63 | 0 | 22.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50.3966 | 574.63 | 0 | 0.05921 | 5.1707 | 0 | 0 | 110.9759 | 0 | off_peak | 574.63 |  |  | 0 | 0 | 100 | 0 | 0
1685 | 599.92 | 0 | 22.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50.3966 | 599.92 | 0 | 0.05921 | 4.7271 | 0 | 0 | 110.9759 | 0 | off_peak | 599.92 |  |  | 0 | 0 | 100 | 0 | 0
1686 | 669.45 | 0 | 22.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50.3966 | 669.45 | 0 | 0.05921 | 4.1959 | 0 | 0 | 110.9759 | 0 | off_peak | 669.45 |  |  | 0 | 0 | 100 | 0 | 0
1687 | 747.7 | 0 | 22.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50.3966 | 747.7 | 0 | 0.05921 | 3.6791 | 0 | 0 | 110.9759 | 0 | off_peak | 747.7 |  |  | 0 | 0 | 100 | 0 | 0
1688 | 784.87 | 149.217 | 23.5 | 30.3796 | 30.3796 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50.3966 | 754.4904 | 0 | 0.05921 | 0 | 0 | 0 | 110.9759 | 30.3796 | off_peak | 754.4904 |  |  | 3.87 | 0 | 96.13 | 0 | 0
1689 | 793.94 | 366.841 | 24 | 74.5527 | 74.5527 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50.3966 | 719.3873 | 0 | 0.05921 | 3.3164 | 0 | 0 | 110.9759 | 74.5527 | off_peak | 719.3873 |  |  | 9.39 | 0 | 90.61 | 247.2479 | 0
1690 | 746.76 | 571.38 | 24.4 | 115.9544 | 115.9544 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50.3966 | 630.8056 | 0 | 0.05921 | 3.0601 | 0 | 0 | 110.9759 | 115.9544 | off_peak | 630.8056 |  |  | 15.53 | 0 | 84.47 | 354.8338 | 0
1691 | 748.17 | 621.398 | 24.7 | 125.969 | 125.969 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50.3966 | 622.201 | 0 | 0.05921 | 2.9246 | 0 | 0 | 110.9759 | 125.969 | off_peak | 622.201 |  |  | 16.84 | 0 | 83.16 | 368.4031 | 0
1692 | 802.98 | 727.307 | 24.9 | 147.3327 | 147.3327 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50.3966 | 655.6473 | 0 | 0.05921 | 2.8896 | 0 | 0 | 110.9759 | 147.3327 | off_peak | 655.6473 |  |  | 18.35 | 0 | 81.65 | 425.7314 | 0
1693 | 733.66 | 824.387 | 24.9 | 166.9985 | 166.9985 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50.3966 | 566.6615 | 0 | 0.05921 | 2.9704 | 0 | 0 | 110.9759 | 166.9985 | off_peak | 566.6615 |  |  | 22.76 | 0 | 77.24 | 496.0501 | 0
1694 | 743.93 | 670.536 | 24.9 | 135.8324 | 135.8324 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50.3966 | 608.0976 | 0 | 0.05921 | 3.2052 | 0 | 0 | 110.9759 | 135.8324 | off_peak | 608.0976 |  |  | 18.26 | 0 | 81.74 | 435.3765 | 0
1695 | 722.12 | 649.334 | 24.7 | 131.6321 | 131.6321 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50.3966 | 590.4879 | 0 | 0.05921 | 3.3831 | 0 | 0 | 110.9759 | 131.6321 | off_peak | 590.4879 |  |  | 18.23 | 0 | 81.77 | 445.3207 | 0
1696 | 711.31 | 569.212 | 24.5 | 115.4729 | 103.074 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 0 | 61.9947 | 608.236 | 0 | 0.05921 | 3.4986 | 0 | 0 | 122.574 | 103.074 | off_peak | 608.236 | 100 | 0 | 14.49 | 0 | 85.51 | 360.6167 | 0
1697 | 717.56 | 367.005 | 24.2 | 74.5325 | 74.5325 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 61.9947 | 643.0275 | 0 | 0.05921 | 3.7123 | 0 | 0 | 122.574 | 74.5325 | off_peak | 643.0275 |  |  | 10.39 | 0 | 89.61 | 276.6888 | 0
1698 | 650.06 | 152.425 | 23.6 | 31.0216 | 31.0216 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 73.5928 | 631.4373 | 0 | 0.05921 | 3.9391 | 0 | 0 | 122.574 | 31.0216 | off_peak | 619.0384 | 0 | 100 | 4.77 | 0 | 95.23 | 122.1979 | 0
1699 | 603.97 | 0 | 23.3 | 0 | 0 | 0 | 0 | 0.80079 | 0.80079 | 0 | 0 | 0 | 74.3419 | 604.7708 | 0 | 0.05921 | 4.394 | 0 | 0 | 122.574 | 0 | off_peak | 603.97 | 0 | 100 | 0 | 0 | 100 | 0 | 0
1700 | 586.93 | 0 | 23.1 | 0 | 0 | 0 | 0 | 0.05172 | 0.05172 | 0 | 0 | 0 | 74.3903 | 586.9817 | 0 | 0.05921 | 4.9323 | 0 | 0 | 122.574 | 0 | off_peak | 586.93 | 0 | 100 | 0 | 0 | 100 | 0 | 0
1701 | 587.62 | 0 | 23 | 0 | 0 | 0 | 0 | 0.0033404 | 0.0033404 | 0 | 0 | 0 | 74.3934 | 587.6233 | 0 | 0.05921 | 5.3567 | 0 | 0 | 122.574 | 0 | off_peak | 587.62 | 0 | 100 | 0 | 0 | 100 | 0 | 0
1702 | 609.26 | 0 | 23 | 0 | 0 | 0 | 0 | 0.00021574 | 0.00021574 | 0 | 0 | 0 | 74.3936 | 609.2602 | 0 | 0.05921 | 5.7688 | 0 | 0 | 122.574 | 0 | off_peak | 609.26 | 0 | 100 | 0 | 0 | 100 | 0 | 0
1703 | 568.28 | 0 | 22.9 | 0 | 0 | 0 | 0 | 1.4896e-05 | 1.4896e-05 | 0 | 0 | 0 | 74.3936 | 568.28 | 0 | 0.05921 | 6.2299 | 0 | 0 | 122.574 | 0 | off_peak | 568.28 | 0 | 100 | 0 | 0 | 100 | 0 | 0
1704 | 583.66 | 0 | 22.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 583.66 | 0 | 0.05921 | 6.4964 | 0 | 0 | 122.574 | 0 | off_peak | 583.66 |  |  | 0 | 0 | 100 | 0 | 0
1705 | 567.29 | 0 | 22.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 567.29 | 0 | 0.05921 | 6.7196 | 0 | 0 | 122.574 | 0 | off_peak | 567.29 |  |  | 0 | 0 | 100 | 0 | 0
1706 | 550.26 | 0 | 22.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 550.26 | 0 | 0.05921 | 6.7051 | 0 | 0 | 122.574 | 0 | off_peak | 550.26 |  |  | 0 | 0 | 100 | 0 | 0
1707 | 558.68 | 0 | 22.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 558.68 | 0 | 0.05921 | 6.5639 | 0 | 0 | 122.574 | 0 | off_peak | 558.68 |  |  | 0 | 0 | 100 | 0 | 0
1708 | 553.99 | 0 | 22.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 553.99 | 0 | 0.05921 | 6.0659 | 0 | 0 | 122.574 | 0 | off_peak | 553.99 |  |  | 0 | 0 | 100 | 0 | 0
1709 | 570.26 | 0 | 22.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 570.26 | 0 | 0.05921 | 5.4747 | 0 | 0 | 122.574 | 0 | off_peak | 570.26 |  |  | 0 | 0 | 100 | 0 | 0
1710 | 721.86 | 0 | 22.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 721.86 | 0 | 0.05921 | 4.1099 | 0 | 0 | 122.574 | 0 | off_peak | 721.86 |  |  | 0 | 0 | 100 | 0 | 0
1711 | 780.51 | 0 | 22.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 780.51 | 0 | 0.088511 | 3.672 | 0 | 0 | 122.574 | 0 | on_peak | 780.51 |  |  | 0 | 0 | 100 | 0 | 0
1712 | 834.81 | 141.453 | 23.7 | 28.7783 | 28.7783 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 806.0317 | 0 | 0.088511 | 3.4553 | 0 | 0 | 122.574 | 28.7783 | on_peak | 806.0317 |  |  | 3.45 | 0 | 96.55 | 99.4368 | 0
1713 | 909.69 | 354.179 | 24.3 | 71.902 | 71.902 | 0 | 0 | 0 | 0 | 62.63 | 62.63 | 0 | 7.4394 | 775.158 | 0 | 0.088511 | 3.3389 | 0 | 0 | 122.574 | 71.902 | on_peak | 775.158 |  |  | 7.9 | 6.88 | 85.21 | 240.0723 | 0
1714 | 876.24 | 555.783 | 24.8 | 112.6271 | 112.6271 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 763.6129 | 0 | 0.088511 | 3.2867 | 0 | 0 | 122.574 | 112.6271 | on_peak | 763.6129 |  |  | 12.85 | 0 | 87.15 | 370.1702 | 0
1715 | 828.55 | 707.971 | 25.1 | 143.3125 | 143.3125 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 19.0375 | 697.6364 | 0 | 0.05921 | 3.5284 | 0 | 0 | 122.574 | 143.3125 | off_peak | 685.2375 | 0 | 100 | 17.3 | 0 | 82.7 | 505.663 | 0
1716 | 961.11 | 806.913 | 25.3 | 163.2234 | 150.8245 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 0 | 30.6357 | 810.2855 | 0 | 0.05921 | 3.9299 | 0 | 0 | 134.1722 | 150.8245 | off_peak | 810.2855 | 100 | 0 | 15.69 | 0 | 84.31 | 592.719 | 0
1717 | 906.47 | 825.898 | 25.3 | 167.0637 | 154.6648 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 0 | 42.2338 | 751.8052 | 0 | 0.05921 | 4.2651 | 0 | 0 | 145.7703 | 154.6648 | off_peak | 751.8052 | 100 | 0 | 17.06 | 0 | 82.94 | 659.6586 | 0
1718 | 944.52 | 793.266 | 25.2 | 160.5207 | 160.5207 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 53.832 | 796.3982 | 0 | 0.05921 | 4.4591 | 0 | 0 | 145.7703 | 160.5207 | off_peak | 783.9993 | 0 | 100 | 16.99 | 0 | 83.01 | 715.77 | 0
1719 | 993.81 | 686.373 | 25 | 138.9905 | 138.9905 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 65.4301 | 867.2184 | 0 | 0.05921 | 4.7369 | 0 | 0 | 145.7703 | 138.9905 | off_peak | 854.8195 | 0 | 100 | 13.99 | 0 | 86.01 | 658.3912 | 0
1720 | 859.74 | 555.193 | 24.8 | 112.5075 | 112.5075 | 0 | 0 | 8.9635 | 8.9635 | 0 | 0 | 0 | 73.8147 | 756.196 | 0 | 0.05921 | 5.0304 | 0 | 0 | 145.7703 | 112.5075 | off_peak | 747.2325 | 0 | 100 | 13.09 | 0 | 86.91 | 565.9543 | 0
1721 | 911.12 | 356.039 | 24.6 | 72.2017 | 72.2017 | 0 | 0 | 0.57892 | 0.57892 | 0 | 0 | 0 | 74.3563 | 839.4972 | 0 | 0.05921 | 5.284 | 0 | 0 | 145.7703 | 72.2017 | off_peak | 838.9183 | 0 | 100 | 7.92 | 0 | 92.08 | 381.5114 | 0
1722 | 888.88 | 145.078 | 24.3 | 29.4523 | 29.4523 | 0 | 0 | 0.03739 | 0.03739 | 0 | 0 | 0 | 74.3912 | 859.4651 | 0 | 0.05921 | 5.5898 | 0 | 0 | 145.7703 | 29.4523 | off_peak | 859.4277 | 0 | 100 | 3.31 | 0 | 96.69 | 164.6318 | 0
1723 | 845.93 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 62.6277 | 62.6277 | 0 | 7.4394 | 783.3023 | 0 | 0.088511 | 5.828 | 0 | 0 | 145.7703 | 0 | on_peak | 783.3023 |  |  | 0 | 7.4 | 92.6 | 0 | 0
1724 | 847.66 | 0 | 23.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 847.66 | 0 | 0.088511 | 5.9392 | 0 | 0 | 145.7703 | 0 | on_peak | 847.66 |  |  | 0 | 0 | 100 | 0 | 0
1725 | 850.04 | 0 | 23.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 850.04 | 0 | 0.088511 | 6.3208 | 0 | 0 | 145.7703 | 0 | on_peak | 850.04 |  |  | 0 | 0 | 100 | 0 | 0
1726 | 792.93 | 0 | 23.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 792.93 | 0 | 0.088511 | 6.5974 | 0 | 0 | 145.7703 | 0 | on_peak | 792.93 |  |  | 0 | 0 | 100 | 0 | 0
1727 | 798.91 | 0 | 23.4 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 19.0375 | 811.3089 | 0 | 0.05921 | 6.6911 | 0 | 0 | 145.7703 | 0 | off_peak | 798.91 | 0 | 100 | 0 | 0 | 100 | 0 | 0
1728 | 804.16 | 0 | 23.3 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 30.6357 | 816.5589 | 0 | 0.05921 | 6.7765 | 0 | 0 | 145.7703 | 0 | off_peak | 804.16 | 0 | 100 | 0 | 0 | 100 | 0 | 0
1729 | 761.41 | 0 | 23.3 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 42.2338 | 773.8089 | 0 | 0.05921 | 6.7022 | 0 | 0 | 145.7703 | 0 | off_peak | 761.41 | 0 | 100 | 0 | 0 | 100 | 0 | 0
1730 | 688.56 | 0 | 23.1 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 53.832 | 700.9589 | 0 | 0.05921 | 6.594 | 0 | 0 | 145.7703 | 0 | off_peak | 688.56 | 0 | 100 | 0 | 0 | 100 | 0 | 0
1731 | 617.91 | 0 | 22.9 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 65.4301 | 630.3089 | 0 | 0.05921 | 6.1859 | 0 | 0 | 145.7703 | 0 | off_peak | 617.91 | 0 | 100 | 0 | 0 | 100 | 0 | 0
1732 | 652.6 | 0 | 22.8 | 0 | 0 | 0 | 0 | 8.9635 | 8.9635 | 0 | 0 | 0 | 73.8147 | 661.5635 | 0 | 0.05921 | 5.5334 | 0 | 0 | 145.7703 | 0 | off_peak | 652.6 | 0 | 100 | 0 | 0 | 100 | 0 | 0
1733 | 634.11 | 0 | 22.7 | 0 | 0 | 0 | 0 | 0.57892 | 0.57892 | 0 | 0 | 0 | 74.3563 | 634.6889 | 0 | 0.05921 | 4.8023 | 0 | 0 | 145.7703 | 0 | off_peak | 634.11 | 0 | 100 | 0 | 0 | 100 | 0 | 0
1734 | 755.48 | 0 | 22.8 | 0 | 0 | 0 | 0 | 0.03739 | 0.03739 | 0 | 0 | 0 | 74.3912 | 755.5174 | 0 | 0.05921 | 4.2489 | 0 | 0 | 145.7703 | 0 | off_peak | 755.48 | 0 | 100 | 0 | 0 | 100 | 0 | 0
1735 | 789.63 | 0 | 23.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3912 | 789.63 | 0 | 0.088511 | 3.8315 | 0 | 0 | 145.7703 | 0 | on_peak | 789.63 |  |  | 0 | 0 | 100 | 0 | 0
1736 | 799.26 | 98.2648 | 24.4 | 19.9416 | 19.9416 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3912 | 779.3184 | 0 | 0.088511 | 3.5918 | 0 | 0 | 145.7703 | 19.9416 | on_peak | 779.3184 |  |  | 2.5 | 0 | 97.5 | 71.6265 | 0
1737 | 827.23 | 340.003 | 25 | 68.8506 | 68.8506 | 0 | 0 | 0 | 0 | 62.6277 | 62.6277 | 0 | 7.4394 | 695.7517 | 0 | 0.088511 | 3.3641 | 0 | 0 | 145.7703 | 68.8506 | on_peak | 695.7517 |  |  | 8.32 | 7.57 | 84.11 | 231.6236 | 0
1738 | 810.54 | 525.568 | 25.5 | 106.236 | 106.236 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 704.304 | 0 | 0.088511 | 3.3094 | 0 | 0 | 145.7703 | 106.236 | on_peak | 704.304 |  |  | 13.11 | 0 | 86.89 | 351.5788 | 0
1739 | 833.3 | 666.365 | 26 | 134.4531 | 134.4531 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 19.0375 | 711.2458 | 0 | 0.05921 | 3.4648 | 0 | 0 | 145.7703 | 134.4531 | off_peak | 698.8469 | 0 | 100 | 16.14 | 0 | 83.86 | 465.8493 | 0
1740 | 960.52 | 507.027 | 26.4 | 102.1555 | 102.1555 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 30.6357 | 870.7634 | 0 | 0.05921 | 3.9707 | 0 | 0 | 145.7703 | 102.1555 | off_peak | 858.3645 | 0 | 100 | 10.64 | 0 | 89.36 | 405.627 | 0
1741 | 839.3 | 525.004 | 26.7 | 105.6627 | 105.6627 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 42.2338 | 746.0363 | 0 | 0.05921 | 4.3025 | 0 | 0 | 145.7703 | 105.6627 | off_peak | 733.6373 | 0 | 100 | 12.59 | 0 | 87.41 | 454.6142 | 0
1742 | 927.61 | 681.843 | 26.9 | 137.1288 | 137.1288 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 53.832 | 802.8802 | 0 | 0.05921 | 4.3216 | 0 | 0 | 145.7703 | 137.1288 | off_peak | 790.4812 | 0 | 100 | 14.78 | 0 | 85.22 | 592.6197 | 0
1743 | 938.71 | 447.201 | 26.9 | 89.9388 | 89.9388 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 65.4301 | 861.1702 | 0 | 0.05921 | 4.1881 | 0 | 0 | 145.7703 | 89.9388 | off_peak | 848.7712 | 0 | 100 | 9.58 | 0 | 90.42 | 376.6725 | 0
1744 | 930.31 | 390.336 | 26.7 | 78.5593 | 78.5593 | 0 | 0 | 8.9635 | 8.9635 | 0 | 0 | 0 | 73.8147 | 860.7142 | 0 | 0.05921 | 4.1851 | 0 | 0 | 145.7703 | 78.5593 | off_peak | 851.7507 | 0 | 100 | 8.44 | 0 | 91.56 | 328.7783 | 0
1745 | 904.44 | 222.158 | 26.4 | 44.7603 | 44.1813 | 0 | 0.57892 | 0.57892 | 0 | 0 | 0 | 0 | 74.3563 | 860.2587 | 0 | 0.05921 | 4.2976 | 0 | 0 | 146.3119 | 44.1813 | off_peak | 860.2587 | 100 | 0 | 4.88 | 0 | 95.12 | 189.8753 | 0
1746 | 845.63 | 146.106 | 25.8 | 29.5013 | 29.5013 | 0 | 0 | 0.03739 | 0.03739 | 0 | 0 | 0 | 74.3912 | 816.1661 | 0 | 0.05921 | 4.198 | 0 | 0 | 146.3119 | 29.5013 | off_peak | 816.1287 | 0 | 100 | 3.49 | 0 | 96.51 | 123.8453 | 0
1747 | 858.09 | 0 | 25.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3912 | 858.09 | 0 | 0.088511 | 4.2215 | 0 | 0 | 146.3119 | 0 | on_peak | 858.09 |  |  | 0 | 0 | 100 | 0 | 0
1748 | 881.4 | 0 | 24.7 | 0 | 0 | 0 | 0 | 0 | 0 | 62.6277 | 62.6277 | 0 | 7.4394 | 818.7723 | 0 | 0.088511 | 4.3246 | 0 | 0 | 146.3119 | 0 | on_peak | 818.7723 |  |  | 0 | 7.11 | 92.89 | 0 | 0
1749 | 840.57 | 0 | 24.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 840.57 | 0 | 0.088511 | 4.5134 | 0 | 0 | 146.3119 | 0 | on_peak | 840.57 |  |  | 0 | 0 | 100 | 0 | 0
1750 | 818.32 | 0 | 23.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 818.32 | 0 | 0.088511 | 4.8088 | 0 | 0 | 146.3119 | 0 | on_peak | 818.32 |  |  | 0 | 0 | 100 | 0 | 0
1751 | 809.86 | 0 | 22.8 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 19.0375 | 822.2589 | 0 | 0.05921 | 5.0746 | 0 | 0 | 146.3119 | 0 | off_peak | 809.86 | 0 | 100 | 0 | 0 | 100 | 0 | 0
1752 | 781.55 | 0 | 22.3 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 30.6357 | 793.9489 | 0 | 0.05921 | 5.5818 | 0 | 0 | 146.3119 | 0 | off_peak | 781.55 | 0 | 100 | 0 | 0 | 100 | 0 | 0
1753 | 785.4 | 0 | 21.9 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 42.2338 | 797.7989 | 0 | 0.05921 | 5.8579 | 0 | 0 | 146.3119 | 0 | off_peak | 785.4 | 0 | 100 | 0 | 0 | 100 | 0 | 0
1754 | 690.82 | 0 | 21.7 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 53.832 | 703.2189 | 0 | 0.05921 | 5.8293 | 0 | 0 | 146.3119 | 0 | off_peak | 690.82 | 0 | 100 | 0 | 0 | 100 | 0 | 0
1755 | 642.01 | 0 | 21.6 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 65.4301 | 654.4089 | 0 | 0.05921 | 5.4623 | 0 | 0 | 146.3119 | 0 | off_peak | 642.01 | 0 | 100 | 0 | 0 | 100 | 0 | 0
1756 | 640.23 | 0 | 21.7 | 0 | 0 | 0 | 0 | 8.9635 | 8.9635 | 0 | 0 | 0 | 73.8147 | 649.1935 | 0 | 0.05921 | 4.926 | 0 | 0 | 146.3119 | 0 | off_peak | 640.23 | 0 | 100 | 0 | 0 | 100 | 0 | 0
1757 | 642.84 | 0 | 21.7 | 0 | 0 | 0 | 0 | 0.57892 | 0.57892 | 0 | 0 | 0 | 74.3563 | 643.4189 | 0 | 0.05921 | 4.1978 | 0 | 0 | 146.3119 | 0 | off_peak | 642.84 | 0 | 100 | 0 | 0 | 100 | 0 | 0
1758 | 743.67 | 0 | 21.8 | 0 | 0 | 0 | 0 | 0.03739 | 0.03739 | 0 | 0 | 0 | 74.3912 | 743.7074 | 0 | 0.05921 | 3.5386 | 0 | 0 | 146.3119 | 0 | off_peak | 743.67 | 0 | 100 | 0 | 0 | 100 | 0 | 0
1759 | 765.1 | 0 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3912 | 765.1 | 0 | 0.088511 | 3.1591 | 0 | 0 | 146.3119 | 0 | on_peak | 765.1 |  |  | 0 | 0 | 100 | 0 | 0
1760 | 862.6 | 67.7378 | 22.7 | 13.8305 | 13.8305 | 0 | 0 | 0 | 0 | 62.6277 | 62.6277 | 0 | 7.4394 | 786.1418 | 0 | 0.088511 | 2.9548 | 0 | 0 | 146.3119 | 13.8305 | on_peak | 786.1418 |  |  | 1.6 | 7.26 | 91.14 | 40.8664 | 0
1761 | 874.18 | 220.072 | 23.5 | 44.8052 | 44.8052 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 829.3748 | 0 | 0.088511 | 2.8958 | 0 | 0 | 146.3119 | 44.8052 | on_peak | 829.3748 |  |  | 5.13 | 0 | 94.87 | 129.7462 | 0
1762 | 823.52 | 392.275 | 24.2 | 79.6645 | 79.6645 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 743.8555 | 0 | 0.088511 | 2.9127 | 0 | 0 | 146.3119 | 79.6645 | on_peak | 743.8555 |  |  | 9.67 | 0 | 90.33 | 232.0353 | 0
1763 | 850.19 | 324.113 | 24.7 | 65.7038 | 65.7038 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 19.0375 | 796.8852 | 0 | 0.05921 | 3.1544 | 0 | 0 | 146.3119 | 65.7038 | off_peak | 784.4862 | 0 | 100 | 7.73 | 0 | 92.27 | 207.2582 | 0
1764 | 947.96 | 481.018 | 25 | 97.4061 | 97.4061 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 30.6357 | 862.9528 | 0 | 0.05921 | 3.6357 | 0 | 0 | 146.3119 | 97.4061 | off_peak | 850.5539 | 0 | 100 | 10.28 | 0 | 89.72 | 354.1367 | 0
1765 | 853.05 | 192.74 | 25.1 | 39.0158 | 39.0158 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 42.2338 | 826.4331 | 0 | 0.05921 | 4.0979 | 0 | 0 | 146.3119 | 39.0158 | off_peak | 814.0342 | 0 | 100 | 4.57 | 0 | 95.43 | 159.8824 | 0
1766 | 961.59 | 294.011 | 24.9 | 59.5587 | 59.5587 | 0 | 0 | 10.5757 | 10.5757 | 0 | 0 | 0 | 52.1265 | 912.6071 | 0 | 0.05921 | 4.269 | 0 | 0 | 146.3119 | 59.5587 | off_peak | 902.0313 | 0 | 100 | 6.19 | 0 | 93.81 | 254.2578 | 0
1767 | 946.9 | 105.952 | 24.6 | 21.4862 | 21.4862 | 0 | 0 | 0 | 0 | 12.8067 | 12.8067 | 0 | 38.4355 | 912.6071 | 0 | 0.05921 | 4.3004 | 0 | 0 | 146.3119 | 21.4862 | off_peak | 912.6071 |  |  | 2.27 | 1.35 | 96.38 | 92.3984 | 0
1768 | 930.75 | 110.071 | 24.1 | 22.3616 | 22.3616 | 0 | 0 | 4.2187 | 4.2187 | 0 | 0 | 0 | 42.3817 | 912.6071 | 0 | 0.05921 | 4.1346 | 0 | 0 | 146.3119 | 22.3616 | off_peak | 908.3884 | 0 | 100 | 2.4 | 0 | 97.6 | 92.4568 | 0
1769 | 868.42 | 75.4637 | 23.6 | 15.3584 | 2.9595 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 0 | 53.9799 | 865.4605 | 0 | 0.05921 | 4.1266 | 0 | 0 | 157.91 | 2.9595 | off_peak | 865.4605 | 100 | 0 | 0.34 | 0 | 99.66 | 12.2125 | 0
1770 | 831.17 | 64.2502 | 23 | 13.1043 | 0.7054 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 0 | 65.578 | 830.4646 | 0 | 0.05921 | 4.0695 | 0 | 0 | 169.5081 | 0.7054 | off_peak | 830.4646 | 100 | 0 | 0.08 | 0 | 99.92 | 2.8706 | 0
1771 | 826.81 | 0 | 22.7 | 0 | 0 | 0 | 0 | 0 | 0 | 54.3837 | 54.3837 | 0 | 7.4394 | 772.4263 | 0 | 0.088511 | 3.9366 | 0 | 0 | 169.5081 | 0 | on_peak | 772.4263 |  |  | 0 | 6.58 | 93.42 | 0 | 0
1772 | 811.34 | 0 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 811.34 | 0 | 0.088511 | 3.5924 | 0 | 0 | 169.5081 | 0 | on_peak | 811.34 |  |  | 0 | 0 | 100 | 0 | 0
1773 | 815.38 | 0 | 21.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 815.38 | 0 | 0.088511 | 3.2528 | 0 | 0 | 169.5081 | 0 | on_peak | 815.38 |  |  | 0 | 0 | 100 | 0 | 0
1774 | 785.81 | 0 | 21.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 785.81 | 0 | 0.088511 | 3.1633 | 0 | 0 | 169.5081 | 0 | on_peak | 785.81 |  |  | 0 | 0 | 100 | 0 | 0
1775 | 793.61 | 0 | 21.2 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 19.0375 | 806.0089 | 0 | 0.05921 | 3.5635 | 0 | 0 | 169.5081 | 0 | off_peak | 793.61 | 0 | 100 | 0 | 0 | 100 | 0 | 0
1776 | 789.97 | 0 | 21 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 30.6357 | 802.3689 | 0 | 0.05921 | 4.2586 | 0 | 0 | 169.5081 | 0 | off_peak | 789.97 | 0 | 100 | 0 | 0 | 100 | 0 | 0
1777 | 750.13 | 0 | 20.8 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 42.2338 | 762.5289 | 0 | 0.05921 | 4.7609 | 0 | 0 | 169.5081 | 0 | off_peak | 750.13 | 0 | 100 | 0 | 0 | 100 | 0 | 0
1778 | 630.49 | 0 | 20.7 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 53.832 | 642.8889 | 0 | 0.05921 | 4.9116 | 0 | 0 | 169.5081 | 0 | off_peak | 630.49 | 0 | 100 | 0 | 0 | 100 | 0 | 0
1779 | 633.1 | 0 | 20.6 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 65.4301 | 645.4989 | 0 | 0.05921 | 4.6382 | 0 | 0 | 169.5081 | 0 | off_peak | 633.1 | 0 | 100 | 0 | 0 | 100 | 0 | 0
1780 | 598.97 | 0 | 20.5 | 0 | 0 | 0 | 0 | 8.9635 | 8.9635 | 0 | 0 | 0 | 73.8147 | 607.9335 | 0 | 0.05921 | 4.2241 | 0 | 0 | 169.5081 | 0 | off_peak | 598.97 | 0 | 100 | 0 | 0 | 100 | 0 | 0
1781 | 598.72 | 0 | 20.5 | 0 | 0 | 0 | 0 | 0.57892 | 0.57892 | 0 | 0 | 0 | 74.3563 | 599.2989 | 0 | 0.05921 | 3.5725 | 0 | 0 | 169.5081 | 0 | off_peak | 598.72 | 0 | 100 | 0 | 0 | 100 | 0 | 0
1782 | 752.84 | 0 | 20.4 | 0 | 0 | 0 | 0 | 0.03739 | 0.03739 | 0 | 0 | 0 | 74.3912 | 752.8774 | 0 | 0.05921 | 3.1176 | 0 | 0 | 169.5081 | 0 | off_peak | 752.84 | 0 | 100 | 0 | 0 | 100 | 0 | 0
1783 | 773.48 | 6.65 | 21 | 1.366 | 1.366 | 0 | 0 | 0 | 0 | 62.6277 | 62.6277 | 0 | 7.4394 | 709.4862 | 0 | 0.088511 | 2.847 | 0 | 0 | 169.5081 | 1.366 | on_peak | 709.4862 |  |  | 0.18 | 8.1 | 91.73 | 3.889 | 0
1784 | 840.4 | 169.576 | 21.8 | 34.7347 | 34.7347 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 805.6653 | 0 | 0.088511 | 2.7104 | 0 | 0 | 169.5081 | 34.7347 | on_peak | 805.6653 |  |  | 4.13 | 0 | 95.87 | 94.1442 | 0
1785 | 893.76 | 289.681 | 22.4 | 59.2095 | 59.2095 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 834.5505 | 0 | 0.088511 | 2.68 | 0 | 0 | 169.5081 | 59.2095 | on_peak | 834.5505 |  |  | 6.62 | 0 | 93.38 | 158.6785 | 0
1786 | 885.23 | 455.155 | 22.8 | 92.8989 | 92.8989 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 792.3311 | 0 | 0.088511 | 2.7994 | 0 | 0 | 169.5081 | 92.8989 | on_peak | 792.3311 |  |  | 10.49 | 0 | 89.51 | 260.0598 | 0
1787 | 859.27 | 667.871 | 23.1 | 136.1689 | 136.1689 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 19.0375 | 735.5 | 0 | 0.05921 | 3.1099 | 0 | 0 | 169.5081 | 136.1689 | off_peak | 723.1011 | 0 | 100 | 15.85 | 0 | 84.15 | 423.4651 | 0
1788 | 877.17 | 871.968 | 23.4 | 177.5906 | 177.5906 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 30.6357 | 711.9784 | 0 | 0.05921 | 3.6985 | 0 | 0 | 169.5081 | 177.5906 | off_peak | 699.5794 | 0 | 100 | 20.25 | 0 | 79.75 | 656.8102 | 0
1789 | 847.27 | 916.546 | 23.6 | 186.536 | 186.536 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 42.2338 | 673.1329 | 0 | 0.05921 | 4.2934 | 0 | 0 | 169.5081 | 186.536 | off_peak | 660.734 | 0 | 100 | 22.02 | 0 | 77.98 | 800.8814 | 0
1790 | 922.46 | 881.526 | 23.6 | 179.4087 | 179.4087 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 53.832 | 755.4502 | 0 | 0.05921 | 4.1999 | 0 | 0 | 169.5081 | 179.4087 | off_peak | 743.0513 | 0 | 100 | 19.45 | 0 | 80.55 | 753.4976 | 0
1791 | 939.4 | 757.529 | 23.6 | 154.1728 | 154.1728 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 65.4301 | 797.6262 | 0 | 0.05921 | 3.6412 | 0 | 0 | 169.5081 | 154.1728 | off_peak | 785.2272 | 0 | 100 | 16.41 | 0 | 83.59 | 561.3724 | 0
1792 | 854.49 | 610.146 | 23.4 | 124.2662 | 124.2662 | 0 | 0 | 8.9635 | 8.9635 | 0 | 0 | 0 | 73.8147 | 739.1873 | 0 | 0.05921 | 3.2083 | 0 | 0 | 169.5081 | 124.2662 | off_peak | 730.2238 | 0 | 100 | 14.54 | 0 | 85.46 | 398.6828 | 0
1793 | 891.22 | 400.195 | 23 | 81.623 | 81.623 | 0 | 0 | 0.57892 | 0.57892 | 0 | 0 | 0 | 74.3563 | 810.1759 | 0 | 0.05921 | 3.0388 | 0 | 0 | 169.5081 | 81.623 | off_peak | 809.597 | 0 | 100 | 9.16 | 0 | 90.84 | 248.0387 | 0
1794 | 788.93 | 172.531 | 22.3 | 35.2771 | 35.2771 | 0 | 0 | 0.03739 | 0.03739 | 0 | 0 | 0 | 74.3912 | 753.6903 | 0 | 0.05921 | 3.0304 | 0 | 0 | 169.5081 | 35.2771 | off_peak | 753.6529 | 0 | 100 | 4.47 | 0 | 95.53 | 106.9049 | 0
1795 | 774.98 | 6.65 | 21.8 | 1.3621 | 1.3621 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3912 | 773.6179 | 0 | 0.088511 | 3.1204 | 0 | 0 | 169.5081 | 1.3621 | on_peak | 773.6179 |  |  | 0.18 | 0 | 99.82 | 4.2504 | 0
1796 | 793.81 | 0 | 21.4 | 0 | 0 | 0 | 0 | 0 | 0 | 62.6277 | 62.6277 | 0 | 7.4394 | 731.1823 | 0 | 0.088511 | 3.2532 | 0 | 0 | 169.5081 | 0 | on_peak | 731.1823 |  |  | 0 | 7.89 | 92.11 | 0 | 0
1797 | 799.67 | 0 | 21.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 799.67 | 0 | 0.088511 | 3.451 | 0 | 0 | 169.5081 | 0 | on_peak | 799.67 |  |  | 0 | 0 | 100 | 0 | 0
1798 | 768.62 | 0 | 21.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 768.62 | 0 | 0.088511 | 3.7343 | 0 | 0 | 169.5081 | 0 | on_peak | 768.62 |  |  | 0 | 0 | 100 | 0 | 0
1799 | 806.14 | 0 | 21.1 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 19.0375 | 818.5389 | 0 | 0.05921 | 4.1901 | 0 | 0 | 169.5081 | 0 | off_peak | 806.14 | 0 | 100 | 0 | 0 | 100 | 0 | 0
1800 | 734.12 | 0 | 21 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 30.6357 | 746.5189 | 0 | 0.05921 | 4.7701 | 0 | 0 | 169.5081 | 0 | off_peak | 734.12 | 0 | 100 | 0 | 0 | 100 | 0 | 0
1801 | 743.63 | 0 | 21 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 42.2338 | 756.0289 | 0 | 0.05921 | 5.1611 | 0 | 0 | 169.5081 | 0 | off_peak | 743.63 | 0 | 100 | 0 | 0 | 100 | 0 | 0
1802 | 627.65 | 0 | 21.1 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 53.832 | 640.0489 | 0 | 0.05921 | 5.1478 | 0 | 0 | 169.5081 | 0 | off_peak | 627.65 | 0 | 100 | 0 | 0 | 100 | 0 | 0
1803 | 607.82 | 0 | 21.1 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 65.4301 | 620.2189 | 0 | 0.05921 | 4.8557 | 0 | 0 | 169.5081 | 0 | off_peak | 607.82 | 0 | 100 | 0 | 0 | 100 | 0 | 0
1804 | 604.45 | 0 | 21.1 | 0 | 0 | 0 | 0 | 8.9635 | 8.9635 | 0 | 0 | 0 | 73.8147 | 613.4135 | 0 | 0.05921 | 4.401 | 0 | 0 | 169.5081 | 0 | off_peak | 604.45 | 0 | 100 | 0 | 0 | 100 | 0 | 0
1805 | 577.18 | 0 | 21.1 | 0 | 0 | 0 | 0 | 0.57892 | 0.57892 | 0 | 0 | 0 | 74.3563 | 577.7589 | 0 | 0.05921 | 3.7937 | 0 | 0 | 169.5081 | 0 | off_peak | 577.18 | 0 | 100 | 0 | 0 | 100 | 0 | 0
1806 | 754.18 | 0 | 21.2 | 0 | 0 | 0 | 0 | 0.03739 | 0.03739 | 0 | 0 | 0 | 74.3912 | 754.2174 | 0 | 0.05921 | 3.2304 | 0 | 0 | 169.5081 | 0 | off_peak | 754.18 | 0 | 100 | 0 | 0 | 100 | 0 | 0
1807 | 822.57 | 7.6155 | 21.6 | 1.561 | 1.561 | 0 | 0 | 0 | 0 | 62.6277 | 62.6277 | 0 | 7.4394 | 758.3813 | 0 | 0.088511 | 2.9055 | 0 | 0 | 169.5081 | 1.561 | on_peak | 758.3813 |  |  | 0.19 | 7.61 | 92.2 | 4.5355 | 0
1808 | 821.44 | 168.263 | 22.3 | 34.4044 | 34.4044 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 787.0356 | 0 | 0.088511 | 2.7528 | 0 | 0 | 169.5081 | 34.4044 | on_peak | 787.0356 |  |  | 4.19 | 0 | 95.81 | 94.7089 | 0
1809 | 892.42 | 390.782 | 22.9 | 79.7316 | 79.7316 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 812.6884 | 0 | 0.088511 | 2.6687 | 0 | 0 | 169.5081 | 79.7316 | on_peak | 812.6884 |  |  | 8.93 | 0 | 91.07 | 212.7831 | 0
1810 | 868.75 | 596.18 | 23.5 | 121.3784 | 121.3784 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 747.3716 | 0 | 0.088511 | 2.6506 | 0 | 0 | 169.5081 | 121.3784 | on_peak | 747.3716 |  |  | 13.97 | 0 | 86.03 | 321.7242 | 0
1811 | 868.01 | 760.303 | 24.2 | 154.4048 | 142.0058 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 0 | 19.0375 | 726.0042 | 0 | 0.05921 | 2.8776 | 0 | 0 | 181.1063 | 142.0058 | off_peak | 726.0042 | 100 | 0 | 16.36 | 0 | 83.64 | 408.6359 | 0
1812 | 893 | 841.082 | 24.7 | 170.503 | 170.503 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 30.6357 | 734.8959 | 0 | 0.05921 | 3.2839 | 0 | 0 | 181.1063 | 170.503 | off_peak | 722.497 | 0 | 100 | 19.09 | 0 | 80.91 | 559.9149 | 0
1813 | 860.13 | 885.377 | 25.1 | 179.2243 | 179.2243 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 42.2338 | 693.3046 | 0 | 0.05921 | 3.6866 | 0 | 0 | 181.1063 | 179.2243 | off_peak | 680.9057 | 0 | 100 | 20.84 | 0 | 79.16 | 660.73 | 0
1814 | 885.51 | 861.997 | 25.4 | 174.303 | 174.303 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 53.832 | 723.6059 | 0 | 0.05921 | 3.7842 | 0 | 0 | 181.1063 | 174.303 | off_peak | 711.207 | 0 | 100 | 19.68 | 0 | 80.32 | 659.6027 | 0
1815 | 895.58 | 757.678 | 25.7 | 153.0432 | 140.6442 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 0 | 65.4301 | 754.9358 | 0 | 0.05921 | 3.6004 | 0 | 0 | 192.7044 | 140.6442 | off_peak | 754.9358 | 100 | 0 | 15.7 | 0 | 84.3 | 506.3744 | 0
1816 | 880.68 | 593.098 | 25.8 | 119.7565 | 119.7565 | 0 | 0 | 8.9635 | 8.9635 | 0 | 0 | 0 | 73.8147 | 769.8871 | 0 | 0.05921 | 3.4628 | 0 | 0 | 192.7044 | 119.7565 | off_peak | 760.9235 | 0 | 100 | 13.6 | 0 | 86.4 | 414.6967 | 0
1817 | 910.57 | 386.791 | 25.5 | 78.1842 | 78.1842 | 0 | 0 | 0.57892 | 0.57892 | 0 | 0 | 0 | 74.3563 | 832.9647 | 0 | 0.05921 | 3.5866 | 0 | 0 | 192.7044 | 78.1842 | off_peak | 832.3858 | 0 | 100 | 8.59 | 0 | 91.41 | 280.4184 | 0
1818 | 868.3 | 164.263 | 24.9 | 33.2752 | 33.2752 | 0 | 0 | 0.03739 | 0.03739 | 0 | 0 | 0 | 74.3912 | 835.0622 | 0 | 0.05921 | 3.8583 | 0 | 0 | 192.7044 | 33.2752 | off_peak | 835.0248 | 0 | 100 | 3.83 | 0 | 96.17 | 128.3874 | 0
1819 | 805.96 | 6.65 | 24.5 | 1.349 | 1.349 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3912 | 804.611 | 0 | 0.088511 | 4.1339 | 0 | 0 | 192.7044 | 1.349 | on_peak | 804.611 |  |  | 0.17 | 0 | 99.83 | 5.5769 | 0
1820 | 829.5 | 0 | 23.9 | 0 | 0 | 0 | 0 | 0 | 0 | 62.6277 | 62.6277 | 0 | 7.4394 | 766.8723 | 0 | 0.088511 | 4.4745 | 0 | 0 | 192.7044 | 0 | on_peak | 766.8723 |  |  | 0 | 7.55 | 92.45 | 0 | 0
1821 | 767.13 | 0 | 23.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 767.13 | 0 | 0.088511 | 4.7995 | 0 | 0 | 192.7044 | 0 | on_peak | 767.13 |  |  | 0 | 0 | 100 | 0 | 0
1822 | 744.87 | 0 | 22.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 744.87 | 0 | 0.088511 | 5.129 | 0 | 0 | 192.7044 | 0 | on_peak | 744.87 |  |  | 0 | 0 | 100 | 0 | 0
1823 | 797.77 | 0 | 22.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 797.77 | 0 | 0.05921 | 5.5191 | 0 | 0 | 192.7044 | 0 | off_peak | 797.77 |  |  | 0 | 0 | 100 | 0 | 0
1824 | 788.77 | 0 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 788.77 | 0 | 0.05921 | 5.8157 | 0 | 0 | 192.7044 | 0 | off_peak | 788.77 |  |  | 0 | 0 | 100 | 0 | 0
1825 | 711.76 | 0 | 21.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 711.76 | 0 | 0.05921 | 5.7927 | 0 | 0 | 192.7044 | 0 | off_peak | 711.76 |  |  | 0 | 0 | 100 | 0 | 0
1826 | 644.74 | 0 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 644.74 | 0 | 0.05921 | 5.5798 | 0 | 0 | 192.7044 | 0 | off_peak | 644.74 |  |  | 0 | 0 | 100 | 0 | 0
1827 | 601.01 | 0 | 20.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 601.01 | 0 | 0.05921 | 5.1473 | 0 | 0 | 192.7044 | 0 | off_peak | 601.01 |  |  | 0 | 0 | 100 | 0 | 0
1828 | 599.58 | 0 | 20.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 599.58 | 0 | 0.05921 | 4.6593 | 0 | 0 | 192.7044 | 0 | off_peak | 599.58 |  |  | 0 | 0 | 100 | 0 | 0
1829 | 620.42 | 0 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 620.42 | 0 | 0.05921 | 4.1609 | 0 | 0 | 192.7044 | 0 | off_peak | 620.42 |  |  | 0 | 0 | 100 | 0 | 0
1830 | 713.82 | 0 | 19.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 713.82 | 0 | 0.05921 | 3.639 | 0 | 0 | 192.7044 | 0 | off_peak | 713.82 |  |  | 0 | 0 | 100 | 0 | 0
1831 | 749.98 | 8.7068 | 20.3 | 1.793 | 1.793 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 748.187 | 0 | 0.05921 | 3.2447 | 0 | 0 | 192.7044 | 1.793 | off_peak | 748.187 |  |  | 0.24 | 0 | 99.76 | 5.8176 | 0
1832 | 771.02 | 173.144 | 21.2 | 35.5413 | 35.5413 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 735.4787 | 0 | 0.05921 | 2.9934 | 0 | 0 | 192.7044 | 35.5413 | off_peak | 735.4787 |  |  | 4.61 | 0 | 95.39 | 106.3892 | 0
1833 | 836.56 | 394.098 | 22.2 | 80.6093 | 80.6093 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 755.9507 | 0 | 0.05921 | 2.8407 | 0 | 0 | 192.7044 | 80.6093 | off_peak | 755.9507 |  |  | 9.64 | 0 | 90.36 | 228.983 | 0
1834 | 792.5 | 596.579 | 23.1 | 121.6336 | 121.6336 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 670.8664 | 0 | 0.05921 | 2.8122 | 0 | 0 | 192.7044 | 121.6336 | off_peak | 670.8664 |  |  | 15.35 | 0 | 84.65 | 342.0542 | 0
1835 | 786.68 | 703.962 | 23.9 | 143.1168 | 143.1168 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 643.5632 | 0 | 0.05921 | 2.8521 | 0 | 0 | 192.7044 | 143.1168 | off_peak | 643.5632 |  |  | 18.19 | 0 | 81.81 | 408.1796 | 0
1836 | 815.27 | 855.517 | 24.6 | 173.4917 | 173.4917 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 641.7783 | 0 | 0.05921 | 3.0038 | 0 | 0 | 192.7044 | 173.4917 | off_peak | 641.7783 |  |  | 21.28 | 0 | 78.72 | 521.1257 | 0
1837 | 781.63 | 708.427 | 25.1 | 143.4048 | 143.4048 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 638.2252 | 0 | 0.05921 | 3.3206 | 0 | 0 | 192.7044 | 143.4048 | off_peak | 638.2252 |  |  | 18.35 | 0 | 81.65 | 476.187 | 0
1838 | 753.71 | 703.557 | 25.5 | 142.2138 | 142.2138 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 611.4962 | 0 | 0.05921 | 3.6764 | 0 | 0 | 192.7044 | 142.2138 | off_peak | 611.4962 |  |  | 18.87 | 0 | 81.13 | 522.836 | 0
1839 | 743.71 | 748.432 | 25.8 | 151.121 | 151.121 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 592.589 | 0 | 0.05921 | 4.0847 | 0 | 0 | 192.7044 | 151.121 | off_peak | 592.589 |  |  | 20.32 | 0 | 79.68 | 617.2818 | 0
1840 | 762.81 | 537.507 | 25.9 | 108.4925 | 108.4925 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 654.3175 | 0 | 0.05921 | 4.4164 | 0 | 0 | 192.7044 | 108.4925 | off_peak | 654.3175 |  |  | 14.22 | 0 | 85.78 | 479.1428 | 0
1841 | 799.61 | 325.896 | 25.6 | 65.8514 | 65.8514 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 733.7586 | 0 | 0.05921 | 4.6503 | 0 | 0 | 192.7044 | 65.8514 | off_peak | 733.7586 |  |  | 8.24 | 0 | 91.76 | 306.2301 | 0
1842 | 679.42 | 82.5613 | 25 | 16.7187 | 16.7187 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 19.0375 | 675.1003 | 0 | 0.05921 | 4.941 | 0 | 0 | 192.7044 | 16.7187 | off_peak | 662.7013 | 0 | 100 | 2.46 | 0 | 97.54 | 82.6062 | 0
1843 | 652.68 | 5.7042 | 24.5 | 1.1572 | 1.1572 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19.0375 | 651.5228 | 0 | 0.05921 | 5.2343 | 0 | 0 | 192.7044 | 1.1572 | off_peak | 651.5228 |  |  | 0.18 | 0 | 99.82 | 6.057 | 0
1844 | 635.12 | 0 | 23.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19.0375 | 635.12 | 0 | 0.05921 | 5.5657 | 0 | 0 | 192.7044 | 0 | off_peak | 635.12 |  |  | 0 | 0 | 100 | 0 | 0
1845 | 605.48 | 0 | 23.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19.0375 | 605.48 | 0 | 0.05921 | 5.8448 | 0 | 0 | 192.7044 | 0 | off_peak | 605.48 |  |  | 0 | 0 | 100 | 0 | 0
1846 | 606.84 | 0 | 22.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19.0375 | 606.84 | 0 | 0.05921 | 6.178 | 0 | 0 | 192.7044 | 0 | off_peak | 606.84 |  |  | 0 | 0 | 100 | 0 | 0
1847 | 603.78 | 0 | 22.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19.0375 | 603.78 | 0 | 0.05921 | 6.4105 | 0 | 0 | 192.7044 | 0 | off_peak | 603.78 |  |  | 0 | 0 | 100 | 0 | 0
1848 | 611.16 | 0 | 22.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19.0375 | 611.16 | 0 | 0.05921 | 6.3919 | 0 | 0 | 192.7044 | 0 | off_peak | 611.16 |  |  | 0 | 0 | 100 | 0 | 0
1849 | 592.22 | 0 | 22.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19.0375 | 592.22 | 0 | 0.05921 | 6.161 | 0 | 0 | 192.7044 | 0 | off_peak | 592.22 |  |  | 0 | 0 | 100 | 0 | 0
1850 | 586.83 | 0 | 22.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19.0375 | 586.83 | 0 | 0.05921 | 6.011 | 0 | 0 | 192.7044 | 0 | off_peak | 586.83 |  |  | 0 | 0 | 100 | 0 | 0
1851 | 618.36 | 0 | 22.2 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 30.6357 | 630.7589 | 0 | 0.05921 | 5.4921 | 0 | 0 | 192.7044 | 0 | off_peak | 618.36 | 0 | 100 | 0 | 0 | 100 | 0 | 0
1852 | 597.78 | 0 | 22.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30.6357 | 597.78 | 0 | 0.05921 | 4.9742 | 0 | 0 | 192.7044 | 0 | off_peak | 597.78 |  |  | 0 | 0 | 100 | 0 | 0
1853 | 608.71 | 0 | 22.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30.6357 | 608.71 | 0 | 0.05921 | 4.4062 | 0 | 0 | 192.7044 | 0 | off_peak | 608.71 |  |  | 0 | 0 | 100 | 0 | 0
1854 | 720.55 | 0 | 22.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30.6357 | 720.55 | 0 | 0.05921 | 3.9429 | 0 | 0 | 192.7044 | 0 | off_peak | 720.55 |  |  | 0 | 0 | 100 | 0 | 0
1855 | 720.16 | 6.6719 | 22.7 | 1.3622 | 1.3622 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30.6357 | 718.7978 | 0 | 0.05921 | 3.534 | 0 | 0 | 192.7044 | 1.3622 | off_peak | 718.7978 |  |  | 0.19 | 0 | 99.81 | 4.8142 | 0
1856 | 779.02 | 147.105 | 23.3 | 29.9711 | 29.9711 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30.6357 | 749.0489 | 0 | 0.05921 | 3.2397 | 0 | 0 | 192.7044 | 29.9711 | off_peak | 749.0489 |  |  | 3.85 | 0 | 96.15 | 97.0985 | 0
1857 | 802.27 | 254.763 | 23.9 | 51.7938 | 51.7938 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30.6357 | 750.4762 | 0 | 0.05921 | 3.0564 | 0 | 0 | 192.7044 | 51.7938 | off_peak | 750.4762 |  |  | 6.46 | 0 | 93.54 | 158.3042 | 0
1858 | 767.51 | 399.616 | 24.5 | 81.0679 | 81.0679 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30.6357 | 686.4421 | 0 | 0.05921 | 2.9666 | 0 | 0 | 192.7044 | 81.0679 | off_peak | 686.4421 |  |  | 10.56 | 0 | 89.44 | 240.499 | 0
1859 | 753.03 | 424.011 | 24.9 | 85.8931 | 85.8931 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 42.2338 | 679.5358 | 0 | 0.05921 | 2.9918 | 0 | 0 | 192.7044 | 85.8931 | off_peak | 667.1369 | 0 | 100 | 11.41 | 0 | 88.59 | 256.9733 | 0
1860 | 769.59 | 295.199 | 25.2 | 59.7348 | 59.7348 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 42.2338 | 709.8552 | 0 | 0.05921 | 3.0731 | 0 | 0 | 192.7044 | 59.7348 | off_peak | 709.8552 |  |  | 7.76 | 0 | 92.24 | 183.5683 | 0
1861 | 716.23 | 392.151 | 25.5 | 79.2676 | 79.2676 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 42.2338 | 636.9624 | 0 | 0.05921 | 3.325 | 0 | 0 | 192.7044 | 79.2676 | off_peak | 636.9624 |  |  | 11.07 | 0 | 88.93 | 263.5643 | 0
1862 | 753.43 | 415.717 | 25.6 | 84.0009 | 84.0009 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 42.2338 | 669.4291 | 0 | 0.05921 | 3.5934 | 0 | 0 | 192.7044 | 84.0009 | off_peak | 669.4291 |  |  | 11.15 | 0 | 88.85 | 301.845 | 0
1863 | 771.68 | 185.342 | 25.6 | 37.4507 | 37.4507 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 42.2338 | 734.2293 | 0 | 0.05921 | 3.8257 | 0 | 0 | 192.7044 | 37.4507 | off_peak | 734.2293 |  |  | 4.85 | 0 | 95.15 | 143.2759 | 0
1864 | 743.16 | 231.884 | 25.3 | 46.9058 | 46.9058 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 42.2338 | 696.2542 | 0 | 0.05921 | 3.869 | 0 | 0 | 192.7044 | 46.9058 | off_peak | 696.2542 |  |  | 6.31 | 0 | 93.69 | 181.4769 | 0
1865 | 733.61 | 164.334 | 25 | 33.2776 | 33.2776 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 42.2338 | 700.3324 | 0 | 0.05921 | 4.0049 | 0 | 0 | 192.7044 | 33.2776 | off_peak | 700.3324 |  |  | 4.54 | 0 | 95.46 | 133.275 | 0
1866 | 654.03 | 50.35 | 24.4 | 10.2179 | 1.4916 | 0 | 8.7263 | 8.7263 | 0 | 0 | 0 | 0 | 50.3966 | 652.5384 | 0 | 0.05921 | 4.0308 | 0 | 0 | 200.8672 | 1.4916 | off_peak | 652.5384 | 100 | 0 | 0.23 | 0 | 99.77 | 6.0121 | 0
1867 | 592.08 | 2.85 | 24.1 | 0.57899 | 0.57899 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50.3966 | 591.501 | 0 | 0.05921 | 4.0841 | 0 | 0 | 200.8672 | 0.57899 | off_peak | 591.501 |  |  | 0.1 | 0 | 99.9 | 2.3647 | 0
1868 | 572.23 | 0 | 23.7 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 61.9947 | 584.6289 | 0 | 0.05921 | 4.2387 | 0 | 0 | 200.8672 | 0 | off_peak | 572.23 | 0 | 100 | 0 | 0 | 100 | 0 | 0
1869 | 562.73 | 0 | 23.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 61.9947 | 562.73 | 0 | 0.05921 | 4.3369 | 0 | 0 | 200.8672 | 0 | off_peak | 562.73 |  |  | 0 | 0 | 100 | 0 | 0
1870 | 556.99 | 0 | 23.5 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 73.5928 | 569.3889 | 0 | 0.05921 | 4.4316 | 0 | 0 | 200.8672 | 0 | off_peak | 556.99 | 0 | 100 | 0 | 0 | 100 | 0 | 0
1871 | 573.41 | 0 | 23.3 | 0 | 0 | 0 | 0 | 0.80079 | 0.80079 | 0 | 0 | 0 | 74.3419 | 574.2108 | 0 | 0.05921 | 4.4576 | 0 | 0 | 200.8672 | 0 | off_peak | 573.41 | 0 | 100 | 0 | 0 | 100 | 0 | 0
1872 | 565.19 | 0 | 23.1 | 0 | 0 | 0 | 0 | 0.05172 | 0.05172 | 0 | 0 | 0 | 74.3903 | 565.2417 | 0 | 0.05921 | 4.5582 | 0 | 0 | 200.8672 | 0 | off_peak | 565.19 | 0 | 100 | 0 | 0 | 100 | 0 | 0
1873 | 559.96 | 0 | 23 | 0 | 0 | 0 | 0 | 0.0033404 | 0.0033404 | 0 | 0 | 0 | 74.3934 | 559.9633 | 0 | 0.05921 | 4.759 | 0 | 0 | 200.8672 | 0 | off_peak | 559.96 | 0 | 100 | 0 | 0 | 100 | 0 | 0
1874 | 561.16 | 0 | 22.9 | 0 | 0 | 0 | 0 | 0.00021574 | 0.00021574 | 0 | 0 | 0 | 74.3936 | 561.1602 | 0 | 0.05921 | 4.6822 | 0 | 0 | 200.8672 | 0 | off_peak | 561.16 | 0 | 100 | 0 | 0 | 100 | 0 | 0
1875 | 567.83 | 0 | 22.7 | 0 | 0 | 0 | 0 | 1.3934e-05 | 1.3934e-05 | 0 | 0 | 0 | 74.3936 | 567.83 | 0 | 0.05921 | 4.367 | 0 | 0 | 200.8672 | 0 | off_peak | 567.83 | 0 | 100 | 0 | 0 | 100 | 0 | 0
1876 | 569.05 | 0 | 22.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 569.05 | 0 | 0.05921 | 3.9786 | 0 | 0 | 200.8672 | 0 | off_peak | 569.05 |  |  | 0 | 0 | 100 | 0 | 0
1877 | 576.51 | 0 | 22.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 576.51 | 0 | 0.05921 | 3.434 | 0 | 0 | 200.8672 | 0 | off_peak | 576.51 |  |  | 0 | 0 | 100 | 0 | 0
1878 | 675.66 | 0 | 22.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 675.66 | 0 | 0.05921 | 2.9654 | 0 | 0 | 200.8672 | 0 | off_peak | 675.66 |  |  | 0 | 0 | 100 | 0 | 0
1879 | 738.67 | 2.85 | 23.2 | 0.58086 | 0.58086 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 738.0891 | 0 | 0.088511 | 2.6267 | 0 | 0 | 200.8672 | 0.58086 | on_peak | 738.0891 |  |  | 0.08 | 0 | 99.92 | 1.5257 | 0
1880 | 753.94 | 48.0374 | 24.1 | 9.7591 | 9.7591 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 744.1809 | 0 | 0.088511 | 2.5277 | 0 | 0 | 200.8672 | 9.7591 | on_peak | 744.1809 |  |  | 1.29 | 0 | 98.71 | 24.6679 | 0
1881 | 836.18 | 98.6245 | 24.7 | 19.993 | 19.993 | 0 | 0 | 0 | 0 | 62.63 | 62.63 | 0 | 7.4394 | 753.557 | 0 | 0.088511 | 2.4854 | 0 | 0 | 200.8672 | 19.993 | on_peak | 753.557 |  |  | 2.39 | 7.49 | 90.12 | 49.6916 | 0
1882 | 784.13 | 317.671 | 25.1 | 64.3052 | 64.3052 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 719.8248 | 0 | 0.088511 | 2.5668 | 0 | 0 | 200.8672 | 64.3052 | on_peak | 719.8248 |  |  | 8.2 | 0 | 91.8 | 165.0587 | 0
1883 | 776.5 | 578.014 | 25.5 | 116.8371 | 116.8371 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 19.0375 | 672.0618 | 0 | 0.05921 | 2.8425 | 0 | 0 | 200.8672 | 116.8371 | off_peak | 659.6629 | 0 | 100 | 15.05 | 0 | 84.95 | 332.1116 | 0
1884 | 867.59 | 716.705 | 25.8 | 144.7148 | 144.7148 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 30.6357 | 735.2742 | 0 | 0.05921 | 3.421 | 0 | 0 | 200.8672 | 144.7148 | off_peak | 722.8752 | 0 | 100 | 16.68 | 0 | 83.32 | 495.0735 | 0
1885 | 835.09 | 588.74 | 25.9 | 118.8336 | 118.8336 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 42.2338 | 728.6554 | 0 | 0.05921 | 3.9138 | 0 | 0 | 200.8672 | 118.8336 | off_peak | 716.2564 | 0 | 100 | 14.23 | 0 | 85.77 | 465.0902 | 0
1886 | 852.08 | 776.858 | 25.9 | 156.804 | 156.804 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 53.832 | 707.6749 | 0 | 0.05921 | 3.9753 | 0 | 0 | 200.8672 | 156.804 | off_peak | 695.276 | 0 | 100 | 18.4 | 0 | 81.6 | 623.3369 | 0
1887 | 851.56 | 681.318 | 25.8 | 137.5696 | 137.5696 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 65.4301 | 726.3894 | 0 | 0.05921 | 3.5004 | 0 | 0 | 200.8672 | 137.5696 | off_peak | 713.9904 | 0 | 100 | 16.16 | 0 | 83.84 | 481.5545 | 0
1888 | 835.07 | 528.214 | 25.5 | 106.7708 | 106.7708 | 0 | 0 | 8.9635 | 8.9635 | 0 | 0 | 0 | 73.8147 | 737.2627 | 0 | 0.05921 | 3.0847 | 0 | 0 | 200.8672 | 106.7708 | off_peak | 728.2992 | 0 | 100 | 12.79 | 0 | 87.21 | 329.3531 | 0
1889 | 841.69 | 137.889 | 25.2 | 27.9024 | 27.9024 | 0 | 0 | 0.57892 | 0.57892 | 0 | 0 | 0 | 74.3563 | 814.3665 | 0 | 0.05921 | 2.8395 | 0 | 0 | 200.8672 | 27.9024 | off_peak | 813.7876 | 0 | 100 | 3.32 | 0 | 96.68 | 79.2301 | 0
1890 | 841.61 | 158.202 | 24.6 | 32.082 | 32.082 | 0 | 0 | 0.03739 | 0.03739 | 0 | 0 | 0 | 74.3912 | 809.5654 | 0 | 0.05921 | 2.7419 | 0 | 0 | 200.8672 | 32.082 | off_peak | 809.528 | 0 | 100 | 3.81 | 0 | 96.19 | 87.9665 | 0
1891 | 821.39 | 7.6891 | 24.3 | 1.561 | 1.561 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3912 | 819.829 | 0 | 0.088511 | 2.6109 | 0 | 0 | 200.8672 | 1.561 | on_peak | 819.829 |  |  | 0.19 | 0 | 99.81 | 4.0754 | 0
1892 | 819.31 | 0 | 23.8 | 0 | 0 | 0 | 0 | 0 | 0 | 62.6277 | 62.6277 | 0 | 7.4394 | 756.6823 | 0 | 0.088511 | 2.5631 | 0 | 0 | 200.8672 | 0 | on_peak | 756.6823 |  |  | 0 | 7.64 | 92.36 | 0 | 0
1893 | 795.14 | 0 | 23.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 795.14 | 0 | 0.088511 | 2.6187 | 0 | 0 | 200.8672 | 0 | on_peak | 795.14 |  |  | 0 | 0 | 100 | 0 | 0
1894 | 759.44 | 0 | 23.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 759.44 | 0 | 0.088511 | 2.7665 | 0 | 0 | 200.8672 | 0 | on_peak | 759.44 |  |  | 0 | 0 | 100 | 0 | 0
1895 | 785.36 | 0 | 23.6 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 19.0375 | 797.7589 | 0 | 0.05921 | 3.1412 | 0 | 0 | 200.8672 | 0 | off_peak | 785.36 | 0 | 100 | 0 | 0 | 100 | 0 | 0
1896 | 803.72 | 0 | 23.6 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 30.6357 | 816.1189 | 0 | 0.05921 | 3.7911 | 0 | 0 | 200.8672 | 0 | off_peak | 803.72 | 0 | 100 | 0 | 0 | 100 | 0 | 0
1897 | 726.3 | 0 | 23.6 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 42.2338 | 738.6989 | 0 | 0.05921 | 4.4013 | 0 | 0 | 200.8672 | 0 | off_peak | 726.3 | 0 | 100 | 0 | 0 | 100 | 0 | 0
1898 | 667.95 | 0 | 23.5 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 53.832 | 680.3489 | 0 | 0.05921 | 4.5175 | 0 | 0 | 200.8672 | 0 | off_peak | 667.95 | 0 | 100 | 0 | 0 | 100 | 0 | 0
1899 | 634.75 | 0 | 23.5 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 65.4301 | 647.1489 | 0 | 0.05921 | 4.2265 | 0 | 0 | 200.8672 | 0 | off_peak | 634.75 | 0 | 100 | 0 | 0 | 100 | 0 | 0
1900 | 579.05 | 0 | 23.5 | 0 | 0 | 0 | 0 | 8.9635 | 8.9635 | 0 | 0 | 0 | 73.8147 | 588.0135 | 0 | 0.05921 | 3.7856 | 0 | 0 | 200.8672 | 0 | off_peak | 579.05 | 0 | 100 | 0 | 0 | 100 | 0 | 0
1901 | 602.87 | 0 | 23.5 | 0 | 0 | 0 | 0 | 0.57892 | 0.57892 | 0 | 0 | 0 | 74.3563 | 603.4489 | 0 | 0.05921 | 3.2618 | 0 | 0 | 200.8672 | 0 | off_peak | 602.87 | 0 | 100 | 0 | 0 | 100 | 0 | 0
1902 | 709.7 | 0 | 23.6 | 0 | 0 | 0 | 0 | 0.03739 | 0.03739 | 0 | 0 | 0 | 74.3912 | 709.7374 | 0 | 0.05921 | 2.7818 | 0 | 0 | 200.8672 | 0 | off_peak | 709.7 | 0 | 100 | 0 | 0 | 100 | 0 | 0
1903 | 702.36 | 10.9076 | 24.2 | 2.2152 | 2.2152 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3912 | 700.1448 | 0 | 0.088511 | 2.5205 | 0 | 0 | 200.8672 | 2.2152 | on_peak | 700.1448 |  |  | 0.32 | 0 | 99.68 | 5.5833 | 0
1904 | 766.27 | 177.597 | 25 | 35.9634 | 35.9634 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3912 | 730.3066 | 0 | 0.088511 | 2.3927 | 0 | 0 | 200.8672 | 35.9634 | on_peak | 730.3066 |  |  | 4.69 | 0 | 95.31 | 86.0493 | 0
1905 | 765.58 | 398.551 | 25.6 | 80.5323 | 80.5323 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3912 | 685.0477 | 0 | 0.088511 | 2.3687 | 0 | 0 | 200.8672 | 80.5323 | on_peak | 685.0477 |  |  | 10.52 | 0 | 89.48 | 190.7531 | 0
1906 | 802.13 | 606.512 | 26.2 | 122.2881 | 122.2881 | 0 | 0 | 0 | 0 | 62.6277 | 62.6277 | 0 | 7.4394 | 617.2142 | 0 | 0.088511 | 2.4438 | 62.6277 | 0 | 133.9153 | 184.9158 | on_peak | 617.2142 |  |  | 15.25 | 7.81 | 76.95 | 451.8957 | 0
1907 | 788.94 | 614.625 | 26.8 | 123.6551 | 123.6551 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 19.0375 | 677.6839 | 0 | 0.05921 | 2.7718 | 0 | 0 | 133.9153 | 123.6551 | off_peak | 665.2849 | 0 | 100 | 15.67 | 0 | 84.33 | 342.7509 | 0
1908 | 876.54 | 821.984 | 27.3 | 165.0735 | 165.0735 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 30.6357 | 723.8654 | 0 | 0.05921 | 3.3811 | 0 | 0 | 133.9153 | 165.0735 | off_peak | 711.4665 | 0 | 100 | 18.83 | 0 | 81.17 | 558.133 | 0
1909 | 848.37 | 896.988 | 27.6 | 179.9399 | 179.9399 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 42.2338 | 680.829 | 0 | 0.05921 | 3.8877 | 0 | 0 | 133.9153 | 179.9399 | off_peak | 668.4301 | 0 | 100 | 21.21 | 0 | 78.79 | 699.5458 | 0
1910 | 917.86 | 703.417 | 27.9 | 140.9548 | 140.9548 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 53.832 | 789.3041 | 0 | 0.05921 | 3.8079 | 0 | 0 | 133.9153 | 140.9548 | off_peak | 776.9052 | 0 | 100 | 15.36 | 0 | 84.64 | 536.7361 | 0
1911 | 932.17 | 720.69 | 27.9 | 144.4161 | 144.4161 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 65.4301 | 800.1528 | 0 | 0.05921 | 3.3059 | 0 | 0 | 133.9153 | 144.4161 | off_peak | 787.7539 | 0 | 100 | 15.49 | 0 | 84.51 | 477.4296 | 0
1912 | 912.06 | 600.228 | 27.8 | 120.321 | 120.321 | 0 | 0 | 8.9635 | 8.9635 | 0 | 0 | 0 | 73.8147 | 800.7026 | 0 | 0.05921 | 2.9433 | 0 | 0 | 133.9153 | 120.321 | off_peak | 791.739 | 0 | 100 | 13.19 | 0 | 86.81 | 354.1404 | 0
1913 | 883.74 | 393.231 | 27.4 | 78.9413 | 78.9413 | 0 | 0 | 0.57892 | 0.57892 | 0 | 0 | 0 | 74.3563 | 805.3776 | 0 | 0.05921 | 2.7635 | 0 | 0 | 133.9153 | 78.9413 | off_peak | 804.7987 | 0 | 100 | 8.93 | 0 | 91.07 | 218.1525 | 0
1914 | 869.47 | 170.157 | 26.7 | 34.2459 | 34.2459 | 0 | 0 | 0.03739 | 0.03739 | 0 | 0 | 0 | 74.3912 | 835.2615 | 0 | 0.05921 | 2.8546 | 0 | 0 | 133.9153 | 34.2459 | off_peak | 835.2241 | 0 | 100 | 3.94 | 0 | 96.06 | 97.7569 | 0
1915 | 839.59 | 8.7466 | 26.2 | 1.7635 | 1.7635 | 0 | 0 | 0 | 0 | 62.6277 | 62.6277 | 0 | 7.4394 | 775.1987 | 0 | 0.088511 | 2.9292 | 0 | 0 | 133.9153 | 1.7635 | on_peak | 775.1987 |  |  | 0.21 | 7.46 | 92.33 | 5.1658 | 0
1916 | 823.95 | 0 | 25.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 823.95 | 0 | 0.088511 | 3.0344 | 0 | 0 | 133.9153 | 0 | on_peak | 823.95 |  |  | 0 | 0 | 100 | 0 | 0
1917 | 799.43 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 799.43 | 0 | 0.088511 | 3.2084 | 0 | 0 | 133.9153 | 0 | on_peak | 799.43 |  |  | 0 | 0 | 100 | 0 | 0
1918 | 753.67 | 0 | 24.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 753.67 | 0 | 0.088511 | 3.554 | 0 | 0 | 133.9153 | 0 | on_peak | 753.67 |  |  | 0 | 0 | 100 | 0 | 0
1919 | 822.87 | 0 | 24.4 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 19.0375 | 835.2689 | 0 | 0.05921 | 3.9968 | 0 | 0 | 133.9153 | 0 | off_peak | 822.87 | 0 | 100 | 0 | 0 | 100 | 0 | 0
1920 | 773.78 | 0 | 24.2 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 30.6357 | 786.1789 | 0 | 0.05921 | 4.4813 | 0 | 0 | 133.9153 | 0 | off_peak | 773.78 | 0 | 100 | 0 | 0 | 100 | 0 | 0
1921 | 738.56 | 0 | 24.1 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 42.2338 | 750.9589 | 0 | 0.05921 | 4.7934 | 0 | 0 | 133.9153 | 0 | off_peak | 738.56 | 0 | 100 | 0 | 0 | 100 | 0 | 0
1922 | 688.39 | 0 | 24 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 53.832 | 700.7889 | 0 | 0.05921 | 4.774 | 0 | 0 | 133.9153 | 0 | off_peak | 688.39 | 0 | 100 | 0 | 0 | 100 | 0 | 0
1923 | 619.89 | 0 | 24 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 65.4301 | 632.2889 | 0 | 0.05921 | 4.3646 | 0 | 0 | 133.9153 | 0 | off_peak | 619.89 | 0 | 100 | 0 | 0 | 100 | 0 | 0
1924 | 624.96 | 0 | 23.9 | 0 | 0 | 0 | 0 | 8.9635 | 8.9635 | 0 | 0 | 0 | 73.8147 | 633.9235 | 0 | 0.05921 | 3.8768 | 0 | 0 | 133.9153 | 0 | off_peak | 624.96 | 0 | 100 | 0 | 0 | 100 | 0 | 0
1925 | 622.18 | 0 | 23.8 | 0 | 0 | 0 | 0 | 0.57892 | 0.57892 | 0 | 0 | 0 | 74.3563 | 622.7589 | 0 | 0.05921 | 3.323 | 0 | 0 | 133.9153 | 0 | off_peak | 622.18 | 0 | 100 | 0 | 0 | 100 | 0 | 0
1926 | 700.72 | 0 | 23.7 | 0 | 0 | 0 | 0 | 0.03739 | 0.03739 | 0 | 0 | 0 | 74.3912 | 700.7574 | 0 | 0.05921 | 2.7348 | 0 | 0 | 133.9153 | 0 | off_peak | 700.72 | 0 | 100 | 0 | 0 | 100 | 0 | 0
1927 | 781.82 | 14.4363 | 24.1 | 2.9328 | 2.9328 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3912 | 778.8872 | 0 | 0.088511 | 2.4101 | 0 | 0 | 133.9153 | 2.9328 | on_peak | 778.8872 |  |  | 0.38 | 0 | 99.62 | 7.0683 | 0
1928 | 778.61 | 166.434 | 25 | 33.7029 | 33.7029 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3912 | 744.9071 | 0 | 0.088511 | 2.2603 | 0 | 0 | 133.9153 | 33.7029 | on_peak | 744.9071 |  |  | 4.33 | 0 | 95.67 | 76.18 | 0
1929 | 827.37 | 410.642 | 25.8 | 82.9155 | 82.9155 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3912 | 744.4545 | 0 | 0.088511 | 2.1911 | 0 | 0 | 133.9153 | 82.9155 | on_peak | 744.4545 |  |  | 10.02 | 0 | 89.98 | 181.6788 | 0
1930 | 834.53 | 614.371 | 26.5 | 123.7383 | 123.7383 | 0 | 0 | 0 | 0 | 62.6277 | 62.6277 | 0 | 7.4394 | 648.164 | 0 | 0.088511 | 2.2393 | 0 | 0 | 133.9153 | 123.7383 | on_peak | 648.164 |  |  | 14.83 | 7.5 | 77.67 | 277.0837 | 0
1931 | 799.06 | 764.699 | 27.1 | 153.6809 | 153.6809 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 19.0375 | 657.7781 | 0 | 0.05921 | 2.4764 | 0 | 0 | 133.9153 | 153.6809 | off_peak | 645.3791 | 0 | 100 | 19.23 | 0 | 80.77 | 380.5723 | 0
1932 | 866.03 | 861.91 | 27.6 | 172.9031 | 172.9031 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 30.6357 | 705.5258 | 0 | 0.05921 | 2.9292 | 0 | 0 | 133.9153 | 172.9031 | off_peak | 693.1269 | 0 | 100 | 19.97 | 0 | 80.03 | 506.4684 | 0
1933 | 876.84 | 794.731 | 28.1 | 159.137 | 159.137 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 42.2338 | 730.1019 | 0 | 0.05921 | 3.3268 | 0 | 0 | 133.9153 | 159.137 | off_peak | 717.703 | 0 | 100 | 18.15 | 0 | 81.85 | 529.4243 | 0
1934 | 889.41 | 766.15 | 28.4 | 153.2464 | 153.2464 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 53.832 | 748.5625 | 0 | 0.05921 | 3.4131 | 0 | 0 | 133.9153 | 153.2464 | off_peak | 736.1636 | 0 | 100 | 17.23 | 0 | 82.77 | 523.04 | 0
1935 | 938.1 | 754.838 | 28.5 | 150.9287 | 150.9287 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 65.4301 | 799.5702 | 0 | 0.05921 | 3.2323 | 0 | 0 | 133.9153 | 150.9287 | off_peak | 787.1713 | 0 | 100 | 16.09 | 0 | 83.91 | 487.8499 | 0
1936 | 891.59 | 568.279 | 28.3 | 113.7094 | 113.7094 | 0 | 0 | 8.9635 | 8.9635 | 0 | 0 | 0 | 73.8147 | 786.8442 | 0 | 0.05921 | 3.125 | 0 | 0 | 133.9153 | 113.7094 | off_peak | 777.8806 | 0 | 100 | 12.75 | 0 | 87.25 | 355.3445 | 0
1937 | 867.63 | 267.681 | 27.8 | 53.659 | 53.659 | 0 | 0 | 0.57892 | 0.57892 | 0 | 0 | 0 | 74.3563 | 814.5499 | 0 | 0.05921 | 3.2323 | 0 | 0 | 133.9153 | 53.659 | off_peak | 813.971 | 0 | 100 | 6.18 | 0 | 93.82 | 173.4394 | 0
1938 | 849.44 | 129.525 | 26.9 | 26.0494 | 26.0494 | 0 | 0 | 0.03739 | 0.03739 | 0 | 0 | 0 | 74.3912 | 823.428 | 0 | 0.05921 | 3.3354 | 0 | 0 | 133.9153 | 26.0494 | off_peak | 823.3906 | 0 | 100 | 3.07 | 0 | 96.93 | 86.8845 | 0
1939 | 821.99 | 6.7021 | 26.3 | 1.3508 | 1.3508 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3912 | 820.6392 | 0 | 0.088511 | 3.4904 | 0 | 0 | 133.9153 | 1.3508 | on_peak | 820.6392 |  |  | 0.16 | 0 | 99.84 | 4.7148 | 0
1940 | 835.56 | 0 | 25.1 | 0 | 0 | 0 | 0 | 0 | 0 | 62.6277 | 62.6277 | 0 | 7.4394 | 772.9323 | 0 | 0.088511 | 3.733 | 0 | 0 | 133.9153 | 0 | on_peak | 772.9323 |  |  | 0 | 7.5 | 92.5 | 0 | 0
1941 | 827 | 0 | 24.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 827 | 0 | 0.088511 | 4.042 | 0 | 0 | 133.9153 | 0 | on_peak | 827 |  |  | 0 | 0 | 100 | 0 | 0
1942 | 761.75 | 0 | 23.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 761.75 | 0 | 0.088511 | 4.3159 | 0 | 0 | 133.9153 | 0 | on_peak | 761.75 |  |  | 0 | 0 | 100 | 0 | 0
1943 | 816.98 | 0 | 23.6 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 19.0375 | 829.3789 | 0 | 0.05921 | 4.6962 | 0 | 0 | 133.9153 | 0 | off_peak | 816.98 | 0 | 100 | 0 | 0 | 100 | 0 | 0
1944 | 818.81 | 0 | 23.5 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 30.6357 | 831.2089 | 0 | 0.05921 | 5.1867 | 0 | 0 | 133.9153 | 0 | off_peak | 818.81 | 0 | 100 | 0 | 0 | 100 | 0 | 0
1945 | 794.46 | 0 | 23.3 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 42.2338 | 806.8589 | 0 | 0.05921 | 5.327 | 0 | 0 | 133.9153 | 0 | off_peak | 794.46 | 0 | 100 | 0 | 0 | 100 | 0 | 0
1946 | 735.11 | 0 | 23.1 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 53.832 | 747.5089 | 0 | 0.05921 | 5.3095 | 0 | 0 | 133.9153 | 0 | off_peak | 735.11 | 0 | 100 | 0 | 0 | 100 | 0 | 0
1947 | 672.81 | 0 | 23.1 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 65.4301 | 685.2089 | 0 | 0.05921 | 4.8386 | 0 | 0 | 133.9153 | 0 | off_peak | 672.81 | 0 | 100 | 0 | 0 | 100 | 0 | 0
1948 | 656.32 | 0 | 23.1 | 0 | 0 | 0 | 0 | 8.9635 | 8.9635 | 0 | 0 | 0 | 73.8147 | 665.2835 | 0 | 0.05921 | 4.3525 | 0 | 0 | 133.9153 | 0 | off_peak | 656.32 | 0 | 100 | 0 | 0 | 100 | 0 | 0
1949 | 650.75 | 0 | 23.1 | 0 | 0 | 0 | 0 | 0.57892 | 0.57892 | 0 | 0 | 0 | 74.3563 | 651.3289 | 0 | 0.05921 | 3.6507 | 0 | 0 | 133.9153 | 0 | off_peak | 650.75 | 0 | 100 | 0 | 0 | 100 | 0 | 0
1950 | 687.76 | 0 | 23.2 | 0 | 0 | 0 | 0 | 0.03739 | 0.03739 | 0 | 0 | 0 | 74.3912 | 687.7974 | 0 | 0.05921 | 3.0834 | 0 | 0 | 133.9153 | 0 | off_peak | 687.76 | 0 | 100 | 0 | 0 | 100 | 0 | 0
1951 | 771.32 | 14.7269 | 23.8 | 2.9951 | 2.9951 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3912 | 768.3249 | 0 | 0.088511 | 2.6912 | 0 | 0 | 133.9153 | 2.9951 | on_peak | 768.3249 |  |  | 0.39 | 0 | 99.61 | 8.0604 | 0
1952 | 779.45 | 191.652 | 24.5 | 38.8794 | 38.8794 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3912 | 740.5706 | 0 | 0.088511 | 2.4642 | 0 | 0 | 133.9153 | 38.8794 | on_peak | 740.5706 |  |  | 4.99 | 0 | 95.01 | 95.8082 | 0
1953 | 811.49 | 416.65 | 25.1 | 84.3413 | 84.3413 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3912 | 727.1487 | 0 | 0.088511 | 2.3659 | 0 | 0 | 133.9153 | 84.3413 | on_peak | 727.1487 |  |  | 10.39 | 0 | 89.61 | 199.5423 | 0
1954 | 838.96 | 623.401 | 25.5 | 126.0115 | 126.0115 | 0 | 0 | 0 | 0 | 62.6277 | 62.6277 | 0 | 7.4394 | 650.3208 | 0 | 0.088511 | 2.3742 | 0 | 0 | 133.9153 | 126.0115 | on_peak | 650.3208 |  |  | 15.02 | 7.46 | 77.52 | 299.1737 | 0
1955 | 829.32 | 775.007 | 25.8 | 156.4869 | 156.4869 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 19.0375 | 685.232 | 0 | 0.05921 | 2.5867 | 0 | 0 | 133.9153 | 156.4869 | off_peak | 672.8331 | 0 | 100 | 18.87 | 0 | 81.13 | 404.7793 | 0
1956 | 907.1 | 843.708 | 26 | 170.2358 | 170.2358 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 30.6357 | 749.2631 | 0 | 0.05921 | 3.066 | 0 | 0 | 133.9153 | 170.2358 | off_peak | 736.8642 | 0 | 100 | 18.77 | 0 | 81.23 | 521.9505 | 0
1957 | 843.08 | 919.53 | 26 | 185.5345 | 185.5345 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 42.2338 | 669.9445 | 0 | 0.05921 | 3.4019 | 0 | 0 | 133.9153 | 185.5345 | off_peak | 657.5455 | 0 | 100 | 22.01 | 0 | 77.99 | 631.1759 | 0
1958 | 866.78 | 870.782 | 26.1 | 175.6351 | 175.6351 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 53.832 | 703.5439 | 0 | 0.05921 | 3.5222 | 0 | 0 | 133.9153 | 175.6351 | off_peak | 691.1449 | 0 | 100 | 20.26 | 0 | 79.74 | 618.6147 | 0
1959 | 919.49 | 756.588 | 26.1 | 152.6024 | 152.6024 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 65.4301 | 779.2866 | 0 | 0.05921 | 3.4925 | 0 | 0 | 133.9153 | 152.6024 | off_peak | 766.8876 | 0 | 100 | 16.6 | 0 | 83.4 | 532.9601 | 0
1960 | 842.79 | 570.695 | 25.9 | 115.1913 | 115.1913 | 0 | 0 | 8.9635 | 8.9635 | 0 | 0 | 0 | 73.8147 | 736.5622 | 0 | 0.05921 | 3.3179 | 0 | 0 | 133.9153 | 115.1913 | off_peak | 727.5987 | 0 | 100 | 13.67 | 0 | 86.33 | 382.1915 | 0
1961 | 904.28 | 404.093 | 25.5 | 81.6815 | 81.6815 | 0 | 0 | 0.57892 | 0.57892 | 0 | 0 | 0 | 74.3563 | 823.1774 | 0 | 0.05921 | 3.3902 | 0 | 0 | 133.9153 | 81.6815 | off_peak | 822.5985 | 0 | 100 | 9.03 | 0 | 90.97 | 276.9144 | 0
1962 | 884.02 | 180.113 | 25 | 36.4729 | 36.4729 | 0 | 0 | 0.03739 | 0.03739 | 0 | 0 | 0 | 74.3912 | 847.5845 | 0 | 0.05921 | 3.6477 | 0 | 0 | 133.9153 | 36.4729 | off_peak | 847.5471 | 0 | 100 | 4.13 | 0 | 95.87 | 133.0421 | 0
1963 | 837.03 | 10.8416 | 24.7 | 2.1978 | 2.1978 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3912 | 834.8322 | 0 | 0.088511 | 3.928 | 0 | 0 | 133.9153 | 2.1978 | on_peak | 834.8322 |  |  | 0.26 | 0 | 99.74 | 8.633 | 0
1964 | 884.32 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 17.7184 | 17.7184 | 0 | 55.4495 | 866.6016 | 0 | 0.088511 | 4.2412 | 0 | 0 | 133.9153 | 0 | on_peak | 866.6016 |  |  | 0 | 2 | 98 | 0 | 0
1965 | 832.15 | 0 | 23.6 | 0 | 0 | 0 | 0 | 0 | 0 | 44.9094 | 44.9094 | 0 | 7.4394 | 787.2406 | 0 | 0.088511 | 4.5012 | 0 | 0 | 133.9153 | 0 | on_peak | 787.2406 |  |  | 0 | 5.4 | 94.6 | 0 | 0
1966 | 768.44 | 0 | 23.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 768.44 | 0 | 0.088511 | 4.8766 | 0 | 0 | 133.9153 | 0 | on_peak | 768.44 |  |  | 0 | 0 | 100 | 0 | 0
1967 | 842.42 | 0 | 23.1 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 19.0375 | 854.8189 | 0 | 0.05921 | 5.2626 | 0 | 0 | 133.9153 | 0 | off_peak | 842.42 | 0 | 100 | 0 | 0 | 100 | 0 | 0
1968 | 842.09 | 0 | 22.9 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 30.6357 | 854.4889 | 0 | 0.05921 | 5.6589 | 0 | 0 | 133.9153 | 0 | off_peak | 842.09 | 0 | 100 | 0 | 0 | 100 | 0 | 0
1969 | 778.56 | 0 | 22.8 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 42.2338 | 790.9589 | 0 | 0.05921 | 5.7896 | 0 | 0 | 133.9153 | 0 | off_peak | 778.56 | 0 | 100 | 0 | 0 | 100 | 0 | 0
1970 | 754.46 | 0 | 22.8 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 53.832 | 766.8589 | 0 | 0.05921 | 5.703 | 0 | 0 | 133.9153 | 0 | off_peak | 754.46 | 0 | 100 | 0 | 0 | 100 | 0 | 0
1971 | 660.8 | 0 | 22.7 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 65.4301 | 673.1989 | 0 | 0.05921 | 5.2334 | 0 | 0 | 133.9153 | 0 | off_peak | 660.8 | 0 | 100 | 0 | 0 | 100 | 0 | 0
1972 | 605.6 | 0 | 22.6 | 0 | 0 | 0 | 0 | 8.9635 | 8.9635 | 0 | 0 | 0 | 73.8147 | 614.5635 | 0 | 0.05921 | 4.6169 | 0 | 0 | 133.9153 | 0 | off_peak | 605.6 | 0 | 100 | 0 | 0 | 100 | 0 | 0
1973 | 641.18 | 0 | 22.4 | 0 | 0 | 0 | 0 | 0.57892 | 0.57892 | 0 | 0 | 0 | 74.3563 | 641.7589 | 0 | 0.05921 | 3.9276 | 0 | 0 | 133.9153 | 0 | off_peak | 641.18 | 0 | 100 | 0 | 0 | 100 | 0 | 0
1974 | 728.6 | 0 | 22 | 0 | 0 | 0 | 0 | 0.03739 | 0.03739 | 0 | 0 | 0 | 74.3912 | 728.6374 | 0 | 0.05921 | 3.2733 | 0 | 0 | 133.9153 | 0 | off_peak | 728.6 | 0 | 100 | 0 | 0 | 100 | 0 | 0
1975 | 771.58 | 18.1102 | 21.5 | 3.7135 | 3.7135 | 0 | 0 | 0 | 0 | 62.6277 | 62.6277 | 0 | 7.4394 | 705.2387 | 0 | 0.088511 | 2.9007 | 0 | 0 | 133.9153 | 3.7135 | on_peak | 705.2387 |  |  | 0.48 | 8.12 | 91.4 | 10.772 | 0
1976 | 859.22 | 202.097 | 21.3 | 41.4698 | 41.4698 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 817.7502 | 0 | 0.088511 | 2.6584 | 0 | 0 | 133.9153 | 41.4698 | on_peak | 817.7502 |  |  | 4.83 | 0 | 95.17 | 110.2436 | 0
1977 | 843.32 | 426.417 | 21.4 | 87.4685 | 87.4685 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 755.8515 | 0 | 0.088511 | 2.5453 | 0 | 0 | 133.9153 | 87.4685 | on_peak | 755.8515 |  |  | 10.37 | 0 | 89.63 | 222.6322 | 0
1978 | 915.07 | 611.334 | 21.9 | 125.1767 | 125.1767 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 789.8933 | 0 | 0.088511 | 2.5396 | 0 | 0 | 133.9153 | 125.1767 | on_peak | 789.8933 |  |  | 13.68 | 0 | 86.32 | 317.8931 | 0
1979 | 851.88 | 700.589 | 22.4 | 143.1972 | 143.1972 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 19.0375 | 721.0818 | 0 | 0.05921 | 2.6726 | 0 | 0 | 133.9153 | 143.1972 | off_peak | 708.6828 | 0 | 100 | 16.81 | 0 | 83.19 | 382.7073 | 0
1980 | 920.79 | 782.237 | 22.9 | 159.6005 | 159.6005 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 30.6357 | 773.5884 | 0 | 0.05921 | 3.0663 | 0 | 0 | 133.9153 | 159.6005 | off_peak | 761.1895 | 0 | 100 | 17.33 | 0 | 82.67 | 489.3909 | 0
1981 | 894.87 | 651.085 | 23.3 | 132.6516 | 132.6516 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 42.2338 | 774.6173 | 0 | 0.05921 | 3.4449 | 0 | 0 | 133.9153 | 132.6516 | off_peak | 762.2184 | 0 | 100 | 14.82 | 0 | 85.18 | 456.9731 | 0
1982 | 889.92 | 755.459 | 23.6 | 153.7515 | 153.7515 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 53.832 | 748.5675 | 0 | 0.05921 | 3.6325 | 0 | 0 | 133.9153 | 153.7515 | off_peak | 736.1685 | 0 | 100 | 17.28 | 0 | 82.72 | 558.5007 | 0
1983 | 903.82 | 542.121 | 23.7 | 110.2933 | 110.2933 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 65.4301 | 805.9257 | 0 | 0.05921 | 3.5885 | 0 | 0 | 133.9153 | 110.2933 | off_peak | 793.5267 | 0 | 100 | 12.2 | 0 | 87.8 | 395.7873 | 0
1984 | 883.85 | 508.505 | 23.6 | 103.4912 | 103.4912 | 0 | 0 | 8.9635 | 8.9635 | 0 | 0 | 0 | 73.8147 | 789.3223 | 0 | 0.05921 | 3.5993 | 0 | 0 | 133.9153 | 103.4912 | off_peak | 780.3588 | 0 | 100 | 11.71 | 0 | 88.29 | 372.4988 | 0
1985 | 920.72 | 362.524 | 23.2 | 73.8868 | 73.8868 | 0 | 0 | 0.57892 | 0.57892 | 0 | 0 | 0 | 74.3563 | 847.4121 | 0 | 0.05921 | 3.8723 | 0 | 0 | 133.9153 | 73.8868 | off_peak | 846.8332 | 0 | 100 | 8.02 | 0 | 91.98 | 286.1101 | 0
1986 | 927.1 | 167.027 | 22.4 | 34.1396 | 34.1396 | 0 | 0 | 0.03739 | 0.03739 | 0 | 0 | 0 | 74.3912 | 892.9978 | 0 | 0.05921 | 4.2077 | 0 | 0 | 133.9153 | 34.1396 | off_peak | 892.9604 | 0 | 100 | 3.68 | 0 | 96.32 | 143.6473 | 0
1987 | 857.78 | 9.9994 | 21.8 | 2.0482 | 2.0482 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3912 | 855.7318 | 0 | 0.088511 | 4.6016 | 0 | 0 | 133.9153 | 2.0482 | on_peak | 855.7318 |  |  | 0.24 | 0 | 99.76 | 9.425 | 0
1988 | 873.04 | 0 | 20.4 | 0 | 0 | 0 | 0 | 0 | 0 | 6.4384 | 6.4384 | 0 | 67.5083 | 866.6016 | 0 | 0.088511 | 5.0055 | 0 | 0 | 133.9153 | 0 | on_peak | 866.6016 |  |  | 0 | 0.74 | 99.26 | 0 | 0
1989 | 817.61 | 0 | 19.5 | 0 | 0 | 0 | 0 | 0 | 0 | 56.1894 | 56.1894 | 0 | 7.4394 | 761.4206 | 0 | 0.088511 | 5.1505 | 0 | 0 | 133.9153 | 0 | on_peak | 761.4206 |  |  | 0 | 6.87 | 93.13 | 0 | 0
1990 | 766.1 | 0 | 18.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 766.1 | 0 | 0.088511 | 5.4918 | 0 | 0 | 133.9153 | 0 | on_peak | 766.1 |  |  | 0 | 0 | 100 | 0 | 0
1991 | 860.31 | 0 | 17.8 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 19.0375 | 872.7089 | 0 | 0.05921 | 5.8736 | 0 | 0 | 133.9153 | 0 | off_peak | 860.31 | 0 | 100 | 0 | 0 | 100 | 0 | 0
1992 | 777.98 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19.0375 | 777.98 | 0 | 0.05921 | 6.1382 | 0 | 0 | 133.9153 | 0 | off_peak | 777.98 |  |  | 0 | 0 | 100 | 0 | 0
1993 | 729.53 | 0 | 16.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19.0375 | 729.53 | 0 | 0.05921 | 6.1441 | 0 | 0 | 133.9153 | 0 | off_peak | 729.53 |  |  | 0 | 0 | 100 | 0 | 0
1994 | 617.28 | 0 | 15.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19.0375 | 617.28 | 0 | 0.05921 | 6.019 | 0 | 0 | 133.9153 | 0 | off_peak | 617.28 |  |  | 0 | 0 | 100 | 0 | 0
1995 | 522.6 | 0 | 15.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19.0375 | 522.6 | 0 | 0.05921 | 5.5528 | 0 | 0 | 133.9153 | 0 | off_peak | 522.6 |  |  | 0 | 0 | 100 | 0 | 0
1996 | 559.51 | 0 | 15.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19.0375 | 559.51 | 0 | 0.05921 | 5.0711 | 0 | 0 | 133.9153 | 0 | off_peak | 559.51 |  |  | 0 | 0 | 100 | 0 | 0
1997 | 581.01 | 0 | 15.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19.0375 | 581.01 | 0 | 0.05921 | 4.4785 | 0 | 0 | 133.9153 | 0 | off_peak | 581.01 |  |  | 0 | 0 | 100 | 0 | 0
1998 | 732.55 | 0 | 15.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19.0375 | 732.55 | 0 | 0.05921 | 3.986 | 0 | 0 | 133.9153 | 0 | off_peak | 732.55 |  |  | 0 | 0 | 100 | 0 | 0
1999 | 797.18 | 17.9608 | 15.6 | 3.7601 | 0 | 0 | 3.7601 | 3.7601 | 0 | 0 | 0 | 0 | 22.5548 | 797.18 | 0 | 0.05921 | 3.5568 | 0 | 0 | 137.4326 | 0 | off_peak | 797.18 | 100 | 0 | 0 | 0 | 100 | 0 | 0
2000 | 827.98 | 199.371 | 16.3 | 41.6371 | 41.6371 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22.5548 | 786.3429 | 0 | 0.05921 | 3.2876 | 0 | 0 | 137.4326 | 41.6371 | off_peak | 786.3429 |  |  | 5.03 | 0 | 94.97 | 136.8882 | 0
2001 | 795.9 | 420.826 | 17.1 | 87.6408 | 87.6408 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22.5548 | 708.2592 | 0 | 0.05921 | 3.1145 | 0 | 0 | 137.4326 | 87.6408 | off_peak | 708.2592 |  |  | 11.01 | 0 | 88.99 | 272.9531 | 0
2002 | 824.65 | 618.963 | 18 | 128.4986 | 128.4986 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22.5548 | 696.1514 | 0 | 0.05921 | 3.0265 | 0 | 0 | 137.4326 | 128.4986 | off_peak | 696.1514 |  |  | 15.58 | 0 | 84.42 | 388.9029 | 0
2003 | 808.91 | 771.737 | 18.8 | 159.7648 | 159.7648 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 34.1529 | 661.5441 | 0 | 0.05921 | 3.0337 | 0 | 0 | 137.4326 | 159.7648 | off_peak | 649.1452 | 0 | 100 | 19.75 | 0 | 80.25 | 484.6799 | 0
2004 | 820.65 | 846.773 | 19.5 | 174.8667 | 174.8667 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 45.7511 | 658.1823 | 0 | 0.05921 | 3.1935 | 0 | 0 | 137.4326 | 174.8667 | off_peak | 645.7833 | 0 | 100 | 21.31 | 0 | 78.69 | 558.4414 | 0
2005 | 798.08 | 899.675 | 20 | 185.4635 | 185.4635 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 45.7511 | 612.6165 | 0 | 0.05921 | 3.3507 | 0 | 0 | 137.4326 | 185.4635 | off_peak | 612.6165 |  |  | 23.24 | 0 | 76.76 | 621.4276 | 0
2006 | 733.81 | 863.468 | 20.3 | 177.8108 | 177.8108 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 45.7511 | 555.9992 | 0 | 0.05921 | 3.8324 | 0 | 0 | 137.4326 | 177.8108 | off_peak | 555.9992 |  |  | 24.23 | 0 | 75.77 | 681.4344 | 0
2007 | 708.21 | 757.887 | 20.5 | 155.9584 | 155.9584 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 45.7511 | 552.2516 | 0 | 0.05921 | 4.2641 | 0 | 0 | 137.4326 | 155.9584 | off_peak | 552.2516 |  |  | 22.02 | 0 | 77.98 | 665.0154 | 0
2008 | 735.52 | 595.702 | 20.5 | 122.5839 | 122.5839 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 45.7511 | 612.9361 | 0 | 0.05921 | 4.5413 | 0 | 0 | 137.4326 | 122.5839 | off_peak | 612.9361 |  |  | 16.67 | 0 | 83.33 | 556.6916 | 0
2009 | 697.4 | 391.311 | 20.2 | 80.6098 | 80.6098 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 45.7511 | 616.7902 | 0 | 0.05921 | 4.9286 | 0 | 0 | 137.4326 | 80.6098 | off_peak | 616.7902 |  |  | 11.56 | 0 | 88.44 | 397.2941 | 0
2010 | 649.93 | 173.632 | 19.5 | 35.8567 | 35.8567 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 45.7511 | 614.0733 | 0 | 0.05921 | 5.1418 | 0 | 0 | 137.4326 | 35.8567 | off_peak | 614.0733 |  |  | 5.52 | 0 | 94.48 | 184.3664 | 0
2011 | 587.47 | 10.9294 | 19 | 2.261 | 2.261 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 45.7511 | 585.209 | 0 | 0.05921 | 5.5102 | 0 | 0 | 137.4326 | 2.261 | off_peak | 585.209 |  |  | 0.38 | 0 | 99.62 | 12.4587 | 0
2012 | 561.04 | 0 | 18.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 45.7511 | 561.04 | 0 | 0.05921 | 5.9165 | 0 | 0 | 137.4326 | 0 | off_peak | 561.04 |  |  | 0 | 0 | 100 | 0 | 0
2013 | 577.66 | 0 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 45.7511 | 577.66 | 0 | 0.05921 | 6.1329 | 0 | 0 | 137.4326 | 0 | off_peak | 577.66 |  |  | 0 | 0 | 100 | 0 | 0
2014 | 556.45 | 0 | 17.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 45.7511 | 556.45 | 0 | 0.05921 | 6.316 | 0 | 0 | 137.4326 | 0 | off_peak | 556.45 |  |  | 0 | 0 | 100 | 0 | 0
2015 | 589.71 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 45.7511 | 589.71 | 0 | 0.05921 | 6.6298 | 0 | 0 | 137.4326 | 0 | off_peak | 589.71 |  |  | 0 | 0 | 100 | 0 | 0
2016 | 572.82 | 0 | 16.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 45.7511 | 572.82 | 0 | 0.05921 | 6.8222 | 0 | 0 | 137.4326 | 0 | off_peak | 572.82 |  |  | 0 | 0 | 100 | 0 | 0
2017 | 591.26 | 0 | 15.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 45.7511 | 591.26 | 0 | 0.05921 | 6.6905 | 0 | 0 | 137.4326 | 0 | off_peak | 591.26 |  |  | 0 | 0 | 100 | 0 | 0
2018 | 563.2 | 0 | 15.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 45.7511 | 563.2 | 0 | 0.05921 | 6.5014 | 0 | 0 | 137.4326 | 0 | off_peak | 563.2 |  |  | 0 | 0 | 100 | 0 | 0
2019 | 587.06 | 0 | 14.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 45.7511 | 587.06 | 0 | 0.05921 | 6.0415 | 0 | 0 | 137.4326 | 0 | off_peak | 587.06 |  |  | 0 | 0 | 100 | 0 | 0
2020 | 585.53 | 0 | 14.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 45.7511 | 585.53 | 0 | 0.05921 | 5.5276 | 0 | 0 | 137.4326 | 0 | off_peak | 585.53 |  |  | 0 | 0 | 100 | 0 | 0
2021 | 611.12 | 0 | 14.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 45.7511 | 611.12 | 0 | 0.05921 | 4.9023 | 0 | 0 | 137.4326 | 0 | off_peak | 611.12 |  |  | 0 | 0 | 100 | 0 | 0
2022 | 691.02 | 0 | 14.4 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 57.3492 | 703.4189 | 0 | 0.05921 | 4.3332 | 0 | 0 | 137.4326 | 0 | off_peak | 691.02 | 0 | 100 | 0 | 0 | 100 | 0 | 0
2023 | 698.77 | 18.7018 | 14.9 | 3.9248 | 0 | 0 | 3.9248 | 12.3989 | 8.4741 | 0 | 0 | 0 | 68.9474 | 707.2441 | 0 | 0.05921 | 4.0177 | 0 | 0 | 141.1039 | 0 | off_peak | 698.77 | 31.65 | 68.35 | 0 | 0 | 100 | 0 | 0
2024 | 736.1 | 204.89 | 16 | 42.8345 | 42.8345 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 68.9474 | 693.2655 | 0 | 0.05921 | 3.6562 | 0 | 0 | 141.1039 | 42.8345 | off_peak | 693.2655 |  |  | 5.82 | 0 | 94.18 | 156.6111 | 0
2025 | 777.12 | 427.621 | 17.2 | 89.0248 | 89.0248 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 68.9474 | 688.0952 | 0 | 0.05921 | 3.4228 | 0 | 0 | 141.1039 | 89.0248 | off_peak | 688.0952 |  |  | 11.46 | 0 | 88.54 | 304.7156 | 0
2026 | 759.01 | 629.632 | 18.3 | 130.5758 | 130.5758 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 68.9474 | 628.4342 | 0 | 0.05921 | 3.2766 | 0 | 0 | 141.1039 | 130.5758 | off_peak | 628.4342 |  |  | 17.2 | 0 | 82.8 | 427.8403 | 0
2027 | 731.1 | 787.858 | 19.2 | 162.8725 | 157.4262 | 0 | 5.4463 | 5.4463 | 0 | 0 | 0 | 0 | 74.0419 | 573.6738 | 0 | 0.05921 | 3.256 | 0 | 0 | 146.1984 | 157.4262 | off_peak | 573.6738 | 100 | 0 | 21.53 | 0 | 78.47 | 512.5811 | 0
2028 | 764.03 | 888.45 | 19.9 | 183.2143 | 183.2143 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.0419 | 580.8157 | 0 | 0.05921 | 3.3552 | 0 | 0 | 146.1984 | 183.2143 | off_peak | 580.8157 |  |  | 23.98 | 0 | 76.02 | 614.7137 | 0
2029 | 733.44 | 876.402 | 20.5 | 180.3464 | 180.3464 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.0419 | 553.0936 | 0 | 0.05921 | 3.5424 | 0 | 0 | 146.1984 | 180.3464 | off_peak | 553.0936 |  |  | 24.59 | 0 | 75.41 | 638.8634 | 0
2030 | 699.84 | 880.795 | 20.8 | 181.0578 | 181.0578 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.0419 | 518.7822 | 0 | 0.05921 | 3.9273 | 0 | 0 | 146.1984 | 181.0578 | off_peak | 518.7822 |  |  | 25.87 | 0 | 74.13 | 711.0684 | 0
2031 | 715.04 | 766.456 | 21 | 157.4423 | 157.4423 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.0419 | 557.5977 | 0 | 0.05921 | 4.2558 | 0 | 0 | 146.1984 | 157.4423 | off_peak | 557.5977 |  |  | 22.02 | 0 | 77.98 | 670.0457 | 0
2032 | 715.64 | 612.238 | 21 | 125.7635 | 125.7635 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.0419 | 589.8765 | 0 | 0.05921 | 4.5717 | 0 | 0 | 146.1984 | 125.7635 | off_peak | 589.8765 |  |  | 17.57 | 0 | 82.43 | 574.9523 | 0
2033 | 694.23 | 405.984 | 20.7 | 83.4844 | 83.4844 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.0419 | 610.7456 | 0 | 0.05921 | 4.9175 | 0 | 0 | 146.1984 | 83.4844 | off_peak | 610.7456 |  |  | 12.03 | 0 | 87.97 | 410.534 | 0
2034 | 620.39 | 183.709 | 19.9 | 37.8841 | 37.8841 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.0419 | 582.5059 | 0 | 0.05921 | 5.544 | 0 | 0 | 146.1984 | 37.8841 | off_peak | 582.5059 |  |  | 6.11 | 0 | 93.89 | 210.0308 | 0
2035 | 576.26 | 11.3053 | 19.3 | 2.3363 | 2.3363 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.0419 | 573.9237 | 0 | 0.05921 | 6.0224 | 0 | 0 | 146.1984 | 2.3363 | off_peak | 573.9237 |  |  | 0.41 | 0 | 99.59 | 14.0701 | 0
2036 | 581.76 | 0 | 18.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.0419 | 581.76 | 0 | 0.05921 | 6.3873 | 0 | 0 | 146.1984 | 0 | off_peak | 581.76 |  |  | 0 | 0 | 100 | 0 | 0
2037 | 556.56 | 0 | 18.3 | 0 | 0 | 0 | 0 | 0.35175 | 0.35175 | 0 | 0 | 0 | 74.3709 | 556.9117 | 0 | 0.05921 | 6.5534 | 0 | 0 | 146.1984 | 0 | off_peak | 556.56 | 0 | 100 | 0 | 0 | 100 | 0 | 0
2038 | 559.92 | 0 | 17.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3709 | 559.92 | 0 | 0.05921 | 6.7736 | 0 | 0 | 146.1984 | 0 | off_peak | 559.92 |  |  | 0 | 0 | 100 | 0 | 0
2039 | 574.16 | 0 | 17.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3709 | 574.16 | 0 | 0.05921 | 7.091 | 0 | 0 | 146.1984 | 0 | off_peak | 574.16 |  |  | 0 | 0 | 100 | 0 | 0
2040 | 578.2 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3709 | 578.2 | 0 | 0.05921 | 7.2943 | 0 | 0 | 146.1984 | 0 | off_peak | 578.2 |  |  | 0 | 0 | 100 | 0 | 0
2041 | 582.03 | 0 | 16.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3709 | 582.03 | 0 | 0.05921 | 7.224 | 0 | 0 | 146.1984 | 0 | off_peak | 582.03 |  |  | 0 | 0 | 100 | 0 | 0
2042 | 583.26 | 0 | 16.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3709 | 583.26 | 0 | 0.05921 | 6.9581 | 0 | 0 | 146.1984 | 0 | off_peak | 583.26 |  |  | 0 | 0 | 100 | 0 | 0
2043 | 586.09 | 0 | 16 | 0 | 0 | 0 | 0 | 0.022718 | 0.022718 | 0 | 0 | 0 | 74.3922 | 586.1127 | 0 | 0.05921 | 6.3454 | 0 | 0 | 146.1984 | 0 | off_peak | 586.09 | 0 | 100 | 0 | 0 | 100 | 0 | 0
2044 | 568.94 | 0 | 16 | 0 | 0 | 0 | 0 | 0.0014673 | 0.0014673 | 0 | 0 | 0 | 74.3935 | 568.9415 | 0 | 0.05921 | 5.6247 | 0 | 0 | 146.1984 | 0 | off_peak | 568.94 | 0 | 100 | 0 | 0 | 100 | 0 | 0
2045 | 576.7 | 0 | 16.1 | 0 | 0 | 0 | 0 | 0.00010131 | 0.00010131 | 0 | 0 | 0 | 74.3936 | 576.7001 | 0 | 0.05921 | 4.9215 | 0 | 0 | 146.1984 | 0 | off_peak | 576.7 | 0 | 100 | 0 | 0 | 100 | 0 | 0
2046 | 685.97 | 0 | 16.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 685.97 | 0 | 0.05921 | 4.1922 | 0 | 0 | 146.1984 | 0 | off_peak | 685.97 |  |  | 0 | 0 | 100 | 0 | 0
2047 | 770.85 | 22.1506 | 17.3 | 4.6098 | 4.6098 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 766.2402 | 0 | 0.088511 | 3.807 | 0 | 0 | 146.1984 | 4.6098 | on_peak | 766.2402 |  |  | 0.6 | 0 | 99.4 | 17.5497 | 0
2048 | 848.51 | 203.376 | 18.7 | 42.1177 | 42.1177 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 806.3923 | 0 | 0.088511 | 3.5463 | 0 | 0 | 146.1984 | 42.1177 | on_peak | 806.3923 |  |  | 4.96 | 0 | 95.04 | 149.3599 | 0
2049 | 880.15 | 425.947 | 19.8 | 87.8689 | 87.8689 | 0 | 0 | 0 | 0 | 62.63 | 62.63 | 0 | 7.4394 | 729.6511 | 0 | 0.088511 | 3.3892 | 0 | 0 | 146.1984 | 87.8689 | on_peak | 729.6511 |  |  | 9.98 | 7.12 | 82.9 | 297.8066 | 0
2050 | 854.76 | 626.28 | 20.7 | 128.7849 | 128.7849 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 725.9751 | 0 | 0.088511 | 3.3431 | 0 | 0 | 146.1984 | 128.7849 | on_peak | 725.9751 |  |  | 15.07 | 0 | 84.93 | 430.546 | 0
2051 | 868.24 | 780.985 | 21.4 | 160.1991 | 160.1991 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 19.0375 | 720.4399 | 0 | 0.05921 | 3.5064 | 0 | 0 | 146.1984 | 160.1991 | off_peak | 708.0409 | 0 | 100 | 18.45 | 0 | 81.55 | 561.7192 | 0
2052 | 928.66 | 880.847 | 21.8 | 180.4264 | 168.0274 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 0 | 30.6357 | 760.6326 | 0 | 0.05921 | 3.8903 | 0 | 0 | 157.7966 | 168.0274 | off_peak | 760.6326 | 100 | 0 | 18.09 | 0 | 81.91 | 653.6721 | 0
2053 | 888.65 | 904.204 | 22.1 | 185.0129 | 185.0129 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 42.2338 | 716.0361 | 0 | 0.05921 | 4.135 | 0 | 0 | 157.7966 | 185.0129 | off_peak | 703.6371 | 0 | 100 | 20.82 | 0 | 79.18 | 765.0248 | 0
2054 | 869.54 | 849.346 | 22.2 | 173.7263 | 173.7263 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 53.832 | 708.2127 | 0 | 0.05921 | 4.2846 | 0 | 0 | 157.7966 | 173.7263 | off_peak | 695.8137 | 0 | 100 | 19.98 | 0 | 80.02 | 744.3401 | 0
2055 | 925.4 | 752.721 | 22.2 | 153.9625 | 153.9625 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 65.4301 | 783.8365 | 0 | 0.05921 | 4.4294 | 0 | 0 | 157.7966 | 153.9625 | off_peak | 771.4375 | 0 | 100 | 16.64 | 0 | 83.36 | 681.9601 | 0
2056 | 940.74 | 595.242 | 22 | 121.8383 | 121.8383 | 0 | 0 | 8.9635 | 8.9635 | 0 | 0 | 0 | 73.8147 | 827.8652 | 0 | 0.05921 | 4.7026 | 0 | 0 | 157.7966 | 121.8383 | off_peak | 818.9017 | 0 | 100 | 12.95 | 0 | 87.05 | 572.9551 | 0
2057 | 922.51 | 386.211 | 21.6 | 79.165 | 79.165 | 0 | 0 | 0.57892 | 0.57892 | 0 | 0 | 0 | 74.3563 | 843.9239 | 0 | 0.05921 | 5.0739 | 0 | 0 | 157.7966 | 79.165 | off_peak | 843.345 | 0 | 100 | 8.58 | 0 | 91.42 | 401.6728 | 0
2058 | 947.69 | 170.911 | 20.9 | 35.1203 | 35.1203 | 0 | 0 | 0.03739 | 0.03739 | 0 | 0 | 0 | 74.3912 | 912.6071 | 0 | 0.05921 | 5.4229 | 0 | 0 | 157.7966 | 35.1203 | off_peak | 912.5697 | 0 | 100 | 3.71 | 0 | 96.29 | 190.4527 | 0
2059 | 873.63 | 7.7112 | 20.4 | 1.5874 | 1.5874 | 0 | 0 | 0 | 0 | 5.441 | 5.441 | 0 | 68.5746 | 866.6016 | 0 | 0.088511 | 5.8215 | 0 | 0 | 157.7966 | 1.5874 | on_peak | 866.6016 |  |  | 0.18 | 0.62 | 99.2 | 9.2409 | 0
2060 | 903.3 | 0 | 19.9 | 0 | 0 | 0 | 0 | 0 | 0 | 36.6984 | 36.6984 | 0 | 29.3424 | 866.6016 | 0 | 0.088511 | 6.1267 | 36.6984 | 0 | 118.5644 | 36.6984 | on_peak | 866.6016 |  |  | 0 | 4.06 | 95.94 | 224.8411 | 0
2061 | 887.09 | 0 | 19.8 | 0 | 0 | 0 | 0 | 0 | 0 | 20.4884 | 20.4884 | 0 | 7.4394 | 866.6016 | 0 | 0.088511 | 6.3616 | 0 | 0 | 118.5644 | 0 | on_peak | 866.6016 |  |  | 0 | 2.31 | 97.69 | 0 | 0
2062 | 832.68 | 0 | 19.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 832.68 | 0 | 0.088511 | 6.8458 | 0 | 0 | 118.5644 | 0 | on_peak | 832.68 |  |  | 0 | 0 | 100 | 0 | 0
2063 | 861.87 | 0 | 19.4 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 19.0375 | 874.2689 | 0 | 0.05921 | 7.1267 | 0 | 0 | 118.5644 | 0 | off_peak | 861.87 | 0 | 100 | 0 | 0 | 100 | 0 | 0
2064 | 860.37 | 0 | 19.2 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 30.6357 | 872.7689 | 0 | 0.05921 | 7.265 | 0 | 0 | 118.5644 | 0 | off_peak | 860.37 | 0 | 100 | 0 | 0 | 100 | 0 | 0
2065 | 822.52 | 0 | 19 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 42.2338 | 834.9189 | 0 | 0.05921 | 7.283 | 0 | 0 | 118.5644 | 0 | off_peak | 822.52 | 0 | 100 | 0 | 0 | 100 | 0 | 0
2066 | 749.1 | 0 | 18.9 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 53.832 | 761.4989 | 0 | 0.05921 | 7.1893 | 0 | 0 | 118.5644 | 0 | off_peak | 749.1 | 0 | 100 | 0 | 0 | 100 | 0 | 0
2067 | 714.39 | 0 | 18.8 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 65.4301 | 726.7889 | 0 | 0.05921 | 6.497 | 0 | 0 | 118.5644 | 0 | off_peak | 714.39 | 0 | 100 | 0 | 0 | 100 | 0 | 0
2068 | 684.08 | 0 | 18.7 | 0 | 0 | 0 | 0 | 8.9635 | 8.9635 | 0 | 0 | 0 | 73.8147 | 693.0435 | 0 | 0.05921 | 5.8301 | 0 | 0 | 118.5644 | 0 | off_peak | 684.08 | 0 | 100 | 0 | 0 | 100 | 0 | 0
2069 | 694.28 | 0 | 18.7 | 0 | 0 | 0 | 0 | 0.57892 | 0.57892 | 0 | 0 | 0 | 74.3563 | 694.8589 | 0 | 0.05921 | 4.9676 | 0 | 0 | 118.5644 | 0 | off_peak | 694.28 | 0 | 100 | 0 | 0 | 100 | 0 | 0
2070 | 781.65 | 0 | 18.9 | 0 | 0 | 0 | 0 | 0.03739 | 0.03739 | 0 | 0 | 0 | 74.3912 | 781.6874 | 0 | 0.05921 | 4.3472 | 0 | 0 | 118.5644 | 0 | off_peak | 781.65 | 0 | 100 | 0 | 0 | 100 | 0 | 0
2071 | 809.79 | 23.2259 | 19.8 | 4.7913 | 4.7913 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3912 | 804.9987 | 0 | 0.088511 | 3.9567 | 0 | 0 | 118.5644 | 4.7913 | on_peak | 804.9987 |  |  | 0.59 | 0 | 99.41 | 18.9577 | 0
2072 | 859.75 | 203.649 | 21 | 41.8328 | 41.8328 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3912 | 817.9172 | 0 | 0.088511 | 3.6673 | 0 | 0 | 118.5644 | 41.8328 | on_peak | 817.9172 |  |  | 4.87 | 0 | 95.13 | 153.4112 | 0
2073 | 882.09 | 385.164 | 21.7 | 78.9223 | 78.9223 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3912 | 803.1677 | 0 | 0.088511 | 3.4951 | 0 | 0 | 118.5644 | 78.9223 | on_peak | 803.1677 |  |  | 8.95 | 0 | 91.05 | 275.8431 | 0
2074 | 932.97 | 605.179 | 22.3 | 123.7399 | 123.7399 | 0 | 0 | 0 | 0 | 62.6277 | 62.6277 | 0 | 7.4394 | 746.6023 | 0 | 0.088511 | 3.479 | 0 | 0 | 118.5644 | 123.7399 | on_peak | 746.6023 |  |  | 13.26 | 6.71 | 80.02 | 430.4952 | 0
2075 | 887.7 | 538.188 | 22.6 | 109.9247 | 109.9247 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 19.0375 | 790.1743 | 0 | 0.05921 | 3.7029 | 0 | 0 | 118.5644 | 109.9247 | off_peak | 777.7753 | 0 | 100 | 12.38 | 0 | 87.62 | 407.0385 | 0
2076 | 899.63 | 783.783 | 22.8 | 159.9731 | 159.9731 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 30.6357 | 752.0559 | 0 | 0.05921 | 4.228 | 0 | 0 | 118.5644 | 159.9731 | off_peak | 739.6569 | 0 | 100 | 17.78 | 0 | 82.22 | 676.3691 | 0
2077 | 894.69 | 686.713 | 22.9 | 140.1107 | 140.1107 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 42.2338 | 766.9783 | 0 | 0.05921 | 4.4159 | 0 | 0 | 118.5644 | 140.1107 | off_peak | 754.5793 | 0 | 100 | 15.66 | 0 | 84.34 | 618.717 | 0
2078 | 896.02 | 524.452 | 22.8 | 107.0426 | 107.0426 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 53.832 | 801.3763 | 0 | 0.05921 | 4.5732 | 0 | 0 | 118.5644 | 107.0426 | off_peak | 788.9774 | 0 | 100 | 11.95 | 0 | 88.05 | 489.5293 | 0
2079 | 922.53 | 753.532 | 22.6 | 153.9086 | 153.9086 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 65.4301 | 781.0203 | 0 | 0.05921 | 4.7123 | 0 | 0 | 118.5644 | 153.9086 | off_peak | 768.6214 | 0 | 100 | 16.68 | 0 | 83.32 | 725.2657 | 0
2080 | 921.14 | 590.521 | 22.3 | 120.7428 | 120.7428 | 0 | 0 | 8.9635 | 8.9635 | 0 | 0 | 0 | 73.8147 | 809.3607 | 0 | 0.05921 | 4.8428 | 0 | 0 | 118.5644 | 120.7428 | off_peak | 800.3972 | 0 | 100 | 13.11 | 0 | 86.89 | 584.7312 | 0
2081 | 893.38 | 118.222 | 21.9 | 24.2071 | 23.6282 | 0 | 0.57892 | 0.57892 | 0 | 0 | 0 | 0 | 74.3563 | 869.7518 | 0 | 0.05921 | 5.1952 | 0 | 0 | 119.1059 | 23.6282 | off_peak | 869.7518 | 100 | 0 | 2.64 | 0 | 97.36 | 122.7532 | 0
2082 | 912.61 | 26.6 | 21.4 | 5.4563 | 5.4563 | 0 | 0 | 0.03739 | 0.03739 | 0 | 0 | 0 | 74.3912 | 907.1911 | 0 | 0.05921 | 5.6494 | 0 | 0 | 119.1059 | 5.4563 | off_peak | 907.1537 | 0 | 100 | 0.6 | 0 | 99.4 | 30.8251 | 0
2083 | 868.33 | 3.8 | 21 | 0.78058 | 0.78058 | 0 | 0 | 0 | 0 | 0.94779 | 0.94779 | 0 | 73.378 | 866.6016 | 0 | 0.088511 | 6.1688 | 0 | 0 | 119.1059 | 0.78058 | on_peak | 866.6016 |  |  | 0.09 | 0.11 | 99.8 | 4.8153 | 0
2084 | 871.68 | 0 | 20.6 | 0 | 0 | 0 | 0 | 0 | 0 | 61.6799 | 61.6799 | 0 | 7.4394 | 810.0001 | 0 | 0.088511 | 6.6449 | 0 | 0 | 119.1059 | 0 | on_peak | 810.0001 |  |  | 0 | 7.08 | 92.92 | 0 | 0
2085 | 837.47 | 0 | 20.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 837.47 | 0 | 0.088511 | 6.9302 | 0 | 0 | 119.1059 | 0 | on_peak | 837.47 |  |  | 0 | 0 | 100 | 0 | 0
2086 | 800.93 | 0 | 20.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 800.93 | 0 | 0.088511 | 7.3163 | 0 | 0 | 119.1059 | 0 | on_peak | 800.93 |  |  | 0 | 0 | 100 | 0 | 0
2087 | 848.64 | 0 | 20.3 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 19.0375 | 861.0389 | 0 | 0.05921 | 7.3219 | 0 | 0 | 119.1059 | 0 | off_peak | 848.64 | 0 | 100 | 0 | 0 | 100 | 0 | 0
2088 | 819.96 | 0 | 20.2 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 30.6357 | 832.3589 | 0 | 0.05921 | 7.348 | 0 | 0 | 119.1059 | 0 | off_peak | 819.96 | 0 | 100 | 0 | 0 | 100 | 0 | 0
2089 | 768.22 | 0 | 20.2 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 42.2338 | 780.6189 | 0 | 0.05921 | 7.1448 | 0 | 0 | 119.1059 | 0 | off_peak | 768.22 | 0 | 100 | 0 | 0 | 100 | 0 | 0
2090 | 742.66 | 0 | 20.2 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 53.832 | 755.0589 | 0 | 0.05921 | 6.9614 | 0 | 0 | 119.1059 | 0 | off_peak | 742.66 | 0 | 100 | 0 | 0 | 100 | 0 | 0
2091 | 638.62 | 0 | 20.3 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 65.4301 | 651.0189 | 0 | 0.05921 | 6.2815 | 0 | 0 | 119.1059 | 0 | off_peak | 638.62 | 0 | 100 | 0 | 0 | 100 | 0 | 0
2092 | 628.86 | 0 | 20.4 | 0 | 0 | 0 | 0 | 8.9635 | 8.9635 | 0 | 0 | 0 | 73.8147 | 637.8235 | 0 | 0.05921 | 5.524 | 0 | 0 | 119.1059 | 0 | off_peak | 628.86 | 0 | 100 | 0 | 0 | 100 | 0 | 0
2093 | 649.54 | 0 | 20.5 | 0 | 0 | 0 | 0 | 0.57892 | 0.57892 | 0 | 0 | 0 | 74.3563 | 650.1189 | 0 | 0.05921 | 4.6945 | 0 | 0 | 119.1059 | 0 | off_peak | 649.54 | 0 | 100 | 0 | 0 | 100 | 0 | 0
2094 | 715.78 | 0 | 20.7 | 0 | 0 | 0 | 0 | 0.03739 | 0.03739 | 0 | 0 | 0 | 74.3912 | 715.8174 | 0 | 0.05921 | 4.1428 | 0 | 0 | 119.1059 | 0 | off_peak | 715.78 | 0 | 100 | 0 | 0 | 100 | 0 | 0
2095 | 791.82 | 21.3147 | 21.3 | 4.3737 | 4.3737 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3912 | 787.4463 | 0 | 0.088511 | 3.7548 | 0 | 0 | 119.1059 | 4.3737 | on_peak | 787.4463 |  |  | 0.55 | 0 | 99.45 | 16.4225 | 0
2096 | 804.01 | 206.256 | 22.2 | 42.1878 | 42.1878 | 0 | 0 | 0 | 0 | 62.6277 | 62.6277 | 0 | 7.4394 | 699.1944 | 0 | 0.088511 | 3.4641 | 0 | 0 | 119.1059 | 42.1878 | on_peak | 699.1944 |  |  | 5.25 | 7.79 | 86.96 | 146.1416 | 0
2097 | 777.63 | 424.897 | 22.9 | 86.6921 | 86.6921 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 690.9379 | 0 | 0.088511 | 3.2933 | 0 | 0 | 119.1059 | 86.6921 | on_peak | 690.9379 |  |  | 11.15 | 0 | 88.85 | 285.5047 | 0
2098 | 856.14 | 620.466 | 23.5 | 126.3228 | 126.3228 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 729.8172 | 0 | 0.088511 | 3.2251 | 0 | 0 | 119.1059 | 126.3228 | on_peak | 729.8172 |  |  | 14.75 | 0 | 85.25 | 407.404 | 0
2099 | 813.05 | 770.764 | 23.9 | 156.6978 | 156.6978 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 19.0375 | 668.7512 | 0 | 0.05921 | 3.3823 | 0 | 0 | 119.1059 | 156.6978 | off_peak | 656.3522 | 0 | 100 | 19.27 | 0 | 80.73 | 529.9931 | 0
2100 | 864.28 | 764.596 | 24.2 | 155.2766 | 155.2766 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 30.6357 | 721.4023 | 0 | 0.05921 | 3.8804 | 0 | 0 | 119.1059 | 155.2766 | off_peak | 709.0034 | 0 | 100 | 17.97 | 0 | 82.03 | 602.5325 | 0
2101 | 863.44 | 684.446 | 24.4 | 138.8997 | 138.8997 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 42.2338 | 736.9392 | 0 | 0.05921 | 4.1323 | 0 | 0 | 119.1059 | 138.8997 | off_peak | 724.5403 | 0 | 100 | 16.09 | 0 | 83.91 | 573.9712 | 0
2102 | 868.64 | 203.206 | 24.4 | 41.2381 | 41.2381 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 53.832 | 839.8008 | 0 | 0.05921 | 4.2214 | 0 | 0 | 119.1059 | 41.2381 | off_peak | 827.4019 | 0 | 100 | 4.75 | 0 | 95.25 | 174.0813 | 0
2103 | 952.05 | 254.589 | 24.3 | 51.6842 | 51.6842 | 0 | 0 | 12.2413 | 12.2413 | 0 | 0 | 0 | 65.2826 | 912.6071 | 0 | 0.05921 | 4.0277 | 0 | 0 | 119.1059 | 51.6842 | off_peak | 900.3658 | 0 | 100 | 5.43 | 0 | 94.57 | 208.1664 | 0
2104 | 874.26 | 242.39 | 24.1 | 49.243 | 40.132 | 0 | 9.111 | 9.111 | 0 | 0 | 0 | 0 | 73.8052 | 834.128 | 0 | 0.05921 | 4.1841 | 0 | 0 | 127.6285 | 40.132 | off_peak | 834.128 | 100 | 0 | 4.59 | 0 | 95.41 | 167.9151 | 0
2105 | 882.98 | 289.05 | 23.8 | 58.7855 | 58.7855 | 0 | 0 | 0.58844 | 0.58844 | 0 | 0 | 0 | 74.3556 | 824.783 | 0 | 0.05921 | 4.6761 | 0 | 0 | 127.6285 | 58.7855 | off_peak | 824.1945 | 0 | 100 | 6.66 | 0 | 93.34 | 274.8864 | 0
2106 | 899.69 | 56.0128 | 23.1 | 11.4202 | 11.4202 | 0 | 0 | 0.038005 | 0.038005 | 0 | 0 | 0 | 74.3912 | 888.3078 | 0 | 0.05921 | 4.8887 | 0 | 0 | 127.6285 | 11.4202 | off_peak | 888.2698 | 0 | 100 | 1.27 | 0 | 98.73 | 55.8299 | 0
2107 | 807.95 | 5.7 | 22.6 | 1.1642 | 1.1642 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3912 | 806.7858 | 0 | 0.088511 | 5.3531 | 0 | 0 | 127.6285 | 1.1642 | on_peak | 806.7858 |  |  | 0.14 | 0 | 99.86 | 6.2322 | 0
2108 | 828.31 | 0 | 22.1 | 0 | 0 | 0 | 0 | 0 | 0 | 62.6277 | 62.6277 | 0 | 7.4394 | 765.6823 | 0 | 0.088511 | 5.5508 | 0 | 0 | 127.6285 | 0 | on_peak | 765.6823 |  |  | 0 | 7.56 | 92.44 | 0 | 0
2109 | 827.8 | 0 | 21.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 827.8 | 0 | 0.088511 | 5.7008 | 0 | 0 | 127.6285 | 0 | on_peak | 827.8 |  |  | 0 | 0 | 100 | 0 | 0
2110 | 800.79 | 0 | 21.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 800.79 | 0 | 0.088511 | 5.9403 | 0 | 0 | 127.6285 | 0 | on_peak | 800.79 |  |  | 0 | 0 | 100 | 0 | 0
2111 | 846.35 | 0 | 21.8 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 19.0375 | 858.7489 | 0 | 0.05921 | 6.1444 | 0 | 0 | 127.6285 | 0 | off_peak | 846.35 | 0 | 100 | 0 | 0 | 100 | 0 | 0
2112 | 833.91 | 0 | 21.6 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 30.6357 | 846.3089 | 0 | 0.05921 | 6.3203 | 0 | 0 | 127.6285 | 0 | off_peak | 833.91 | 0 | 100 | 0 | 0 | 100 | 0 | 0
2113 | 809.01 | 0 | 21.4 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 42.2338 | 821.4089 | 0 | 0.05921 | 6.3095 | 0 | 0 | 127.6285 | 0 | off_peak | 809.01 | 0 | 100 | 0 | 0 | 100 | 0 | 0
2114 | 741.51 | 0 | 21.3 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 53.832 | 753.9089 | 0 | 0.05921 | 6.2094 | 0 | 0 | 127.6285 | 0 | off_peak | 741.51 | 0 | 100 | 0 | 0 | 100 | 0 | 0
2115 | 699.89 | 0 | 21.3 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 65.4301 | 712.2889 | 0 | 0.05921 | 5.6896 | 0 | 0 | 127.6285 | 0 | off_peak | 699.89 | 0 | 100 | 0 | 0 | 100 | 0 | 0
2116 | 681.46 | 0 | 21.3 | 0 | 0 | 0 | 0 | 8.9635 | 8.9635 | 0 | 0 | 0 | 73.8147 | 690.4235 | 0 | 0.05921 | 5.0896 | 0 | 0 | 127.6285 | 0 | off_peak | 681.46 | 0 | 100 | 0 | 0 | 100 | 0 | 0
2117 | 680.56 | 0 | 21.2 | 0 | 0 | 0 | 0 | 0.57892 | 0.57892 | 0 | 0 | 0 | 74.3563 | 681.1389 | 0 | 0.05921 | 4.3468 | 0 | 0 | 127.6285 | 0 | off_peak | 680.56 | 0 | 100 | 0 | 0 | 100 | 0 | 0
2118 | 778.9 | 0 | 21.3 | 0 | 0 | 0 | 0 | 0.03739 | 0.03739 | 0 | 0 | 0 | 74.3912 | 778.9374 | 0 | 0.05921 | 3.777 | 0 | 0 | 127.6285 | 0 | off_peak | 778.9 | 0 | 100 | 0 | 0 | 100 | 0 | 0
2119 | 810.52 | 22.2344 | 22 | 4.5511 | 4.5511 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3912 | 805.9689 | 0 | 0.088511 | 3.4524 | 0 | 0 | 127.6285 | 4.5511 | on_peak | 805.9689 |  |  | 0.56 | 0 | 99.44 | 15.7124 | 0
2120 | 811.49 | 203.314 | 22.9 | 41.4823 | 41.4823 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3912 | 770.0077 | 0 | 0.088511 | 3.1889 | 0 | 0 | 127.6285 | 41.4823 | on_peak | 770.0077 |  |  | 5.11 | 0 | 94.89 | 132.282 | 0
2121 | 830.56 | 349.362 | 23.4 | 71.1533 | 71.1533 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3912 | 759.4067 | 0 | 0.088511 | 3.035 | 0 | 0 | 127.6285 | 71.1533 | on_peak | 759.4067 |  |  | 8.57 | 0 | 91.43 | 215.9502 | 0
2122 | 909.88 | 145.403 | 23.9 | 29.5607 | 29.5607 | 0 | 0 | 0 | 0 | 62.6277 | 62.6277 | 0 | 7.4394 | 817.6916 | 0 | 0.088511 | 3.0195 | 0 | 0 | 127.6285 | 29.5607 | on_peak | 817.6916 |  |  | 3.25 | 6.88 | 89.87 | 89.2596 | 0
2123 | 841.21 | 211.323 | 24.2 | 42.9162 | 42.9162 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 19.0375 | 810.6928 | 0 | 0.05921 | 3.2316 | 0 | 0 | 127.6285 | 42.9162 | off_peak | 798.2938 | 0 | 100 | 5.1 | 0 | 94.9 | 138.6886 | 0
2124 | 861.99 | 126.35 | 24.5 | 25.6319 | 25.6319 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 30.6357 | 848.757 | 0 | 0.05921 | 3.7081 | 0 | 0 | 127.6285 | 25.6319 | off_peak | 836.3581 | 0 | 100 | 2.97 | 0 | 97.03 | 95.0451 | 0
2125 | 820.13 | 288.297 | 24.6 | 58.4642 | 46.0653 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 0 | 42.2338 | 774.0647 | 0 | 0.05921 | 4.0204 | 0 | 0 | 139.2267 | 46.0653 | off_peak | 774.0647 | 100 | 0 | 5.62 | 0 | 94.38 | 185.2019 | 0
2126 | 874.94 | 257.786 | 24.5 | 52.2956 | 52.2956 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 53.832 | 835.0433 | 0 | 0.05921 | 3.9046 | 0 | 0 | 139.2267 | 52.2956 | off_peak | 822.6444 | 0 | 100 | 5.98 | 0 | 94.02 | 204.192 | 0
2127 | 885.88 | 476.739 | 24.3 | 96.7829 | 96.7829 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 65.4301 | 801.496 | 0 | 0.05921 | 3.7363 | 0 | 0 | 139.2267 | 96.7829 | off_peak | 789.0971 | 0 | 100 | 10.93 | 0 | 89.07 | 361.6092 | 0
2128 | 852.51 | 390.965 | 24 | 79.4554 | 79.4554 | 0 | 0 | 8.9635 | 8.9635 | 0 | 0 | 0 | 73.8147 | 782.0181 | 0 | 0.05921 | 3.6867 | 0 | 0 | 139.2267 | 79.4554 | off_peak | 773.0546 | 0 | 100 | 9.32 | 0 | 90.68 | 292.9277 | 0
2129 | 799.75 | 194.384 | 23.6 | 39.5611 | 39.5611 | 0 | 0 | 0.57892 | 0.57892 | 0 | 0 | 0 | 74.3563 | 760.7678 | 0 | 0.05921 | 3.7991 | 0 | 0 | 139.2267 | 39.5611 | off_peak | 760.1889 | 0 | 100 | 4.95 | 0 | 95.05 | 150.2957 | 0
2130 | 854.49 | 99.8733 | 23.2 | 20.3554 | 20.3554 | 0 | 0 | 0.03739 | 0.03739 | 0 | 0 | 0 | 74.3912 | 834.172 | 0 | 0.05921 | 3.9385 | 0 | 0 | 139.2267 | 20.3554 | off_peak | 834.1346 | 0 | 100 | 2.38 | 0 | 97.62 | 80.1692 | 0
2131 | 798.65 | 12.1392 | 22.9 | 2.4768 | 2.4768 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3912 | 796.1732 | 0 | 0.088511 | 4.1306 | 0 | 0 | 139.2267 | 2.4768 | on_peak | 796.1732 |  |  | 0.31 | 0 | 99.69 | 10.2306 | 0
2132 | 794.57 | 0 | 22.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3912 | 794.57 | 0 | 0.088511 | 4.3177 | 0 | 0 | 139.2267 | 0 | on_peak | 794.57 |  |  | 0 | 0 | 100 | 0 | 0
2133 | 759.61 | 0 | 22.6 | 0 | 0 | 0 | 0 | 0 | 0 | 62.6277 | 62.6277 | 0 | 7.4394 | 696.9823 | 0 | 0.088511 | 4.562 | 0 | 0 | 139.2267 | 0 | on_peak | 696.9823 |  |  | 0 | 8.24 | 91.76 | 0 | 0
2134 | 804.71 | 0 | 22.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 804.71 | 0 | 0.088511 | 4.915 | 0 | 0 | 139.2267 | 0 | on_peak | 804.71 |  |  | 0 | 0 | 100 | 0 | 0
2135 | 825.43 | 0 | 22.5 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 19.0375 | 837.8289 | 0 | 0.05921 | 5.2899 | 0 | 0 | 139.2267 | 0 | off_peak | 825.43 | 0 | 100 | 0 | 0 | 100 | 0 | 0
2136 | 807.78 | 0 | 22.5 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 30.6357 | 820.1789 | 0 | 0.05921 | 5.7247 | 0 | 0 | 139.2267 | 0 | off_peak | 807.78 | 0 | 100 | 0 | 0 | 100 | 0 | 0
2137 | 736.91 | 0 | 22.4 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 42.2338 | 749.3089 | 0 | 0.05921 | 5.9804 | 0 | 0 | 139.2267 | 0 | off_peak | 736.91 | 0 | 100 | 0 | 0 | 100 | 0 | 0
2138 | 713.23 | 0 | 22.3 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 53.832 | 725.6289 | 0 | 0.05921 | 5.8898 | 0 | 0 | 139.2267 | 0 | off_peak | 713.23 | 0 | 100 | 0 | 0 | 100 | 0 | 0
2139 | 617.49 | 0 | 22.2 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 65.4301 | 629.8889 | 0 | 0.05921 | 5.5153 | 0 | 0 | 139.2267 | 0 | off_peak | 617.49 | 0 | 100 | 0 | 0 | 100 | 0 | 0
2140 | 601.16 | 0 | 22.1 | 0 | 0 | 0 | 0 | 8.9635 | 8.9635 | 0 | 0 | 0 | 73.8147 | 610.1235 | 0 | 0.05921 | 5.0053 | 0 | 0 | 139.2267 | 0 | off_peak | 601.16 | 0 | 100 | 0 | 0 | 100 | 0 | 0
2141 | 649.92 | 0 | 22 | 0 | 0 | 0 | 0 | 0.57892 | 0.57892 | 0 | 0 | 0 | 74.3563 | 650.4989 | 0 | 0.05921 | 4.1675 | 0 | 0 | 139.2267 | 0 | off_peak | 649.92 | 0 | 100 | 0 | 0 | 100 | 0 | 0
2142 | 687.11 | 0 | 22 | 0 | 0 | 0 | 0 | 0.03739 | 0.03739 | 0 | 0 | 0 | 74.3912 | 687.1474 | 0 | 0.05921 | 3.5861 | 0 | 0 | 139.2267 | 0 | off_peak | 687.11 | 0 | 100 | 0 | 0 | 100 | 0 | 0
2143 | 781.5 | 25.4633 | 22.5 | 5.2027 | 5.2027 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3912 | 776.2973 | 0 | 0.088511 | 3.2343 | 0 | 0 | 139.2267 | 5.2027 | on_peak | 776.2973 |  |  | 0.67 | 0 | 99.33 | 16.8272 | 0
2144 | 820.71 | 217.211 | 23.2 | 44.2703 | 44.2703 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3912 | 776.4397 | 0 | 0.088511 | 2.9932 | 0 | 0 | 139.2267 | 44.2703 | on_peak | 776.4397 |  |  | 5.39 | 0 | 94.61 | 132.5085 | 0
2145 | 903.67 | 438.856 | 23.7 | 89.2842 | 89.2842 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3912 | 814.3858 | 0 | 0.088511 | 2.8494 | 0 | 0 | 139.2267 | 89.2842 | on_peak | 814.3858 |  |  | 9.88 | 0 | 90.12 | 254.4087 | 0
2146 | 911.26 | 638.304 | 24.1 | 129.6754 | 129.6754 | 0 | 0 | 0 | 0 | 62.6277 | 62.6277 | 0 | 7.4394 | 718.9569 | 0 | 0.088511 | 2.8293 | 0 | 0 | 139.2267 | 129.6754 | on_peak | 718.9569 |  |  | 14.23 | 6.87 | 78.9 | 366.8939 | 0
2147 | 858.19 | 797.397 | 24.5 | 161.7635 | 161.7635 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 19.0375 | 708.8254 | 0 | 0.05921 | 3.0137 | 0 | 0 | 139.2267 | 161.7635 | off_peak | 696.4265 | 0 | 100 | 18.85 | 0 | 81.15 | 487.5093 | 0
2148 | 925.18 | 864.442 | 24.7 | 175.2386 | 162.8396 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 0 | 30.6357 | 762.3404 | 0 | 0.05921 | 3.4852 | 0 | 0 | 150.8248 | 162.8396 | off_peak | 762.3404 | 100 | 0 | 17.6 | 0 | 82.4 | 567.5242 | 0
2149 | 901.24 | 896.834 | 24.8 | 181.7396 | 181.7396 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 42.2338 | 731.8993 | 0 | 0.05921 | 3.8306 | 0 | 0 | 150.8248 | 181.7396 | off_peak | 719.5004 | 0 | 100 | 20.17 | 0 | 79.83 | 696.1772 | 0
2150 | 838.78 | 866.675 | 24.8 | 175.628 | 175.628 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 53.832 | 675.5509 | 0 | 0.05921 | 3.8556 | 0 | 0 | 150.8248 | 175.628 | off_peak | 663.152 | 0 | 100 | 20.94 | 0 | 79.06 | 677.1517 | 0
2151 | 933.37 | 745.29 | 24.6 | 151.1386 | 151.1386 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 65.4301 | 794.6304 | 0 | 0.05921 | 3.7799 | 0 | 0 | 150.8248 | 151.1386 | off_peak | 782.2314 | 0 | 100 | 16.19 | 0 | 83.81 | 571.2895 | 0
2152 | 793.18 | 610.367 | 24.4 | 123.8663 | 114.9027 | 0 | 8.9635 | 8.9635 | 0 | 0 | 0 | 0 | 73.8147 | 678.2773 | 0 | 0.05921 | 3.8197 | 0 | 0 | 159.2094 | 114.9027 | off_peak | 678.2773 | 100 | 0 | 14.49 | 0 | 85.51 | 438.8932 | 0
2153 | 867.73 | 308.864 | 24 | 62.7701 | 62.7701 | 0 | 0 | 0.57892 | 0.57892 | 0 | 0 | 0 | 74.3563 | 805.5388 | 0 | 0.05921 | 4.1346 | 0 | 0 | 159.2094 | 62.7701 | off_peak | 804.9599 | 0 | 100 | 7.23 | 0 | 92.77 | 259.5318 | 0
2154 | 820.35 | 159.585 | 23.5 | 32.4905 | 32.4905 | 0 | 0 | 0.03739 | 0.03739 | 0 | 0 | 0 | 74.3912 | 787.8969 | 0 | 0.05921 | 4.4287 | 0 | 0 | 159.2094 | 32.4905 | off_peak | 787.8595 | 0 | 100 | 3.96 | 0 | 96.04 | 143.8922 | 0
2155 | 799.11 | 14.4593 | 23.1 | 2.948 | 2.948 | 0 | 0 | 0 | 0 | 62.6277 | 62.6277 | 0 | 7.4394 | 733.5342 | 0 | 0.088511 | 4.7472 | 0 | 0 | 159.2094 | 2.948 | on_peak | 733.5342 |  |  | 0.37 | 7.84 | 91.79 | 13.9949 | 0
2156 | 793 | 0 | 25.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 793 | 0 | 0.088511 | 5.1394 | 0 | 0 | 159.2094 | 0 | on_peak | 793 |  |  | 0 | 0 | 100 | 0 | 0
2157 | 795.78 | 0 | 25.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 795.78 | 0 | 0.088511 | 5.3764 | 0 | 0 | 159.2094 | 0 | on_peak | 795.78 |  |  | 0 | 0 | 100 | 0 | 0
2158 | 768.27 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 768.27 | 0 | 0.088511 | 5.7423 | 0 | 0 | 159.2094 | 0 | on_peak | 768.27 |  |  | 0 | 0 | 100 | 0 | 0
2159 | 782.26 | 0 | 24.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 782.26 | 0 | 0.05921 | 6.0616 | 0 | 0 | 159.2094 | 0 | off_peak | 782.26 |  |  | 0 | 0 | 100 | 0 | 0
2160 | 803.89 | 0 | 24.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 803.89 | 0 | 0.05921 | 6.2023 | 0 | 0 | 159.2094 | 0 | off_peak | 803.89 |  |  | 0 | 0 | 100 | 0 | 0
2161 | 734.4 | 0 | 24.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 734.4 | 0 | 0.05921 | 6.1568 | 0 | 0 | 159.2094 | 0 | off_peak | 734.4 |  |  | 0 | 0 | 100 | 0 | 0
2162 | 684.73 | 0 | 24.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 684.73 | 0 | 0.05921 | 6.073 | 0 | 0 | 159.2094 | 0 | off_peak | 684.73 |  |  | 0 | 0 | 100 | 0 | 0
2163 | 633.98 | 0 | 24.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 633.98 | 0 | 0.05921 | 5.6384 | 0 | 0 | 159.2094 | 0 | off_peak | 633.98 |  |  | 0 | 0 | 100 | 0 | 0
2164 | 609.13 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 609.13 | 0 | 0.05921 | 5.1564 | 0 | 0 | 159.2094 | 0 | off_peak | 609.13 |  |  | 0 | 0 | 100 | 0 | 0
2165 | 630.02 | 0 | 23.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 630.02 | 0 | 0.05921 | 4.4016 | 0 | 0 | 159.2094 | 0 | off_peak | 630.02 |  |  | 0 | 0 | 100 | 0 | 0
2166 | 740.3 | 0 | 22.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 740.3 | 0 | 0.05921 | 3.8009 | 0 | 0 | 159.2094 | 0 | off_peak | 740.3 |  |  | 0 | 0 | 100 | 0 | 0
2167 | 768.3 | 27.3178 | 22.2 | 5.5876 | 0 | 0 | 5.5876 | 5.5876 | 0 | 0 | 0 | 0 | 12.6661 | 768.3 | 0 | 0.05921 | 3.4042 | 0 | 0 | 164.4362 | 0 | off_peak | 768.3 | 100 | 0 | 0 | 0 | 100 | 0 | 0
2168 | 806.07 | 212.012 | 22 | 43.3961 | 34.0297 | 0 | 9.3664 | 9.3664 | 0 | 0 | 0 | 0 | 21.4276 | 772.0403 | 0 | 0.05921 | 3.0778 | 0 | 0 | 173.1976 | 34.0297 | off_peak | 772.0403 | 100 | 0 | 4.22 | 0 | 95.78 | 104.7355 | 0
2169 | 820.23 | 428.134 | 22.4 | 87.5086 | 87.5086 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21.4276 | 732.7214 | 0 | 0.05921 | 2.8787 | 0 | 0 | 173.1976 | 87.5086 | off_peak | 732.7214 |  |  | 10.67 | 0 | 89.33 | 251.9145 | 0
2170 | 815.29 | 623.839 | 23.2 | 127.146 | 127.146 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21.4276 | 688.144 | 0 | 0.05921 | 2.7879 | 0 | 0 | 173.1976 | 127.146 | off_peak | 688.144 |  |  | 15.6 | 0 | 84.4 | 354.4747 | 0
2171 | 780.44 | 496.521 | 24 | 100.9075 | 100.9075 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21.4276 | 679.5325 | 0 | 0.05921 | 2.8612 | 0 | 0 | 173.1976 | 100.9075 | off_peak | 679.5325 |  |  | 12.93 | 0 | 87.07 | 288.718 | 0
2172 | 817.86 | 612.757 | 24.8 | 124.1726 | 124.1726 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21.4276 | 693.6874 | 0 | 0.05921 | 3.026 | 0 | 0 | 173.1976 | 124.1726 | off_peak | 693.6874 |  |  | 15.18 | 0 | 84.82 | 375.7441 | 0
2173 | 808.05 | 616.351 | 25.5 | 124.5864 | 124.5864 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21.4276 | 683.4636 | 0 | 0.05921 | 3.2717 | 0 | 0 | 173.1976 | 124.5864 | off_peak | 683.4636 |  |  | 15.42 | 0 | 84.58 | 407.6053 | 0
2174 | 754.61 | 696.078 | 26.1 | 140.3976 | 140.3976 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21.4276 | 614.2124 | 0 | 0.05921 | 3.5627 | 0 | 0 | 173.1976 | 140.3976 | off_peak | 614.2124 |  |  | 18.61 | 0 | 81.39 | 500.1937 | 0
2175 | 797.13 | 628.947 | 26.5 | 126.674 | 126.674 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21.4276 | 670.456 | 0 | 0.05921 | 3.8137 | 0 | 0 | 173.1976 | 126.674 | off_peak | 670.456 |  |  | 15.89 | 0 | 84.11 | 483.0981 | 0
2176 | 769.08 | 491.165 | 26.8 | 98.8164 | 98.8164 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21.4276 | 670.2636 | 0 | 0.05921 | 4.1979 | 0 | 0 | 173.1976 | 98.8164 | off_peak | 670.2636 |  |  | 12.85 | 0 | 87.15 | 414.8251 | 0
2177 | 740.52 | 372.017 | 26.6 | 74.8995 | 74.8995 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21.4276 | 665.6205 | 0 | 0.05921 | 4.6812 | 0 | 0 | 173.1976 | 74.8995 | off_peak | 665.6205 |  |  | 10.11 | 0 | 89.89 | 350.619 | 0
2178 | 651.62 | 169.533 | 25.9 | 34.2192 | 34.2192 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21.4276 | 617.4008 | 0 | 0.05921 | 5.0247 | 0 | 0 | 173.1976 | 34.2192 | off_peak | 617.4008 |  |  | 5.25 | 0 | 94.75 | 171.9408 | 0
2179 | 631.55 | 12.4256 | 25.3 | 2.5135 | 2.5135 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21.4276 | 629.0365 | 0 | 0.05921 | 5.3111 | 0 | 0 | 173.1976 | 2.5135 | off_peak | 629.0365 |  |  | 0.4 | 0 | 99.6 | 13.3492 | 0
2180 | 594.36 | 0 | 24.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21.4276 | 594.36 | 0 | 0.05921 | 5.6201 | 0 | 0 | 173.1976 | 0 | off_peak | 594.36 |  |  | 0 | 0 | 100 | 0 | 0
2181 | 636.1 | 0 | 23.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21.4276 | 636.1 | 0 | 0.05921 | 5.908 | 0 | 0 | 173.1976 | 0 | off_peak | 636.1 |  |  | 0 | 0 | 100 | 0 | 0
2182 | 594.19 | 0 | 22.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21.4276 | 594.19 | 0 | 0.05921 | 6.1296 | 0 | 0 | 173.1976 | 0 | off_peak | 594.19 |  |  | 0 | 0 | 100 | 0 | 0
2183 | 616.94 | 0 | 21.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21.4276 | 616.94 | 0 | 0.05921 | 6.406 | 0 | 0 | 173.1976 | 0 | off_peak | 616.94 |  |  | 0 | 0 | 100 | 0 | 0
2184 | 632.94 | 0 | 20.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21.4276 | 632.94 | 0 | 0.05921 | 6.4197 | 0 | 0 | 173.1976 | 0 | off_peak | 632.94 |  |  | 0 | 0 | 100 | 0 | 0
2185 | 622.15 | 0 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21.4276 | 622.15 | 0 | 0.05921 | 6.3606 | 0 | 0 | 173.1976 | 0 | off_peak | 622.15 |  |  | 0 | 0 | 100 | 0 | 0
2186 | 598.53 | 0 | 19.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21.4276 | 598.53 | 0 | 0.05921 | 6.221 | 0 | 0 | 173.1976 | 0 | off_peak | 598.53 |  |  | 0 | 0 | 100 | 0 | 0
2187 | 616.08 | 0 | 19.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21.4276 | 616.08 | 0 | 0.05921 | 5.8342 | 0 | 0 | 173.1976 | 0 | off_peak | 616.08 |  |  | 0 | 0 | 100 | 0 | 0
2188 | 602.59 | 0 | 19.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21.4276 | 602.59 | 0 | 0.05921 | 5.3513 | 0 | 0 | 173.1976 | 0 | off_peak | 602.59 |  |  | 0 | 0 | 100 | 0 | 0
2189 | 626.28 | 0 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21.4276 | 626.28 | 0 | 0.05921 | 4.785 | 0 | 0 | 173.1976 | 0 | off_peak | 626.28 |  |  | 0 | 0 | 100 | 0 | 0
2190 | 721.05 | 0 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21.4276 | 721.05 | 0 | 0.05921 | 4.2223 | 0 | 0 | 173.1976 | 0 | off_peak | 721.05 |  |  | 0 | 0 | 100 | 0 | 0
2191 | 814.5 | 29.9048 | 19.7 | 6.1713 | 0 | 0 | 6.1713 | 6.1713 | 0 | 0 | 0 | 0 | 27.2003 | 814.5 | 0 | 0.05921 | 3.6744 | 0 | 0 | 178.9703 | 0 | off_peak | 814.5 | 100 | 0 | 0 | 0 | 100 | 0 | 0
2192 | 826.39 | 214.183 | 20.8 | 44.0278 | 44.0278 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27.2003 | 782.3622 | 0 | 0.05921 | 3.4007 | 0 | 0 | 178.9703 | 44.0278 | off_peak | 782.3622 |  |  | 5.33 | 0 | 94.67 | 149.7271 | 0
2193 | 799.19 | 429.948 | 21.9 | 88.0361 | 88.0361 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27.2003 | 711.1539 | 0 | 0.05921 | 3.1331 | 0 | 0 | 178.9703 | 88.0361 | off_peak | 711.1539 |  |  | 11.02 | 0 | 88.98 | 275.8229 | 0
2194 | 781.79 | 624.857 | 23.2 | 127.3535 | 127.3535 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27.2003 | 654.4365 | 0 | 0.05921 | 2.9831 | 0 | 0 | 178.9703 | 127.3535 | off_peak | 654.4365 |  |  | 16.29 | 0 | 83.71 | 379.9118 | 0
2195 | 750.3 | 775.241 | 24.2 | 157.4384 | 157.4384 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27.2003 | 592.8616 | 0 | 0.05921 | 2.9622 | 0 | 0 | 178.9703 | 157.4384 | off_peak | 592.8616 |  |  | 20.98 | 0 | 79.02 | 466.3608 | 0
2196 | 787.66 | 866.565 | 25 | 175.4794 | 175.4794 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27.2003 | 612.1806 | 0 | 0.05921 | 3.0491 | 0 | 0 | 178.9703 | 175.4794 | off_peak | 612.1806 |  |  | 22.28 | 0 | 77.72 | 535.0567 | 0
2197 | 721.57 | 891.587 | 25.5 | 180.2214 | 180.2214 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27.2003 | 541.3486 | 0 | 0.05921 | 3.2174 | 0 | 0 | 178.9703 | 180.2214 | off_peak | 541.3486 |  |  | 24.98 | 0 | 75.02 | 579.8521 | 0
2198 | 712.91 | 847.999 | 25.7 | 171.2871 | 171.2871 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27.2003 | 541.6229 | 0 | 0.05921 | 3.4949 | 0 | 0 | 178.9703 | 171.2871 | off_peak | 541.6229 |  |  | 24.03 | 0 | 75.97 | 598.6256 | 0
2199 | 745.09 | 744.756 | 25.6 | 150.4873 | 150.4873 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27.2003 | 594.6027 | 0 | 0.05921 | 3.8043 | 0 | 0 | 178.9703 | 150.4873 | off_peak | 594.6027 |  |  | 20.2 | 0 | 79.8 | 572.4996 | 0
2200 | 708.73 | 540.946 | 25.3 | 109.4233 | 109.4233 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 38.7984 | 611.7057 | 0 | 0.05921 | 4.043 | 0 | 0 | 178.9703 | 109.4233 | off_peak | 599.3067 | 0 | 100 | 15.44 | 0 | 84.56 | 442.4017 | 0
2201 | 735.83 | 387.932 | 24.8 | 78.6128 | 66.2138 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 0 | 50.3966 | 669.6162 | 0 | 0.05921 | 4.3997 | 0 | 0 | 190.5685 | 66.2138 | off_peak | 669.6162 | 100 | 0 | 9 | 0 | 91 | 291.3238 | 0
2202 | 660.11 | 179.827 | 23.9 | 36.5592 | 36.5592 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50.3966 | 623.5508 | 0 | 0.05921 | 4.8763 | 0 | 0 | 190.5685 | 36.5592 | off_peak | 623.5508 |  |  | 5.54 | 0 | 94.46 | 178.2745 | 0
2203 | 593.42 | 10.4734 | 23.4 | 2.1331 | 2.1331 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 61.9947 | 603.6859 | 0 | 0.05921 | 5.2988 | 0 | 0 | 190.5685 | 2.1331 | off_peak | 591.2869 | 0 | 100 | 0.36 | 0 | 99.64 | 11.3028 | 0
2204 | 630.92 | 0 | 22.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 61.9947 | 630.92 | 0 | 0.05921 | 5.7079 | 0 | 0 | 190.5685 | 0 | off_peak | 630.92 |  |  | 0 | 0 | 100 | 0 | 0
2205 | 590.47 | 0 | 22.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 61.9947 | 590.47 | 0 | 0.05921 | 5.8576 | 0 | 0 | 190.5685 | 0 | off_peak | 590.47 |  |  | 0 | 0 | 100 | 0 | 0
2206 | 584.76 | 0 | 22.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 61.9947 | 584.76 | 0 | 0.05921 | 6.277 | 0 | 0 | 190.5685 | 0 | off_peak | 584.76 |  |  | 0 | 0 | 100 | 0 | 0
2207 | 575.27 | 0 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 61.9947 | 575.27 | 0 | 0.05921 | 6.5253 | 0 | 0 | 190.5685 | 0 | off_peak | 575.27 |  |  | 0 | 0 | 100 | 0 | 0
2208 | 604.68 | 0 | 21.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 61.9947 | 604.68 | 0 | 0.05921 | 6.7138 | 0 | 0 | 190.5685 | 0 | off_peak | 604.68 |  |  | 0 | 0 | 100 | 0 | 0
2209 | 583.05 | 0 | 21.7 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 73.5928 | 595.4489 | 0 | 0.05921 | 6.5851 | 0 | 0 | 190.5685 | 0 | off_peak | 583.05 | 0 | 100 | 0 | 0 | 100 | 0 | 0
2210 | 589.49 | 0 | 21.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 73.5928 | 589.49 | 0 | 0.05921 | 6.4484 | 0 | 0 | 190.5685 | 0 | off_peak | 589.49 |  |  | 0 | 0 | 100 | 0 | 0
2211 | 552.91 | 0 | 21.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 73.5928 | 552.91 | 0 | 0.05921 | 6.0652 | 0 | 0 | 190.5685 | 0 | off_peak | 552.91 |  |  | 0 | 0 | 100 | 0 | 0
2212 | 582.56 | 0 | 21.4 | 0 | 0 | 0 | 0 | 0.80079 | 0.80079 | 0 | 0 | 0 | 74.3419 | 583.3608 | 0 | 0.05921 | 5.4616 | 0 | 0 | 190.5685 | 0 | off_peak | 582.56 | 0 | 100 | 0 | 0 | 100 | 0 | 0
2213 | 579.9 | 0 | 21.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3419 | 579.9 | 0 | 0.05921 | 4.7032 | 0 | 0 | 190.5685 | 0 | off_peak | 579.9 |  |  | 0 | 0 | 100 | 0 | 0
2214 | 676.74 | 0 | 21.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3419 | 676.74 | 0 | 0.05921 | 4.078 | 0 | 0 | 190.5685 | 0 | off_peak | 676.74 |  |  | 0 | 0 | 100 | 0 | 0
2215 | 786.49 | 23.6622 | 22.1 | 4.8416 | 4.8416 | 0 | 0 | 0.05172 | 0.05172 | 0 | 0 | 0 | 74.3903 | 781.7001 | 0 | 0.05921 | 3.6458 | 0 | 0 | 190.5685 | 4.8416 | off_peak | 781.6484 | 0 | 100 | 0.62 | 0 | 99.38 | 17.6515 | 0
2216 | 808.33 | 171.16 | 23.1 | 34.897 | 34.897 | 0 | 0 | 0.0033404 | 0.0033404 | 0 | 0 | 0 | 74.3934 | 773.4364 | 0 | 0.05921 | 3.3243 | 0 | 0 | 190.5685 | 34.897 | off_peak | 773.433 | 0 | 100 | 4.32 | 0 | 95.68 | 116.0086 | 0
2217 | 804.91 | 323.594 | 23.6 | 65.858 | 65.8578 | 0 | 0.00021574 | 0.00021574 | 0 | 0 | 0 | 0 | 74.3936 | 739.0522 | 0 | 0.05921 | 3.1663 | 0 | 0 | 190.5687 | 65.8578 | off_peak | 739.0522 | 100 | 0 | 8.18 | 0 | 91.82 | 208.5234 | 0
2218 | 842.98 | 283.812 | 24.1 | 57.6581 | 57.6581 | 0 | 0 | 1.3934e-05 | 1.3934e-05 | 0 | 0 | 0 | 74.3936 | 785.3219 | 0 | 0.05921 | 3.148 | 0 | 0 | 190.5687 | 57.6581 | off_peak | 785.3219 | 0 | 100 | 6.84 | 0 | 93.16 | 181.5094 | 0
2219 | 846.61 | 606.214 | 24.6 | 122.9351 | 122.9351 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 723.6749 | 0 | 0.05921 | 3.374 | 0 | 0 | 190.5687 | 122.9351 | off_peak | 723.6749 |  |  | 14.52 | 0 | 85.48 | 414.7832 | 0
2220 | 897.95 | 827.245 | 25 | 167.5171 | 167.5171 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 730.4329 | 0 | 0.05921 | 3.7669 | 0 | 0 | 190.5687 | 167.5171 | off_peak | 730.4329 |  |  | 18.66 | 0 | 81.34 | 631.0166 | 0
2221 | 870.46 | 641.216 | 25.2 | 129.7528 | 129.7528 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 740.7072 | 0 | 0.088511 | 4.0562 | 0 | 0 | 190.5687 | 129.7528 | on_peak | 740.7072 |  |  | 14.91 | 0 | 85.09 | 526.3054 | 0
2222 | 965.63 | 600.514 | 25.3 | 121.4728 | 121.4728 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 844.1572 | 0 | 0.088511 | 4.2361 | 0 | 0 | 190.5687 | 121.4728 | on_peak | 844.1572 |  |  | 12.58 | 0 | 87.42 | 514.5671 | 0
2223 | 944.56 | 530.417 | 25.3 | 107.2934 | 107.2934 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 837.2666 | 0 | 0.088511 | 4.4587 | 0 | 0 | 190.5687 | 107.2934 | on_peak | 837.2666 |  |  | 11.36 | 0 | 88.64 | 478.3875 | 0
2224 | 892.73 | 381.839 | 25.1 | 77.2946 | 77.2946 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 815.4354 | 0 | 0.088511 | 4.7004 | 0 | 0 | 190.5687 | 77.2946 | on_peak | 815.4354 |  |  | 8.66 | 0 | 91.34 | 363.3177 | 0
2225 | 912.39 | 148.879 | 24.8 | 30.1697 | 30.1697 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 882.2203 | 0 | 0.088511 | 4.9386 | 0 | 0 | 190.5687 | 30.1697 | on_peak | 882.2203 |  |  | 3.31 | 0 | 96.69 | 148.9962 | 0
2226 | 884.45 | 35.3912 | 24.2 | 7.1874 | 7.1874 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 877.2626 | 0 | 0.088511 | 5.3577 | 0 | 0 | 190.5687 | 7.1874 | on_peak | 877.2626 |  |  | 0.81 | 0 | 99.19 | 38.5077 | 0
2227 | 838.25 | 9.5 | 23.8 | 1.9321 | 1.9321 | 0 | 0 | 0 | 0 | 62.63 | 62.63 | 0 | 7.4394 | 773.6879 | 0 | 0.088511 | 5.7818 | 0 | 0 | 190.5687 | 1.9321 | on_peak | 773.6879 |  |  | 0.23 | 7.47 | 92.3 | 11.1707 | 0
2228 | 869.78 | 0 | 23.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 869.78 | 0 | 0.088511 | 6.1013 | 0 | 0 | 190.5687 | 0 | on_peak | 869.78 |  |  | 0 | 0 | 100 | 0 | 0
2229 | 841.48 | 0 | 23.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 841.48 | 0 | 0.088511 | 6.4183 | 0 | 0 | 190.5687 | 0 | on_peak | 841.48 |  |  | 0 | 0 | 100 | 0 | 0
2230 | 828.91 | 0 | 23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 828.91 | 0 | 0.05921 | 6.7141 | 0 | 0 | 190.5687 | 0 | off_peak | 828.91 |  |  | 0 | 0 | 100 | 0 | 0
2231 | 864.52 | 0 | 22.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 864.52 | 0 | 0.05921 | 6.9707 | 0 | 0 | 190.5687 | 0 | off_peak | 864.52 |  |  | 0 | 0 | 100 | 0 | 0
2232 | 824.67 | 0 | 22.8 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 19.0375 | 837.0689 | 0 | 0.05921 | 7.2093 | 0 | 0 | 190.5687 | 0 | off_peak | 824.67 | 0 | 100 | 0 | 0 | 100 | 0 | 0
2233 | 794.03 | 0 | 22.7 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 30.6357 | 806.4289 | 0 | 0.05921 | 7.1956 | 0 | 0 | 190.5687 | 0 | off_peak | 794.03 | 0 | 100 | 0 | 0 | 100 | 0 | 0
2234 | 708.39 | 0 | 22.6 | 0 | 0 | 0 | 0 | 2.122 | 2.122 | 0 | 0 | 0 | 32.6206 | 710.512 | 0 | 0.05921 | 7.0516 | 0 | 0 | 190.5687 | 0 | off_peak | 708.39 | 0 | 100 | 0 | 0 | 100 | 0 | 0
2235 | 606.21 | 0 | 22.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 32.6206 | 606.21 | 0 | 0.05921 | 6.5042 | 0 | 0 | 190.5687 | 0 | off_peak | 606.21 |  |  | 0 | 0 | 100 | 0 | 0
2236 | 596.4 | 0 | 22.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 32.6206 | 596.4 | 0 | 0.05921 | 5.7911 | 0 | 0 | 190.5687 | 0 | off_peak | 596.4 |  |  | 0 | 0 | 100 | 0 | 0
2237 | 646.03 | 0 | 22.3 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 44.2187 | 658.4289 | 0 | 0.05921 | 4.8102 | 0 | 0 | 190.5687 | 0 | off_peak | 646.03 | 0 | 100 | 0 | 0 | 100 | 0 | 0
2238 | 681.16 | 0 | 22.4 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 55.8169 | 693.5589 | 0 | 0.05921 | 4.451 | 0 | 0 | 190.5687 | 0 | off_peak | 681.16 | 0 | 100 | 0 | 0 | 100 | 0 | 0
2239 | 763.22 | 32.381 | 23 | 6.6044 | 0 | 0 | 6.6044 | 6.6044 | 0 | 0 | 0 | 0 | 61.9947 | 763.22 | 0 | 0.05921 | 3.9341 | 0 | 0 | 196.7465 | 0 | off_peak | 763.22 | 100 | 0 | 0 | 0 | 100 | 0 | 0
2240 | 803.85 | 216.696 | 24 | 44.0389 | 31.64 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 0 | 73.5928 | 772.21 | 0 | 0.05921 | 3.5258 | 0 | 0 | 208.3446 | 31.64 | off_peak | 772.21 | 100 | 0 | 3.94 | 0 | 96.06 | 111.556 | 0
2241 | 845.38 | 287.892 | 24.5 | 58.4031 | 58.4031 | 0 | 0 | 0.80079 | 0.80079 | 0 | 0 | 0 | 74.3419 | 787.7777 | 0 | 0.05921 | 3.285 | 0 | 0 | 208.3446 | 58.4031 | off_peak | 786.9769 | 0 | 100 | 6.91 | 0 | 93.09 | 191.856 | 0
2242 | 846.94 | 620.744 | 25 | 125.7007 | 125.7007 | 0 | 0 | 0.05172 | 0.05172 | 0 | 0 | 0 | 74.3903 | 721.2911 | 0 | 0.05921 | 3.2386 | 0 | 0 | 208.3446 | 125.7007 | off_peak | 721.2393 | 0 | 100 | 14.84 | 0 | 85.16 | 407.0897 | 0
2243 | 865.84 | 55.1 | 25.4 | 11.1417 | 11.1417 | 0 | 0 | 0.0033404 | 0.0033404 | 0 | 0 | 0 | 74.3934 | 854.7017 | 0 | 0.05921 | 3.3771 | 0 | 0 | 208.3446 | 11.1417 | off_peak | 854.6983 | 0 | 100 | 1.29 | 0 | 98.71 | 37.6262 | 0
2244 | 893.48 | 81.7 | 25.7 | 16.5026 | 16.5023 | 0 | 0.00021574 | 0.00021574 | 0 | 0 | 0 | 0 | 74.3936 | 876.9777 | 0 | 0.05921 | 3.8233 | 0 | 0 | 208.3448 | 16.5023 | off_peak | 876.9777 | 100 | 0 | 1.85 | 0 | 98.15 | 63.0928 | 0
2245 | 907.18 | 120.65 | 25.9 | 24.3525 | 24.3525 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 882.8275 | 0 | 0.088511 | 4.1595 | 0 | 0 | 208.3448 | 24.3525 | on_peak | 882.8275 |  |  | 2.68 | 0 | 97.32 | 101.293 | 0
2246 | 924.29 | 609.374 | 26 | 122.954 | 122.954 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 801.336 | 0 | 0.088511 | 4.3584 | 0 | 0 | 208.3448 | 122.954 | on_peak | 801.336 |  |  | 13.3 | 0 | 86.7 | 535.8888 | 0
2247 | 987.05 | 691.877 | 26 | 139.6007 | 139.6007 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 847.4493 | 0 | 0.088511 | 4.5748 | 0 | 0 | 208.3448 | 139.6007 | on_peak | 847.4493 |  |  | 14.14 | 0 | 85.86 | 638.6429 | 0
2248 | 925.05 | 64.2787 | 25.9 | 12.9743 | 12.9743 | 0 | 0 | 0 | 0 | 27.3357 | 27.3357 | 0 | 45.1705 | 884.74 | 0 | 0.088511 | 4.8283 | 0 | 0 | 208.3448 | 12.9743 | on_peak | 884.74 |  |  | 1.4 | 2.96 | 95.64 | 62.644 | 0
2249 | 908.3 | 34.2 | 25.5 | 6.913 | 6.913 | 0 | 0 | 0 | 0 | 16.647 | 16.647 | 0 | 27.3741 | 884.74 | 0 | 0.088511 | 5.2035 | 0 | 0 | 208.3448 | 6.913 | on_peak | 884.74 |  |  | 0.76 | 1.83 | 97.41 | 35.9723 | 0
2250 | 896.48 | 28.7428 | 24.9 | 5.8225 | 5.8225 | 0 | 0 | 0 | 0 | 5.9175 | 5.9175 | 0 | 21.0481 | 884.74 | 0 | 0.088511 | 5.5684 | 0 | 0 | 208.3448 | 5.8225 | on_peak | 884.74 |  |  | 0.65 | 0.66 | 98.69 | 32.422 | 0
2251 | 860.84 | 9.5 | 24.5 | 1.9272 | 1.9272 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21.0481 | 858.9128 | 0 | 0.088511 | 6.0427 | 0 | 0 | 208.3448 | 1.9272 | on_peak | 858.9128 |  |  | 0.22 | 0 | 99.78 | 11.6456 | 0
2252 | 894.94 | 0 | 24.1 | 0 | 0 | 0 | 0 | 0 | 0 | 12.7298 | 12.7298 | 0 | 7.4394 | 882.2102 | 0 | 0.088511 | 6.4067 | 0 | 0 | 208.3448 | 0 | on_peak | 882.2102 |  |  | 0 | 1.42 | 98.58 | 0 | 0
2253 | 884.18 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 884.18 | 0 | 0.088511 | 6.7037 | 0 | 0 | 208.3448 | 0 | on_peak | 884.18 |  |  | 0 | 0 | 100 | 0 | 0
2254 | 858.14 | 0 | 23.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 858.14 | 0 | 0.05921 | 7.0191 | 0 | 0 | 208.3448 | 0 | off_peak | 858.14 |  |  | 0 | 0 | 100 | 0 | 0
2255 | 836.37 | 0 | 23.7 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 19.0375 | 848.7689 | 0 | 0.05921 | 7.2017 | 0 | 0 | 208.3448 | 0 | off_peak | 836.37 | 0 | 100 | 0 | 0 | 100 | 0 | 0
2256 | 860.06 | 0 | 23.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19.0375 | 860.06 | 0 | 0.05921 | 7.3645 | 0 | 0 | 208.3448 | 0 | off_peak | 860.06 |  |  | 0 | 0 | 100 | 0 | 0
2257 | 819.36 | 0 | 23.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19.0375 | 819.36 | 0 | 0.05921 | 7.2593 | 0 | 0 | 208.3448 | 0 | off_peak | 819.36 |  |  | 0 | 0 | 100 | 0 | 0
2258 | 702.51 | 0 | 23.5 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 30.6357 | 714.9089 | 0 | 0.05921 | 7.0482 | 0 | 0 | 208.3448 | 0 | off_peak | 702.51 | 0 | 100 | 0 | 0 | 100 | 0 | 0
2259 | 648.1 | 0 | 23.4 | 0 | 0 | 0 | 0 | 8.7263 | 8.7263 | 0 | 0 | 0 | 38.7984 | 656.8263 | 0 | 0.05921 | 6.6237 | 0 | 0 | 208.3448 | 0 | off_peak | 648.1 | 0 | 100 | 0 | 0 | 100 | 0 | 0
2260 | 623.03 | 0 | 23.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 38.7984 | 623.03 | 0 | 0.05921 | 6.0284 | 0 | 0 | 208.3448 | 0 | off_peak | 623.03 |  |  | 0 | 0 | 100 | 0 | 0
2261 | 645.52 | 0 | 22.9 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 50.3966 | 657.9189 | 0 | 0.05921 | 5.1186 | 0 | 0 | 208.3448 | 0 | off_peak | 645.52 | 0 | 100 | 0 | 0 | 100 | 0 | 0
2262 | 731.57 | 0 | 22.7 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 61.9947 | 743.9689 | 0 | 0.05921 | 4.5506 | 0 | 0 | 208.3448 | 0 | off_peak | 731.57 | 0 | 100 | 0 | 0 | 100 | 0 | 0
2263 | 766.68 | 39.6343 | 23.1 | 8.0808 | 8.0808 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 61.9947 | 758.5992 | 0 | 0.05921 | 3.9995 | 0 | 0 | 208.3448 | 8.0808 | off_peak | 758.5992 |  |  | 1.05 | 0 | 98.95 | 32.3191 | 0
2264 | 840.41 | 232.7 | 23.8 | 47.3253 | 47.3253 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 73.5928 | 805.4836 | 0 | 0.05921 | 3.653 | 0 | 0 | 208.3448 | 47.3253 | off_peak | 793.0847 | 0 | 100 | 5.63 | 0 | 94.37 | 172.8791 | 0
2265 | 813.31 | 449.964 | 24.3 | 91.3473 | 91.3473 | 0 | 0 | 0.80079 | 0.80079 | 0 | 0 | 0 | 74.3419 | 722.7635 | 0 | 0.05921 | 3.4391 | 0 | 0 | 208.3448 | 91.3473 | off_peak | 721.9627 | 0 | 100 | 11.23 | 0 | 88.77 | 314.1526 | 0
2266 | 860.12 | 638.471 | 24.8 | 129.3835 | 129.3835 | 0 | 0 | 0.05172 | 0.05172 | 0 | 0 | 0 | 74.3903 | 730.7883 | 0 | 0.05921 | 3.3321 | 0 | 0 | 208.3448 | 129.3835 | off_peak | 730.7365 | 0 | 100 | 15.04 | 0 | 84.96 | 431.1144 | 0
2267 | 818.14 | 792.866 | 25.3 | 160.382 | 160.382 | 0 | 0 | 0.0033404 | 0.0033404 | 0 | 0 | 0 | 74.3934 | 657.7614 | 0 | 0.05921 | 3.5149 | 0 | 0 | 208.3448 | 160.382 | off_peak | 657.758 | 0 | 100 | 19.6 | 0 | 80.4 | 563.7271 | 0
2268 | 856.37 | 887.018 | 25.6 | 179.2332 | 179.2329 | 0 | 0.00021574 | 0.00021574 | 0 | 0 | 0 | 0 | 74.3936 | 677.1371 | 0 | 0.05921 | 3.9751 | 0 | 0 | 208.345 | 179.2329 | off_peak | 677.1371 | 100 | 0 | 20.93 | 0 | 79.07 | 712.4771 | 0
2269 | 862.66 | 859.503 | 25.8 | 173.5481 | 173.5481 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 689.1119 | 0 | 0.088511 | 4.3143 | 0 | 0 | 208.345 | 173.5481 | on_peak | 689.1119 |  |  | 20.12 | 0 | 79.88 | 748.7404 | 0
2270 | 900.52 | 854.905 | 25.9 | 172.5574 | 172.5574 | 0 | 0 | 1.4896e-05 | 1.4896e-05 | 0 | 0 | 0 | 74.3936 | 727.9627 | 0 | 0.088511 | 4.5065 | 0 | 0 | 208.345 | 172.5574 | on_peak | 727.9626 | 0 | 100 | 19.16 | 0 | 80.84 | 777.6335 | 0
2271 | 975.07 | 769.155 | 25.9 | 155.2492 | 155.2492 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 819.8208 | 0 | 0.088511 | 4.545 | 0 | 0 | 208.345 | 155.2492 | on_peak | 819.8208 |  |  | 15.92 | 0 | 84.08 | 705.6044 | 0
2272 | 982.28 | 606.807 | 25.7 | 122.5688 | 122.5688 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 859.7112 | 0 | 0.088511 | 4.7488 | 0 | 0 | 208.345 | 122.5688 | on_peak | 859.7112 |  |  | 12.48 | 0 | 87.52 | 582.0586 | 0
2273 | 974.71 | 405.535 | 25.4 | 82.0026 | 82.0026 | 0 | 0 | 0 | 0 | 7.9674 | 7.9674 | 0 | 65.8761 | 884.74 | 0 | 0.088511 | 4.9407 | 0 | 0 | 208.345 | 82.0026 | on_peak | 884.74 |  |  | 8.41 | 0.82 | 90.77 | 405.1522 | 0
2274 | 945.35 | 188.692 | 24.8 | 38.2376 | 38.2376 | 0 | 0 | 0 | 0 | 22.3724 | 22.3724 | 0 | 41.9591 | 884.74 | 0 | 0.088511 | 5.3181 | 0 | 0 | 208.345 | 38.2376 | on_peak | 884.74 |  |  | 4.04 | 2.37 | 93.59 | 203.3532 | 0
2275 | 905.52 | 16.3494 | 24.5 | 3.3167 | 3.3167 | 0 | 0 | 0 | 0 | 17.4633 | 17.4633 | 0 | 23.29 | 884.74 | 0 | 0.088511 | 5.7227 | 0 | 0 | 208.345 | 3.3167 | on_peak | 884.74 |  |  | 0.37 | 1.93 | 97.71 | 18.9804 | 0
2276 | 884.74 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 23.29 | 884.74 | 0 | 0.088511 | 6.0266 | 0 | 0 | 208.345 | 0 | on_peak | 884.74 |  |  | 0 | 0 | 100 | 0 | 0
2277 | 899.17 | 0 | 23.8 | 0 | 0 | 0 | 0 | 0 | 0 | 14.43 | 14.43 | 0 | 7.8637 | 884.74 | 0 | 0.088511 | 6.1862 | 0 | 0 | 208.345 | 0 | on_peak | 884.74 |  |  | 0 | 1.6 | 98.4 | 0 | 0
2278 | 864.22 | 0 | 23.7 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 19.4618 | 876.6189 | 0 | 0.05921 | 6.483 | 0 | 0 | 208.345 | 0 | off_peak | 864.22 | 0 | 100 | 0 | 0 | 100 | 0 | 0
2279 | 922.01 | 0 | 23.6 | 0 | 0 | 0 | 0 | 0 | 0 | 11.246 | 11.246 | 0 | 7.4394 | 910.764 | 0 | 0.05921 | 6.7797 | 0 | 0 | 208.345 | 0 | off_peak | 910.764 |  |  | 0 | 1.22 | 98.78 | 0 | 0
2280 | 910.32 | 0 | 23.5 | 0 | 0 | 0 | 0 | 0.444 | 0.444 | 0 | 0 | 0 | 7.8547 | 910.764 | 0 | 0.05921 | 6.9928 | 0 | 0 | 208.345 | 0 | off_peak | 910.32 | 0 | 100 | 0 | 0 | 100 | 0 | 0
2281 | 843.27 | 0 | 23.4 | 0 | 0 | 0 | 0 | 8.2824 | 8.2824 | 0 | 0 | 0 | 15.6021 | 851.5524 | 0 | 0.05921 | 6.9495 | 0 | 0 | 208.345 | 0 | off_peak | 843.27 | 0 | 100 | 0 | 0 | 100 | 0 | 0
2282 | 744.42 | 0 | 23.2 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 27.2003 | 756.8189 | 0 | 0.05921 | 6.8292 | 0 | 0 | 208.345 | 0 | off_peak | 744.42 | 0 | 100 | 0 | 0 | 100 | 0 | 0
2283 | 703.51 | 0 | 23.1 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 38.7984 | 715.9089 | 0 | 0.05921 | 6.4052 | 0 | 0 | 208.345 | 0 | off_peak | 703.51 | 0 | 100 | 0 | 0 | 100 | 0 | 0
2284 | 691.37 | 0 | 23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 38.7984 | 691.37 | 0 | 0.05921 | 5.8001 | 0 | 0 | 208.345 | 0 | off_peak | 691.37 |  |  | 0 | 0 | 100 | 0 | 0
2285 | 711.26 | 0 | 22.8 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 50.3966 | 723.6589 | 0 | 0.05921 | 5.0415 | 0 | 0 | 208.345 | 0 | off_peak | 711.26 | 0 | 100 | 0 | 0 | 100 | 0 | 0
2286 | 780.68 | 0 | 22.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50.3966 | 780.68 | 0 | 0.05921 | 4.337 | 0 | 0 | 208.345 | 0 | off_peak | 780.68 |  |  | 0 | 0 | 100 | 0 | 0
2287 | 843.52 | 38.1885 | 23.2 | 7.7833 | 0 | 0 | 7.7833 | 12.3989 | 4.6157 | 0 | 0 | 0 | 61.9947 | 848.1357 | 0 | 0.05921 | 3.8635 | 0 | 0 | 215.6256 | 0 | off_peak | 843.52 | 62.77 | 37.23 | 0 | 0 | 100 | 0 | 0
2288 | 856.85 | 225.656 | 23.7 | 45.9092 | 45.9092 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 73.5928 | 823.3397 | 0 | 0.05921 | 3.5656 | 0 | 0 | 215.6256 | 45.9092 | off_peak | 810.9408 | 0 | 100 | 5.36 | 0 | 94.64 | 163.6933 | 0
2289 | 873.9 | 443.096 | 24.1 | 90.0177 | 89.2169 | 0 | 0.80079 | 0.80079 | 0 | 0 | 0 | 0 | 74.3419 | 784.6831 | 0 | 0.05921 | 3.3703 | 0 | 0 | 216.3747 | 89.2169 | off_peak | 784.6831 | 100 | 0 | 10.21 | 0 | 89.79 | 300.6899 | 0
2290 | 893.97 | 635.581 | 24.6 | 128.8905 | 128.8905 | 0 | 0 | 0.05172 | 0.05172 | 0 | 0 | 0 | 74.3903 | 765.1312 | 0 | 0.05921 | 3.3205 | 0 | 0 | 216.3747 | 128.8905 | off_peak | 765.0795 | 0 | 100 | 14.42 | 0 | 85.58 | 427.9854 | 0
2291 | 859.38 | 783.373 | 25 | 158.633 | 158.633 | 0 | 0 | 0.0033404 | 0.0033404 | 0 | 0 | 0 | 74.3934 | 700.7503 | 0 | 0.05921 | 3.5362 | 0 | 0 | 216.3747 | 158.633 | off_peak | 700.747 | 0 | 100 | 18.46 | 0 | 81.54 | 560.9611 | 0
2292 | 920.9 | 879.963 | 25.2 | 178.0642 | 178.0642 | 0 | 0 | 0.00021574 | 0.00021574 | 0 | 0 | 0 | 74.3936 | 742.836 | 0 | 0.05921 | 3.9338 | 0 | 0 | 216.3747 | 178.0642 | off_peak | 742.8358 | 0 | 100 | 19.34 | 0 | 80.66 | 700.469 | 0
2293 | 880.91 | 907.584 | 25.3 | 183.5873 | 183.5873 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 697.3227 | 0 | 0.088511 | 4.0722 | 0 | 0 | 216.3747 | 183.5873 | on_peak | 697.3227 |  |  | 20.84 | 0 | 79.16 | 747.6097 | 0
2294 | 895.12 | 764.44 | 25.2 | 154.6876 | 154.6876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 740.4324 | 0 | 0.088511 | 4.1835 | 0 | 0 | 216.3747 | 154.6876 | on_peak | 740.4324 |  |  | 17.28 | 0 | 82.72 | 647.1289 | 0
2295 | 963.43 | 753.22 | 25.1 | 152.4721 | 152.4721 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 810.9579 | 0 | 0.088511 | 4.3124 | 0 | 0 | 216.3747 | 152.4721 | on_peak | 810.9579 |  |  | 15.83 | 0 | 84.17 | 657.5173 | 0
2296 | 956.79 | 580.294 | 24.8 | 117.5941 | 117.5941 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 839.1959 | 0 | 0.088511 | 4.5048 | 0 | 0 | 216.3747 | 117.5941 | on_peak | 839.1959 |  |  | 12.29 | 0 | 87.71 | 529.7387 | 0
2297 | 878.84 | 397.654 | 24.6 | 80.6409 | 80.6409 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 798.1991 | 0 | 0.088511 | 4.8462 | 0 | 0 | 216.3747 | 80.6409 | on_peak | 798.1991 |  |  | 9.18 | 0 | 90.82 | 390.7995 | 0
2298 | 913.88 | 183.13 | 24.2 | 37.1906 | 37.1906 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 876.6894 | 0 | 0.088511 | 5.1637 | 0 | 0 | 216.3747 | 37.1906 | on_peak | 876.6894 |  |  | 4.07 | 0 | 95.93 | 192.0427 | 0
2299 | 829.58 | 14.8353 | 24 | 3.015 | 3.015 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 826.565 | 0 | 0.088511 | 5.5735 | 0 | 0 | 216.3747 | 3.015 | on_peak | 826.565 |  |  | 0.36 | 0 | 99.64 | 16.8038 | 0
2300 | 839.63 | 0 | 23.8 | 0 | 0 | 0 | 0 | 0 | 0 | 62.63 | 62.63 | 0 | 7.4394 | 777 | 0 | 0.088511 | 5.9319 | 0 | 0 | 216.3747 | 0 | on_peak | 777 |  |  | 0 | 7.46 | 92.54 | 0 | 0
2301 | 810.54 | 0 | 23.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 810.54 | 0 | 0.088511 | 6.1713 | 0 | 0 | 216.3747 | 0 | on_peak | 810.54 |  |  | 0 | 0 | 100 | 0 | 0
2302 | 757.46 | 0 | 23.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 757.46 | 0 | 0.05921 | 6.441 | 0 | 0 | 216.3747 | 0 | off_peak | 757.46 |  |  | 0 | 0 | 100 | 0 | 0
2303 | 826.51 | 0 | 23.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 826.51 | 0 | 0.05921 | 6.6986 | 0 | 0 | 216.3747 | 0 | off_peak | 826.51 |  |  | 0 | 0 | 100 | 0 | 0
2304 | 787.17 | 0 | 23.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 787.17 | 0 | 0.05921 | 6.9214 | 0 | 0 | 216.3747 | 0 | off_peak | 787.17 |  |  | 0 | 0 | 100 | 0 | 0
2305 | 757.57 | 0 | 23.6 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 19.0375 | 769.9689 | 0 | 0.05921 | 6.7986 | 0 | 0 | 216.3747 | 0 | off_peak | 757.57 | 0 | 100 | 0 | 0 | 100 | 0 | 0
2306 | 679.44 | 0 | 23.5 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 30.6357 | 691.8389 | 0 | 0.05921 | 6.5808 | 0 | 0 | 216.3747 | 0 | off_peak | 679.44 | 0 | 100 | 0 | 0 | 100 | 0 | 0
2307 | 669.89 | 0 | 23.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30.6357 | 669.89 | 0 | 0.05921 | 6.1111 | 0 | 0 | 216.3747 | 0 | off_peak | 669.89 |  |  | 0 | 0 | 100 | 0 | 0
2308 | 610.83 | 0 | 23.4 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 42.2338 | 623.2289 | 0 | 0.05921 | 5.5949 | 0 | 0 | 216.3747 | 0 | off_peak | 610.83 | 0 | 100 | 0 | 0 | 100 | 0 | 0
2309 | 664.21 | 0 | 23.4 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 53.832 | 676.6089 | 0 | 0.05921 | 5.0769 | 0 | 0 | 216.3747 | 0 | off_peak | 664.21 | 0 | 100 | 0 | 0 | 100 | 0 | 0
2310 | 708.34 | 0 | 23.4 | 0 | 0 | 0 | 0 | 8.7263 | 8.7263 | 0 | 0 | 0 | 61.9947 | 717.0663 | 0 | 0.05921 | 4.4587 | 0 | 0 | 216.3747 | 0 | off_peak | 708.34 | 0 | 100 | 0 | 0 | 100 | 0 | 0
2311 | 775.53 | 41.8244 | 23.9 | 8.503 | 8.503 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 61.9947 | 767.027 | 0 | 0.05921 | 4.0495 | 0 | 0 | 216.3747 | 8.503 | off_peak | 767.027 |  |  | 1.1 | 0 | 98.9 | 34.433 | 0
2312 | 828.92 | 232.582 | 24.5 | 47.1826 | 47.1826 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 73.5928 | 794.1363 | 0 | 0.05921 | 3.7456 | 0 | 0 | 216.3747 | 47.1826 | off_peak | 781.7374 | 0 | 100 | 5.69 | 0 | 94.31 | 176.7291 | 0
2313 | 790.05 | 449.507 | 24.9 | 91.0579 | 91.0579 | 0 | 0 | 0.80079 | 0.80079 | 0 | 0 | 0 | 74.3419 | 699.7929 | 0 | 0.05921 | 3.5645 | 0 | 0 | 216.3747 | 91.0579 | off_peak | 698.9921 | 0 | 100 | 11.53 | 0 | 88.47 | 324.5783 | 0
2314 | 807.7 | 645.758 | 25.3 | 130.6248 | 130.6248 | 0 | 0 | 0.05172 | 0.05172 | 0 | 0 | 0 | 74.3903 | 677.127 | 0 | 0.05921 | 3.5666 | 0 | 0 | 216.3747 | 130.6248 | off_peak | 677.0752 | 0 | 100 | 16.17 | 0 | 83.83 | 465.8914 | 0
2315 | 767.29 | 724.189 | 25.7 | 146.2787 | 146.2787 | 0 | 0 | 0.0033404 | 0.0033404 | 0 | 0 | 0 | 74.3934 | 621.0146 | 0 | 0.05921 | 3.6927 | 0 | 0 | 216.3747 | 146.2787 | off_peak | 621.0113 | 0 | 100 | 19.06 | 0 | 80.94 | 540.1625 | 0
2316 | 856.97 | 463.243 | 26 | 93.469 | 93.469 | 0 | 0 | 0.00021574 | 0.00021574 | 0 | 0 | 0 | 74.3936 | 763.5012 | 0 | 0.05921 | 4.0149 | 0 | 0 | 216.3747 | 93.469 | off_peak | 763.501 | 0 | 100 | 10.91 | 0 | 89.09 | 375.2669 | 0
2317 | 762.9 | 441.716 | 26.1 | 89.0933 | 89.0933 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 673.8067 | 0 | 0.088511 | 4.1521 | 0 | 0 | 216.3747 | 89.0933 | on_peak | 673.8067 |  |  | 11.68 | 0 | 88.32 | 369.9198 | 0
2318 | 879.14 | 668.863 | 26.1 | 134.9084 | 134.9084 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 744.2316 | 0 | 0.088511 | 4.444 | 0 | 0 | 216.3747 | 134.9084 | on_peak | 744.2316 |  |  | 15.35 | 0 | 84.65 | 599.5303 | 0
2319 | 874.33 | 603.913 | 26.1 | 121.8081 | 121.8081 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 752.5219 | 0 | 0.088511 | 4.6273 | 0 | 0 | 216.3747 | 121.8081 | on_peak | 752.5219 |  |  | 13.93 | 0 | 86.07 | 563.6398 | 0
2320 | 845.39 | 290.687 | 25.9 | 58.6734 | 58.6734 | 0 | 0 | 0 | 0 | 62.63 | 62.63 | 0 | 7.4394 | 724.0866 | 0 | 0.088511 | 4.946 | 0 | 0 | 216.3747 | 58.6734 | on_peak | 724.0866 |  |  | 6.94 | 7.41 | 85.65 | 290.1978 | 0
2321 | 845.87 | 299.835 | 25.6 | 60.5854 | 60.5854 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 785.2846 | 0 | 0.088511 | 5.2996 | 0 | 0 | 216.3747 | 60.5854 | on_peak | 785.2846 |  |  | 7.16 | 0 | 92.84 | 321.0765 | 0
2322 | 846.52 | 148.922 | 25.1 | 30.1458 | 30.1458 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 816.3742 | 0 | 0.088511 | 5.5701 | 0 | 0 | 216.3747 | 30.1458 | on_peak | 816.3742 |  |  | 3.56 | 0 | 96.44 | 167.9149 | 0
2323 | 783.17 | 13.3311 | 24.8 | 2.7015 | 2.7015 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 780.4685 | 0 | 0.088511 | 5.8301 | 0 | 0 | 216.3747 | 2.7015 | on_peak | 780.4685 |  |  | 0.34 | 0 | 99.66 | 15.75 | 0
2324 | 802.38 | 0 | 24.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 802.38 | 0 | 0.088511 | 6.1334 | 0 | 0 | 216.3747 | 0 | on_peak | 802.38 |  |  | 0 | 0 | 100 | 0 | 0
2325 | 731.1 | 0 | 24.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 731.1 | 0 | 0.088511 | 6.4067 | 0 | 0 | 216.3747 | 0 | on_peak | 731.1 |  |  | 0 | 0 | 100 | 0 | 0
2326 | 746.53 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 746.53 | 0 | 0.05921 | 6.6541 | 0 | 0 | 216.3747 | 0 | off_peak | 746.53 |  |  | 0 | 0 | 100 | 0 | 0
2327 | 766.78 | 0 | 23.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 766.78 | 0 | 0.05921 | 6.8113 | 0 | 0 | 216.3747 | 0 | off_peak | 766.78 |  |  | 0 | 0 | 100 | 0 | 0
2328 | 719.3 | 0 | 23.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 719.3 | 0 | 0.05921 | 7.0045 | 0 | 0 | 216.3747 | 0 | off_peak | 719.3 |  |  | 0 | 0 | 100 | 0 | 0
2329 | 710.93 | 0 | 23.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 710.93 | 0 | 0.05921 | 6.8165 | 0 | 0 | 216.3747 | 0 | off_peak | 710.93 |  |  | 0 | 0 | 100 | 0 | 0
2330 | 574.71 | 0 | 23.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 574.71 | 0 | 0.05921 | 6.6449 | 0 | 0 | 216.3747 | 0 | off_peak | 574.71 |  |  | 0 | 0 | 100 | 0 | 0
2331 | 502.13 | 0 | 23.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 502.13 | 0 | 0.05921 | 6.2321 | 0 | 0 | 216.3747 | 0 | off_peak | 502.13 |  |  | 0 | 0 | 100 | 0 | 0
2332 | 483.54 | 0 | 23.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 483.54 | 0 | 0.05921 | 5.674 | 0 | 0 | 216.3747 | 0 | off_peak | 483.54 |  |  | 0 | 0 | 100 | 0 | 0
2333 | 521.29 | 0 | 23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 521.29 | 0 | 0.05921 | 5.1398 | 0 | 0 | 216.3747 | 0 | off_peak | 521.29 |  |  | 0 | 0 | 100 | 0 | 0
2334 | 707.03 | 0 | 23.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 707.03 | 0 | 0.05921 | 4.6108 | 0 | 0 | 216.3747 | 0 | off_peak | 707.03 |  |  | 0 | 0 | 100 | 0 | 0
2335 | 768.21 | 41.274 | 23.7 | 8.3971 | 8.3971 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 759.8129 | 0 | 0.05921 | 4.1257 | 0 | 0 | 216.3747 | 8.3971 | off_peak | 759.8129 |  |  | 1.09 | 0 | 98.91 | 34.6439 | 0
2336 | 717.23 | 233.62 | 24.4 | 47.4102 | 47.4102 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 669.8198 | 0 | 0.05921 | 3.7673 | 0 | 0 | 216.3747 | 47.4102 | off_peak | 669.8198 |  |  | 6.61 | 0 | 93.39 | 178.6074 | 0
2337 | 773.17 | 449.476 | 24.9 | 91.0517 | 91.0517 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 682.1183 | 0 | 0.05921 | 3.5525 | 0 | 0 | 216.3747 | 91.0517 | off_peak | 682.1183 |  |  | 11.78 | 0 | 88.22 | 323.4606 | 0
2338 | 719.95 | 637.961 | 25.3 | 129.0476 | 129.0476 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 590.9024 | 0 | 0.05921 | 3.4656 | 0 | 0 | 216.3747 | 129.0476 | off_peak | 590.9024 |  |  | 17.92 | 0 | 82.08 | 447.2289 | 0
2339 | 698.57 | 752.035 | 25.7 | 151.9033 | 151.9033 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 546.6667 | 0 | 0.05921 | 3.4737 | 0 | 0 | 216.3747 | 151.9033 | off_peak | 546.6667 |  |  | 21.74 | 0 | 78.26 | 527.6679 | 0
2340 | 775.17 | 874.009 | 25.9 | 176.4134 | 176.4134 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 598.7566 | 0 | 0.05921 | 3.6007 | 0 | 0 | 216.3747 | 176.4134 | off_peak | 598.7566 |  |  | 22.76 | 0 | 77.24 | 635.209 | 0
2341 | 702.05 | 897.767 | 26 | 181.1433 | 181.1433 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 520.9067 | 0 | 0.05921 | 3.779 | 0 | 0 | 216.3747 | 181.1433 | off_peak | 520.9067 |  |  | 25.8 | 0 | 74.2 | 684.5384 | 0
2342 | 690.31 | 754.544 | 25.9 | 152.3001 | 152.3001 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 538.0099 | 0 | 0.05921 | 4.2222 | 0 | 0 | 216.3747 | 152.3001 | off_peak | 538.0099 |  |  | 22.06 | 0 | 77.94 | 643.0391 | 0
2343 | 733.69 | 369.75 | 25.8 | 74.6587 | 74.6587 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 659.0313 | 0 | 0.05921 | 4.6022 | 0 | 0 | 216.3747 | 74.6587 | off_peak | 659.0313 |  |  | 10.18 | 0 | 89.82 | 343.595 | 0
2344 | 680.02 | 382.69 | 25.5 | 77.3552 | 77.3552 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 602.6648 | 0 | 0.05921 | 5.0693 | 0 | 0 | 216.3747 | 77.3552 | off_peak | 602.6648 |  |  | 11.38 | 0 | 88.62 | 392.1371 | 0
2345 | 672.63 | 358.943 | 25.1 | 72.6598 | 72.6598 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 599.9702 | 0 | 0.05921 | 5.5282 | 0 | 0 | 216.3747 | 72.6598 | off_peak | 599.9702 |  |  | 10.8 | 0 | 89.2 | 401.6792 | 0
2346 | 615.84 | 180.675 | 24.6 | 36.6394 | 36.6394 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 579.2006 | 0 | 0.05921 | 5.8652 | 0 | 0 | 216.3747 | 36.6394 | off_peak | 579.2006 |  |  | 5.95 | 0 | 94.05 | 214.8967 | 0
2347 | 589.03 | 15.5582 | 24.2 | 3.1596 | 0 | 0 | 3.1596 | 3.1596 | 0 | 0 | 0 | 0 | 10.3949 | 589.03 | 0 | 0.05921 | 6.2432 | 0 | 0 | 219.3303 | 0 | off_peak | 589.03 | 100 | 0 | 0 | 0 | 100 | 0 | 0
2348 | 526.95 | 0 | 23.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10.3949 | 526.95 | 0 | 0.05921 | 6.5123 | 0 | 0 | 219.3303 | 0 | off_peak | 526.95 |  |  | 0 | 0 | 100 | 0 | 0
2349 | 552.16 | 0 | 23.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10.3949 | 552.16 | 0 | 0.05921 | 6.8984 | 0 | 0 | 219.3303 | 0 | off_peak | 552.16 |  |  | 0 | 0 | 100 | 0 | 0
2350 | 547.73 | 0 | 23.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10.3949 | 547.73 | 0 | 0.05921 | 6.9997 | 0 | 0 | 219.3303 | 0 | off_peak | 547.73 |  |  | 0 | 0 | 100 | 0 | 0
2351 | 546.36 | 0 | 23.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10.3949 | 546.36 | 0 | 0.05921 | 7.2246 | 0 | 0 | 219.3303 | 0 | off_peak | 546.36 |  |  | 0 | 0 | 100 | 0 | 0
2352 | 540.75 | 0 | 23.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10.3949 | 540.75 | 0 | 0.05921 | 7.2605 | 0 | 0 | 219.3303 | 0 | off_peak | 540.75 |  |  | 0 | 0 | 100 | 0 | 0
2353 | 545.53 | 0 | 22.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10.3949 | 545.53 | 0 | 0.05921 | 6.8999 | 0 | 0 | 219.3303 | 0 | off_peak | 545.53 |  |  | 0 | 0 | 100 | 0 | 0
2354 | 538.73 | 0 | 22.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10.3949 | 538.73 | 0 | 0.05921 | 6.667 | 0 | 0 | 219.3303 | 0 | off_peak | 538.73 |  |  | 0 | 0 | 100 | 0 | 0
2355 | 513.75 | 0 | 22.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10.3949 | 513.75 | 0 | 0.05921 | 6.2643 | 0 | 0 | 219.3303 | 0 | off_peak | 513.75 |  |  | 0 | 0 | 100 | 0 | 0
2356 | 541.22 | 0 | 22.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10.3949 | 541.22 | 0 | 0.05921 | 5.8201 | 0 | 0 | 219.3303 | 0 | off_peak | 541.22 |  |  | 0 | 0 | 100 | 0 | 0
2357 | 532.31 | 0 | 22.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10.3949 | 532.31 | 0 | 0.05921 | 5.197 | 0 | 0 | 219.3303 | 0 | off_peak | 532.31 |  |  | 0 | 0 | 100 | 0 | 0
2358 | 635.15 | 0 | 22.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10.3949 | 635.15 | 0 | 0.05921 | 4.5247 | 0 | 0 | 219.3303 | 0 | off_peak | 635.15 |  |  | 0 | 0 | 100 | 0 | 0
2359 | 693.85 | 49.0826 | 23.2 | 10.0036 | 10.0036 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 21.9931 | 696.2453 | 0 | 0.05921 | 4.0663 | 0 | 0 | 219.3303 | 10.0036 | off_peak | 683.8464 | 0 | 100 | 1.44 | 0 | 98.56 | 40.6781 | 0
2360 | 710.69 | 248.029 | 23.9 | 50.4248 | 50.4248 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21.9931 | 660.2652 | 0 | 0.05921 | 3.7257 | 0 | 0 | 219.3303 | 50.4248 | off_peak | 660.2652 |  |  | 7.1 | 0 | 92.9 | 187.8684 | 0
2361 | 732 | 433.331 | 24.4 | 87.9391 | 87.9391 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21.9931 | 644.0609 | 0 | 0.05921 | 3.473 | 0 | 0 | 219.3303 | 87.9391 | off_peak | 644.0609 |  |  | 12.01 | 0 | 87.99 | 305.4146 | 0
2362 | 697.41 | 671.021 | 25 | 135.8818 | 135.8818 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21.9931 | 561.5282 | 0 | 0.05921 | 3.3517 | 0 | 0 | 219.3303 | 135.8818 | off_peak | 561.5282 |  |  | 19.48 | 0 | 80.52 | 455.4315 | 0
2363 | 706.42 | 826.017 | 25.5 | 166.9674 | 166.9674 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21.9931 | 539.4526 | 0 | 0.05921 | 3.3176 | 0 | 0 | 219.3303 | 166.9674 | off_peak | 539.4526 |  |  | 23.64 | 0 | 76.36 | 553.9339 | 0
2364 | 765.55 | 769.372 | 25.9 | 155.293 | 155.293 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21.9931 | 610.257 | 0 | 0.05921 | 3.4358 | 0 | 0 | 219.3303 | 155.293 | off_peak | 610.257 |  |  | 20.29 | 0 | 79.71 | 533.5526 | 0
2365 | 696.84 | 901.053 | 26.2 | 181.675 | 181.675 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21.9931 | 515.165 | 0 | 0.05921 | 3.59 | 0 | 0 | 219.3303 | 181.675 | off_peak | 515.165 |  |  | 26.07 | 0 | 73.93 | 652.2215 | 0
2366 | 657.32 | 832.687 | 26.3 | 167.83 | 167.83 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21.9931 | 489.49 | 0 | 0.05921 | 4.0183 | 0 | 0 | 219.3303 | 167.83 | off_peak | 489.49 |  |  | 25.53 | 0 | 74.47 | 674.3953 | 0
2367 | 738.32 | 775.273 | 26.3 | 156.2581 | 156.2581 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21.9931 | 582.0619 | 0 | 0.05921 | 4.5834 | 0 | 0 | 219.3303 | 156.2581 | off_peak | 582.0619 |  |  | 21.16 | 0 | 78.84 | 716.1974 | 0
2368 | 726.36 | 648.654 | 26.1 | 130.8323 | 130.8323 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21.9931 | 595.5277 | 0 | 0.05921 | 5.0475 | 0 | 0 | 219.3303 | 130.8323 | off_peak | 595.5277 |  |  | 18.01 | 0 | 81.99 | 660.378 | 0
2369 | 692.31 | 438.745 | 25.7 | 88.622 | 88.622 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 33.5912 | 616.087 | 0 | 0.05921 | 5.3311 | 0 | 0 | 219.3303 | 88.622 | off_peak | 603.688 | 0 | 100 | 12.8 | 0 | 87.2 | 472.4568 | 0
2370 | 619.6 | 211.504 | 24.9 | 42.845 | 42.845 | 0 | 0 | 5.5667 | 5.5667 | 0 | 0 | 0 | 38.7984 | 582.3218 | 0 | 0.05921 | 5.5819 | 0 | 0 | 219.3303 | 42.845 | off_peak | 576.755 | 0 | 100 | 6.91 | 0 | 93.09 | 239.1555 | 0
2371 | 578.95 | 21.8572 | 24.5 | 4.434 | 4.434 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 38.7984 | 574.516 | 0 | 0.05921 | 5.7209 | 0 | 0 | 219.3303 | 4.434 | off_peak | 574.516 |  |  | 0.77 | 0 | 99.23 | 25.367 | 0
2372 | 530.94 | 0 | 23.7 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 50.3966 | 543.3389 | 0 | 0.05921 | 5.8012 | 0 | 0 | 219.3303 | 0 | off_peak | 530.94 | 0 | 100 | 0 | 0 | 100 | 0 | 0
2373 | 583.39 | 0 | 23.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50.3966 | 583.39 | 0 | 0.05921 | 5.7892 | 0 | 0 | 219.3303 | 0 | off_peak | 583.39 |  |  | 0 | 0 | 100 | 0 | 0
2374 | 547.06 | 0 | 23.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50.3966 | 547.06 | 0 | 0.05921 | 5.6512 | 0 | 0 | 219.3303 | 0 | off_peak | 547.06 |  |  | 0 | 0 | 100 | 0 | 0
2375 | 564.86 | 0 | 23.2 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 61.9947 | 577.2589 | 0 | 0.05921 | 5.4576 | 0 | 0 | 219.3303 | 0 | off_peak | 564.86 | 0 | 100 | 0 | 0 | 100 | 0 | 0
2376 | 532.69 | 0 | 23.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 61.9947 | 532.69 | 0 | 0.05921 | 5.445 | 0 | 0 | 219.3303 | 0 | off_peak | 532.69 |  |  | 0 | 0 | 100 | 0 | 0
2377 | 563.43 | 0 | 23.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 61.9947 | 563.43 | 0 | 0.05921 | 5.4743 | 0 | 0 | 219.3303 | 0 | off_peak | 563.43 |  |  | 0 | 0 | 100 | 0 | 0
2378 | 541.99 | 0 | 23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 61.9947 | 541.99 | 0 | 0.05921 | 5.5318 | 0 | 0 | 219.3303 | 0 | off_peak | 541.99 |  |  | 0 | 0 | 100 | 0 | 0
2379 | 554.44 | 0 | 22.9 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 73.5928 | 566.8389 | 0 | 0.05921 | 5.223 | 0 | 0 | 219.3303 | 0 | off_peak | 554.44 | 0 | 100 | 0 | 0 | 100 | 0 | 0
2380 | 562.36 | 0 | 22.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 73.5928 | 562.36 | 0 | 0.05921 | 4.7371 | 0 | 0 | 219.3303 | 0 | off_peak | 562.36 |  |  | 0 | 0 | 100 | 0 | 0
2381 | 566.02 | 0 | 22.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 73.5928 | 566.02 | 0 | 0.05921 | 4.1283 | 0 | 0 | 219.3303 | 0 | off_peak | 566.02 |  |  | 0 | 0 | 100 | 0 | 0
2382 | 701.57 | 0 | 23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 73.5928 | 701.57 | 0 | 0.05921 | 3.5965 | 0 | 0 | 219.3303 | 0 | off_peak | 701.57 |  |  | 0 | 0 | 100 | 0 | 0
2383 | 771.17 | 60.7795 | 23.5 | 12.3743 | 12.3743 | 0 | 0 | 0.80079 | 0.80079 | 0 | 0 | 0 | 74.3419 | 759.5965 | 0 | 0.05921 | 3.2446 | 0 | 0 | 219.3303 | 12.3743 | off_peak | 758.7957 | 0 | 100 | 1.6 | 0 | 98.4 | 40.1494 | 0
2384 | 860.88 | 276 | 24.1 | 56.0711 | 56.0711 | 0 | 0 | 0.05172 | 0.05172 | 0 | 0 | 0 | 74.3903 | 804.8606 | 0 | 0.05921 | 3.0689 | 0 | 0 | 219.3303 | 56.0711 | off_peak | 804.8089 | 0 | 100 | 6.51 | 0 | 93.49 | 172.0745 | 0
2385 | 827.65 | 507.802 | 24.7 | 102.941 | 102.9376 | 0 | 0.0033404 | 0.0033404 | 0 | 0 | 0 | 0 | 74.3934 | 724.7124 | 0 | 0.05921 | 2.9581 | 0 | 0 | 219.3334 | 102.9376 | off_peak | 724.7124 | 100 | 0 | 12.44 | 0 | 87.56 | 304.4978 | 0
2386 | 847.32 | 710.105 | 25.3 | 143.641 | 143.641 | 0 | 0 | 0.00021574 | 0.00021574 | 0 | 0 | 0 | 74.3936 | 703.6793 | 0 | 0.05921 | 2.9837 | 0 | 0 | 219.3334 | 143.641 | off_peak | 703.679 | 0 | 100 | 16.95 | 0 | 83.05 | 428.5768 | 0
2387 | 807.93 | 864.48 | 25.9 | 174.49 | 174.49 | 0 | 1.3934e-05 | 1.3934e-05 | 0 | 0 | 0 | 0 | 74.3936 | 633.44 | 0 | 0.05921 | 3.2594 | 0 | 0 | 219.3334 | 174.49 | off_peak | 633.44 | 100 | 0 | 21.6 | 0 | 78.4 | 568.7304 | 0
2388 | 938.37 | 957.743 | 26.4 | 192.9655 | 192.9655 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 745.4045 | 0 | 0.05921 | 3.7213 | 0 | 0 | 219.3334 | 192.9655 | off_peak | 745.4045 |  |  | 20.56 | 0 | 79.44 | 718.0758 | 0
2389 | 840.89 | 981.111 | 26.7 | 197.4591 | 197.4591 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 643.4309 | 0 | 0.088511 | 3.9991 | 0 | 0 | 219.3334 | 197.4591 | on_peak | 643.4309 |  |  | 23.48 | 0 | 76.52 | 789.6652 | 0
2390 | 907.11 | 934.138 | 26.9 | 187.8691 | 187.8691 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 719.2409 | 0 | 0.088511 | 4.1509 | 0 | 0 | 219.3334 | 187.8691 | on_peak | 719.2409 |  |  | 20.71 | 0 | 79.29 | 779.8182 | 0
2391 | 952.74 | 819.798 | 26.9 | 164.8736 | 164.8736 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 787.8664 | 0 | 0.088511 | 4.2494 | 0 | 0 | 219.3334 | 164.8736 | on_peak | 787.8664 |  |  | 17.31 | 0 | 82.69 | 700.6084 | 0
2392 | 884.46 | 649.191 | 26.7 | 130.6566 | 130.6566 | 0 | 0 | 0 | 0 | 62.63 | 62.63 | 0 | 7.4394 | 691.1734 | 0 | 0.088511 | 4.4526 | 0 | 0 | 219.3334 | 130.6566 | on_peak | 691.1734 |  |  | 14.77 | 7.08 | 78.15 | 581.7653 | 0
2393 | 851.02 | 435.867 | 26.3 | 87.85 | 87.85 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 763.17 | 0 | 0.088511 | 4.5598 | 0 | 0 | 219.3334 | 87.85 | on_peak | 763.17 |  |  | 10.32 | 0 | 89.68 | 400.5752 | 0
2394 | 867.55 | 208.367 | 25.5 | 42.1184 | 42.1184 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 825.4316 | 0 | 0.088511 | 4.6125 | 0 | 0 | 219.3334 | 42.1184 | on_peak | 825.4316 |  |  | 4.85 | 0 | 95.15 | 194.2719 | 0
2395 | 815.54 | 21.4965 | 25 | 4.353 | 4.353 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 811.187 | 0 | 0.088511 | 4.5837 | 0 | 0 | 219.3334 | 4.353 | on_peak | 811.187 |  |  | 0.53 | 0 | 99.47 | 19.953 | 0
2396 | 826.71 | 0 | 24.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 826.71 | 0 | 0.088511 | 4.7287 | 0 | 0 | 219.3334 | 0 | on_peak | 826.71 |  |  | 0 | 0 | 100 | 0 | 0
2397 | 830.73 | 0 | 23.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 830.73 | 0 | 0.088511 | 4.9755 | 0 | 0 | 219.3334 | 0 | on_peak | 830.73 |  |  | 0 | 0 | 100 | 0 | 0
2398 | 779.63 | 0 | 23.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 779.63 | 0 | 0.05921 | 5.0247 | 0 | 0 | 219.3334 | 0 | off_peak | 779.63 |  |  | 0 | 0 | 100 | 0 | 0
2399 | 802.36 | 0 | 23.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 802.36 | 0 | 0.05921 | 5.213 | 0 | 0 | 219.3334 | 0 | off_peak | 802.36 |  |  | 0 | 0 | 100 | 0 | 0
2400 | 776.45 | 0 | 23.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 776.45 | 0 | 0.05921 | 5.3372 | 0 | 0 | 219.3334 | 0 | off_peak | 776.45 |  |  | 0 | 0 | 100 | 0 | 0
2401 | 768.18 | 0 | 23.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 768.18 | 0 | 0.05921 | 5.4528 | 0 | 0 | 219.3334 | 0 | off_peak | 768.18 |  |  | 0 | 0 | 100 | 0 | 0
2402 | 724.5 | 0 | 23.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 724.5 | 0 | 0.05921 | 5.4418 | 0 | 0 | 219.3334 | 0 | off_peak | 724.5 |  |  | 0 | 0 | 100 | 0 | 0
2403 | 649.39 | 0 | 23.4 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 19.0375 | 661.7889 | 0 | 0.05921 | 5.1234 | 0 | 0 | 219.3334 | 0 | off_peak | 649.39 | 0 | 100 | 0 | 0 | 100 | 0 | 0
2404 | 629.87 | 0 | 23.4 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 30.6357 | 642.2689 | 0 | 0.05921 | 4.6756 | 0 | 0 | 219.3334 | 0 | off_peak | 629.87 | 0 | 100 | 0 | 0 | 100 | 0 | 0
2405 | 657.05 | 0 | 23.5 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 42.2338 | 669.4489 | 0 | 0.05921 | 3.9918 | 0 | 0 | 219.3334 | 0 | off_peak | 657.05 | 0 | 100 | 0 | 0 | 100 | 0 | 0
2406 | 727.61 | 0 | 23.6 | 0 | 0 | 0 | 0 | 8.7263 | 8.7263 | 0 | 0 | 0 | 50.3966 | 736.3363 | 0 | 0.05921 | 3.4148 | 0 | 0 | 219.3334 | 0 | off_peak | 727.61 | 0 | 100 | 0 | 0 | 100 | 0 | 0
2407 | 743.75 | 57.4715 | 24.4 | 11.6631 | 0 | 0 | 11.6631 | 12.3989 | 0.73582 | 0 | 0 | 0 | 61.9947 | 744.4858 | 0 | 0.05921 | 3.1246 | 0 | 0 | 230.2432 | 0 | off_peak | 743.75 | 94.07 | 5.93 | 0 | 0 | 100 | 0 | 0
2408 | 792.14 | 266.144 | 25.3 | 53.836 | 53.836 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 73.5928 | 750.703 | 0 | 0.05921 | 2.9303 | 0 | 0 | 230.2432 | 53.836 | off_peak | 738.304 | 0 | 100 | 6.8 | 0 | 93.2 | 157.7534 | 0
2409 | 845.56 | 444.36 | 25.8 | 89.7237 | 89.7237 | 0 | 0 | 0.80079 | 0.80079 | 0 | 0 | 0 | 74.3419 | 756.637 | 0 | 0.05921 | 2.8139 | 0 | 0 | 230.2432 | 89.7237 | off_peak | 755.8363 | 0 | 100 | 10.61 | 0 | 89.39 | 252.4771 | 0
2410 | 828.52 | 581.609 | 26.3 | 117.2246 | 117.2246 | 0 | 0 | 0.05172 | 0.05172 | 0 | 0 | 0 | 74.3903 | 711.3471 | 0 | 0.05921 | 2.8497 | 0 | 0 | 230.2432 | 117.2246 | off_peak | 711.2954 | 0 | 100 | 14.15 | 0 | 85.85 | 334.0512 | 0
2411 | 817.92 | 709.021 | 26.8 | 142.6464 | 142.6464 | 0 | 0 | 0.0033404 | 0.0033404 | 0 | 0 | 0 | 74.3934 | 675.277 | 0 | 0.05921 | 3.1224 | 0 | 0 | 230.2432 | 142.6464 | off_peak | 675.2736 | 0 | 100 | 17.44 | 0 | 82.56 | 445.402 | 0
2412 | 957.79 | 845.486 | 27.2 | 169.8549 | 169.8549 | 0 | 0 | 0.00021574 | 0.00021574 | 0 | 0 | 0 | 74.3936 | 787.9353 | 0 | 0.05921 | 3.6686 | 0 | 0 | 230.2432 | 169.8549 | off_peak | 787.9351 | 0 | 100 | 17.73 | 0 | 82.27 | 623.1254 | 0
2413 | 897.82 | 838.624 | 27.4 | 168.3541 | 168.3541 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 729.4659 | 0 | 0.088511 | 3.9741 | 0 | 0 | 230.2432 | 168.3541 | on_peak | 729.4659 |  |  | 18.75 | 0 | 81.25 | 669.0544 | 0
2414 | 912.03 | 917.337 | 27.5 | 184.0889 | 184.0889 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 727.9411 | 0 | 0.088511 | 3.9034 | 0 | 0 | 230.2432 | 184.0889 | on_peak | 727.9411 |  |  | 20.18 | 0 | 79.82 | 718.5696 | 0
2415 | 902.19 | 817.135 | 27.4 | 164.0402 | 164.0402 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 738.1498 | 0 | 0.088511 | 3.8867 | 0 | 0 | 230.2432 | 164.0402 | on_peak | 738.1498 |  |  | 18.18 | 0 | 81.82 | 637.5713 | 0
2416 | 940.69 | 648.219 | 27.2 | 130.2247 | 130.2247 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 810.4653 | 0 | 0.088511 | 3.9898 | 0 | 0 | 230.2432 | 130.2247 | on_peak | 810.4653 |  |  | 13.84 | 0 | 86.16 | 519.567 | 0
2417 | 883.34 | 437.511 | 26.8 | 88.0219 | 88.0219 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 795.3181 | 0 | 0.088511 | 4.1612 | 0 | 0 | 230.2432 | 88.0219 | on_peak | 795.3181 |  |  | 9.96 | 0 | 90.04 | 366.2753 | 0
2418 | 902.99 | 208.869 | 26.3 | 42.098 | 42.098 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 860.892 | 0 | 0.088511 | 4.2641 | 0 | 0 | 230.2432 | 42.098 | on_peak | 860.892 |  |  | 4.66 | 0 | 95.34 | 179.5097 | 0
2419 | 839.26 | 23.1574 | 25.9 | 4.6742 | 4.6742 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 834.5858 | 0 | 0.088511 | 4.3009 | 0 | 0 | 230.2432 | 4.6742 | on_peak | 834.5858 |  |  | 0.56 | 0 | 99.44 | 20.1032 | 0
2420 | 864.74 | 0 | 25.4 | 0 | 0 | 0 | 0 | 0 | 0 | 62.63 | 62.63 | 0 | 7.4394 | 802.11 | 0 | 0.088511 | 4.4412 | 0 | 0 | 230.2432 | 0 | on_peak | 802.11 |  |  | 0 | 7.24 | 92.76 | 0 | 0
2421 | 881.11 | 0 | 25.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 881.11 | 0 | 0.088511 | 4.5776 | 0 | 0 | 230.2432 | 0 | on_peak | 881.11 |  |  | 0 | 0 | 100 | 0 | 0
2422 | 842.53 | 0 | 25.2 | 0 | 0 | 0 | 0 | 8.7263 | 8.7263 | 0 | 0 | 0 | 15.6021 | 851.2563 | 0 | 0.05921 | 4.8315 | 0 | 0 | 230.2432 | 0 | off_peak | 842.53 | 0 | 100 | 0 | 0 | 100 | 0 | 0
2423 | 859.27 | 0 | 25.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15.6021 | 859.27 | 0 | 0.05921 | 5.0286 | 0 | 0 | 230.2432 | 0 | off_peak | 859.27 |  |  | 0 | 0 | 100 | 0 | 0
2424 | 811.26 | 0 | 25.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15.6021 | 811.26 | 0 | 0.05921 | 5.2783 | 0 | 0 | 230.2432 | 0 | off_peak | 811.26 |  |  | 0 | 0 | 100 | 0 | 0
2425 | 816.96 | 0 | 25.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15.6021 | 816.96 | 0 | 0.05921 | 5.5411 | 0 | 0 | 230.2432 | 0 | off_peak | 816.96 |  |  | 0 | 0 | 100 | 0 | 0
2426 | 723.74 | 0 | 24.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15.6021 | 723.74 | 0 | 0.05921 | 5.5665 | 0 | 0 | 230.2432 | 0 | off_peak | 723.74 |  |  | 0 | 0 | 100 | 0 | 0
2427 | 702.4 | 0 | 24.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15.6021 | 702.4 | 0 | 0.05921 | 5.265 | 0 | 0 | 230.2432 | 0 | off_peak | 702.4 |  |  | 0 | 0 | 100 | 0 | 0
2428 | 658.52 | 0 | 24.6 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 27.2003 | 670.9189 | 0 | 0.05921 | 4.7446 | 0 | 0 | 230.2432 | 0 | off_peak | 658.52 | 0 | 100 | 0 | 0 | 100 | 0 | 0
2429 | 686.44 | 0 | 24.5 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 38.7984 | 698.8389 | 0 | 0.05921 | 3.9943 | 0 | 0 | 230.2432 | 0 | off_peak | 686.44 | 0 | 100 | 0 | 0 | 100 | 0 | 0
2430 | 721.43 | 0 | 24.7 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 50.3966 | 733.8289 | 0 | 0.05921 | 3.4744 | 0 | 0 | 230.2432 | 0 | off_peak | 721.43 | 0 | 100 | 0 | 0 | 100 | 0 | 0
2431 | 810.58 | 27.4527 | 25.3 | 5.5532 | 0 | 0 | 5.5532 | 12.3989 | 6.8458 | 0 | 0 | 0 | 61.9947 | 817.4258 | 0 | 0.05921 | 3.1767 | 0 | 0 | 235.4378 | 0 | off_peak | 810.58 | 44.79 | 55.21 | 0 | 0 | 100 | 0 | 0
2432 | 878.2 | 122.888 | 26.1 | 24.7863 | 12.3873 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 0 | 73.5928 | 865.8127 | 0 | 0.05921 | 3.0682 | 0 | 0 | 247.0359 | 12.3873 | off_peak | 865.8127 | 100 | 0 | 1.41 | 0 | 98.59 | 38.0068 | 0
2433 | 854.68 | 320.282 | 26.5 | 64.5069 | 64.5069 | 0 | 0 | 0.80079 | 0.80079 | 0 | 0 | 0 | 74.3419 | 790.9739 | 0 | 0.05921 | 2.9871 | 0 | 0 | 247.0359 | 64.5069 | off_peak | 790.1731 | 0 | 100 | 7.55 | 0 | 92.45 | 192.6893 | 0
2434 | 852.19 | 581.828 | 26.9 | 117.0143 | 116.9626 | 0 | 0.05172 | 0.05172 | 0 | 0 | 0 | 0 | 74.3903 | 735.2274 | 0 | 0.05921 | 3.0524 | 0 | 0 | 247.0843 | 116.9626 | off_peak | 735.2274 | 100 | 0 | 13.72 | 0 | 86.28 | 357.0218 | 0
2435 | 815.36 | 644.788 | 27.2 | 129.5355 | 129.5355 | 0 | 0 | 0.0033404 | 0.0033404 | 0 | 0 | 0 | 74.3934 | 685.8279 | 0 | 0.05921 | 3.3366 | 0 | 0 | 247.0843 | 129.5355 | off_peak | 685.8245 | 0 | 100 | 15.89 | 0 | 84.11 | 432.2066 | 0
2436 | 863.24 | 679.158 | 27.5 | 136.2917 | 136.2917 | 0 | 0 | 0.00021574 | 0.00021574 | 0 | 0 | 0 | 74.3936 | 726.9485 | 0 | 0.05921 | 3.8156 | 0 | 0 | 247.0843 | 136.2917 | off_peak | 726.9483 | 0 | 100 | 15.79 | 0 | 84.21 | 520.0356 | 0
2437 | 813.24 | 817.879 | 27.6 | 164.0703 | 164.0703 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 649.1697 | 0 | 0.088511 | 4.1184 | 0 | 0 | 247.0843 | 164.0703 | on_peak | 649.1697 |  |  | 20.17 | 0 | 79.83 | 675.7033 | 0
2438 | 856.88 | 915.574 | 27.7 | 183.6016 | 183.6016 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 673.2784 | 0 | 0.088511 | 4.2454 | 0 | 0 | 247.0843 | 183.6016 | on_peak | 673.2784 |  |  | 21.43 | 0 | 78.57 | 779.4655 | 0
2439 | 866.31 | 806.161 | 27.6 | 161.7196 | 161.7196 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 704.5904 | 0 | 0.088511 | 4.2787 | 0 | 0 | 247.0843 | 161.7196 | on_peak | 704.5904 |  |  | 18.67 | 0 | 81.33 | 691.9426 | 0
2440 | 836.9 | 623.684 | 27.5 | 125.1593 | 125.1593 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 711.7407 | 0 | 0.088511 | 4.4074 | 0 | 0 | 247.0843 | 125.1593 | on_peak | 711.7407 |  |  | 14.96 | 0 | 85.04 | 551.6226 | 0
2441 | 844.49 | 371.775 | 27.2 | 74.6882 | 74.6882 | 0 | 0 | 0 | 0 | 62.63 | 62.63 | 0 | 7.4394 | 707.1718 | 0 | 0.088511 | 4.5136 | 0 | 0 | 247.0843 | 74.6882 | on_peak | 707.1718 |  |  | 8.84 | 7.42 | 83.74 | 337.1135 | 0
2442 | 803.8 | 207.469 | 26.6 | 41.7705 | 41.7705 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 762.0295 | 0 | 0.088511 | 4.5071 | 0 | 0 | 247.0843 | 41.7705 | on_peak | 762.0295 |  |  | 5.2 | 0 | 94.8 | 188.2649 | 0
2443 | 801.3 | 23.0567 | 26.3 | 4.6471 | 4.6471 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 796.6529 | 0 | 0.088511 | 4.7201 | 0 | 0 | 247.0843 | 4.6471 | on_peak | 796.6529 |  |  | 0.58 | 0 | 99.42 | 21.9351 | 0
2444 | 773.15 | 0 | 25.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 773.15 | 0 | 0.088511 | 4.7434 | 0 | 0 | 247.0843 | 0 | on_peak | 773.15 |  |  | 0 | 0 | 100 | 0 | 0
2445 | 803.43 | 0 | 25.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 803.43 | 0 | 0.088511 | 4.7344 | 0 | 0 | 247.0843 | 0 | on_peak | 803.43 |  |  | 0 | 0 | 100 | 0 | 0
2446 | 762.26 | 0 | 25.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 762.26 | 0 | 0.05921 | 4.8321 | 0 | 0 | 247.0843 | 0 | off_peak | 762.26 |  |  | 0 | 0 | 100 | 0 | 0
2447 | 797.55 | 0 | 25.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 797.55 | 0 | 0.05921 | 4.9288 | 0 | 0 | 247.0843 | 0 | off_peak | 797.55 |  |  | 0 | 0 | 100 | 0 | 0
2448 | 751.72 | 0 | 25.2 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 19.0375 | 764.1189 | 0 | 0.05921 | 5.1431 | 0 | 0 | 247.0843 | 0 | off_peak | 751.72 | 0 | 100 | 0 | 0 | 100 | 0 | 0
2449 | 707.62 | 0 | 25.2 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 30.6357 | 720.0189 | 0 | 0.05921 | 5.2731 | 0 | 0 | 247.0843 | 0 | off_peak | 707.62 | 0 | 100 | 0 | 0 | 100 | 0 | 0
2450 | 612.24 | 0 | 25.1 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 42.2338 | 624.6389 | 0 | 0.05921 | 5.3298 | 0 | 0 | 247.0843 | 0 | off_peak | 612.24 | 0 | 100 | 0 | 0 | 100 | 0 | 0
2451 | 578.92 | 0 | 25 | 0 | 0 | 0 | 0 | 8.7263 | 8.7263 | 0 | 0 | 0 | 50.3966 | 587.6463 | 0 | 0.05921 | 5.0828 | 0 | 0 | 247.0843 | 0 | off_peak | 578.92 | 0 | 100 | 0 | 0 | 100 | 0 | 0
2452 | 575.64 | 0 | 25 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 61.9947 | 588.0389 | 0 | 0.05921 | 4.639 | 0 | 0 | 247.0843 | 0 | off_peak | 575.64 | 0 | 100 | 0 | 0 | 100 | 0 | 0
2453 | 590.47 | 0 | 24.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 61.9947 | 590.47 | 0 | 0.05921 | 3.995 | 0 | 0 | 247.0843 | 0 | off_peak | 590.47 |  |  | 0 | 0 | 100 | 0 | 0
2454 | 714.38 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 61.9947 | 714.38 | 0 | 0.05921 | 3.4343 | 0 | 0 | 247.0843 | 0 | off_peak | 714.38 |  |  | 0 | 0 | 100 | 0 | 0
2455 | 773.33 | 60.4583 | 25.5 | 12.2208 | 12.2208 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 73.5928 | 773.5082 | 0 | 0.05921 | 3.1862 | 0 | 0 | 247.0843 | 12.2208 | off_peak | 761.1092 | 0 | 100 | 1.58 | 0 | 98.42 | 38.9384 | 0
2456 | 782.34 | 241.608 | 26.1 | 48.7319 | 48.7319 | 0 | 0 | 0.80079 | 0.80079 | 0 | 0 | 0 | 74.3419 | 734.4089 | 0 | 0.05921 | 3.1016 | 0 | 0 | 247.0843 | 48.7319 | off_peak | 733.6081 | 0 | 100 | 6.23 | 0 | 93.77 | 151.145 | 0
2457 | 872.69 | 488.042 | 26.6 | 98.2593 | 98.2593 | 0 | 0 | 0.05172 | 0.05172 | 0 | 0 | 0 | 74.3903 | 774.4825 | 0 | 0.05921 | 3.018 | 0 | 0 | 247.0843 | 98.2593 | off_peak | 774.4307 | 0 | 100 | 11.26 | 0 | 88.74 | 296.5477 | 0
2458 | 851.15 | 493.601 | 27 | 99.2345 | 99.2345 | 0 | 0 | 0.0033404 | 0.0033404 | 0 | 0 | 0 | 74.3934 | 751.9188 | 0 | 0.05921 | 3.038 | 0 | 0 | 247.0843 | 99.2345 | off_peak | 751.9155 | 0 | 100 | 11.66 | 0 | 88.34 | 301.4787 | 0
2459 | 796.87 | 377.83 | 27.5 | 75.822 | 75.822 | 0 | 0 | 0.00021574 | 0.00021574 | 0 | 0 | 0 | 74.3936 | 721.0482 | 0 | 0.05921 | 3.2946 | 0 | 0 | 247.0843 | 75.822 | off_peak | 721.048 | 0 | 100 | 9.51 | 0 | 90.49 | 249.7995 | 0
2460 | 871.71 | 522.219 | 27.9 | 104.6453 | 104.6453 | 0 | 0 | 1.3934e-05 | 1.3934e-05 | 0 | 0 | 0 | 74.3936 | 767.0647 | 0 | 0.05921 | 3.7863 | 0 | 0 | 247.0843 | 104.6453 | off_peak | 767.0647 | 0 | 100 | 12 | 0 | 88 | 396.2194 | 0
2461 | 829.93 | 662.746 | 28.2 | 132.66 | 132.66 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 697.27 | 0 | 0.088511 | 4.0758 | 0 | 0 | 247.0843 | 132.66 | on_peak | 697.27 |  |  | 15.98 | 0 | 84.02 | 540.6926 | 0
2462 | 851.41 | 599.597 | 28.4 | 119.9322 | 119.9322 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 731.4778 | 0 | 0.088511 | 4.2969 | 0 | 0 | 247.0843 | 119.9322 | on_peak | 731.4778 |  |  | 14.09 | 0 | 85.91 | 515.3338 | 0
2463 | 866.55 | 712.359 | 28.4 | 142.487 | 142.487 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 724.063 | 0 | 0.088511 | 4.4812 | 0 | 0 | 247.0843 | 142.487 | on_peak | 724.063 |  |  | 16.44 | 0 | 83.56 | 638.5199 | 0
2464 | 882.03 | 544.365 | 28.3 | 108.9243 | 108.9243 | 0 | 0 | 0 | 0 | 62.63 | 62.63 | 0 | 7.4394 | 710.4757 | 0 | 0.088511 | 4.5126 | 0 | 0 | 247.0843 | 108.9243 | on_peak | 710.4757 |  |  | 12.35 | 7.1 | 80.55 | 491.5331 | 0
2465 | 833.72 | 359.068 | 28 | 71.926 | 71.926 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 761.794 | 0 | 0.088511 | 4.8276 | 0 | 0 | 247.0843 | 71.926 | on_peak | 761.794 |  |  | 8.63 | 0 | 91.37 | 347.2265 | 0
2466 | 811.65 | 184.857 | 27.4 | 37.1101 | 37.1101 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 774.5399 | 0 | 0.088511 | 5.166 | 0 | 0 | 247.0843 | 37.1101 | on_peak | 774.5399 |  |  | 4.57 | 0 | 95.43 | 191.7122 | 0
2467 | 743.42 | 18.1311 | 27 | 3.6451 | 3.6451 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 739.7749 | 0 | 0.088511 | 5.5774 | 0 | 0 | 247.0843 | 3.6451 | on_peak | 739.7749 |  |  | 0.49 | 0 | 99.51 | 20.3302 | 0
2468 | 787.93 | 0 | 26.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 787.93 | 0 | 0.088511 | 5.7291 | 0 | 0 | 247.0843 | 0 | on_peak | 787.93 |  |  | 0 | 0 | 100 | 0 | 0
2469 | 735.22 | 0 | 25.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 735.22 | 0 | 0.088511 | 5.9705 | 0 | 0 | 247.0843 | 0 | on_peak | 735.22 |  |  | 0 | 0 | 100 | 0 | 0
2470 | 743.23 | 0 | 25.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 743.23 | 0 | 0.05921 | 6.1252 | 0 | 0 | 247.0843 | 0 | off_peak | 743.23 |  |  | 0 | 0 | 100 | 0 | 0
2471 | 750.62 | 0 | 25.4 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 19.0375 | 763.0189 | 0 | 0.05921 | 5.9857 | 0 | 0 | 247.0843 | 0 | off_peak | 750.62 | 0 | 100 | 0 | 0 | 100 | 0 | 0
2472 | 719.97 | 0 | 25.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19.0375 | 719.97 | 0 | 0.05921 | 6.0907 | 0 | 0 | 247.0843 | 0 | off_peak | 719.97 |  |  | 0 | 0 | 100 | 0 | 0
2473 | 729.26 | 0 | 25.1 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 30.6357 | 741.6589 | 0 | 0.05921 | 6.1523 | 0 | 0 | 247.0843 | 0 | off_peak | 729.26 | 0 | 100 | 0 | 0 | 100 | 0 | 0
2474 | 671.05 | 0 | 25.1 | 0 | 0 | 0 | 0 | 8.7263 | 8.7263 | 0 | 0 | 0 | 38.7984 | 679.7763 | 0 | 0.05921 | 6.1258 | 0 | 0 | 247.0843 | 0 | off_peak | 671.05 | 0 | 100 | 0 | 0 | 100 | 0 | 0
2475 | 578.91 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 38.7984 | 578.91 | 0 | 0.05921 | 5.8013 | 0 | 0 | 247.0843 | 0 | off_peak | 578.91 |  |  | 0 | 0 | 100 | 0 | 0
2476 | 578.39 | 0 | 24.9 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 50.3966 | 590.7889 | 0 | 0.05921 | 5.2421 | 0 | 0 | 247.0843 | 0 | off_peak | 578.39 | 0 | 100 | 0 | 0 | 100 | 0 | 0
2477 | 595.1 | 0 | 24.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50.3966 | 595.1 | 0 | 0.05921 | 4.4804 | 0 | 0 | 247.0843 | 0 | off_peak | 595.1 |  |  | 0 | 0 | 100 | 0 | 0
2478 | 656.21 | 0 | 24.8 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 61.9947 | 668.6089 | 0 | 0.05921 | 3.8722 | 0 | 0 | 247.0843 | 0 | off_peak | 656.21 | 0 | 100 | 0 | 0 | 100 | 0 | 0
2479 | 741.95 | 61.6075 | 25.2 | 12.4665 | 12.4665 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 73.5928 | 741.8824 | 0 | 0.05921 | 3.4342 | 0 | 0 | 247.0843 | 12.4665 | off_peak | 729.4835 | 0 | 100 | 1.68 | 0 | 98.32 | 42.8127 | 0
2480 | 766.99 | 264.229 | 25.8 | 53.3523 | 53.3523 | 0 | 0 | 0.80079 | 0.80079 | 0 | 0 | 0 | 74.3419 | 714.4385 | 0 | 0.05921 | 3.2622 | 0 | 0 | 247.0843 | 53.3523 | off_peak | 713.6377 | 0 | 100 | 6.96 | 0 | 93.04 | 174.0483 | 0
2481 | 815.99 | 463.229 | 26.5 | 93.2973 | 93.2973 | 0 | 0 | 0.05172 | 0.05172 | 0 | 0 | 0 | 74.3903 | 722.7444 | 0 | 0.05921 | 3.1453 | 0 | 0 | 247.0843 | 93.2973 | off_peak | 722.6927 | 0 | 100 | 11.43 | 0 | 88.57 | 293.4494 | 0
2482 | 810.64 | 636.34 | 27.3 | 127.7919 | 127.7919 | 0 | 0 | 0.0033404 | 0.0033404 | 0 | 0 | 0 | 74.3934 | 682.8514 | 0 | 0.05921 | 3.1317 | 0 | 0 | 247.0843 | 127.7919 | off_peak | 682.8481 | 0 | 100 | 15.76 | 0 | 84.24 | 400.2113 | 0
2483 | 772.91 | 730.735 | 28.1 | 146.3224 | 146.3224 | 0 | 0 | 0.00021574 | 0.00021574 | 0 | 0 | 0 | 74.3936 | 626.5878 | 0 | 0.05921 | 3.3095 | 0 | 0 | 247.0843 | 146.3224 | off_peak | 626.5876 | 0 | 100 | 18.93 | 0 | 81.07 | 484.2552 | 0
2484 | 823.58 | 776.192 | 28.9 | 154.9721 | 154.9721 | 0 | 0 | 1.3934e-05 | 1.3934e-05 | 0 | 0 | 0 | 74.3936 | 668.6079 | 0 | 0.05921 | 3.7221 | 0 | 0 | 247.0843 | 154.9721 | off_peak | 668.6079 | 0 | 100 | 18.82 | 0 | 81.18 | 576.821 | 0
2485 | 797.09 | 939.417 | 29.5 | 187.1502 | 187.1502 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 609.9398 | 0 | 0.088511 | 4.023 | 0 | 0 | 247.0843 | 187.1502 | on_peak | 609.9398 |  |  | 23.48 | 0 | 76.52 | 752.9079 | 0
2486 | 797.11 | 778.345 | 30 | 154.7778 | 154.7778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 642.3322 | 0 | 0.088511 | 4.2191 | 0 | 0 | 247.0843 | 154.7778 | on_peak | 642.3322 |  |  | 19.42 | 0 | 80.58 | 653.0294 | 0
2487 | 831.99 | 704.381 | 30.1 | 140.0183 | 140.0183 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 691.9717 | 0 | 0.088511 | 4.4209 | 0 | 0 | 247.0843 | 140.0183 | on_peak | 691.9717 |  |  | 16.83 | 0 | 83.17 | 619.007 | 0
2488 | 815.01 | 403.727 | 29.9 | 80.3126 | 80.3126 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 734.6974 | 0 | 0.088511 | 4.6639 | 0 | 0 | 247.0843 | 80.3126 | on_peak | 734.6974 |  |  | 9.85 | 0 | 90.15 | 374.5732 | 0
2489 | 784.85 | 312.462 | 29.4 | 62.2713 | 62.2713 | 0 | 0 | 0 | 0 | 62.63 | 62.63 | 0 | 7.4394 | 659.9487 | 0 | 0.088511 | 5.0644 | 0 | 0 | 247.0843 | 62.2713 | on_peak | 659.9487 |  |  | 7.93 | 7.98 | 84.09 | 315.3672 | 0
2490 | 765.07 | 78.9043 | 28.5 | 15.7768 | 15.7768 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 749.2932 | 0 | 0.088511 | 5.4992 | 0 | 0 | 247.0843 | 15.7768 | on_peak | 749.2932 |  |  | 2.06 | 0 | 97.94 | 86.7593 | 0
2491 | 717.29 | 14.2048 | 28 | 2.8454 | 2.8454 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 714.4446 | 0 | 0.088511 | 5.9818 | 0 | 0 | 247.0843 | 2.8454 | on_peak | 714.4446 |  |  | 0.4 | 0 | 99.6 | 17.0206 | 0
2492 | 733.03 | 0 | 27.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 733.03 | 0 | 0.088511 | 6.2587 | 0 | 0 | 247.0843 | 0 | on_peak | 733.03 |  |  | 0 | 0 | 100 | 0 | 0
2493 | 706.84 | 0 | 26.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 706.84 | 0 | 0.088511 | 6.4961 | 0 | 0 | 247.0843 | 0 | on_peak | 706.84 |  |  | 0 | 0 | 100 | 0 | 0
2494 | 728.4 | 0 | 26.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 728.4 | 0 | 0.05921 | 6.5883 | 0 | 0 | 247.0843 | 0 | off_peak | 728.4 |  |  | 0 | 0 | 100 | 0 | 0
2495 | 711.05 | 0 | 25.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 711.05 | 0 | 0.05921 | 6.6967 | 0 | 0 | 247.0843 | 0 | off_peak | 711.05 |  |  | 0 | 0 | 100 | 0 | 0
2496 | 727.15 | 0 | 25.7 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 19.0375 | 739.5489 | 0 | 0.05921 | 6.7956 | 0 | 0 | 247.0843 | 0 | off_peak | 727.15 | 0 | 100 | 0 | 0 | 100 | 0 | 0
2497 | 678.8 | 0 | 25.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19.0375 | 678.8 | 0 | 0.05921 | 6.9013 | 0 | 0 | 247.0843 | 0 | off_peak | 678.8 |  |  | 0 | 0 | 100 | 0 | 0
2498 | 598.14 | 0 | 25.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19.0375 | 598.14 | 0 | 0.05921 | 6.7714 | 0 | 0 | 247.0843 | 0 | off_peak | 598.14 |  |  | 0 | 0 | 100 | 0 | 0
2499 | 549.95 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19.0375 | 549.95 | 0 | 0.05921 | 6.2743 | 0 | 0 | 247.0843 | 0 | off_peak | 549.95 |  |  | 0 | 0 | 100 | 0 | 0
2500 | 556.56 | 0 | 24.9 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 30.6357 | 568.9589 | 0 | 0.05921 | 5.6992 | 0 | 0 | 247.0843 | 0 | off_peak | 556.56 | 0 | 100 | 0 | 0 | 100 | 0 | 0
2501 | 570.63 | 0 | 24.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30.6357 | 570.63 | 0 | 0.05921 | 4.8693 | 0 | 0 | 247.0843 | 0 | off_peak | 570.63 |  |  | 0 | 0 | 100 | 0 | 0
2502 | 637.69 | 0 | 24.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30.6357 | 637.69 | 0 | 0.05921 | 4.3474 | 0 | 0 | 247.0843 | 0 | off_peak | 637.69 |  |  | 0 | 0 | 100 | 0 | 0
2503 | 720.39 | 30.6102 | 25.1 | 6.1963 | 0 | 0 | 6.1963 | 12.3989 | 6.2026 | 0 | 0 | 0 | 42.2338 | 726.5926 | 0 | 0.05921 | 3.9221 | 0 | 0 | 252.8804 | 0 | off_peak | 720.39 | 49.97 | 50.03 | 0 | 0 | 100 | 0 | 0
2504 | 681.46 | 190.146 | 26 | 38.3659 | 38.3659 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 42.2338 | 643.0941 | 0 | 0.05921 | 3.6885 | 0 | 0 | 252.8804 | 38.3659 | off_peak | 643.0941 |  |  | 5.63 | 0 | 94.37 | 141.5124 | 0
2505 | 702.71 | 323.641 | 27.1 | 65.0418 | 65.0418 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 42.2338 | 637.6682 | 0 | 0.05921 | 3.4966 | 0 | 0 | 252.8804 | 65.0418 | off_peak | 637.6682 |  |  | 9.26 | 0 | 90.74 | 227.4281 | 0
2506 | 699.73 | 391.891 | 28 | 78.5009 | 78.5009 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 42.2338 | 621.2291 | 0 | 0.05921 | 3.3807 | 0 | 0 | 252.8804 | 78.5009 | off_peak | 621.2291 |  |  | 11.22 | 0 | 88.78 | 265.3903 | 0
2507 | 694.38 | 466.863 | 28.7 | 93.2805 | 93.2805 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 42.2338 | 601.0995 | 0 | 0.05921 | 3.3708 | 0 | 0 | 252.8804 | 93.2805 | off_peak | 601.0995 |  |  | 13.43 | 0 | 86.57 | 314.431 | 0
2508 | 715.52 | 684.097 | 29.3 | 136.3852 | 136.3852 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 42.2338 | 579.1348 | 0 | 0.05921 | 3.5195 | 0 | 0 | 252.8804 | 136.3852 | off_peak | 579.1348 |  |  | 19.06 | 0 | 80.94 | 480.0078 | 0
2509 | 661.14 | 767.339 | 29.7 | 152.757 | 152.757 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 42.2338 | 508.383 | 0 | 0.05921 | 3.6783 | 0 | 0 | 252.8804 | 152.757 | off_peak | 508.383 |  |  | 23.11 | 0 | 76.89 | 561.8824 | 0
2510 | 642.53 | 181.228 | 29.9 | 36.0513 | 36.0513 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 42.2338 | 606.4787 | 0 | 0.05921 | 3.9948 | 0 | 0 | 252.8804 | 36.0513 | off_peak | 606.4787 |  |  | 5.61 | 0 | 94.39 | 144.0178 | 0
2511 | 689.79 | 227.625 | 30 | 45.2644 | 45.2644 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 42.2338 | 644.5256 | 0 | 0.05921 | 4.3036 | 0 | 0 | 252.8804 | 45.2644 | off_peak | 644.5256 |  |  | 6.56 | 0 | 93.44 | 194.7991 | 0
2512 | 662.83 | 500.496 | 29.9 | 99.5626 | 99.5626 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 42.2338 | 563.2674 | 0 | 0.05921 | 4.71 | 0 | 0 | 252.8804 | 99.5626 | off_peak | 563.2674 |  |  | 15.02 | 0 | 84.98 | 468.9382 | 0
2513 | 670.66 | 81.6799 | 29.6 | 16.2663 | 16.2663 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 42.2338 | 654.3937 | 0 | 0.05921 | 5.2421 | 0 | 0 | 252.8804 | 16.2663 | off_peak | 654.3937 |  |  | 2.43 | 0 | 97.57 | 85.2696 | 0
2514 | 632.73 | 44.9093 | 29 | 8.9632 | 8.9632 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 42.2338 | 623.7668 | 0 | 0.05921 | 5.7883 | 0 | 0 | 252.8804 | 8.9632 | off_peak | 623.7668 |  |  | 1.42 | 0 | 98.58 | 51.8812 | 0
2515 | 608.01 | 7.6 | 28.6 | 1.5191 | 0 | 0 | 1.5191 | 1.5191 | 0 | 0 | 0 | 0 | 43.6548 | 608.01 | 0 | 0.05921 | 6.2443 | 0 | 0 | 254.3014 | 0 | off_peak | 608.01 | 100 | 0 | 0 | 0 | 100 | 0 | 0
2516 | 608.31 | 0 | 27.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 43.6548 | 608.31 | 0 | 0.05921 | 6.7467 | 0 | 0 | 254.3014 | 0 | off_peak | 608.31 |  |  | 0 | 0 | 100 | 0 | 0
2517 | 594.57 | 0 | 26.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 43.6548 | 594.57 | 0 | 0.05921 | 7.101 | 0 | 0 | 254.3014 | 0 | off_peak | 594.57 |  |  | 0 | 0 | 100 | 0 | 0
2518 | 543.93 | 0 | 26.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 43.6548 | 543.93 | 0 | 0.05921 | 7.3343 | 0 | 0 | 254.3014 | 0 | off_peak | 543.93 |  |  | 0 | 0 | 100 | 0 | 0
2519 | 529.49 | 0 | 25.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 43.6548 | 529.49 | 0 | 0.05921 | 7.4876 | 0 | 0 | 254.3014 | 0 | off_peak | 529.49 |  |  | 0 | 0 | 100 | 0 | 0
2520 | 545.3 | 0 | 24.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 43.6548 | 545.3 | 0 | 0.05921 | 7.6233 | 0 | 0 | 254.3014 | 0 | off_peak | 545.3 |  |  | 0 | 0 | 100 | 0 | 0
2521 | 492.5 | 0 | 24.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 43.6548 | 492.5 | 0 | 0.05921 | 7.3131 | 0 | 0 | 254.3014 | 0 | off_peak | 492.5 |  |  | 0 | 0 | 100 | 0 | 0
2522 | 542.13 | 0 | 23.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 43.6548 | 542.13 | 0 | 0.05921 | 6.9723 | 0 | 0 | 254.3014 | 0 | off_peak | 542.13 |  |  | 0 | 0 | 100 | 0 | 0
2523 | 503.65 | 0 | 23.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 43.6548 | 503.65 | 0 | 0.05921 | 6.6138 | 0 | 0 | 254.3014 | 0 | off_peak | 503.65 |  |  | 0 | 0 | 100 | 0 | 0
2524 | 547.75 | 0 | 23.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 43.6548 | 547.75 | 0 | 0.05921 | 6.1346 | 0 | 0 | 254.3014 | 0 | off_peak | 547.75 |  |  | 0 | 0 | 100 | 0 | 0
2525 | 516.96 | 0 | 23.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 43.6548 | 516.96 | 0 | 0.05921 | 5.4552 | 0 | 0 | 254.3014 | 0 | off_peak | 516.96 |  |  | 0 | 0 | 100 | 0 | 0
2526 | 605.96 | 0 | 23.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 43.6548 | 605.96 | 0 | 0.05921 | 4.8246 | 0 | 0 | 254.3014 | 0 | off_peak | 605.96 |  |  | 0 | 0 | 100 | 0 | 0
2527 | 658.94 | 67.1673 | 23.9 | 13.6552 | 13.6552 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 43.6548 | 645.2848 | 0 | 0.05921 | 4.4158 | 0 | 0 | 254.3014 | 13.6552 | off_peak | 645.2848 |  |  | 2.07 | 0 | 97.93 | 60.2989 | 0
2528 | 702.36 | 270.528 | 24.9 | 54.8016 | 54.8016 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 43.6548 | 647.5584 | 0 | 0.05921 | 4.0924 | 0 | 0 | 254.3014 | 54.8016 | off_peak | 647.5584 |  |  | 7.8 | 0 | 92.2 | 224.2699 | 0
2529 | 676.1 | 487.683 | 25.8 | 98.4714 | 98.4714 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 43.6548 | 577.6286 | 0 | 0.05921 | 3.8265 | 0 | 0 | 254.3014 | 98.4714 | off_peak | 577.6286 |  |  | 14.56 | 0 | 85.44 | 376.7967 | 0
2530 | 680.98 | 610.91 | 26.8 | 122.9076 | 122.9076 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 43.6548 | 558.0724 | 0 | 0.05921 | 3.6645 | 0 | 0 | 254.3014 | 122.9076 | off_peak | 558.0724 |  |  | 18.05 | 0 | 81.95 | 450.3955 | 0
2531 | 683.7 | 828.885 | 27.8 | 166.1573 | 166.1573 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 43.6548 | 517.5427 | 0 | 0.05921 | 3.6005 | 0 | 0 | 254.3014 | 166.1573 | off_peak | 517.5427 |  |  | 24.3 | 0 | 75.7 | 598.2515 | 0
2532 | 688 | 908.665 | 28.6 | 181.62 | 181.62 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 43.6548 | 506.38 | 0 | 0.05921 | 3.6497 | 0 | 0 | 254.3014 | 181.62 | off_peak | 506.38 |  |  | 26.4 | 0 | 73.6 | 662.8626 | 0
2533 | 694.46 | 882.516 | 29.1 | 176.0717 | 176.0717 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 43.6548 | 518.3883 | 0 | 0.05921 | 3.7668 | 0 | 0 | 254.3014 | 176.0717 | off_peak | 518.3883 |  |  | 25.35 | 0 | 74.65 | 663.2347 | 0
2534 | 634.59 | 900.782 | 29.5 | 179.4533 | 179.4533 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 43.6548 | 455.1367 | 0 | 0.05921 | 4.1781 | 0 | 0 | 254.3014 | 179.4533 | off_peak | 455.1367 |  |  | 28.28 | 0 | 71.72 | 749.7826 | 0
2535 | 676.7 | 790.116 | 29.5 | 157.4065 | 157.4065 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 43.6548 | 519.2935 | 0 | 0.05921 | 4.7296 | 0 | 0 | 254.3014 | 157.4065 | off_peak | 519.2935 |  |  | 23.26 | 0 | 76.74 | 744.4651 | 0
2536 | 672.58 | 626.502 | 29.4 | 124.8571 | 124.8571 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 43.6548 | 547.7229 | 0 | 0.05921 | 5.0743 | 0 | 0 | 254.3014 | 124.8571 | off_peak | 547.7229 |  |  | 18.56 | 0 | 81.44 | 633.5618 | 0
2537 | 704.19 | 422.725 | 29.1 | 84.3383 | 84.3383 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 55.2529 | 632.2506 | 0 | 0.05921 | 5.5262 | 0 | 0 | 254.3014 | 84.3383 | off_peak | 619.8517 | 0 | 100 | 11.98 | 0 | 88.02 | 466.0679 | 0
2538 | 609.11 | 204.361 | 28.7 | 40.8319 | 40.8319 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 55.2529 | 568.2781 | 0 | 0.05921 | 6.0009 | 0 | 0 | 254.3014 | 40.8319 | off_peak | 568.2781 |  |  | 6.7 | 0 | 93.3 | 245.029 | 0
2539 | 579.58 | 22.546 | 28.4 | 4.5097 | 4.5097 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 55.2529 | 575.0703 | 0 | 0.05921 | 6.5461 | 0 | 0 | 254.3014 | 4.5097 | off_peak | 575.0703 |  |  | 0.78 | 0 | 99.22 | 29.5207 | 0
2540 | 540.12 | 0 | 27.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 55.2529 | 540.12 | 0 | 0.05921 | 6.9299 | 0 | 0 | 254.3014 | 0 | off_peak | 540.12 |  |  | 0 | 0 | 100 | 0 | 0
2541 | 523.27 | 0 | 27.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 55.2529 | 523.27 | 0 | 0.05921 | 7.1424 | 0 | 0 | 254.3014 | 0 | off_peak | 523.27 |  |  | 0 | 0 | 100 | 0 | 0
2542 | 499.71 | 0 | 26.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 55.2529 | 499.71 | 0 | 0.05921 | 7.3416 | 0 | 0 | 254.3014 | 0 | off_peak | 499.71 |  |  | 0 | 0 | 100 | 0 | 0
2543 | 506.68 | 0 | 26 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 55.2529 | 506.68 | 0 | 0.05921 | 7.4461 | 0 | 0 | 254.3014 | 0 | off_peak | 506.68 |  |  | 0 | 0 | 100 | 0 | 0
2544 | 513.47 | 0 | 25.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 55.2529 | 513.47 | 0 | 0.05921 | 7.3655 | 0 | 0 | 254.3014 | 0 | off_peak | 513.47 |  |  | 0 | 0 | 100 | 0 | 0
2545 | 500.03 | 0 | 24.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 55.2529 | 500.03 | 0 | 0.05921 | 7.1996 | 0 | 0 | 254.3014 | 0 | off_peak | 500.03 |  |  | 0 | 0 | 100 | 0 | 0
2546 | 518.96 | 0 | 24.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 55.2529 | 518.96 | 0 | 0.05921 | 6.8494 | 0 | 0 | 254.3014 | 0 | off_peak | 518.96 |  |  | 0 | 0 | 100 | 0 | 0
2547 | 492.38 | 0 | 23.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 55.2529 | 492.38 | 0 | 0.05921 | 6.3041 | 0 | 0 | 254.3014 | 0 | off_peak | 492.38 |  |  | 0 | 0 | 100 | 0 | 0
2548 | 502.36 | 0 | 23.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 55.2529 | 502.36 | 0 | 0.05921 | 5.6733 | 0 | 0 | 254.3014 | 0 | off_peak | 502.36 |  |  | 0 | 0 | 100 | 0 | 0
2549 | 538.02 | 0 | 23.1 | 0 | 0 | 0 | 0 | 7.2073 | 7.2073 | 0 | 0 | 0 | 61.9947 | 545.2273 | 0 | 0.05921 | 4.8751 | 0 | 0 | 254.3014 | 0 | off_peak | 538.02 | 0 | 100 | 0 | 0 | 100 | 0 | 0
2550 | 608.5 | 0 | 23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 61.9947 | 608.5 | 0 | 0.05921 | 4.1615 | 0 | 0 | 254.3014 | 0 | off_peak | 608.5 |  |  | 0 | 0 | 100 | 0 | 0
2551 | 678.04 | 71.341 | 23.3 | 14.535 | 14.535 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 61.9947 | 663.505 | 0 | 0.05921 | 3.8777 | 0 | 0 | 254.3014 | 14.535 | off_peak | 663.505 |  |  | 2.14 | 0 | 97.86 | 56.3618 | 0
2552 | 730.1 | 277.644 | 24.1 | 56.4051 | 44.0061 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 0 | 73.5928 | 686.0939 | 0 | 0.05921 | 3.6214 | 0 | 0 | 265.8995 | 44.0061 | off_peak | 686.0939 | 100 | 0 | 6.03 | 0 | 93.97 | 159.363 | 0
2553 | 783.61 | 497.059 | 25.2 | 100.582 | 100.582 | 0 | 0 | 0.80079 | 0.80079 | 0 | 0 | 0 | 74.3419 | 683.8288 | 0 | 0.05921 | 3.4511 | 0 | 0 | 265.8995 | 100.582 | off_peak | 683.028 | 0 | 100 | 12.84 | 0 | 87.16 | 347.1141 | 0
2554 | 765.53 | 690.397 | 26.2 | 139.2014 | 139.2014 | 0 | 0 | 0.05172 | 0.05172 | 0 | 0 | 0 | 74.3903 | 626.3803 | 0 | 0.05921 | 3.4006 | 0 | 0 | 265.8995 | 139.2014 | off_peak | 626.3286 | 0 | 100 | 18.18 | 0 | 81.82 | 473.3703 | 0
2555 | 743.87 | 839.222 | 27.1 | 168.6577 | 168.6577 | 0 | 0 | 0.0033404 | 0.0033404 | 0 | 0 | 0 | 74.3934 | 575.2157 | 0 | 0.05921 | 3.5994 | 0 | 0 | 265.8995 | 168.6577 | off_peak | 575.2123 | 0 | 100 | 22.67 | 0 | 77.33 | 607.0608 | 0
2556 | 804.47 | 927.606 | 27.9 | 185.8792 | 185.8792 | 0 | 0 | 0.00021574 | 0.00021574 | 0 | 0 | 0 | 74.3936 | 618.5911 | 0 | 0.05921 | 4.0271 | 0 | 0 | 265.8995 | 185.8792 | off_peak | 618.5908 | 0 | 100 | 23.11 | 0 | 76.89 | 748.5607 | 0
2557 | 753.46 | 948.502 | 28.6 | 189.5824 | 189.5824 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 563.8776 | 0 | 0.088511 | 4.3354 | 0 | 0 | 265.8995 | 189.5824 | on_peak | 563.8776 |  |  | 25.16 | 0 | 74.84 | 821.9248 | 0
2558 | 820.09 | 902.941 | 29.1 | 180.1468 | 180.1468 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 639.9432 | 0 | 0.088511 | 4.467 | 0 | 0 | 265.8995 | 180.1468 | on_peak | 639.9432 |  |  | 21.97 | 0 | 78.03 | 804.7234 | 0
2559 | 869.79 | 792.826 | 29.4 | 158.0042 | 158.0042 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 711.7858 | 0 | 0.088511 | 4.6037 | 0 | 0 | 265.8995 | 158.0042 | on_peak | 711.7858 |  |  | 18.17 | 0 | 81.83 | 727.3986 | 0
2560 | 811.4 | 629.058 | 29.5 | 125.3206 | 125.3206 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 686.0794 | 0 | 0.088511 | 4.7024 | 0 | 0 | 265.8995 | 125.3206 | on_peak | 686.0794 |  |  | 15.44 | 0 | 84.56 | 589.3057 | 0
2561 | 852.78 | 399.046 | 29.2 | 79.585 | 79.585 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 773.195 | 0 | 0.088511 | 4.9192 | 0 | 0 | 265.8995 | 79.585 | on_peak | 773.195 |  |  | 9.33 | 0 | 90.67 | 391.4983 | 0
2562 | 853.87 | 180.421 | 28.4 | 36.0881 | 36.0881 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 817.7819 | 0 | 0.088511 | 4.9309 | 0 | 0 | 265.8995 | 36.0881 | on_peak | 817.7819 |  |  | 4.23 | 0 | 95.77 | 177.9453 | 0
2563 | 766.5 | 17.0003 | 27.9 | 3.4066 | 3.4066 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 763.0934 | 0 | 0.088511 | 4.7179 | 0 | 0 | 265.8995 | 3.4066 | on_peak | 763.0934 |  |  | 0.44 | 0 | 99.56 | 16.0722 | 0
2564 | 815.05 | 0 | 26.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 815.05 | 0 | 0.088511 | 4.6502 | 0 | 0 | 265.8995 | 0 | on_peak | 815.05 |  |  | 0 | 0 | 100 | 0 | 0
2565 | 820.96 | 0 | 26 | 0 | 0 | 0 | 0 | 0 | 0 | 62.63 | 62.63 | 0 | 7.4394 | 758.33 | 0 | 0.088511 | 4.8674 | 0 | 0 | 265.8995 | 0 | on_peak | 758.33 |  |  | 0 | 7.63 | 92.37 | 0 | 0
2566 | 712.62 | 0 | 25.3 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 19.0375 | 725.0189 | 0 | 0.05921 | 5.2589 | 0 | 0 | 265.8995 | 0 | off_peak | 712.62 | 0 | 100 | 0 | 0 | 100 | 0 | 0
2567 | 803.32 | 0 | 24.7 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 30.6357 | 815.7189 | 0 | 0.05921 | 5.6452 | 0 | 0 | 265.8995 | 0 | off_peak | 803.32 | 0 | 100 | 0 | 0 | 100 | 0 | 0
2568 | 773.42 | 0 | 24.1 | 0 | 0 | 0 | 0 | 8.7263 | 8.7263 | 0 | 0 | 0 | 38.7984 | 782.1463 | 0 | 0.05921 | 6.0349 | 0 | 0 | 265.8995 | 0 | off_peak | 773.42 | 0 | 100 | 0 | 0 | 100 | 0 | 0
2569 | 725.89 | 0 | 23.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 38.7984 | 725.89 | 0 | 0.05921 | 6.179 | 0 | 0 | 265.8995 | 0 | off_peak | 725.89 |  |  | 0 | 0 | 100 | 0 | 0
2570 | 645.9 | 0 | 23.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 38.7984 | 645.9 | 0 | 0.05921 | 6.1386 | 0 | 0 | 265.8995 | 0 | off_peak | 645.9 |  |  | 0 | 0 | 100 | 0 | 0
2571 | 596.3 | 0 | 22.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 38.7984 | 596.3 | 0 | 0.05921 | 5.7347 | 0 | 0 | 265.8995 | 0 | off_peak | 596.3 |  |  | 0 | 0 | 100 | 0 | 0
2572 | 587.87 | 0 | 21.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 38.7984 | 587.87 | 0 | 0.05921 | 5.1506 | 0 | 0 | 265.8995 | 0 | off_peak | 587.87 |  |  | 0 | 0 | 100 | 0 | 0
2573 | 551.97 | 0 | 21.2 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 50.3966 | 564.3689 | 0 | 0.05921 | 4.4078 | 0 | 0 | 265.8995 | 0 | off_peak | 551.97 | 0 | 100 | 0 | 0 | 100 | 0 | 0
2574 | 642.82 | 0 | 20.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50.3966 | 642.82 | 0 | 0.05921 | 3.6095 | 0 | 0 | 265.8995 | 0 | off_peak | 642.82 |  |  | 0 | 0 | 100 | 0 | 0
2575 | 663.51 | 67.2562 | 20.1 | 13.8596 | 13.8596 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 61.9947 | 662.0493 | 0 | 0.05921 | 3.2063 | 0 | 0 | 265.8995 | 13.8596 | off_peak | 649.6504 | 0 | 100 | 2.09 | 0 | 97.91 | 44.4386 | 0
2576 | 773.6 | 264.669 | 20.4 | 54.483 | 54.483 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 73.5928 | 731.5159 | 0 | 0.05921 | 2.9522 | 0 | 0 | 265.8995 | 54.483 | off_peak | 719.117 | 0 | 100 | 7.04 | 0 | 92.96 | 160.8421 | 0
2577 | 725.61 | 481.026 | 21 | 98.8104 | 98.8104 | 0 | 0 | 0.80079 | 0.80079 | 0 | 0 | 0 | 74.3419 | 627.6004 | 0 | 0.05921 | 2.8306 | 0 | 0 | 265.8995 | 98.8104 | off_peak | 626.7996 | 0 | 100 | 13.62 | 0 | 86.38 | 279.6927 | 0
2578 | 775.65 | 674.15 | 21.8 | 138.088 | 138.088 | 0 | 0 | 0.05172 | 0.05172 | 0 | 0 | 0 | 74.3903 | 637.6137 | 0 | 0.05921 | 2.7738 | 0 | 0 | 265.8995 | 138.088 | off_peak | 637.562 | 0 | 100 | 17.8 | 0 | 82.2 | 383.0309 | 0
2579 | 756.75 | 743.829 | 22.5 | 151.981 | 151.981 | 0 | 0 | 0.0033404 | 0.0033404 | 0 | 0 | 0 | 74.3934 | 604.7723 | 0 | 0.05921 | 2.8615 | 0 | 0 | 265.8995 | 151.981 | off_peak | 604.769 | 0 | 100 | 20.08 | 0 | 79.92 | 434.8976 | 0
2580 | 774.67 | 586.612 | 23.1 | 119.6014 | 119.6014 | 0 | 0 | 0.00021574 | 0.00021574 | 0 | 0 | 0 | 74.3936 | 655.0688 | 0 | 0.05921 | 3.512 | 0 | 0 | 265.8995 | 119.6014 | off_peak | 655.0686 | 0 | 100 | 15.44 | 0 | 84.56 | 420.0404 | 0
2581 | 754.92 | 900.866 | 23.5 | 183.4105 | 183.4105 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 571.5095 | 0 | 0.088511 | 3.722 | 0 | 0 | 265.8995 | 183.4105 | on_peak | 571.5095 |  |  | 24.3 | 0 | 75.7 | 682.6489 | 0
2582 | 774.09 | 881.482 | 23.6 | 179.3997 | 179.3997 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 594.6903 | 0 | 0.088511 | 3.5685 | 0 | 0 | 265.8995 | 179.3997 | on_peak | 594.6903 |  |  | 23.18 | 0 | 76.82 | 640.1859 | 0
2583 | 812.02 | 682.641 | 23.6 | 138.9315 | 138.9315 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 673.0885 | 0 | 0.088511 | 3.2724 | 0 | 0 | 265.8995 | 138.9315 | on_peak | 673.0885 |  |  | 17.11 | 0 | 82.89 | 454.6388 | 0
2584 | 777.86 | 522.992 | 23.3 | 106.554 | 106.554 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 671.306 | 0 | 0.088511 | 3.172 | 0 | 0 | 265.8995 | 106.554 | on_peak | 671.306 |  |  | 13.7 | 0 | 86.3 | 337.9866 | 0
2585 | 789.19 | 86.7342 | 22.9 | 17.6965 | 17.6965 | 0 | 0 | 0 | 0 | 62.63 | 62.63 | 0 | 7.4394 | 708.8636 | 0 | 0.088511 | 3.2868 | 0 | 0 | 265.8995 | 17.6965 | on_peak | 708.8636 |  |  | 2.24 | 7.94 | 89.82 | 58.164 | 0
2586 | 756.42 | 62.1655 | 22.1 | 12.7199 | 12.7199 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 743.7001 | 0 | 0.088511 | 3.562 | 0 | 0 | 265.8995 | 12.7199 | on_peak | 743.7001 |  |  | 1.68 | 0 | 98.32 | 45.3084 | 0
2587 | 715.23 | 13.3 | 21.6 | 2.7262 | 2.7262 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 712.5038 | 0 | 0.088511 | 3.8727 | 0 | 0 | 265.8995 | 2.7262 | on_peak | 712.5038 |  |  | 0.38 | 0 | 99.62 | 10.5578 | 0
2588 | 759.9 | 0 | 20.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 759.9 | 0 | 0.088511 | 4.1315 | 0 | 0 | 265.8995 | 0 | on_peak | 759.9 |  |  | 0 | 0 | 100 | 0 | 0
2589 | 740.84 | 0 | 20.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 740.84 | 0 | 0.088511 | 4.4589 | 0 | 0 | 265.8995 | 0 | on_peak | 740.84 |  |  | 0 | 0 | 100 | 0 | 0
2590 | 706.98 | 0 | 19.8 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 19.0375 | 719.3789 | 0 | 0.05921 | 4.9351 | 0 | 0 | 265.8995 | 0 | off_peak | 706.98 | 0 | 100 | 0 | 0 | 100 | 0 | 0
2591 | 727.08 | 0 | 19.7 | 0 | 0 | 0 | 0 | 8.7263 | 8.7263 | 0 | 0 | 0 | 27.2003 | 735.8063 | 0 | 0.05921 | 5.497 | 0 | 0 | 265.8995 | 0 | off_peak | 727.08 | 0 | 100 | 0 | 0 | 100 | 0 | 0
2592 | 699.09 | 0 | 19.7 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 38.7984 | 711.4889 | 0 | 0.05921 | 6.0801 | 0 | 0 | 265.8995 | 0 | off_peak | 699.09 | 0 | 100 | 0 | 0 | 100 | 0 | 0
2593 | 656.28 | 0 | 19.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 38.7984 | 656.28 | 0 | 0.05921 | 6.2489 | 0 | 0 | 265.8995 | 0 | off_peak | 656.28 |  |  | 0 | 0 | 100 | 0 | 0
2594 | 628.19 | 0 | 19.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 38.7984 | 628.19 | 0 | 0.05921 | 6.1388 | 0 | 0 | 265.8995 | 0 | off_peak | 628.19 |  |  | 0 | 0 | 100 | 0 | 0
2595 | 585.51 | 0 | 19.6 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 50.3966 | 597.9089 | 0 | 0.05921 | 5.7274 | 0 | 0 | 265.8995 | 0 | off_peak | 585.51 | 0 | 100 | 0 | 0 | 100 | 0 | 0
2596 | 545.56 | 0 | 19.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50.3966 | 545.56 | 0 | 0.05921 | 5.1162 | 0 | 0 | 265.8995 | 0 | off_peak | 545.56 |  |  | 0 | 0 | 100 | 0 | 0
2597 | 565.9 | 0 | 19.6 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 61.9947 | 578.2989 | 0 | 0.05921 | 4.339 | 0 | 0 | 265.8995 | 0 | off_peak | 565.9 | 0 | 100 | 0 | 0 | 100 | 0 | 0
2598 | 646.86 | 0 | 19.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 61.9947 | 646.86 | 0 | 0.05921 | 3.647 | 0 | 0 | 265.8995 | 0 | off_peak | 646.86 |  |  | 0 | 0 | 100 | 0 | 0
2599 | 674.69 | 72.5201 | 20.5 | 14.9232 | 14.9232 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 61.9947 | 659.7668 | 0 | 0.05921 | 3.2575 | 0 | 0 | 265.8995 | 14.9232 | off_peak | 659.7668 |  |  | 2.21 | 0 | 97.79 | 48.6125 | 0
2600 | 732.21 | 277.483 | 21.2 | 56.959 | 56.959 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 73.5928 | 687.6499 | 0 | 0.05921 | 3.0092 | 0 | 0 | 265.8995 | 56.959 | off_peak | 675.251 | 0 | 100 | 7.78 | 0 | 92.22 | 171.4033 | 0
2601 | 759.57 | 499.31 | 21.7 | 102.3115 | 102.3115 | 0 | 0 | 0.80079 | 0.80079 | 0 | 0 | 0 | 74.3419 | 658.0593 | 0 | 0.05921 | 2.8781 | 0 | 0 | 265.8995 | 102.3115 | off_peak | 657.2585 | 0 | 100 | 13.47 | 0 | 86.53 | 294.4621 | 0
2602 | 785.04 | 695.243 | 22.2 | 142.2058 | 142.2058 | 0 | 0 | 0.05172 | 0.05172 | 0 | 0 | 0 | 74.3903 | 642.8859 | 0 | 0.05921 | 2.8629 | 0 | 0 | 265.8995 | 142.2058 | off_peak | 642.8342 | 0 | 100 | 18.11 | 0 | 81.89 | 407.1225 | 0
2603 | 757.13 | 844.726 | 22.6 | 172.5349 | 172.5349 | 0 | 0 | 0.0033404 | 0.0033404 | 0 | 0 | 0 | 74.3934 | 584.5984 | 0 | 0.05921 | 3.1031 | 0 | 0 | 265.8995 | 172.5349 | off_peak | 584.5951 | 0 | 100 | 22.79 | 0 | 77.21 | 535.4004 | 0
2604 | 818.07 | 625.592 | 22.9 | 127.6401 | 127.6401 | 0 | 0 | 0.00021574 | 0.00021574 | 0 | 0 | 0 | 74.3936 | 690.4301 | 0 | 0.05921 | 3.5635 | 0 | 0 | 265.8995 | 127.6401 | off_peak | 690.4299 | 0 | 100 | 15.6 | 0 | 84.4 | 454.8502 | 0
2605 | 735.69 | 951.551 | 23.1 | 194.0071 | 194.0071 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 541.6829 | 0 | 0.088511 | 3.8124 | 0 | 0 | 265.8995 | 194.0071 | on_peak | 541.6829 |  |  | 26.37 | 0 | 73.63 | 739.6376 | 0
2606 | 789.82 | 902.437 | 23.2 | 183.9277 | 183.9277 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 605.8923 | 0 | 0.088511 | 3.7882 | 0 | 0 | 265.8995 | 183.9277 | on_peak | 605.8923 |  |  | 23.29 | 0 | 76.71 | 696.7523 | 0
2607 | 828.05 | 715.672 | 23.2 | 145.8627 | 145.8627 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 682.1873 | 0 | 0.088511 | 3.6534 | 0 | 0 | 265.8995 | 145.8627 | on_peak | 682.1873 |  |  | 17.62 | 0 | 82.38 | 532.8902 | 0
2608 | 795.11 | 620.844 | 23.1 | 126.5808 | 126.5808 | 0 | 0 | 0 | 0 | 62.63 | 62.63 | 0 | 7.4394 | 605.8992 | 0 | 0.088511 | 3.662 | 0 | 0 | 265.8995 | 126.5808 | on_peak | 605.8992 |  |  | 15.92 | 7.88 | 76.2 | 463.534 | 0
2609 | 814.66 | 415.096 | 22.8 | 84.7227 | 84.7227 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 729.9373 | 0 | 0.088511 | 3.8644 | 0 | 0 | 265.8995 | 84.7227 | on_peak | 729.9373 |  |  | 10.4 | 0 | 89.6 | 327.4034 | 0
2610 | 789.47 | 197.767 | 22.5 | 40.4082 | 40.4082 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 749.0618 | 0 | 0.088511 | 4.0262 | 0 | 0 | 265.8995 | 40.4082 | on_peak | 749.0618 |  |  | 5.12 | 0 | 94.88 | 162.6935 | 0
2611 | 764.73 | 22.3319 | 22.3 | 4.5662 | 4.5662 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 760.1638 | 0 | 0.088511 | 4.2951 | 0 | 0 | 265.8995 | 4.5662 | on_peak | 760.1638 |  |  | 0.6 | 0 | 99.4 | 19.6119 | 0
2612 | 758.26 | 0 | 21.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 758.26 | 0 | 0.088511 | 4.5318 | 0 | 0 | 265.8995 | 0 | on_peak | 758.26 |  |  | 0 | 0 | 100 | 0 | 0
2613 | 764.15 | 0 | 21.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 764.15 | 0 | 0.088511 | 4.88 | 0 | 0 | 265.8995 | 0 | on_peak | 764.15 |  |  | 0 | 0 | 100 | 0 | 0
2614 | 704.84 | 0 | 21.7 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 19.0375 | 717.2389 | 0 | 0.05921 | 5.3628 | 0 | 0 | 265.8995 | 0 | off_peak | 704.84 | 0 | 100 | 0 | 0 | 100 | 0 | 0
2615 | 725.59 | 0 | 21.7 | 0 | 0 | 0 | 0 | 8.7263 | 8.7263 | 0 | 0 | 0 | 27.2003 | 734.3163 | 0 | 0.05921 | 5.7525 | 0 | 0 | 265.8995 | 0 | off_peak | 725.59 | 0 | 100 | 0 | 0 | 100 | 0 | 0
2616 | 734.97 | 0 | 21.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27.2003 | 734.97 | 0 | 0.05921 | 6.1863 | 0 | 0 | 265.8995 | 0 | off_peak | 734.97 |  |  | 0 | 0 | 100 | 0 | 0
2617 | 693.34 | 0 | 21.8 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 38.7984 | 705.7389 | 0 | 0.05921 | 6.3904 | 0 | 0 | 265.8995 | 0 | off_peak | 693.34 | 0 | 100 | 0 | 0 | 100 | 0 | 0
2618 | 639.66 | 0 | 21.8 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 50.3966 | 652.0589 | 0 | 0.05921 | 6.3206 | 0 | 0 | 265.8995 | 0 | off_peak | 639.66 | 0 | 100 | 0 | 0 | 100 | 0 | 0
2619 | 588.34 | 0 | 21.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50.3966 | 588.34 | 0 | 0.05921 | 5.9353 | 0 | 0 | 265.8995 | 0 | off_peak | 588.34 |  |  | 0 | 0 | 100 | 0 | 0
2620 | 557.03 | 0 | 21.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50.3966 | 557.03 | 0 | 0.05921 | 5.3462 | 0 | 0 | 265.8995 | 0 | off_peak | 557.03 |  |  | 0 | 0 | 100 | 0 | 0
2621 | 582.98 | 0 | 21.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50.3966 | 582.98 | 0 | 0.05921 | 4.4911 | 0 | 0 | 265.8995 | 0 | off_peak | 582.98 |  |  | 0 | 0 | 100 | 0 | 0
2622 | 636 | 0 | 21.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50.3966 | 636 | 0 | 0.05921 | 3.8093 | 0 | 0 | 265.8995 | 0 | off_peak | 636 |  |  | 0 | 0 | 100 | 0 | 0
2623 | 728.97 | 72.2921 | 22.4 | 14.7762 | 14.7762 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 61.9947 | 726.5928 | 0 | 0.05921 | 3.4277 | 0 | 0 | 265.8995 | 14.7762 | off_peak | 714.1938 | 0 | 100 | 2.03 | 0 | 97.97 | 50.648 | 0
2624 | 736.89 | 286.87 | 22.9 | 58.5303 | 58.5303 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 73.5928 | 690.7586 | 0 | 0.05921 | 3.2005 | 0 | 0 | 265.8995 | 58.5303 | off_peak | 678.3597 | 0 | 100 | 7.94 | 0 | 92.06 | 187.3258 | 0
2625 | 764.53 | 507.973 | 23.4 | 103.457 | 103.457 | 0 | 0 | 0.80079 | 0.80079 | 0 | 0 | 0 | 74.3419 | 661.8738 | 0 | 0.05921 | 3.0654 | 0 | 0 | 265.8995 | 103.457 | off_peak | 661.073 | 0 | 100 | 13.53 | 0 | 86.47 | 317.1375 | 0
2626 | 799.26 | 702.105 | 23.9 | 142.7393 | 142.7393 | 0 | 0 | 0.05172 | 0.05172 | 0 | 0 | 0 | 74.3903 | 656.5724 | 0 | 0.05921 | 3.0701 | 0 | 0 | 265.8995 | 142.7393 | off_peak | 656.5207 | 0 | 100 | 17.86 | 0 | 82.14 | 438.2197 | 0
2627 | 751.32 | 694.065 | 24.3 | 140.9023 | 140.9023 | 0 | 0 | 0.0033404 | 0.0033404 | 0 | 0 | 0 | 74.3934 | 610.421 | 0 | 0.05921 | 3.3146 | 0 | 0 | 265.8995 | 140.9023 | off_peak | 610.4177 | 0 | 100 | 18.75 | 0 | 81.25 | 467.0295 | 0
2628 | 819 | 938.19 | 24.6 | 190.2571 | 190.2571 | 0 | 0 | 0.00021574 | 0.00021574 | 0 | 0 | 0 | 74.3936 | 628.7432 | 0 | 0.05921 | 3.8337 | 0 | 0 | 265.8995 | 190.2571 | off_peak | 628.7429 | 0 | 100 | 23.23 | 0 | 76.77 | 729.385 | 0
2629 | 740.19 | 884.843 | 24.7 | 179.3742 | 179.3742 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 560.8158 | 0 | 0.088511 | 4.0011 | 0 | 0 | 265.8995 | 179.3742 | on_peak | 560.8158 |  |  | 24.23 | 0 | 75.77 | 717.7017 | 0
2630 | 794.76 | 776.271 | 24.7 | 157.3646 | 157.3646 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 637.3954 | 0 | 0.088511 | 3.9887 | 0 | 0 | 265.8995 | 157.3646 | on_peak | 637.3954 |  |  | 19.8 | 0 | 80.2 | 627.6854 | 0
2631 | 804.37 | 688.945 | 24.5 | 139.7625 | 139.7625 | 0 | 0 | 0 | 0 | 62.63 | 62.63 | 0 | 7.4394 | 601.9775 | 0 | 0.088511 | 3.9489 | 0 | 0 | 265.8995 | 139.7625 | on_peak | 601.9775 |  |  | 17.38 | 7.79 | 74.84 | 551.9119 | 0
2632 | 805.58 | 593.127 | 24.3 | 120.4109 | 120.4109 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 685.1691 | 0 | 0.088511 | 4.0655 | 0 | 0 | 265.8995 | 120.4109 | on_peak | 685.1691 |  |  | 14.95 | 0 | 85.05 | 489.5357 | 0
2633 | 834.38 | 285.828 | 24 | 58.0885 | 58.0885 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 776.2915 | 0 | 0.088511 | 4.4911 | 0 | 0 | 265.8995 | 58.0885 | on_peak | 776.2915 |  |  | 6.96 | 0 | 93.04 | 260.8826 | 0
2634 | 818.15 | 104.943 | 23.6 | 21.3581 | 21.3581 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 796.7919 | 0 | 0.088511 | 4.9188 | 0 | 0 | 265.8995 | 21.3581 | on_peak | 796.7919 |  |  | 2.61 | 0 | 97.39 | 105.0567 | 0
2635 | 764.47 | 18.3967 | 23.4 | 3.7468 | 3.7468 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 760.7232 | 0 | 0.088511 | 5.1398 | 0 | 0 | 265.8995 | 3.7468 | on_peak | 760.7232 |  |  | 0.49 | 0 | 99.51 | 19.2578 | 0
2636 | 792.24 | 0 | 23.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 792.24 | 0 | 0.088511 | 5.3769 | 0 | 0 | 265.8995 | 0 | on_peak | 792.24 |  |  | 0 | 0 | 100 | 0 | 0
2637 | 745.63 | 0 | 23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 745.63 | 0 | 0.088511 | 5.7109 | 0 | 0 | 265.8995 | 0 | on_peak | 745.63 |  |  | 0 | 0 | 100 | 0 | 0
2638 | 724.39 | 0 | 22.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 724.39 | 0 | 0.05921 | 5.987 | 0 | 0 | 265.8995 | 0 | off_peak | 724.39 |  |  | 0 | 0 | 100 | 0 | 0
2639 | 716.29 | 0 | 22.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 716.29 | 0 | 0.05921 | 6.4292 | 0 | 0 | 265.8995 | 0 | off_peak | 716.29 |  |  | 0 | 0 | 100 | 0 | 0
2640 | 731.39 | 0 | 22.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 731.39 | 0 | 0.05921 | 6.762 | 0 | 0 | 265.8995 | 0 | off_peak | 731.39 |  |  | 0 | 0 | 100 | 0 | 0
2641 | 687.05 | 0 | 22.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 687.05 | 0 | 0.05921 | 6.9511 | 0 | 0 | 265.8995 | 0 | off_peak | 687.05 |  |  | 0 | 0 | 100 | 0 | 0
2642 | 660.79 | 0 | 22.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 660.79 | 0 | 0.05921 | 6.8504 | 0 | 0 | 265.8995 | 0 | off_peak | 660.79 |  |  | 0 | 0 | 100 | 0 | 0
2643 | 601.38 | 0 | 22.8 | 0 | 0 | 0 | 0 | 8.7263 | 8.7263 | 0 | 0 | 0 | 15.6021 | 610.1063 | 0 | 0.05921 | 6.3696 | 0 | 0 | 265.8995 | 0 | off_peak | 601.38 | 0 | 100 | 0 | 0 | 100 | 0 | 0
2644 | 613.41 | 0 | 22.8 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 27.2003 | 625.8089 | 0 | 0.05921 | 5.7607 | 0 | 0 | 265.8995 | 0 | off_peak | 613.41 | 0 | 100 | 0 | 0 | 100 | 0 | 0
2645 | 602.03 | 0 | 22.9 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 38.7984 | 614.4289 | 0 | 0.05921 | 4.9324 | 0 | 0 | 265.8995 | 0 | off_peak | 602.03 | 0 | 100 | 0 | 0 | 100 | 0 | 0
2646 | 649.72 | 0 | 23 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 50.3966 | 662.1189 | 0 | 0.05921 | 4.2795 | 0 | 0 | 265.8995 | 0 | off_peak | 649.72 | 0 | 100 | 0 | 0 | 100 | 0 | 0
2647 | 693.36 | 77.9539 | 23.4 | 15.8766 | 15.8766 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 61.9947 | 689.8824 | 0 | 0.05921 | 3.8344 | 0 | 0 | 265.8995 | 15.8766 | off_peak | 677.4834 | 0 | 100 | 2.29 | 0 | 97.71 | 60.8778 | 0
2648 | 732.88 | 285.878 | 23.9 | 58.1195 | 58.1195 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 73.5928 | 687.1594 | 0 | 0.05921 | 3.5552 | 0 | 0 | 265.8995 | 58.1195 | off_peak | 674.7605 | 0 | 100 | 7.93 | 0 | 92.07 | 206.6259 | 0
2649 | 773.8 | 506.202 | 24.4 | 102.7273 | 102.7273 | 0 | 0 | 0.80079 | 0.80079 | 0 | 0 | 0 | 74.3419 | 671.8735 | 0 | 0.05921 | 3.3757 | 0 | 0 | 265.8995 | 102.7273 | off_peak | 671.0727 | 0 | 100 | 13.28 | 0 | 86.72 | 346.7775 | 0
2650 | 772.82 | 699.744 | 24.9 | 141.7492 | 141.7492 | 0 | 0 | 0.05172 | 0.05172 | 0 | 0 | 0 | 74.3903 | 631.1225 | 0 | 0.05921 | 3.3158 | 0 | 0 | 265.8995 | 141.7492 | off_peak | 631.0708 | 0 | 100 | 18.34 | 0 | 81.66 | 470.0131 | 0
2651 | 784.61 | 849.234 | 25.2 | 171.8461 | 171.8461 | 0 | 0 | 0.0033404 | 0.0033404 | 0 | 0 | 0 | 74.3934 | 612.7673 | 0 | 0.05921 | 3.4775 | 0 | 0 | 265.8995 | 171.8461 | off_peak | 612.7639 | 0 | 100 | 21.9 | 0 | 78.1 | 597.5977 | 0
2652 | 811.24 | 930.431 | 25.5 | 188.0731 | 188.0731 | 0 | 0 | 0.00021574 | 0.00021574 | 0 | 0 | 0 | 74.3936 | 623.1671 | 0 | 0.05921 | 3.8976 | 0 | 0 | 265.8995 | 188.0731 | off_peak | 623.1669 | 0 | 100 | 23.18 | 0 | 76.82 | 733.035 | 0
2653 | 766.74 | 956.92 | 25.6 | 193.3577 | 193.3577 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 573.3823 | 0 | 0.088511 | 4.1473 | 0 | 0 | 265.8995 | 193.3577 | on_peak | 573.3823 |  |  | 25.22 | 0 | 74.78 | 801.9205 | 0
2654 | 772.38 | 695.169 | 25.7 | 140.417 | 140.417 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 631.963 | 0 | 0.088511 | 4.1462 | 0 | 0 | 265.8995 | 140.417 | on_peak | 631.963 |  |  | 18.18 | 0 | 81.82 | 582.2037 | 0
2655 | 821.07 | 568.675 | 25.6 | 114.9079 | 114.9079 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 706.1621 | 0 | 0.088511 | 4.2306 | 0 | 0 | 265.8995 | 114.9079 | on_peak | 706.1621 |  |  | 13.99 | 0 | 86.01 | 486.1244 | 0
2656 | 805.24 | 432.128 | 25.3 | 87.4114 | 87.4114 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 717.8286 | 0 | 0.088511 | 4.5508 | 0 | 0 | 265.8995 | 87.4114 | on_peak | 717.8286 |  |  | 10.86 | 0 | 89.14 | 397.7898 | 0
2657 | 780.99 | 342.605 | 25 | 69.3775 | 69.3775 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 711.6125 | 0 | 0.088511 | 5.0228 | 0 | 0 | 265.8995 | 69.3775 | on_peak | 711.6125 |  |  | 8.88 | 0 | 91.12 | 348.4705 | 0
2658 | 766.03 | 191.96 | 24.7 | 38.9139 | 38.9139 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 727.1161 | 0 | 0.088511 | 5.3411 | 0 | 0 | 265.8995 | 38.9139 | on_peak | 727.1161 |  |  | 5.08 | 0 | 94.92 | 207.8415 | 0
2659 | 775.06 | 17.9482 | 24.5 | 3.6411 | 3.6411 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 771.4189 | 0 | 0.088511 | 5.6494 | 0 | 0 | 265.8995 | 3.6411 | on_peak | 771.4189 |  |  | 0.47 | 0 | 99.53 | 20.5698 | 0
2660 | 757.61 | 0 | 24.3 | 0 | 0 | 0 | 0 | 0 | 0 | 62.63 | 62.63 | 0 | 7.4394 | 694.98 | 0 | 0.088511 | 6.0604 | 0 | 0 | 265.8995 | 0 | on_peak | 694.98 |  |  | 0 | 8.27 | 91.73 | 0 | 0
2661 | 746.23 | 0 | 24.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 746.23 | 0 | 0.088511 | 6.3715 | 0 | 0 | 265.8995 | 0 | on_peak | 746.23 |  |  | 0 | 0 | 100 | 0 | 0
2662 | 749.33 | 0 | 24.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 749.33 | 0 | 0.05921 | 6.7065 | 0 | 0 | 265.8995 | 0 | off_peak | 749.33 |  |  | 0 | 0 | 100 | 0 | 0
2663 | 749.04 | 0 | 24.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 749.04 | 0 | 0.05921 | 7.0204 | 0 | 0 | 265.8995 | 0 | off_peak | 749.04 |  |  | 0 | 0 | 100 | 0 | 0
2664 | 710.24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 710.24 | 0 | 0.05921 | 7.125 | 0 | 0 | 265.8995 | 0 | off_peak | 710.24 |  |  | 0 | 0 | 100 | 0 | 0
2665 | 667.48 | 0 | 23.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 667.48 | 0 | 0.05921 | 6.86 | 0 | 0 | 265.8995 | 0 | off_peak | 667.48 |  |  | 0 | 0 | 100 | 0 | 0
2666 | 638.1 | 0 | 23.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 638.1 | 0 | 0.05921 | 6.667 | 0 | 0 | 265.8995 | 0 | off_peak | 638.1 |  |  | 0 | 0 | 100 | 0 | 0
2667 | 587.05 | 0 | 23.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 587.05 | 0 | 0.05921 | 6.2729 | 0 | 0 | 265.8995 | 0 | off_peak | 587.05 |  |  | 0 | 0 | 100 | 0 | 0
2668 | 580.97 | 0 | 23.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 580.97 | 0 | 0.05921 | 5.8064 | 0 | 0 | 265.8995 | 0 | off_peak | 580.97 |  |  | 0 | 0 | 100 | 0 | 0
2669 | 615.23 | 0 | 23.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 615.23 | 0 | 0.05921 | 5.1436 | 0 | 0 | 265.8995 | 0 | off_peak | 615.23 |  |  | 0 | 0 | 100 | 0 | 0
2670 | 656.71 | 0 | 23.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 656.71 | 0 | 0.05921 | 4.4311 | 0 | 0 | 265.8995 | 0 | off_peak | 656.71 |  |  | 0 | 0 | 100 | 0 | 0
2671 | 689.13 | 51.7504 | 24 | 10.5172 | 10.5172 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 678.6128 | 0 | 0.05921 | 4.0288 | 0 | 0 | 265.8995 | 10.5172 | off_peak | 678.6128 |  |  | 1.53 | 0 | 98.47 | 42.3716 | 0
2672 | 711 | 270.603 | 24.6 | 54.876 | 54.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 656.124 | 0 | 0.05921 | 3.7206 | 0 | 0 | 265.8995 | 54.876 | off_peak | 656.124 |  |  | 7.72 | 0 | 92.28 | 204.169 | 0
2673 | 758.58 | 493.201 | 25.2 | 99.8013 | 99.8013 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 658.7787 | 0 | 0.05921 | 3.4598 | 0 | 0 | 265.8995 | 99.8013 | off_peak | 658.7787 |  |  | 13.16 | 0 | 86.84 | 345.2966 | 0
2674 | 727.78 | 521.54 | 25.6 | 105.3837 | 105.3837 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 622.3963 | 0 | 0.05921 | 3.3318 | 0 | 0 | 265.8995 | 105.3837 | off_peak | 622.3963 |  |  | 14.48 | 0 | 85.52 | 351.117 | 0
2675 | 731.54 | 604.586 | 25.9 | 122.032 | 122.032 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 609.508 | 0 | 0.05921 | 3.3319 | 0 | 0 | 265.8995 | 122.032 | off_peak | 609.508 |  |  | 16.68 | 0 | 83.32 | 406.5964 | 0
2676 | 751.08 | 509.589 | 26.1 | 102.7831 | 102.7831 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 648.2969 | 0 | 0.05921 | 3.4998 | 0 | 0 | 265.8995 | 102.7831 | off_peak | 648.2969 |  |  | 13.68 | 0 | 86.32 | 359.7188 | 0
2677 | 710.86 | 545.834 | 26.2 | 110.0539 | 110.0539 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 600.8061 | 0 | 0.05921 | 3.665 | 0 | 0 | 265.8995 | 110.0539 | off_peak | 600.8061 |  |  | 15.48 | 0 | 84.52 | 403.3484 | 0
2678 | 647.35 | 655.45 | 26.2 | 132.1552 | 132.1552 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 515.1948 | 0 | 0.05921 | 3.8405 | 0 | 0 | 265.8995 | 132.1552 | off_peak | 515.1948 |  |  | 20.41 | 0 | 79.59 | 507.5384 | 0
2679 | 653.74 | 518.092 | 26.1 | 104.4982 | 104.4982 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 549.2418 | 0 | 0.05921 | 4.0565 | 0 | 0 | 265.8995 | 104.4982 | off_peak | 549.2418 |  |  | 15.98 | 0 | 84.02 | 423.8924 | 0
2680 | 609.06 | 451.546 | 25.9 | 91.1418 | 91.1418 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 517.9182 | 0 | 0.05921 | 4.4655 | 0 | 0 | 265.8995 | 91.1418 | off_peak | 517.9182 |  |  | 14.96 | 0 | 85.04 | 406.9899 | 0
2681 | 621.52 | 278.992 | 25.6 | 56.3738 | 56.3738 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 565.1462 | 0 | 0.05921 | 4.8227 | 0 | 0 | 265.8995 | 56.3738 | off_peak | 565.1462 |  |  | 9.07 | 0 | 90.93 | 271.8735 | 0
2682 | 591.02 | 186.393 | 25.1 | 37.731 | 37.731 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 553.289 | 0 | 0.05921 | 5.322 | 0 | 0 | 265.8995 | 37.731 | off_peak | 553.289 |  |  | 6.38 | 0 | 93.62 | 200.8041 | 0
2683 | 544.22 | 22.5199 | 24.9 | 4.5619 | 4.5619 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 539.6581 | 0 | 0.05921 | 5.7749 | 0 | 0 | 265.8995 | 4.5619 | off_peak | 539.6581 |  |  | 0.84 | 0 | 99.16 | 26.3447 | 0
2684 | 573.62 | 0 | 24.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 573.62 | 0 | 0.05921 | 6.238 | 0 | 0 | 265.8995 | 0 | off_peak | 573.62 |  |  | 0 | 0 | 100 | 0 | 0
2685 | 548.08 | 0 | 24.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 548.08 | 0 | 0.05921 | 6.5614 | 0 | 0 | 265.8995 | 0 | off_peak | 548.08 |  |  | 0 | 0 | 100 | 0 | 0
2686 | 544.89 | 0 | 24.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 544.89 | 0 | 0.05921 | 6.6622 | 0 | 0 | 265.8995 | 0 | off_peak | 544.89 |  |  | 0 | 0 | 100 | 0 | 0
2687 | 548.21 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 548.21 | 0 | 0.05921 | 6.8655 | 0 | 0 | 265.8995 | 0 | off_peak | 548.21 |  |  | 0 | 0 | 100 | 0 | 0
2688 | 519.88 | 0 | 23.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 519.88 | 0 | 0.05921 | 6.8837 | 0 | 0 | 265.8995 | 0 | off_peak | 519.88 |  |  | 0 | 0 | 100 | 0 | 0
2689 | 525.54 | 0 | 23.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 525.54 | 0 | 0.05921 | 6.7109 | 0 | 0 | 265.8995 | 0 | off_peak | 525.54 |  |  | 0 | 0 | 100 | 0 | 0
2690 | 534.91 | 0 | 23.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 534.91 | 0 | 0.05921 | 6.5905 | 0 | 0 | 265.8995 | 0 | off_peak | 534.91 |  |  | 0 | 0 | 100 | 0 | 0
2691 | 513.81 | 0 | 23.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 513.81 | 0 | 0.05921 | 6.1743 | 0 | 0 | 265.8995 | 0 | off_peak | 513.81 |  |  | 0 | 0 | 100 | 0 | 0
2692 | 550.19 | 0 | 23.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 550.19 | 0 | 0.05921 | 5.5749 | 0 | 0 | 265.8995 | 0 | off_peak | 550.19 |  |  | 0 | 0 | 100 | 0 | 0
2693 | 546.36 | 0 | 23.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 546.36 | 0 | 0.05921 | 5.1134 | 0 | 0 | 265.8995 | 0 | off_peak | 546.36 |  |  | 0 | 0 | 100 | 0 | 0
2694 | 637.55 | 0 | 23.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 637.55 | 0 | 0.05921 | 4.4711 | 0 | 0 | 265.8995 | 0 | off_peak | 637.55 |  |  | 0 | 0 | 100 | 0 | 0
2695 | 701.22 | 75.6388 | 24.3 | 15.3555 | 15.3555 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 685.8645 | 0 | 0.05921 | 4.0341 | 0 | 0 | 265.8995 | 15.3555 | off_peak | 685.8645 |  |  | 2.19 | 0 | 97.81 | 61.9461 | 0
2696 | 708.19 | 253.648 | 24.9 | 51.3822 | 51.3822 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 19.0375 | 669.2067 | 0 | 0.05921 | 3.7061 | 0 | 0 | 265.8995 | 51.3822 | off_peak | 656.8078 | 0 | 100 | 7.26 | 0 | 92.74 | 190.4254 | 0
2697 | 676.59 | 445.336 | 25.4 | 90.0507 | 90.0507 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19.0375 | 586.5393 | 0 | 0.05921 | 3.4442 | 0 | 0 | 265.8995 | 90.0507 | off_peak | 586.5393 |  |  | 13.31 | 0 | 86.69 | 310.1554 | 0
2698 | 694.3 | 703.558 | 25.8 | 142.0602 | 142.0602 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19.0375 | 552.2398 | 0 | 0.05921 | 3.315 | 0 | 0 | 265.8995 | 142.0602 | off_peak | 552.2398 |  |  | 20.46 | 0 | 79.54 | 470.9236 | 0
2699 | 719.24 | 730.865 | 26.1 | 147.4141 | 147.4141 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19.0375 | 571.8259 | 0 | 0.05921 | 3.2766 | 0 | 0 | 265.8995 | 147.4141 | off_peak | 571.8259 |  |  | 20.5 | 0 | 79.5 | 483.0181 | 0
2700 | 677.33 | 914.772 | 26.4 | 184.3077 | 184.3077 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19.0375 | 493.0223 | 0 | 0.05921 | 3.3499 | 0 | 0 | 265.8995 | 184.3077 | off_peak | 493.0223 |  |  | 27.21 | 0 | 72.79 | 617.4098 | 0
2701 | 667.87 | 952.424 | 26.5 | 191.8244 | 191.8244 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19.0375 | 476.0456 | 0 | 0.05921 | 3.4376 | 0 | 0 | 265.8995 | 191.8244 | off_peak | 476.0456 |  |  | 28.72 | 0 | 71.28 | 659.4234 | 0
2702 | 623.42 | 919.662 | 26.5 | 185.2259 | 172.827 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 0 | 30.6357 | 450.593 | 0 | 0.05921 | 3.6849 | 0 | 0 | 277.4977 | 172.827 | off_peak | 450.593 | 100 | 0 | 27.72 | 0 | 72.28 | 636.8457 | 0
2703 | 627.15 | 805.685 | 26.4 | 162.3289 | 162.3289 | 0 | 0 | 2.6691 | 2.6691 | 0 | 0 | 0 | 33.1323 | 467.4901 | 0 | 0.05921 | 3.8938 | 0 | 0 | 277.4977 | 162.3289 | off_peak | 464.8211 | 0 | 100 | 25.88 | 0 | 74.12 | 632.0802 | 0
2704 | 642.23 | 644.413 | 26.2 | 129.9299 | 129.9299 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 33.1323 | 512.3001 | 0 | 0.05921 | 4.1402 | 0 | 0 | 277.4977 | 129.9299 | off_peak | 512.3001 |  |  | 20.23 | 0 | 79.77 | 537.9327 | 0
2705 | 640.46 | 383.885 | 25.9 | 77.4848 | 77.4848 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 33.1323 | 562.9752 | 0 | 0.05921 | 4.453 | 0 | 0 | 277.4977 | 77.4848 | off_peak | 562.9752 |  |  | 12.1 | 0 | 87.9 | 345.0425 | 0
2706 | 599.75 | 218.512 | 25.5 | 44.169 | 44.169 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 33.1323 | 555.581 | 0 | 0.05921 | 4.9242 | 0 | 0 | 277.4977 | 44.169 | off_peak | 555.581 |  |  | 7.36 | 0 | 92.64 | 217.4985 | 0
2707 | 569.61 | 29.9448 | 25.3 | 6.0573 | 0 | 0 | 6.0573 | 6.0573 | 0 | 0 | 0 | 0 | 38.7984 | 569.61 | 0 | 0.05921 | 5.3735 | 0 | 0 | 283.1637 | 0 | off_peak | 569.61 | 100 | 0 | 0 | 0 | 100 | 0 | 0
2708 | 509.76 | 0 | 24.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 38.7984 | 509.76 | 0 | 0.05921 | 5.8521 | 0 | 0 | 283.1637 | 0 | off_peak | 509.76 |  |  | 0 | 0 | 100 | 0 | 0
2709 | 530.83 | 0 | 24.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 38.7984 | 530.83 | 0 | 0.05921 | 6.2474 | 0 | 0 | 283.1637 | 0 | off_peak | 530.83 |  |  | 0 | 0 | 100 | 0 | 0
2710 | 532.98 | 0 | 24.6 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 50.3966 | 545.3789 | 0 | 0.05921 | 6.5849 | 0 | 0 | 283.1637 | 0 | off_peak | 532.98 | 0 | 100 | 0 | 0 | 100 | 0 | 0
2711 | 497.25 | 0 | 24.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50.3966 | 497.25 | 0 | 0.05921 | 6.9215 | 0 | 0 | 283.1637 | 0 | off_peak | 497.25 |  |  | 0 | 0 | 100 | 0 | 0
2712 | 487.61 | 0 | 24.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50.3966 | 487.61 | 0 | 0.05921 | 7.2687 | 0 | 0 | 283.1637 | 0 | off_peak | 487.61 |  |  | 0 | 0 | 100 | 0 | 0
2713 | 515.59 | 0 | 24.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50.3966 | 515.59 | 0 | 0.05921 | 7.173 | 0 | 0 | 283.1637 | 0 | off_peak | 515.59 |  |  | 0 | 0 | 100 | 0 | 0
2714 | 517.03 | 0 | 23.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50.3966 | 517.03 | 0 | 0.05921 | 7.017 | 0 | 0 | 283.1637 | 0 | off_peak | 517.03 |  |  | 0 | 0 | 100 | 0 | 0
2715 | 505.08 | 0 | 23.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50.3966 | 505.08 | 0 | 0.05921 | 6.4851 | 0 | 0 | 283.1637 | 0 | off_peak | 505.08 |  |  | 0 | 0 | 100 | 0 | 0
2716 | 529.47 | 0 | 23.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50.3966 | 529.47 | 0 | 0.05921 | 5.7719 | 0 | 0 | 283.1637 | 0 | off_peak | 529.47 |  |  | 0 | 0 | 100 | 0 | 0
2717 | 535.72 | 0 | 23.4 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 61.9947 | 548.1189 | 0 | 0.05921 | 5.1368 | 0 | 0 | 283.1637 | 0 | off_peak | 535.72 | 0 | 100 | 0 | 0 | 100 | 0 | 0
2718 | 643.78 | 0 | 23.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 61.9947 | 643.78 | 0 | 0.05921 | 4.4572 | 0 | 0 | 283.1637 | 0 | off_peak | 643.78 |  |  | 0 | 0 | 100 | 0 | 0
2719 | 731.73 | 90.0975 | 24.2 | 18.2973 | 18.2973 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 73.5928 | 725.8317 | 0 | 0.05921 | 4.0053 | 0 | 0 | 283.1637 | 18.2973 | off_peak | 713.4327 | 0 | 100 | 2.5 | 0 | 97.5 | 73.2861 | 0
2720 | 770.43 | 303.235 | 24.9 | 61.4272 | 61.4272 | 0 | 0 | 0.80079 | 0.80079 | 0 | 0 | 0 | 74.3419 | 709.8036 | 0 | 0.05921 | 3.6857 | 0 | 0 | 283.1637 | 61.4272 | off_peak | 709.0028 | 0 | 100 | 7.97 | 0 | 92.03 | 226.4025 | 0
2721 | 783.64 | 525.397 | 25.4 | 106.2397 | 106.2397 | 0 | 0 | 0.05172 | 0.05172 | 0 | 0 | 0 | 74.3903 | 677.452 | 0 | 0.05921 | 3.5204 | 0 | 0 | 283.1637 | 106.2397 | off_peak | 677.4003 | 0 | 100 | 13.56 | 0 | 86.44 | 374.0036 | 0
2722 | 801.35 | 719.502 | 25.9 | 145.2271 | 145.2271 | 0 | 0 | 0.0033404 | 0.0033404 | 0 | 0 | 0 | 74.3934 | 656.1263 | 0 | 0.05921 | 3.5327 | 0 | 0 | 283.1637 | 145.2271 | off_peak | 656.1229 | 0 | 100 | 18.12 | 0 | 81.88 | 513.0486 | 0
2723 | 771.32 | 866.785 | 26.3 | 174.7025 | 174.7025 | 0 | 0 | 0.00021574 | 0.00021574 | 0 | 0 | 0 | 74.3936 | 596.6177 | 0 | 0.05921 | 3.7641 | 0 | 0 | 283.1637 | 174.7025 | off_peak | 596.6175 | 0 | 100 | 22.65 | 0 | 77.35 | 657.5976 | 0
2724 | 820.73 | 892.718 | 26.6 | 179.7341 | 179.7341 | 0 | 0 | 1.3934e-05 | 1.3934e-05 | 0 | 0 | 0 | 74.3936 | 640.9959 | 0 | 0.05921 | 4.1804 | 0 | 0 | 283.1637 | 179.7341 | off_peak | 640.9959 | 0 | 100 | 21.9 | 0 | 78.1 | 751.3539 | 0
2725 | 761.82 | 947.76 | 26.7 | 190.7468 | 190.7468 | 0 | 0 | 0 | 0 | 62.63 | 62.63 | 0 | 7.4394 | 508.4432 | 0 | 0.088511 | 4.3885 | 0 | 0 | 283.1637 | 190.7468 | on_peak | 508.4432 |  |  | 25.04 | 8.22 | 66.74 | 837.0943 | 0
2726 | 784.31 | 814.594 | 26.7 | 163.9458 | 163.9458 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 620.3642 | 0 | 0.088511 | 4.6203 | 0 | 0 | 283.1637 | 163.9458 | on_peak | 620.3642 |  |  | 20.9 | 0 | 79.1 | 757.4816 | 0
2727 | 820.12 | 421.143 | 26.6 | 84.7902 | 84.7902 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 735.3298 | 0 | 0.088511 | 4.8741 | 0 | 0 | 283.1637 | 84.7902 | on_peak | 735.3298 |  |  | 10.34 | 0 | 89.66 | 413.2768 | 0
2728 | 808.87 | 423.547 | 26.4 | 85.336 | 85.336 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 723.534 | 0 | 0.088511 | 4.9043 | 0 | 0 | 283.1637 | 85.336 | on_peak | 723.534 |  |  | 10.55 | 0 | 89.45 | 418.5131 | 0
2729 | 793.51 | 333.124 | 26 | 67.2148 | 67.2148 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 726.2952 | 0 | 0.088511 | 4.9146 | 0 | 0 | 283.1637 | 67.2148 | on_peak | 726.2952 |  |  | 8.47 | 0 | 91.53 | 330.3331 | 0
2730 | 778.28 | 217.673 | 25.5 | 43.9994 | 43.9994 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 734.2806 | 0 | 0.088511 | 5.1022 | 0 | 0 | 283.1637 | 43.9994 | on_peak | 734.2806 |  |  | 5.65 | 0 | 94.35 | 224.4961 | 0
2731 | 691.55 | 26.3459 | 25.2 | 5.3312 | 5.3312 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 686.2188 | 0 | 0.088511 | 5.3279 | 0 | 0 | 283.1637 | 5.3312 | on_peak | 686.2188 |  |  | 0.77 | 0 | 99.23 | 28.4042 | 0
2732 | 790.29 | 0 | 24.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 790.29 | 0 | 0.088511 | 5.7664 | 0 | 0 | 283.1637 | 0 | on_peak | 790.29 |  |  | 0 | 0 | 100 | 0 | 0
2733 | 734.23 | 0 | 24.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 734.23 | 0 | 0.088511 | 6.0095 | 0 | 0 | 283.1637 | 0 | on_peak | 734.23 |  |  | 0 | 0 | 100 | 0 | 0
2734 | 708.23 | 0 | 24.3 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 19.0375 | 720.6289 | 0 | 0.05921 | 6.4042 | 0 | 0 | 283.1637 | 0 | off_peak | 708.23 | 0 | 100 | 0 | 0 | 100 | 0 | 0
2735 | 741.87 | 0 | 24 | 0 | 0 | 0 | 0 | 8.7263 | 8.7263 | 0 | 0 | 0 | 27.2003 | 750.5963 | 0 | 0.05921 | 6.5878 | 0 | 0 | 283.1637 | 0 | off_peak | 741.87 | 0 | 100 | 0 | 0 | 100 | 0 | 0
2736 | 759.61 | 0 | 23.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27.2003 | 759.61 | 0 | 0.05921 | 6.6498 | 0 | 0 | 283.1637 | 0 | off_peak | 759.61 |  |  | 0 | 0 | 100 | 0 | 0
2737 | 711.05 | 0 | 23.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27.2003 | 711.05 | 0 | 0.05921 | 6.4964 | 0 | 0 | 283.1637 | 0 | off_peak | 711.05 |  |  | 0 | 0 | 100 | 0 | 0
2738 | 639.19 | 0 | 23.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27.2003 | 639.19 | 0 | 0.05921 | 6.4154 | 0 | 0 | 283.1637 | 0 | off_peak | 639.19 |  |  | 0 | 0 | 100 | 0 | 0
2739 | 598.69 | 0 | 23.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27.2003 | 598.69 | 0 | 0.05921 | 6.0588 | 0 | 0 | 283.1637 | 0 | off_peak | 598.69 |  |  | 0 | 0 | 100 | 0 | 0
2740 | 580.32 | 0 | 23.5 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 38.7984 | 592.7189 | 0 | 0.05921 | 5.3624 | 0 | 0 | 283.1637 | 0 | off_peak | 580.32 | 0 | 100 | 0 | 0 | 100 | 0 | 0
2741 | 568.08 | 0 | 23.6 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 50.3966 | 580.4789 | 0 | 0.05921 | 4.6398 | 0 | 0 | 283.1637 | 0 | off_peak | 568.08 | 0 | 100 | 0 | 0 | 100 | 0 | 0
2742 | 651.58 | 0 | 23.7 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 61.9947 | 663.9789 | 0 | 0.05921 | 3.9641 | 0 | 0 | 283.1637 | 0 | off_peak | 651.58 | 0 | 100 | 0 | 0 | 100 | 0 | 0
2743 | 740.12 | 93.352 | 24.1 | 18.965 | 18.965 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 73.5928 | 733.5539 | 0 | 0.05921 | 3.5917 | 0 | 0 | 283.1637 | 18.965 | off_peak | 721.155 | 0 | 100 | 2.56 | 0 | 97.44 | 68.1172 | 0
2744 | 733.58 | 305.604 | 24.5 | 61.9962 | 61.9962 | 0 | 0 | 0.80079 | 0.80079 | 0 | 0 | 0 | 74.3419 | 672.3846 | 0 | 0.05921 | 3.3802 | 0 | 0 | 283.1637 | 61.9962 | off_peak | 671.5838 | 0 | 100 | 8.45 | 0 | 91.55 | 209.5626 | 0
2745 | 768.86 | 525.57 | 24.9 | 106.4662 | 106.4662 | 0 | 0 | 0.05172 | 0.05172 | 0 | 0 | 0 | 74.3903 | 662.4455 | 0 | 0.05921 | 3.2673 | 0 | 0 | 283.1637 | 106.4662 | off_peak | 662.3938 | 0 | 100 | 13.85 | 0 | 86.15 | 347.8525 | 0
2746 | 784.87 | 715.671 | 25.3 | 144.7669 | 144.7669 | 0 | 0 | 0.0033404 | 0.0033404 | 0 | 0 | 0 | 74.3934 | 640.1065 | 0 | 0.05921 | 3.3158 | 0 | 0 | 283.1637 | 144.7669 | off_peak | 640.1031 | 0 | 100 | 18.44 | 0 | 81.56 | 480.0131 | 0
2747 | 736.42 | 859.989 | 25.9 | 173.5835 | 173.5835 | 0 | 0 | 0.00021574 | 0.00021574 | 0 | 0 | 0 | 74.3936 | 562.8367 | 0 | 0.05921 | 3.5574 | 0 | 0 | 283.1637 | 173.5835 | off_peak | 562.8365 | 0 | 100 | 23.57 | 0 | 76.43 | 617.5041 | 0
2748 | 769.87 | 947.38 | 26.4 | 190.8776 | 190.8776 | 0 | 0 | 1.3934e-05 | 1.3934e-05 | 0 | 0 | 0 | 74.3936 | 578.9925 | 0 | 0.05921 | 3.946 | 0 | 0 | 283.1637 | 190.8776 | off_peak | 578.9924 | 0 | 100 | 24.79 | 0 | 75.21 | 753.2035 | 0
2749 | 731.21 | 923.517 | 26.8 | 185.8004 | 185.8004 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 545.4096 | 0 | 0.088511 | 4.127 | 0 | 0 | 283.1637 | 185.8004 | on_peak | 545.4096 |  |  | 25.41 | 0 | 74.59 | 766.8053 | 0
2750 | 805.67 | 921.048 | 26.9 | 185.2365 | 185.2365 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 620.4335 | 0 | 0.088511 | 4.1006 | 0 | 0 | 283.1637 | 185.2365 | on_peak | 620.4335 |  |  | 22.99 | 0 | 77.01 | 759.583 | 0
2751 | 804.61 | 809.297 | 26.9 | 162.7617 | 162.7617 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 641.8483 | 0 | 0.088511 | 4.0995 | 0 | 0 | 283.1637 | 162.7617 | on_peak | 641.8483 |  |  | 20.23 | 0 | 79.77 | 667.2368 | 0
2752 | 830.75 | 644.368 | 26.7 | 129.686 | 129.686 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 701.064 | 0 | 0.088511 | 4.3863 | 0 | 0 | 283.1637 | 129.686 | on_peak | 701.064 |  |  | 15.61 | 0 | 84.39 | 568.8369 | 0
2753 | 809.42 | 441.292 | 26.4 | 88.9112 | 88.9112 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 720.5088 | 0 | 0.088511 | 4.6928 | 0 | 0 | 283.1637 | 88.9112 | on_peak | 720.5088 |  |  | 10.98 | 0 | 89.02 | 417.2408 | 0
2754 | 782.03 | 221.89 | 26 | 44.771 | 44.771 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 737.259 | 0 | 0.088511 | 5.131 | 0 | 0 | 283.1637 | 44.771 | on_peak | 737.259 |  |  | 5.72 | 0 | 94.28 | 229.721 | 0
2755 | 711.41 | 32.8168 | 25.7 | 6.6287 | 6.6287 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 704.7813 | 0 | 0.088511 | 5.5106 | 0 | 0 | 283.1637 | 6.6287 | on_peak | 704.7813 |  |  | 0.93 | 0 | 99.07 | 36.5281 | 0
2756 | 764.27 | 0 | 25.1 | 0 | 0 | 0 | 0 | 0 | 0 | 62.63 | 62.63 | 0 | 7.4394 | 701.64 | 0 | 0.088511 | 5.8321 | 62.63 | 0 | 216.2094 | 62.63 | on_peak | 701.64 |  |  | 0 | 8.19 | 91.81 | 365.2659 | 0
2757 | 746.82 | 0 | 24.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 746.82 | 0 | 0.088511 | 6.1868 | 0 | 0 | 216.2094 | 0 | on_peak | 746.82 |  |  | 0 | 0 | 100 | 0 | 0
2758 | 713.66 | 0 | 24.3 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 19.0375 | 726.0589 | 0 | 0.05921 | 6.8817 | 0 | 0 | 216.2094 | 0 | off_peak | 713.66 | 0 | 100 | 0 | 0 | 100 | 0 | 0
2759 | 757.13 | 0 | 24.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19.0375 | 757.13 | 0 | 0.05921 | 7.2246 | 0 | 0 | 216.2094 | 0 | off_peak | 757.13 |  |  | 0 | 0 | 100 | 0 | 0
2760 | 727.45 | 0 | 23.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19.0375 | 727.45 | 0 | 0.05921 | 7.2536 | 0 | 0 | 216.2094 | 0 | off_peak | 727.45 |  |  | 0 | 0 | 100 | 0 | 0
2761 | 705.38 | 0 | 23.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19.0375 | 705.38 | 0 | 0.05921 | 7.136 | 0 | 0 | 216.2094 | 0 | off_peak | 705.38 |  |  | 0 | 0 | 100 | 0 | 0
2762 | 607.39 | 0 | 23.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19.0375 | 607.39 | 0 | 0.05921 | 6.9883 | 0 | 0 | 216.2094 | 0 | off_peak | 607.39 |  |  | 0 | 0 | 100 | 0 | 0
2763 | 524.57 | 0 | 23.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19.0375 | 524.57 | 0 | 0.05921 | 6.359 | 0 | 0 | 216.2094 | 0 | off_peak | 524.57 |  |  | 0 | 0 | 100 | 0 | 0
2764 | 500.53 | 0 | 23.3 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 30.6357 | 512.9289 | 0 | 0.05921 | 5.6479 | 0 | 0 | 216.2094 | 0 | off_peak | 500.53 | 0 | 100 | 0 | 0 | 100 | 0 | 0
2765 | 520.11 | 0 | 23.1 | 0 | 0 | 0 | 0 | 8.7263 | 8.7263 | 0 | 0 | 0 | 38.7984 | 528.8363 | 0 | 0.05921 | 4.8684 | 0 | 0 | 216.2094 | 0 | off_peak | 520.11 | 0 | 100 | 0 | 0 | 100 | 0 | 0
2766 | 663.27 | 0 | 23.1 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 50.3966 | 675.6689 | 0 | 0.05921 | 4.1524 | 0 | 0 | 216.2094 | 0 | off_peak | 663.27 | 0 | 100 | 0 | 0 | 100 | 0 | 0
2767 | 674.26 | 93.5085 | 23.5 | 19.0377 | 19.0377 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 61.9947 | 667.6212 | 0 | 0.05921 | 3.7064 | 0 | 0 | 216.2094 | 19.0377 | off_peak | 655.2223 | 0 | 100 | 2.82 | 0 | 97.18 | 70.5609 | 0
2768 | 733.52 | 304.009 | 24.1 | 61.7613 | 61.7613 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 73.5928 | 684.1577 | 0 | 0.05921 | 3.4022 | 0 | 0 | 216.2094 | 61.7613 | off_peak | 671.7587 | 0 | 100 | 8.42 | 0 | 91.58 | 210.1246 | 0
2769 | 770.9 | 522.591 | 24.9 | 105.8628 | 105.8628 | 0 | 0 | 0.80079 | 0.80079 | 0 | 0 | 0 | 74.3419 | 665.838 | 0 | 0.05921 | 3.2381 | 0 | 0 | 216.2094 | 105.8628 | off_peak | 665.0372 | 0 | 100 | 13.73 | 0 | 86.27 | 342.7984 | 0
2770 | 780.13 | 716.309 | 25.7 | 144.687 | 144.687 | 0 | 0 | 0.05172 | 0.05172 | 0 | 0 | 0 | 74.3903 | 635.4947 | 0 | 0.05921 | 3.206 | 0 | 0 | 216.2094 | 144.687 | off_peak | 635.443 | 0 | 100 | 18.55 | 0 | 81.45 | 463.8733 | 0
2771 | 756.28 | 864.136 | 26.2 | 174.2316 | 174.2316 | 0 | 0 | 0.0033404 | 0.0033404 | 0 | 0 | 0 | 74.3934 | 582.0517 | 0 | 0.05921 | 3.375 | 0 | 0 | 216.2094 | 174.2316 | off_peak | 582.0484 | 0 | 100 | 23.04 | 0 | 76.96 | 588.0268 | 0
2772 | 737.76 | 952.902 | 26.5 | 191.9207 | 191.9207 | 0 | 0 | 0.00021574 | 0.00021574 | 0 | 0 | 0 | 74.3936 | 545.8396 | 0 | 0.05921 | 3.8116 | 0 | 0 | 216.2094 | 191.9207 | off_peak | 545.8393 | 0 | 100 | 26.01 | 0 | 73.99 | 731.5302 | 0
2773 | 753.14 | 973.238 | 26.7 | 195.8746 | 195.8746 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 557.2654 | 0 | 0.088511 | 4.0073 | 0 | 0 | 216.2094 | 195.8746 | on_peak | 557.2654 |  |  | 26.01 | 0 | 73.99 | 784.9209 | 0
2774 | 744.51 | 923.858 | 26.7 | 185.9363 | 185.9363 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 558.5737 | 0 | 0.088511 | 4.0995 | 0 | 0 | 216.2094 | 185.9363 | on_peak | 558.5737 |  |  | 24.97 | 0 | 75.03 | 762.2513 | 0
2775 | 822.75 | 813.351 | 26.4 | 163.8735 | 163.8735 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 658.8765 | 0 | 0.088511 | 4.2692 | 0 | 0 | 216.2094 | 163.8735 | on_peak | 658.8765 |  |  | 19.92 | 0 | 80.08 | 699.6027 | 0
2776 | 799.25 | 647.871 | 26 | 130.7216 | 130.7216 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 668.5284 | 0 | 0.088511 | 4.6843 | 0 | 0 | 216.2094 | 130.7216 | on_peak | 668.5284 |  |  | 16.36 | 0 | 83.64 | 612.3337 | 0
2777 | 801.74 | 443.622 | 25.3 | 89.7364 | 89.7364 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 712.0036 | 0 | 0.088511 | 5.0667 | 0 | 0 | 216.2094 | 89.7364 | on_peak | 712.0036 |  |  | 11.19 | 0 | 88.81 | 454.6702 | 0
2778 | 796.3 | 223.503 | 24.6 | 45.3245 | 45.3245 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 750.9755 | 0 | 0.088511 | 5.5601 | 0 | 0 | 216.2094 | 45.3245 | on_peak | 750.9755 |  |  | 5.69 | 0 | 94.31 | 252.0072 | 0
2779 | 732.16 | 32.9971 | 24.3 | 6.6988 | 6.6988 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 725.4612 | 0 | 0.088511 | 6.08 | 0 | 0 | 216.2094 | 6.6988 | on_peak | 725.4612 |  |  | 0.91 | 0 | 99.09 | 40.7285 | 0
2780 | 824.66 | 0 | 23.7 | 0 | 0 | 0 | 0 | 0 | 0 | 62.63 | 62.63 | 0 | 7.4394 | 762.03 | 0 | 0.088511 | 6.4766 | 0 | 0 | 216.2094 | 0 | on_peak | 762.03 |  |  | 0 | 7.59 | 92.41 | 0 | 0
2781 | 792.38 | 0 | 23.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 792.38 | 0 | 0.088511 | 6.8744 | 0 | 0 | 216.2094 | 0 | on_peak | 792.38 |  |  | 0 | 0 | 100 | 0 | 0
2782 | 792.29 | 0 | 23.3 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 19.0375 | 804.6889 | 0 | 0.05921 | 7.0904 | 0 | 0 | 216.2094 | 0 | off_peak | 792.29 | 0 | 100 | 0 | 0 | 100 | 0 | 0
2783 | 783.82 | 0 | 23.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19.0375 | 783.82 | 0 | 0.05921 | 7.1101 | 0 | 0 | 216.2094 | 0 | off_peak | 783.82 |  |  | 0 | 0 | 100 | 0 | 0
2784 | 794.49 | 0 | 23.2 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 30.6357 | 806.8889 | 0 | 0.05921 | 7.2007 | 0 | 0 | 216.2094 | 0 | off_peak | 794.49 | 0 | 100 | 0 | 0 | 100 | 0 | 0
2785 | 742.63 | 0 | 23.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30.6357 | 742.63 | 0 | 0.05921 | 7.1179 | 0 | 0 | 216.2094 | 0 | off_peak | 742.63 |  |  | 0 | 0 | 100 | 0 | 0
2786 | 653.53 | 0 | 22.9 | 0 | 0 | 0 | 0 | 8.7263 | 8.7263 | 0 | 0 | 0 | 38.7984 | 662.2563 | 0 | 0.05921 | 6.9813 | 0 | 0 | 216.2094 | 0 | off_peak | 653.53 | 0 | 100 | 0 | 0 | 100 | 0 | 0
2787 | 621.49 | 0 | 22.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 38.7984 | 621.49 | 0 | 0.05921 | 6.5526 | 0 | 0 | 216.2094 | 0 | off_peak | 621.49 |  |  | 0 | 0 | 100 | 0 | 0
2788 | 575.42 | 0 | 22.8 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 50.3966 | 587.8189 | 0 | 0.05921 | 5.8735 | 0 | 0 | 216.2094 | 0 | off_peak | 575.42 | 0 | 100 | 0 | 0 | 100 | 0 | 0
2789 | 644.53 | 0 | 22.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50.3966 | 644.53 | 0 | 0.05921 | 5.0274 | 0 | 0 | 216.2094 | 0 | off_peak | 644.53 |  |  | 0 | 0 | 100 | 0 | 0
2790 | 692.45 | 0 | 22.7 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 61.9947 | 704.8489 | 0 | 0.05921 | 4.342 | 0 | 0 | 216.2094 | 0 | off_peak | 692.45 | 0 | 100 | 0 | 0 | 100 | 0 | 0
2791 | 753.97 | 94.1219 | 23.1 | 19.1901 | 19.1901 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 73.5928 | 747.1789 | 0 | 0.05921 | 3.8877 | 0 | 0 | 216.2094 | 19.1901 | off_peak | 734.7799 | 0 | 100 | 2.55 | 0 | 97.45 | 74.6054 | 0
2792 | 804.32 | 302.592 | 23.7 | 61.5616 | 61.5616 | 0 | 0 | 0.80079 | 0.80079 | 0 | 0 | 0 | 74.3419 | 743.5591 | 0 | 0.05921 | 3.5781 | 0 | 0 | 216.2094 | 61.5616 | off_peak | 742.7584 | 0 | 100 | 7.65 | 0 | 92.35 | 220.2742 | 0
2793 | 804.33 | 519.552 | 24.3 | 105.4744 | 105.4744 | 0 | 0 | 0.05172 | 0.05172 | 0 | 0 | 0 | 74.3903 | 698.9073 | 0 | 0.05921 | 3.4045 | 0 | 0 | 216.2094 | 105.4744 | off_peak | 698.8556 | 0 | 100 | 13.11 | 0 | 86.89 | 359.0929 | 0
2794 | 847.72 | 708.5 | 24.8 | 143.5745 | 143.5745 | 0 | 0 | 0.0033404 | 0.0033404 | 0 | 0 | 0 | 74.3934 | 704.1488 | 0 | 0.05921 | 3.3328 | 0 | 0 | 216.2094 | 143.5745 | off_peak | 704.1455 | 0 | 100 | 16.94 | 0 | 83.06 | 478.5014 | 0
2795 | 851.86 | 850.73 | 25.2 | 172.1488 | 172.1488 | 0 | 0 | 0.00021574 | 0.00021574 | 0 | 0 | 0 | 74.3936 | 679.7114 | 0 | 0.05921 | 3.4914 | 0 | 0 | 216.2094 | 172.1488 | off_peak | 679.7112 | 0 | 100 | 20.21 | 0 | 79.79 | 601.048 | 0
2796 | 892.37 | 880.741 | 25.4 | 178.0932 | 178.0932 | 0 | 0 | 1.3934e-05 | 1.3934e-05 | 0 | 0 | 0 | 74.3936 | 714.2768 | 0 | 0.05921 | 3.9561 | 0 | 0 | 216.2094 | 178.0932 | off_peak | 714.2768 | 0 | 100 | 19.96 | 0 | 80.04 | 704.556 | 0
2797 | 855.52 | 919.198 | 25.4 | 185.8696 | 185.8696 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 669.6504 | 0 | 0.088511 | 4.1893 | 0 | 0 | 216.2094 | 185.8696 | on_peak | 669.6504 |  |  | 21.73 | 0 | 78.27 | 778.672 | 0
2798 | 849.78 | 821.786 | 25.4 | 166.172 | 166.172 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 683.608 | 0 | 0.088511 | 4.5083 | 0 | 0 | 216.2094 | 166.172 | on_peak | 683.608 |  |  | 19.55 | 0 | 80.45 | 749.1604 | 0
2799 | 859.31 | 579.392 | 25.2 | 117.2424 | 117.2424 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 742.0676 | 0 | 0.088511 | 4.8428 | 0 | 0 | 216.2094 | 117.2424 | on_peak | 742.0676 |  |  | 13.64 | 0 | 86.36 | 567.7792 | 0
2800 | 851.97 | 356.558 | 24.9 | 72.229 | 72.229 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 779.741 | 0 | 0.088511 | 5.247 | 0 | 0 | 216.2094 | 72.229 | on_peak | 779.741 |  |  | 8.48 | 0 | 91.52 | 378.986 | 0
2801 | 816.05 | 294.704 | 24.5 | 59.785 | 59.785 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 756.265 | 0 | 0.088511 | 5.6733 | 0 | 0 | 216.2094 | 59.785 | on_peak | 756.265 |  |  | 7.33 | 0 | 92.67 | 339.1798 | 0
2802 | 873.29 | 193.805 | 24.2 | 39.3585 | 39.3585 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 833.9315 | 0 | 0.088511 | 6.1721 | 0 | 0 | 216.2094 | 39.3585 | on_peak | 833.9315 |  |  | 4.51 | 0 | 95.49 | 242.925 | 0
2803 | 824.12 | 31.6524 | 24 | 6.4327 | 6.4327 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 817.6873 | 0 | 0.088511 | 6.6719 | 0 | 0 | 216.2094 | 6.4327 | on_peak | 817.6873 |  |  | 0.78 | 0 | 99.22 | 42.9185 | 0
2804 | 814.08 | 0 | 23.7 | 0 | 0 | 0 | 0 | 0 | 0 | 62.63 | 62.63 | 0 | 7.4394 | 751.45 | 0 | 0.088511 | 7.0598 | 0 | 0 | 216.2094 | 0 | on_peak | 751.45 |  |  | 0 | 7.69 | 92.31 | 0 | 0
2805 | 810.68 | 0 | 23.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 810.68 | 0 | 0.088511 | 7.5463 | 0 | 0 | 216.2094 | 0 | on_peak | 810.68 |  |  | 0 | 0 | 100 | 0 | 0
2806 | 775.51 | 0 | 23.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 775.51 | 0 | 0.05921 | 7.6788 | 0 | 0 | 216.2094 | 0 | off_peak | 775.51 |  |  | 0 | 0 | 100 | 0 | 0
2807 | 814.96 | 0 | 23.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 814.96 | 0 | 0.05921 | 7.6576 | 0 | 0 | 216.2094 | 0 | off_peak | 814.96 |  |  | 0 | 0 | 100 | 0 | 0
2808 | 754.25 | 0 | 23.4 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 19.0375 | 766.6489 | 0 | 0.05921 | 7.7557 | 0 | 0 | 216.2094 | 0 | off_peak | 754.25 | 0 | 100 | 0 | 0 | 100 | 0 | 0
2809 | 773.34 | 0 | 23.3 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 30.6357 | 785.7389 | 0 | 0.05921 | 7.6586 | 0 | 0 | 216.2094 | 0 | off_peak | 773.34 | 0 | 100 | 0 | 0 | 100 | 0 | 0
2810 | 675.2 | 0 | 23.2 | 0 | 0 | 0 | 0 | 8.7263 | 8.7263 | 0 | 0 | 0 | 38.7984 | 683.9263 | 0 | 0.05921 | 7.4647 | 0 | 0 | 216.2094 | 0 | off_peak | 675.2 | 0 | 100 | 0 | 0 | 100 | 0 | 0
2811 | 594.68 | 0 | 23.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 38.7984 | 594.68 | 0 | 0.05921 | 7.0046 | 0 | 0 | 216.2094 | 0 | off_peak | 594.68 |  |  | 0 | 0 | 100 | 0 | 0
2812 | 582.44 | 0 | 23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 38.7984 | 582.44 | 0 | 0.05921 | 6.3361 | 0 | 0 | 216.2094 | 0 | off_peak | 582.44 |  |  | 0 | 0 | 100 | 0 | 0
2813 | 617.11 | 0 | 22.8 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 50.3966 | 629.5089 | 0 | 0.05921 | 5.455 | 0 | 0 | 216.2094 | 0 | off_peak | 617.11 | 0 | 100 | 0 | 0 | 100 | 0 | 0
2814 | 677.85 | 0 | 23 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 61.9947 | 690.2489 | 0 | 0.05921 | 4.7682 | 0 | 0 | 216.2094 | 0 | off_peak | 677.85 | 0 | 100 | 0 | 0 | 100 | 0 | 0
2815 | 730.64 | 89.6793 | 23.5 | 18.2581 | 18.2581 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 73.5928 | 724.7808 | 0 | 0.05921 | 4.2456 | 0 | 0 | 216.2094 | 18.2581 | off_peak | 712.3819 | 0 | 100 | 2.5 | 0 | 97.5 | 77.5165 | 0
2816 | 787.84 | 298.696 | 24 | 60.7037 | 60.7037 | 0 | 0 | 0.80079 | 0.80079 | 0 | 0 | 0 | 74.3419 | 727.9371 | 0 | 0.05921 | 3.9117 | 0 | 0 | 216.2094 | 60.7037 | off_peak | 727.1363 | 0 | 100 | 7.71 | 0 | 92.29 | 237.4574 | 0
2817 | 819.79 | 515.907 | 24.4 | 104.6968 | 104.6968 | 0 | 0 | 0.05172 | 0.05172 | 0 | 0 | 0 | 74.3903 | 715.1449 | 0 | 0.05921 | 3.6762 | 0 | 0 | 216.2094 | 104.6968 | off_peak | 715.0932 | 0 | 100 | 12.77 | 0 | 87.23 | 384.8909 | 0
2818 | 829.21 | 706.302 | 24.7 | 143.1806 | 143.1806 | 0 | 0 | 0.0033404 | 0.0033404 | 0 | 0 | 0 | 74.3934 | 686.0327 | 0 | 0.05921 | 3.601 | 0 | 0 | 216.2094 | 143.1806 | off_peak | 686.0294 | 0 | 100 | 17.27 | 0 | 82.73 | 515.593 | 0
2819 | 793.04 | 850.106 | 24.9 | 172.2084 | 172.2084 | 0 | 0 | 0.00021574 | 0.00021574 | 0 | 0 | 0 | 74.3936 | 620.8318 | 0 | 0.05921 | 3.7766 | 0 | 0 | 216.2094 | 172.2084 | off_peak | 620.8316 | 0 | 100 | 21.71 | 0 | 78.29 | 650.3545 | 0
2820 | 877.87 | 787.485 | 25.1 | 159.4083 | 159.4083 | 0 | 0 | 1.3934e-05 | 1.3934e-05 | 0 | 0 | 0 | 74.3936 | 718.4617 | 0 | 0.05921 | 4.2087 | 0 | 0 | 216.2094 | 159.4083 | off_peak | 718.4617 | 0 | 100 | 18.16 | 0 | 81.84 | 670.8953 | 0
2821 | 807.36 | 812.071 | 25 | 164.4444 | 164.4444 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 642.9156 | 0 | 0.088511 | 4.4144 | 0 | 0 | 216.2094 | 164.4444 | on_peak | 642.9156 |  |  | 20.37 | 0 | 79.63 | 725.9292 | 0
2822 | 883.02 | 839.32 | 25 | 169.9623 | 169.9623 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 713.0577 | 0 | 0.088511 | 4.6779 | 0 | 0 | 216.2094 | 169.9623 | on_peak | 713.0577 |  |  | 19.25 | 0 | 80.75 | 795.0667 | 0
2823 | 915.73 | 541.505 | 24.9 | 109.6942 | 109.6942 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 806.0358 | 0 | 0.088511 | 5.0064 | 0 | 0 | 216.2094 | 109.6942 | on_peak | 806.0358 |  |  | 11.98 | 0 | 88.02 | 549.1707 | 0
2824 | 796.47 | 138.439 | 24.8 | 28.0541 | 28.0541 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 768.4159 | 0 | 0.088511 | 5.3451 | 0 | 0 | 216.2094 | 28.0541 | on_peak | 768.4159 |  |  | 3.52 | 0 | 96.48 | 149.9529 | 0
2825 | 823.38 | 45.1313 | 24.6 | 9.1522 | 9.1522 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 814.2278 | 0 | 0.088511 | 5.5348 | 0 | 0 | 216.2094 | 9.1522 | on_peak | 814.2278 |  |  | 1.11 | 0 | 98.89 | 50.6563 | 0
2826 | 837.09 | 23.75 | 24.3 | 4.8215 | 4.8215 | 0 | 0 | 0 | 0 | 62.63 | 62.63 | 0 | 7.4394 | 769.6385 | 0 | 0.088511 | 5.6497 | 0 | 0 | 216.2094 | 4.8215 | on_peak | 769.6385 |  |  | 0.58 | 7.48 | 91.94 | 27.2402 | 0
2827 | 788.85 | 18.0472 | 24.2 | 3.6651 | 3.6651 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 785.1849 | 0 | 0.088511 | 5.8404 | 0 | 0 | 216.2094 | 3.6651 | on_peak | 785.1849 |  |  | 0.46 | 0 | 99.54 | 21.4055 | 0
2828 | 837.9 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 837.9 | 0 | 0.088511 | 6.0447 | 0 | 0 | 216.2094 | 0 | on_peak | 837.9 |  |  | 0 | 0 | 100 | 0 | 0
2829 | 796.43 | 0 | 23.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 796.43 | 0 | 0.088511 | 6.5043 | 0 | 0 | 216.2094 | 0 | on_peak | 796.43 |  |  | 0 | 0 | 100 | 0 | 0
2830 | 742.76 | 0 | 23.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 742.76 | 0 | 0.05921 | 7.0824 | 0 | 0 | 216.2094 | 0 | off_peak | 742.76 |  |  | 0 | 0 | 100 | 0 | 0
2831 | 823.08 | 0 | 23.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 823.08 | 0 | 0.05921 | 7.4707 | 0 | 0 | 216.2094 | 0 | off_peak | 823.08 |  |  | 0 | 0 | 100 | 0 | 0
2832 | 786.04 | 0 | 23.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 786.04 | 0 | 0.05921 | 7.5049 | 0 | 0 | 216.2094 | 0 | off_peak | 786.04 |  |  | 0 | 0 | 100 | 0 | 0
2833 | 743.69 | 0 | 23.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 743.69 | 0 | 0.05921 | 7.3598 | 0 | 0 | 216.2094 | 0 | off_peak | 743.69 |  |  | 0 | 0 | 100 | 0 | 0
2834 | 645.4 | 0 | 23.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 645.4 | 0 | 0.05921 | 7.2687 | 0 | 0 | 216.2094 | 0 | off_peak | 645.4 |  |  | 0 | 0 | 100 | 0 | 0
2835 | 661.13 | 0 | 23.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 661.13 | 0 | 0.05921 | 6.7949 | 0 | 0 | 216.2094 | 0 | off_peak | 661.13 |  |  | 0 | 0 | 100 | 0 | 0
2836 | 587.11 | 0 | 23.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 587.11 | 0 | 0.05921 | 6.216 | 0 | 0 | 216.2094 | 0 | off_peak | 587.11 |  |  | 0 | 0 | 100 | 0 | 0
2837 | 612.99 | 0 | 23.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 612.99 | 0 | 0.05921 | 5.6832 | 0 | 0 | 216.2094 | 0 | off_peak | 612.99 |  |  | 0 | 0 | 100 | 0 | 0
2838 | 703.27 | 0 | 23.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 703.27 | 0 | 0.05921 | 4.9328 | 0 | 0 | 216.2094 | 0 | off_peak | 703.27 |  |  | 0 | 0 | 100 | 0 | 0
2839 | 722.61 | 23.75 | 23.5 | 4.8353 | 4.8353 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 717.7747 | 0 | 0.05921 | 4.4492 | 0 | 0 | 216.2094 | 4.8353 | off_peak | 717.7747 |  |  | 0.67 | 0 | 99.33 | 21.5134 | 0
2840 | 836.96 | 171.644 | 23.5 | 34.9456 | 34.9456 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 802.0144 | 0 | 0.05921 | 4.1671 | 0 | 0 | 216.2094 | 34.9456 | off_peak | 802.0144 |  |  | 4.18 | 0 | 95.82 | 145.6232 | 0
2841 | 806.43 | 245.922 | 23.4 | 50.086 | 50.086 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 756.344 | 0 | 0.05921 | 3.9518 | 0 | 0 | 216.2094 | 50.086 | off_peak | 756.344 |  |  | 6.21 | 0 | 93.79 | 197.9325 | 0
2842 | 792.84 | 614.365 | 23.4 | 125.1255 | 125.1255 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 667.7145 | 0 | 0.05921 | 3.8474 | 0 | 0 | 216.2094 | 125.1255 | off_peak | 667.7145 |  |  | 15.78 | 0 | 84.22 | 481.4067 | 0
2843 | 790.3 | 746.915 | 23.4 | 152.1215 | 152.1215 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 638.1785 | 0 | 0.05921 | 3.8474 | 0 | 0 | 216.2094 | 152.1215 | off_peak | 638.1785 |  |  | 19.25 | 0 | 80.75 | 585.2708 | 0
2844 | 778.13 | 523.68 | 23.4 | 106.656 | 106.656 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 671.474 | 0 | 0.05921 | 3.9559 | 0 | 0 | 216.2094 | 106.656 | off_peak | 671.474 |  |  | 13.71 | 0 | 86.29 | 421.9174 | 0
2845 | 750.36 | 780.477 | 23.3 | 159.0138 | 159.0138 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 19.0375 | 603.7451 | 0 | 0.05921 | 4.1292 | 0 | 0 | 216.2094 | 159.0138 | off_peak | 591.3462 | 0 | 100 | 21.19 | 0 | 78.81 | 656.6012 | 0
2846 | 729.92 | 229.828 | 23.3 | 46.825 | 46.825 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19.0375 | 683.095 | 0 | 0.05921 | 4.5235 | 0 | 0 | 216.2094 | 46.825 | off_peak | 683.095 |  |  | 6.42 | 0 | 93.58 | 211.8109 | 0
2847 | 752.69 | 238.34 | 23.1 | 48.594 | 48.594 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 30.6357 | 716.495 | 0 | 0.05921 | 5.0033 | 0 | 0 | 216.2094 | 48.594 | off_peak | 704.096 | 0 | 100 | 6.46 | 0 | 93.54 | 243.1292 | 0
2848 | 746.97 | 278.732 | 22.8 | 56.8903 | 56.8903 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30.6357 | 690.0797 | 0 | 0.05921 | 5.5862 | 0 | 0 | 216.2094 | 56.8903 | off_peak | 690.0797 |  |  | 7.62 | 0 | 92.38 | 317.8025 | 0
2849 | 723.46 | 375.331 | 22.6 | 76.6612 | 76.6612 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30.6357 | 646.7988 | 0 | 0.05921 | 6.1305 | 0 | 0 | 216.2094 | 76.6612 | off_peak | 646.7988 |  |  | 10.6 | 0 | 89.4 | 469.974 | 0
2850 | 712.59 | 155.826 | 22.4 | 31.8501 | 31.8501 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30.6357 | 680.7399 | 0 | 0.05921 | 6.7208 | 0 | 0 | 216.2094 | 31.8501 | off_peak | 680.7399 |  |  | 4.47 | 0 | 95.53 | 214.0598 | 0
2851 | 646.02 | 23.6764 | 22.3 | 4.8411 | 4.8411 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30.6357 | 641.1789 | 0 | 0.05921 | 7.1564 | 0 | 0 | 216.2094 | 4.8411 | off_peak | 641.1789 |  |  | 0.75 | 0 | 99.25 | 34.6446 | 0
2852 | 684.9 | 0 | 22.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30.6357 | 684.9 | 0 | 0.05921 | 7.6033 | 0 | 0 | 216.2094 | 0 | off_peak | 684.9 |  |  | 0 | 0 | 100 | 0 | 0
2853 | 637.76 | 0 | 22.3 | 0 | 0 | 0 | 0 | 6.482 | 6.482 | 0 | 0 | 0 | 36.699 | 644.242 | 0 | 0.05921 | 7.7675 | 0 | 0 | 216.2094 | 0 | off_peak | 637.76 | 0 | 100 | 0 | 0 | 100 | 0 | 0
2854 | 660.22 | 0 | 22.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 36.699 | 660.22 | 0 | 0.05921 | 7.6443 | 0 | 0 | 216.2094 | 0 | off_peak | 660.22 |  |  | 0 | 0 | 100 | 0 | 0
2855 | 561.97 | 0 | 22.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 36.699 | 561.97 | 0 | 0.05921 | 7.4046 | 0 | 0 | 216.2094 | 0 | off_peak | 561.97 |  |  | 0 | 0 | 100 | 0 | 0
2856 | 605.37 | 0 | 22.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 36.699 | 605.37 | 0 | 0.05921 | 7.0627 | 0 | 0 | 216.2094 | 0 | off_peak | 605.37 |  |  | 0 | 0 | 100 | 0 | 0
2857 | 589.44 | 0 | 22.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 36.699 | 589.44 | 0 | 0.05921 | 6.8721 | 0 | 0 | 216.2094 | 0 | off_peak | 589.44 |  |  | 0 | 0 | 100 | 0 | 0
2858 | 570.08 | 0 | 22.6 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 48.2972 | 582.4789 | 0 | 0.05921 | 6.7885 | 0 | 0 | 216.2094 | 0 | off_peak | 570.08 | 0 | 100 | 0 | 0 | 100 | 0 | 0
2859 | 585.27 | 0 | 22.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 48.2972 | 585.27 | 0 | 0.05921 | 6.4028 | 0 | 0 | 216.2094 | 0 | off_peak | 585.27 |  |  | 0 | 0 | 100 | 0 | 0
2860 | 584.4 | 0 | 22.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 48.2972 | 584.4 | 0 | 0.05921 | 5.9243 | 0 | 0 | 216.2094 | 0 | off_peak | 584.4 |  |  | 0 | 0 | 100 | 0 | 0
2861 | 594.35 | 0 | 22.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 48.2972 | 594.35 | 0 | 0.05921 | 5.4815 | 0 | 0 | 216.2094 | 0 | off_peak | 594.35 |  |  | 0 | 0 | 100 | 0 | 0
2862 | 668.37 | 0 | 22.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 48.2972 | 668.37 | 0 | 0.05921 | 5.0032 | 0 | 0 | 216.2094 | 0 | off_peak | 668.37 |  |  | 0 | 0 | 100 | 0 | 0
2863 | 728.12 | 55.3733 | 23 | 11.2938 | 11.2938 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 48.2972 | 716.8262 | 0 | 0.05921 | 4.5916 | 0 | 0 | 216.2094 | 11.2938 | off_peak | 716.8262 |  |  | 1.55 | 0 | 98.45 | 51.8568 | 0
2864 | 716.31 | 152.933 | 23.2 | 31.1696 | 31.1696 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 48.2972 | 685.1404 | 0 | 0.05921 | 4.2711 | 0 | 0 | 216.2094 | 31.1696 | off_peak | 685.1404 |  |  | 4.35 | 0 | 95.65 | 133.1287 | 0
2865 | 794.54 | 423.047 | 23.5 | 86.1296 | 86.1296 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 48.2972 | 708.4104 | 0 | 0.05921 | 4.0922 | 0 | 0 | 216.2094 | 86.1296 | off_peak | 708.4104 |  |  | 10.84 | 0 | 89.16 | 352.4587 | 0
2866 | 781.68 | 274.747 | 23.7 | 55.8966 | 55.8966 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 48.2972 | 725.7834 | 0 | 0.05921 | 4.0303 | 0 | 0 | 216.2094 | 55.8966 | off_peak | 725.7834 |  |  | 7.15 | 0 | 92.85 | 225.2809 | 0
2867 | 784.05 | 675.974 | 23.9 | 137.4268 | 137.4268 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 48.2972 | 646.6232 | 0 | 0.05921 | 4.0852 | 0 | 0 | 216.2094 | 137.4268 | off_peak | 646.6232 |  |  | 17.53 | 0 | 82.47 | 561.4159 | 0
2868 | 737.53 | 909.756 | 24.2 | 184.7562 | 184.7562 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 48.2972 | 552.7738 | 0 | 0.05921 | 4.2109 | 0 | 0 | 216.2094 | 184.7562 | off_peak | 552.7738 |  |  | 25.05 | 0 | 74.95 | 777.9923 | 0
2869 | 739.49 | 739.763 | 24.4 | 150.1256 | 150.1256 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 59.8953 | 601.7634 | 0 | 0.05921 | 4.3788 | 0 | 0 | 216.2094 | 150.1256 | off_peak | 589.3644 | 0 | 100 | 20.3 | 0 | 79.7 | 657.3648 | 0
2870 | 726.4 | 713.48 | 24.5 | 144.7398 | 144.7398 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 59.8953 | 581.6602 | 0 | 0.05921 | 4.6344 | 0 | 0 | 216.2094 | 144.7398 | off_peak | 581.6602 |  |  | 19.93 | 0 | 80.07 | 670.789 | 0
2871 | 679.85 | 781.2 | 24.5 | 158.4777 | 158.4777 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 71.4935 | 533.7712 | 0 | 0.05921 | 4.8875 | 0 | 0 | 216.2094 | 158.4777 | off_peak | 521.3723 | 0 | 100 | 23.31 | 0 | 76.69 | 774.5551 | 0
2872 | 716.54 | 578.989 | 24.4 | 117.4985 | 117.4985 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 71.4935 | 599.0415 | 0 | 0.05921 | 4.9352 | 0 | 0 | 216.2094 | 117.4985 | off_peak | 599.0415 |  |  | 16.4 | 0 | 83.6 | 579.8766 | 0
2873 | 683.62 | 419.958 | 24.1 | 85.317 | 85.317 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 71.4935 | 598.303 | 0 | 0.05921 | 4.8299 | 0 | 0 | 216.2094 | 85.317 | off_peak | 598.303 |  |  | 12.48 | 0 | 87.52 | 412.0703 | 0
2874 | 680.35 | 89.3322 | 23.8 | 18.1679 | 18.1679 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 71.4935 | 662.1821 | 0 | 0.05921 | 4.7272 | 0 | 0 | 216.2094 | 18.1679 | off_peak | 662.1821 |  |  | 2.67 | 0 | 97.33 | 85.8839 | 0
2875 | 591.66 | 14.25 | 23.6 | 2.9002 | 0 | 0 | 2.9002 | 2.9002 | 0 | 0 | 0 | 0 | 74.2063 | 591.66 | 0 | 0.05921 | 4.7975 | 0 | 0 | 218.9223 | 0 | off_peak | 591.66 | 100 | 0 | 0 | 0 | 100 | 0 | 0
2876 | 577.36 | 0 | 22.9 | 0 | 0 | 0 | 0 | 0.18731 | 0.18731 | 0 | 0 | 0 | 74.3815 | 577.5473 | 0 | 0.05921 | 4.9324 | 0 | 0 | 218.9223 | 0 | off_peak | 577.36 | 0 | 100 | 0 | 0 | 100 | 0 | 0
2877 | 589.25 | 0 | 22.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3815 | 589.25 | 0 | 0.05921 | 5.1128 | 0 | 0 | 218.9223 | 0 | off_peak | 589.25 |  |  | 0 | 0 | 100 | 0 | 0
2878 | 591.34 | 0 | 22.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3815 | 591.34 | 0 | 0.05921 | 5.4154 | 0 | 0 | 218.9223 | 0 | off_peak | 591.34 |  |  | 0 | 0 | 100 | 0 | 0
2879 | 554.2 | 0 | 22.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3815 | 554.2 | 0 | 0.05921 | 5.7363 | 0 | 0 | 218.9223 | 0 | off_peak | 554.2 |  |  | 0 | 0 | 100 | 0 | 0
2880 | 571.5 | 0 | 22.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3815 | 571.5 | 0 | 0.05921 | 6.1091 | 0 | 0 | 218.9223 | 0 | off_peak | 571.5 |  |  | 0 | 0 | 100 | 0 | 0
2881 | 569.12 | 0 | 22.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3815 | 569.12 | 0 | 0.05921 | 6.2649 | 0 | 0 | 218.9223 | 0 | off_peak | 569.12 |  |  | 0 | 0 | 100 | 0 | 0
2882 | 556.12 | 0 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3815 | 556.12 | 0 | 0.05921 | 6.1887 | 0 | 0 | 218.9223 | 0 | off_peak | 556.12 |  |  | 0 | 0 | 100 | 0 | 0
2883 | 546.7 | 0 | 22 | 0 | 0 | 0 | 0 | 0.012097 | 0.012097 | 0 | 0 | 0 | 74.3929 | 546.7121 | 0 | 0.05921 | 5.8471 | 0 | 0 | 218.9223 | 0 | off_peak | 546.7 | 0 | 100 | 0 | 0 | 100 | 0 | 0
2884 | 558.7 | 0 | 21.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3929 | 558.7 | 0 | 0.05921 | 5.2127 | 0 | 0 | 218.9223 | 0 | off_peak | 558.7 |  |  | 0 | 0 | 100 | 0 | 0
2885 | 580.46 | 0 | 21.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3929 | 580.46 | 0 | 0.05921 | 4.481 | 0 | 0 | 218.9223 | 0 | off_peak | 580.46 |  |  | 0 | 0 | 100 | 0 | 0
2886 | 661.12 | 0 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3929 | 661.12 | 0 | 0.05921 | 3.9187 | 0 | 0 | 218.9223 | 0 | off_peak | 661.12 |  |  | 0 | 0 | 100 | 0 | 0
2887 | 740.59 | 96.8793 | 22.6 | 19.7876 | 19.7876 | 0 | 0 | 0.00078132 | 0.00078132 | 0 | 0 | 0 | 74.3936 | 720.8032 | 0 | 0.05921 | 3.4633 | 0 | 0 | 218.9223 | 19.7876 | off_peak | 720.8024 | 0 | 100 | 2.67 | 0 | 97.33 | 68.5293 | 0
2888 | 783.69 | 304.035 | 23.3 | 61.9439 | 61.9439 | 0 | 0 | 5.3947e-05 | 5.3947e-05 | 0 | 0 | 0 | 74.3936 | 721.7462 | 0 | 0.05921 | 3.1644 | 0 | 0 | 218.9223 | 61.9439 | off_peak | 721.7461 | 0 | 100 | 7.9 | 0 | 92.1 | 196.0143 | 0
2889 | 785.25 | 515.318 | 23.9 | 104.7651 | 104.7651 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 680.4849 | 0 | 0.05921 | 3.0063 | 0 | 0 | 218.9223 | 104.7651 | off_peak | 680.4849 |  |  | 13.34 | 0 | 86.66 | 314.9573 | 0
2890 | 785.88 | 703.435 | 24.6 | 142.6507 | 142.6507 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 643.2293 | 0 | 0.05921 | 3.0424 | 0 | 0 | 218.9223 | 142.6507 | off_peak | 643.2293 |  |  | 18.15 | 0 | 81.85 | 434.0035 | 0
2891 | 772.97 | 848.878 | 25.2 | 171.774 | 171.774 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 601.196 | 0 | 0.05921 | 3.2865 | 0 | 0 | 218.9223 | 171.774 | off_peak | 601.196 |  |  | 22.22 | 0 | 77.78 | 564.5416 | 0
2892 | 812.8 | 935.555 | 25.6 | 189.0407 | 189.0407 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 623.7593 | 0 | 0.05921 | 3.7268 | 0 | 0 | 218.9223 | 189.0407 | off_peak | 623.7593 |  |  | 23.26 | 0 | 76.74 | 704.5139 | 0
2893 | 791.66 | 954.667 | 25.9 | 192.6937 | 192.6937 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 598.9663 | 0 | 0.088511 | 3.928 | 0 | 0 | 218.9223 | 192.6937 | on_peak | 598.9663 |  |  | 24.34 | 0 | 75.66 | 756.8936 | 0
2894 | 810.58 | 908.484 | 26.1 | 183.2395 | 183.2395 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 627.3405 | 0 | 0.088511 | 3.8931 | 0 | 0 | 218.9223 | 183.2395 | on_peak | 627.3405 |  |  | 22.61 | 0 | 77.39 | 713.3766 | 0
2895 | 890.07 | 799.786 | 26.2 | 161.257 | 161.257 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 728.813 | 0 | 0.088511 | 3.8408 | 0 | 0 | 218.9223 | 161.257 | on_peak | 728.813 |  |  | 18.12 | 0 | 81.88 | 619.3621 | 0
2896 | 886.03 | 487.256 | 26 | 98.3141 | 98.3141 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 787.7159 | 0 | 0.088511 | 3.8689 | 0 | 0 | 218.9223 | 98.3141 | on_peak | 787.7159 |  |  | 11.1 | 0 | 88.9 | 380.3649 | 0
2897 | 872.97 | 376.005 | 25.7 | 75.9491 | 75.9491 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 797.0209 | 0 | 0.088511 | 4.056 | 0 | 0 | 218.9223 | 75.9491 | on_peak | 797.0209 |  |  | 8.7 | 0 | 91.3 | 308.0497 | 0
2898 | 859.47 | 222.419 | 25 | 45.0398 | 45.0398 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 814.4302 | 0 | 0.088511 | 4.3854 | 0 | 0 | 218.9223 | 45.0398 | on_peak | 814.4302 |  |  | 5.24 | 0 | 94.76 | 197.5174 | 0
2899 | 790.12 | 37.8942 | 24.7 | 7.6819 | 7.6819 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 782.4381 | 0 | 0.088511 | 4.7928 | 0 | 0 | 218.9223 | 7.6819 | on_peak | 782.4381 |  |  | 0.97 | 0 | 99.03 | 36.8173 | 0
2900 | 812.73 | 0 | 23.6 | 0 | 0 | 0 | 0 | 0 | 0 | 62.63 | 62.63 | 0 | 7.4394 | 750.1 | 0 | 0.088511 | 5.2066 | 62.63 | 0 | 151.968 | 62.63 | on_peak | 750.1 |  |  | 0 | 7.71 | 92.29 | 326.0904 | 0
2901 | 795.1 | 0 | 23.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 795.1 | 0 | 0.088511 | 5.5947 | 0 | 0 | 151.968 | 0 | on_peak | 795.1 |  |  | 0 | 0 | 100 | 0 | 0
2902 | 776.16 | 0 | 22.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 776.16 | 0 | 0.05921 | 6.0325 | 0 | 0 | 151.968 | 0 | off_peak | 776.16 |  |  | 0 | 0 | 100 | 0 | 0
2903 | 780.95 | 0 | 22.4 | 0 | 0 | 0 | 0 | 8.7263 | 8.7263 | 0 | 0 | 0 | 15.6021 | 789.6763 | 0 | 0.05921 | 6.4529 | 0 | 0 | 151.968 | 0 | off_peak | 780.95 | 0 | 100 | 0 | 0 | 100 | 0 | 0
2904 | 773.25 | 0 | 22.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15.6021 | 773.25 | 0 | 0.05921 | 6.7591 | 0 | 0 | 151.968 | 0 | off_peak | 773.25 |  |  | 0 | 0 | 100 | 0 | 0
2905 | 705.41 | 0 | 22.1 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 27.2003 | 717.8089 | 0 | 0.05921 | 6.8807 | 0 | 0 | 151.968 | 0 | off_peak | 705.41 | 0 | 100 | 0 | 0 | 100 | 0 | 0
2906 | 664.77 | 0 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27.2003 | 664.77 | 0 | 0.05921 | 6.7393 | 0 | 0 | 151.968 | 0 | off_peak | 664.77 |  |  | 0 | 0 | 100 | 0 | 0
2907 | 638.85 | 0 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27.2003 | 638.85 | 0 | 0.05921 | 6.2395 | 0 | 0 | 151.968 | 0 | off_peak | 638.85 |  |  | 0 | 0 | 100 | 0 | 0
2908 | 582.92 | 0 | 21.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27.2003 | 582.92 | 0 | 0.05921 | 5.5137 | 0 | 0 | 151.968 | 0 | off_peak | 582.92 |  |  | 0 | 0 | 100 | 0 | 0
2909 | 631.39 | 0 | 21.8 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 38.7984 | 643.7889 | 0 | 0.05921 | 4.6711 | 0 | 0 | 151.968 | 0 | off_peak | 631.39 | 0 | 100 | 0 | 0 | 100 | 0 | 0
2910 | 718.52 | 0 | 22 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 50.3966 | 730.9189 | 0 | 0.05921 | 4.0093 | 0 | 0 | 151.968 | 0 | off_peak | 718.52 | 0 | 100 | 0 | 0 | 100 | 0 | 0
2911 | 739.19 | 101.381 | 22.6 | 20.707 | 20.707 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 61.9947 | 730.8819 | 0 | 0.05921 | 3.5747 | 0 | 0 | 151.968 | 20.707 | off_peak | 718.483 | 0 | 100 | 2.8 | 0 | 97.2 | 74.0218 | 0
2912 | 767.59 | 306.249 | 23.4 | 62.3726 | 62.3726 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 73.5928 | 717.6163 | 0 | 0.05921 | 3.3383 | 0 | 0 | 151.968 | 62.3726 | off_peak | 705.2174 | 0 | 100 | 8.13 | 0 | 91.87 | 208.217 | 0
2913 | 801.91 | 518.191 | 24 | 105.3114 | 105.3114 | 0 | 0 | 0.80079 | 0.80079 | 0 | 0 | 0 | 74.3419 | 697.3994 | 0 | 0.05921 | 3.1529 | 0 | 0 | 151.968 | 105.3114 | off_peak | 696.5986 | 0 | 100 | 13.13 | 0 | 86.87 | 332.0331 | 0
2914 | 807.42 | 703.456 | 24.7 | 142.6037 | 142.6037 | 0 | 0 | 0.05172 | 0.05172 | 0 | 0 | 0 | 74.3903 | 664.868 | 0 | 0.05921 | 3.0988 | 0 | 0 | 151.968 | 142.6037 | off_peak | 664.8163 | 0 | 100 | 17.66 | 0 | 82.34 | 441.9005 | 0
2915 | 815.62 | 844.219 | 25.3 | 170.7697 | 170.7697 | 0 | 0 | 0.0033404 | 0.0033404 | 0 | 0 | 0 | 74.3934 | 644.8536 | 0 | 0.05921 | 3.254 | 0 | 0 | 151.968 | 170.7697 | off_peak | 644.8503 | 0 | 100 | 20.94 | 0 | 79.06 | 555.6847 | 0
2916 | 835.82 | 925.063 | 25.7 | 186.8532 | 186.8532 | 0 | 0 | 0.00021574 | 0.00021574 | 0 | 0 | 0 | 74.3936 | 648.967 | 0 | 0.05921 | 3.6966 | 0 | 0 | 151.968 | 186.8532 | off_peak | 648.9668 | 0 | 100 | 22.36 | 0 | 77.64 | 690.7215 | 0
2917 | 825.4 | 943.646 | 26.1 | 190.3316 | 190.3316 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 635.0684 | 0 | 0.088511 | 3.9237 | 0 | 0 | 151.968 | 190.3316 | on_peak | 635.0684 |  |  | 23.06 | 0 | 76.94 | 746.8016 | 0
2918 | 821.64 | 896.105 | 26.3 | 180.612 | 180.612 | 0 | 0 | 1.3934e-05 | 1.3934e-05 | 0 | 0 | 0 | 74.3936 | 641.028 | 0 | 0.088511 | 3.9614 | 0 | 0 | 151.968 | 180.612 | on_peak | 641.028 | 0 | 100 | 21.98 | 0 | 78.02 | 715.4842 | 0
2919 | 903.18 | 784.591 | 26.4 | 158.0789 | 158.0789 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 745.1011 | 0 | 0.088511 | 3.961 | 0 | 0 | 151.968 | 158.0789 | on_peak | 745.1011 |  |  | 17.5 | 0 | 82.5 | 626.1474 | 0
2920 | 887.15 | 624.343 | 26.3 | 125.8378 | 125.8378 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 761.3122 | 0 | 0.088511 | 4.1193 | 0 | 0 | 151.968 | 125.8378 | on_peak | 761.3122 |  |  | 14.18 | 0 | 85.82 | 518.3661 | 0
2921 | 907.78 | 428.655 | 26 | 86.4901 | 86.4901 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 821.2899 | 0 | 0.088511 | 4.3554 | 0 | 0 | 151.968 | 86.4901 | on_peak | 821.2899 |  |  | 9.53 | 0 | 90.47 | 376.6978 | 0
2922 | 894.7 | 218.384 | 25.4 | 44.1591 | 44.1591 | 0 | 0 | 0 | 0 | 7.7529 | 7.7529 | 0 | 66.1054 | 842.788 | 0 | 0.088511 | 4.7485 | 0 | 0 | 151.968 | 44.1591 | on_peak | 842.788 |  |  | 4.94 | 0.87 | 94.2 | 209.6904 | 0
2923 | 814.4 | 34.289 | 24.9 | 6.946 | 2.6638 | 0 | 4.2822 | 4.2822 | 0 | 0 | 0 | 0 | 70.1111 | 811.7362 | 0 | 0.088511 | 5.1986 | 0 | 0 | 155.9737 | 2.6638 | on_peak | 811.7362 | 100 | 0 | 0.33 | 0 | 99.67 | 13.8478 | 0
2924 | 893.12 | 0 | 23.8 | 0 | 0 | 0 | 0 | 0 | 0 | 50.332 | 50.332 | 0 | 16.3039 | 842.788 | 0 | 0.088511 | 5.6316 | 0 | 0 | 155.9737 | 0 | on_peak | 842.788 |  |  | 0 | 5.64 | 94.36 | 0 | 0
2925 | 851.08 | 0 | 23.4 | 0 | 0 | 0 | 0 | 0 | 0 | 8.292 | 8.292 | 0 | 7.4394 | 842.788 | 0 | 0.088511 | 5.9993 | 0 | 0 | 155.9737 | 0 | on_peak | 842.788 |  |  | 0 | 0.97 | 99.03 | 0 | 0
2926 | 773.75 | 0 | 23.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 773.75 | 0 | 0.05921 | 6.4949 | 0 | 0 | 155.9737 | 0 | off_peak | 773.75 |  |  | 0 | 0 | 100 | 0 | 0
2927 | 813.69 | 0 | 22.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 813.69 | 0 | 0.05921 | 6.8912 | 0 | 0 | 155.9737 | 0 | off_peak | 813.69 |  |  | 0 | 0 | 100 | 0 | 0
2928 | 813.48 | 0 | 22.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 813.48 | 0 | 0.05921 | 7.2316 | 0 | 0 | 155.9737 | 0 | off_peak | 813.48 |  |  | 0 | 0 | 100 | 0 | 0
2929 | 718.35 | 0 | 22.6 | 0 | 0 | 0 | 0 | 8.7263 | 8.7263 | 0 | 0 | 0 | 15.6021 | 727.0763 | 0 | 0.05921 | 7.3255 | 0 | 0 | 155.9737 | 0 | off_peak | 718.35 | 0 | 100 | 0 | 0 | 100 | 0 | 0
2930 | 563.84 | 0 | 22.5 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 27.2003 | 576.2389 | 0 | 0.05921 | 7.1506 | 0 | 0 | 155.9737 | 0 | off_peak | 563.84 | 0 | 100 | 0 | 0 | 100 | 0 | 0
2931 | 529.81 | 0 | 22.4 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 38.7984 | 542.2089 | 0 | 0.05921 | 6.5846 | 0 | 0 | 155.9737 | 0 | off_peak | 529.81 | 0 | 100 | 0 | 0 | 100 | 0 | 0
2932 | 500.84 | 0 | 22.3 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 50.3966 | 513.2389 | 0 | 0.05921 | 5.8092 | 0 | 0 | 155.9737 | 0 | off_peak | 500.84 | 0 | 100 | 0 | 0 | 100 | 0 | 0
2933 | 535.74 | 0 | 22.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50.3966 | 535.74 | 0 | 0.05921 | 4.9587 | 0 | 0 | 155.9737 | 0 | off_peak | 535.74 |  |  | 0 | 0 | 100 | 0 | 0
2934 | 711.06 | 0 | 22.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50.3966 | 711.06 | 0 | 0.05921 | 4.212 | 0 | 0 | 155.9737 | 0 | off_peak | 711.06 |  |  | 0 | 0 | 100 | 0 | 0
2935 | 726.3 | 103.821 | 23.2 | 21.16 | 8.761 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 0 | 61.9947 | 717.539 | 0 | 0.05921 | 3.7811 | 0 | 0 | 167.5718 | 8.761 | off_peak | 717.539 | 100 | 0 | 1.21 | 0 | 98.79 | 33.1268 | 0
2936 | 777.28 | 277.582 | 24 | 56.4127 | 56.4127 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 73.5928 | 733.2662 | 0 | 0.05921 | 3.5071 | 0 | 0 | 167.5718 | 56.4127 | off_peak | 720.8673 | 0 | 100 | 7.26 | 0 | 92.74 | 197.8469 | 0
2937 | 815.17 | 423.137 | 24.7 | 85.7778 | 85.7778 | 0 | 0 | 0.80079 | 0.80079 | 0 | 0 | 0 | 74.3419 | 730.193 | 0 | 0.05921 | 3.3311 | 0 | 0 | 167.5718 | 85.7778 | off_peak | 729.3922 | 0 | 100 | 10.52 | 0 | 89.48 | 285.7358 | 0
2938 | 795.03 | 640.256 | 25.3 | 129.5118 | 129.5118 | 0 | 0 | 0.05172 | 0.05172 | 0 | 0 | 0 | 74.3903 | 665.5699 | 0 | 0.05921 | 3.2834 | 0 | 0 | 167.5718 | 129.5118 | off_peak | 665.5182 | 0 | 100 | 16.29 | 0 | 83.71 | 425.2375 | 0
2939 | 796.43 | 818.188 | 25.9 | 165.1463 | 165.1463 | 0 | 0 | 0.0033404 | 0.0033404 | 0 | 0 | 0 | 74.3934 | 631.2871 | 0 | 0.05921 | 3.4849 | 0 | 0 | 167.5718 | 165.1463 | off_peak | 631.2837 | 0 | 100 | 20.74 | 0 | 79.26 | 575.5135 | 0
2940 | 868.83 | 907.304 | 26.3 | 182.8692 | 182.8692 | 0 | 0 | 0.00021574 | 0.00021574 | 0 | 0 | 0 | 74.3936 | 685.961 | 0 | 0.05921 | 3.9311 | 0 | 0 | 167.5718 | 182.8692 | off_peak | 685.9608 | 0 | 100 | 21.05 | 0 | 78.95 | 718.8808 | 0
2941 | 819.49 | 809.286 | 26.7 | 162.8775 | 162.8775 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 656.6125 | 0 | 0.088511 | 4.1135 | 0 | 0 | 167.5718 | 162.8775 | on_peak | 656.6125 |  |  | 19.88 | 0 | 80.12 | 669.9901 | 0
2942 | 849.86 | 805.152 | 26.9 | 161.9281 | 161.9281 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 687.9319 | 0 | 0.088511 | 4.1373 | 0 | 0 | 167.5718 | 161.9281 | on_peak | 687.9319 |  |  | 19.05 | 0 | 80.95 | 669.9408 | 0
2943 | 908.8 | 770.334 | 26.9 | 154.9256 | 154.9256 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 753.8744 | 0 | 0.088511 | 4.1773 | 0 | 0 | 167.5718 | 154.9256 | on_peak | 753.8744 |  |  | 17.05 | 0 | 82.95 | 647.1728 | 0
2944 | 903.54 | 477.687 | 26.7 | 96.1396 | 96.1396 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 807.4004 | 0 | 0.088511 | 4.247 | 0 | 0 | 167.5718 | 96.1396 | on_peak | 807.4004 |  |  | 10.64 | 0 | 89.36 | 408.3078 | 0
2945 | 893.79 | 376.891 | 26.4 | 75.9358 | 75.9358 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 817.8542 | 0 | 0.088511 | 4.3855 | 0 | 0 | 167.5718 | 75.9358 | on_peak | 817.8542 |  |  | 8.5 | 0 | 91.5 | 333.0172 | 0
2946 | 878.74 | 209.42 | 25.7 | 42.3007 | 42.3007 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 836.4393 | 0 | 0.088511 | 4.6583 | 0 | 0 | 167.5718 | 42.3007 | on_peak | 836.4393 |  |  | 4.81 | 0 | 95.19 | 197.0509 | 0
2947 | 835.03 | 35.1914 | 25.2 | 7.1211 | 7.1211 | 0 | 0 | 0 | 0 | 12.696 | 12.696 | 0 | 60.8211 | 815.2129 | 0 | 0.088511 | 5.0567 | 0 | 0 | 167.5718 | 7.1211 | on_peak | 815.2129 |  |  | 0.85 | 1.52 | 97.63 | 36.0097 | 0
2948 | 876.43 | 0 | 24.1 | 0 | 0 | 0 | 0 | 0 | 0 | 33.642 | 33.642 | 0 | 24.8563 | 842.788 | 0 | 0.088511 | 5.4214 | 0 | 0 | 167.5718 | 0 | on_peak | 842.788 |  |  | 0 | 3.84 | 96.16 | 0 | 0
2949 | 859.08 | 0 | 23.9 | 0 | 0 | 0 | 0 | 0 | 0 | 16.292 | 16.292 | 0 | 7.4394 | 842.788 | 0 | 0.088511 | 5.7971 | 0 | 0 | 167.5718 | 0 | on_peak | 842.788 |  |  | 0 | 1.9 | 98.1 | 0 | 0
2950 | 751.38 | 0 | 23.7 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 19.0375 | 763.7789 | 0 | 0.05921 | 6.3501 | 0 | 0 | 167.5718 | 0 | off_peak | 751.38 | 0 | 100 | 0 | 0 | 100 | 0 | 0
2951 | 789.36 | 0 | 23.6 | 0 | 0 | 0 | 0 | 8.7263 | 8.7263 | 0 | 0 | 0 | 27.2003 | 798.0863 | 0 | 0.05921 | 6.7912 | 0 | 0 | 167.5718 | 0 | off_peak | 789.36 | 0 | 100 | 0 | 0 | 100 | 0 | 0
2952 | 736.57 | 0 | 23.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27.2003 | 736.57 | 0 | 0.05921 | 7.138 | 0 | 0 | 167.5718 | 0 | off_peak | 736.57 |  |  | 0 | 0 | 100 | 0 | 0
2953 | 720.64 | 0 | 23.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27.2003 | 720.64 | 0 | 0.05921 | 7.2332 | 0 | 0 | 167.5718 | 0 | off_peak | 720.64 |  |  | 0 | 0 | 100 | 0 | 0
2954 | 652.45 | 0 | 23.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27.2003 | 652.45 | 0 | 0.05921 | 7.0618 | 0 | 0 | 167.5718 | 0 | off_peak | 652.45 |  |  | 0 | 0 | 100 | 0 | 0
2955 | 620.21 | 0 | 23.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27.2003 | 620.21 | 0 | 0.05921 | 6.4713 | 0 | 0 | 167.5718 | 0 | off_peak | 620.21 |  |  | 0 | 0 | 100 | 0 | 0
2956 | 582.57 | 0 | 23 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 38.7984 | 594.9689 | 0 | 0.05921 | 5.7161 | 0 | 0 | 167.5718 | 0 | off_peak | 582.57 | 0 | 100 | 0 | 0 | 100 | 0 | 0
2957 | 594.07 | 0 | 22.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 38.7984 | 594.07 | 0 | 0.05921 | 4.7751 | 0 | 0 | 167.5718 | 0 | off_peak | 594.07 |  |  | 0 | 0 | 100 | 0 | 0
2958 | 694.77 | 0 | 22.7 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 50.3966 | 707.1689 | 0 | 0.05921 | 4.0103 | 0 | 0 | 167.5718 | 0 | off_peak | 694.77 | 0 | 100 | 0 | 0 | 100 | 0 | 0
2959 | 754.74 | 102.764 | 23.3 | 20.9371 | 20.9371 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 61.9947 | 746.2019 | 0 | 0.05921 | 3.5254 | 0 | 0 | 167.5718 | 20.9371 | off_peak | 733.8029 | 0 | 100 | 2.77 | 0 | 97.23 | 73.812 | 0
2960 | 792.23 | 307.97 | 24.3 | 62.5211 | 62.5211 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 73.5928 | 742.1079 | 0 | 0.05921 | 3.3156 | 0 | 0 | 167.5718 | 62.5211 | off_peak | 729.7089 | 0 | 100 | 7.89 | 0 | 92.11 | 207.2962 | 0
2961 | 781.8 | 518.838 | 25.3 | 104.9512 | 104.9512 | 0 | 0 | 0.80079 | 0.80079 | 0 | 0 | 0 | 74.3419 | 677.6496 | 0 | 0.05921 | 3.1461 | 0 | 0 | 167.5718 | 104.9512 | off_peak | 676.8488 | 0 | 100 | 13.42 | 0 | 86.58 | 330.1821 | 0
2962 | 821.14 | 704.72 | 26.4 | 141.9866 | 141.9866 | 0 | 0 | 0.05172 | 0.05172 | 0 | 0 | 0 | 74.3903 | 679.2052 | 0 | 0.05921 | 3.0936 | 0 | 0 | 167.5718 | 141.9866 | off_peak | 679.1534 | 0 | 100 | 17.29 | 0 | 82.71 | 439.2453 | 0
2963 | 798.59 | 845.905 | 27.4 | 169.8158 | 169.8158 | 0 | 0 | 0.0033404 | 0.0033404 | 0 | 0 | 0 | 74.3934 | 628.7776 | 0 | 0.05921 | 3.3459 | 0 | 0 | 167.5718 | 169.8158 | off_peak | 628.7742 | 0 | 100 | 21.26 | 0 | 78.74 | 568.1828 | 0
2964 | 856.49 | 930.411 | 28.2 | 186.2378 | 186.2378 | 0 | 0 | 0.00021574 | 0.00021574 | 0 | 0 | 0 | 74.3936 | 670.2525 | 0 | 0.05921 | 3.7309 | 0 | 0 | 167.5718 | 186.2378 | off_peak | 670.2522 | 0 | 100 | 21.74 | 0 | 78.26 | 694.8367 | 0
2965 | 755.27 | 944.201 | 28.8 | 188.5851 | 188.5851 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 566.6849 | 0 | 0.088511 | 3.8334 | 0 | 0 | 167.5718 | 188.5851 | on_peak | 566.6849 |  |  | 24.97 | 0 | 75.03 | 722.9259 | 0
2966 | 801.68 | 892.899 | 29.1 | 178.1433 | 178.1433 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 623.5367 | 0 | 0.088511 | 3.8157 | 0 | 0 | 167.5718 | 178.1433 | on_peak | 623.5367 |  |  | 22.22 | 0 | 77.78 | 679.7371 | 0
2967 | 916.44 | 787.094 | 29.3 | 156.9192 | 156.9192 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 759.5208 | 0 | 0.088511 | 3.7508 | 0 | 0 | 167.5718 | 156.9192 | on_peak | 759.5208 |  |  | 17.12 | 0 | 82.88 | 588.5667 | 0
2968 | 895.37 | 626.728 | 29.2 | 124.9935 | 124.9935 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 770.3765 | 0 | 0.088511 | 3.7981 | 0 | 0 | 167.5718 | 124.9935 | on_peak | 770.3765 |  |  | 13.96 | 0 | 86.04 | 474.7393 | 0
2969 | 877.93 | 431.158 | 28.8 | 86.1151 | 86.1151 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 791.8149 | 0 | 0.088511 | 3.9897 | 0 | 0 | 167.5718 | 86.1151 | on_peak | 791.8149 |  |  | 9.81 | 0 | 90.19 | 343.5762 | 0
2970 | 901.64 | 221.868 | 28 | 44.443 | 44.443 | 0 | 0 | 0 | 0 | 14.409 | 14.409 | 0 | 58.9898 | 842.788 | 0 | 0.088511 | 4.3449 | 0 | 0 | 167.5718 | 44.443 | on_peak | 842.788 |  |  | 4.93 | 1.6 | 93.47 | 193.0985 | 0
2971 | 822.82 | 32.4252 | 27.4 | 6.5094 | 6.5094 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 58.9898 | 816.3106 | 0 | 0.088511 | 4.829 | 0 | 0 | 167.5718 | 6.5094 | on_peak | 816.3106 |  |  | 0.79 | 0 | 99.21 | 31.434 | 0
2972 | 878.44 | 0 | 26.1 | 0 | 0 | 0 | 0 | 0 | 0 | 48.221 | 48.221 | 0 | 7.4394 | 830.219 | 0 | 0.088511 | 5.2617 | 48.221 | 0 | 116.0214 | 48.221 | on_peak | 830.219 |  |  | 0 | 5.49 | 94.51 | 253.7225 | 0
2973 | 817.62 | 0 | 25.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 817.62 | 0 | 0.088511 | 5.6455 | 0 | 0 | 116.0214 | 0 | on_peak | 817.62 |  |  | 0 | 0 | 100 | 0 | 0
2974 | 767 | 0 | 25.4 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 19.0375 | 779.3989 | 0 | 0.05921 | 6.1147 | 0 | 0 | 116.0214 | 0 | off_peak | 767 | 0 | 100 | 0 | 0 | 100 | 0 | 0
2975 | 796.29 | 0 | 25.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19.0375 | 796.29 | 0 | 0.05921 | 6.5873 | 0 | 0 | 116.0214 | 0 | off_peak | 796.29 |  |  | 0 | 0 | 100 | 0 | 0
2976 | 782.01 | 0 | 24.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19.0375 | 782.01 | 0 | 0.05921 | 6.9155 | 0 | 0 | 116.0214 | 0 | off_peak | 782.01 |  |  | 0 | 0 | 100 | 0 | 0
2977 | 746.71 | 0 | 24.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19.0375 | 746.71 | 0 | 0.05921 | 6.8316 | 0 | 0 | 116.0214 | 0 | off_peak | 746.71 |  |  | 0 | 0 | 100 | 0 | 0
2978 | 694.19 | 0 | 23.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19.0375 | 694.19 | 0 | 0.05921 | 6.748 | 0 | 0 | 116.0214 | 0 | off_peak | 694.19 |  |  | 0 | 0 | 100 | 0 | 0
2979 | 671.64 | 0 | 23.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19.0375 | 671.64 | 0 | 0.05921 | 6.2503 | 0 | 0 | 116.0214 | 0 | off_peak | 671.64 |  |  | 0 | 0 | 100 | 0 | 0
2980 | 596.4 | 0 | 23.3 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 30.6357 | 608.7989 | 0 | 0.05921 | 5.5407 | 0 | 0 | 116.0214 | 0 | off_peak | 596.4 | 0 | 100 | 0 | 0 | 100 | 0 | 0
2981 | 644.53 | 0 | 23.1 | 0 | 0 | 0 | 0 | 8.7263 | 8.7263 | 0 | 0 | 0 | 38.7984 | 653.2563 | 0 | 0.05921 | 4.7183 | 0 | 0 | 116.0214 | 0 | off_peak | 644.53 | 0 | 100 | 0 | 0 | 100 | 0 | 0
2982 | 693.3 | 0 | 23.2 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 50.3966 | 705.6989 | 0 | 0.05921 | 4.0081 | 0 | 0 | 116.0214 | 0 | off_peak | 693.3 | 0 | 100 | 0 | 0 | 100 | 0 | 0
2983 | 782.11 | 106.5 | 23.9 | 21.6517 | 9.2527 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 0 | 61.9947 | 772.8573 | 0 | 0.05921 | 3.5698 | 0 | 0 | 127.6195 | 9.2527 | off_peak | 772.8573 | 100 | 0 | 1.18 | 0 | 98.82 | 33.03 | 0
2984 | 818.09 | 312.857 | 25 | 63.3535 | 63.3535 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 73.5928 | 767.1354 | 0 | 0.05921 | 3.4454 | 0 | 0 | 127.6195 | 63.3535 | off_peak | 754.7365 | 0 | 100 | 7.74 | 0 | 92.26 | 218.279 | 0
2985 | 806.55 | 377.729 | 26.2 | 76.1597 | 76.1597 | 0 | 0 | 0.80079 | 0.80079 | 0 | 0 | 0 | 74.3419 | 731.1911 | 0 | 0.05921 | 3.2768 | 0 | 0 | 127.6195 | 76.1597 | off_peak | 730.3903 | 0 | 100 | 9.44 | 0 | 90.56 | 249.5625 | 0
2986 | 813.48 | 707.985 | 27.4 | 142.1283 | 142.1283 | 0 | 0 | 0.05172 | 0.05172 | 0 | 0 | 0 | 74.3903 | 671.4034 | 0 | 0.05921 | 3.2125 | 0 | 0 | 127.6195 | 142.1283 | off_peak | 671.3517 | 0 | 100 | 17.47 | 0 | 82.53 | 456.5924 | 0
2987 | 795.94 | 847.943 | 28.3 | 169.6686 | 169.6686 | 0 | 0 | 0.0033404 | 0.0033404 | 0 | 0 | 0 | 74.3934 | 626.2748 | 0 | 0.05921 | 3.3841 | 0 | 0 | 127.6195 | 169.6686 | off_peak | 626.2714 | 0 | 100 | 21.32 | 0 | 78.68 | 574.1681 | 0
2988 | 855.11 | 932.051 | 29 | 186.0225 | 186.0225 | 0 | 0 | 0.00021574 | 0.00021574 | 0 | 0 | 0 | 74.3936 | 669.0877 | 0 | 0.05921 | 3.7989 | 0 | 0 | 127.6195 | 186.0225 | off_peak | 669.0875 | 0 | 100 | 21.75 | 0 | 78.25 | 706.6817 | 0
2989 | 795.69 | 953.978 | 29.4 | 190.1206 | 190.1206 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 605.5694 | 0 | 0.088511 | 4.0556 | 0 | 0 | 127.6195 | 190.1206 | on_peak | 605.5694 |  |  | 23.89 | 0 | 76.11 | 771.0622 | 0
2990 | 858.07 | 910.282 | 29.7 | 181.2132 | 181.2132 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 676.8568 | 0 | 0.088511 | 4.2532 | 0 | 0 | 127.6195 | 181.2132 | on_peak | 676.8568 |  |  | 21.12 | 0 | 78.88 | 770.7301 | 0
2991 | 935.42 | 803.439 | 29.8 | 159.885 | 159.885 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 775.535 | 0 | 0.088511 | 4.4019 | 0 | 0 | 127.6195 | 159.885 | on_peak | 775.535 |  |  | 17.09 | 0 | 82.91 | 703.7917 | 0
2992 | 885 | 644.505 | 29.7 | 128.304 | 128.304 | 0 | 0 | 0 | 0 | 48.1564 | 48.1564 | 0 | 22.9123 | 708.5396 | 0 | 0.088511 | 4.6844 | 0 | 0 | 127.6195 | 128.304 | on_peak | 708.5396 |  |  | 14.5 | 5.44 | 80.06 | 601.0278 | 0
2993 | 887.68 | 445.304 | 29.3 | 88.7782 | 88.7782 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22.9123 | 798.9018 | 0 | 0.088511 | 5.1016 | 0 | 0 | 127.6195 | 88.7782 | on_peak | 798.9018 |  |  | 10 | 0 | 90 | 452.9144 | 0
2994 | 903.47 | 231.186 | 28.6 | 46.2084 | 46.2084 | 0 | 0 | 0 | 0 | 14.4736 | 14.4736 | 0 | 7.4394 | 842.788 | 0 | 0.088511 | 5.476 | 0 | 0 | 127.6195 | 46.2084 | on_peak | 842.788 |  |  | 5.11 | 1.6 | 93.28 | 253.0359 | 0
2995 | 838.34 | 39.6236 | 28.2 | 7.9313 | 7.9313 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 830.4087 | 0 | 0.088511 | 5.8178 | 0 | 0 | 127.6195 | 7.9313 | on_peak | 830.4087 |  |  | 0.95 | 0 | 99.05 | 46.1431 | 0
2996 | 825.57 | 0 | 27 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 825.57 | 0 | 0.088511 | 6.1539 | 0 | 0 | 127.6195 | 0 | on_peak | 825.57 |  |  | 0 | 0 | 100 | 0 | 0
2997 | 804.53 | 0 | 26.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 804.53 | 0 | 0.088511 | 6.4419 | 0 | 0 | 127.6195 | 0 | on_peak | 804.53 |  |  | 0 | 0 | 100 | 0 | 0
2998 | 779.28 | 0 | 25.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 779.28 | 0 | 0.05921 | 6.7589 | 0 | 0 | 127.6195 | 0 | off_peak | 779.28 |  |  | 0 | 0 | 100 | 0 | 0
2999 | 777.75 | 0 | 25.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 777.75 | 0 | 0.05921 | 6.9257 | 0 | 0 | 127.6195 | 0 | off_peak | 777.75 |  |  | 0 | 0 | 100 | 0 | 0
3000 | 760.51 | 0 | 24.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 760.51 | 0 | 0.05921 | 6.9351 | 0 | 0 | 127.6195 | 0 | off_peak | 760.51 |  |  | 0 | 0 | 100 | 0 | 0
3001 | 765.17 | 0 | 24.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 765.17 | 0 | 0.05921 | 6.7464 | 0 | 0 | 127.6195 | 0 | off_peak | 765.17 |  |  | 0 | 0 | 100 | 0 | 0
3002 | 682.07 | 0 | 24.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 682.07 | 0 | 0.05921 | 6.6125 | 0 | 0 | 127.6195 | 0 | off_peak | 682.07 |  |  | 0 | 0 | 100 | 0 | 0
3003 | 630.16 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 630.16 | 0 | 0.05921 | 6.2284 | 0 | 0 | 127.6195 | 0 | off_peak | 630.16 |  |  | 0 | 0 | 100 | 0 | 0
3004 | 614.91 | 0 | 23.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 614.91 | 0 | 0.05921 | 5.7437 | 0 | 0 | 127.6195 | 0 | off_peak | 614.91 |  |  | 0 | 0 | 100 | 0 | 0
3005 | 618.43 | 0 | 23.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 618.43 | 0 | 0.05921 | 5.0555 | 0 | 0 | 127.6195 | 0 | off_peak | 618.43 |  |  | 0 | 0 | 100 | 0 | 0
3006 | 722.04 | 0 | 23.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 722.04 | 0 | 0.05921 | 4.3709 | 0 | 0 | 127.6195 | 0 | off_peak | 722.04 |  |  | 0 | 0 | 100 | 0 | 0
3007 | 735.15 | 113.334 | 24.6 | 22.9832 | 22.9832 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 712.1668 | 0 | 0.05921 | 3.998 | 0 | 0 | 127.6195 | 22.9832 | off_peak | 712.1668 |  |  | 3.13 | 0 | 96.87 | 91.8868 | 0
3008 | 743.08 | 320.061 | 25.5 | 64.6957 | 64.6957 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 678.3843 | 0 | 0.05921 | 3.8255 | 0 | 0 | 127.6195 | 64.6957 | off_peak | 678.3843 |  |  | 8.71 | 0 | 91.29 | 247.4932 | 0
3009 | 784.11 | 531.07 | 26.3 | 107.0384 | 107.0384 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 677.0716 | 0 | 0.05921 | 3.5955 | 0 | 0 | 127.6195 | 107.0384 | off_peak | 677.0716 |  |  | 13.65 | 0 | 86.35 | 384.8605 | 0
3010 | 729.85 | 717.709 | 27.2 | 144.185 | 144.185 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 585.665 | 0 | 0.05921 | 3.4806 | 0 | 0 | 127.6195 | 144.185 | off_peak | 585.665 |  |  | 19.76 | 0 | 80.24 | 501.8436 | 0
3011 | 719.27 | 859.24 | 27.9 | 172.1796 | 172.1796 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 547.0904 | 0 | 0.05921 | 3.485 | 0 | 0 | 127.6195 | 172.1796 | off_peak | 547.0904 |  |  | 23.94 | 0 | 76.06 | 600.041 | 0
3012 | 764.83 | 815.187 | 28.6 | 162.936 | 162.936 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 601.894 | 0 | 0.05921 | 3.5678 | 0 | 0 | 127.6195 | 162.936 | off_peak | 601.894 |  |  | 21.3 | 0 | 78.7 | 581.3193 | 0
3013 | 739.99 | 940.012 | 29.1 | 187.5428 | 187.5428 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 552.4472 | 0 | 0.05921 | 3.7384 | 0 | 0 | 127.6195 | 187.5428 | off_peak | 552.4472 |  |  | 25.34 | 0 | 74.66 | 701.113 | 0
3014 | 734.93 | 909.328 | 29.4 | 181.2222 | 181.2222 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 19.0375 | 566.1068 | 0 | 0.05921 | 4.1517 | 0 | 0 | 127.6195 | 181.2222 | off_peak | 553.7078 | 0 | 100 | 24.66 | 0 | 75.34 | 752.3837 | 0
3015 | 751.71 | 773.127 | 29.5 | 154.022 | 154.022 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19.0375 | 597.688 | 0 | 0.05921 | 4.6521 | 0 | 0 | 127.6195 | 154.022 | off_peak | 597.688 |  |  | 20.49 | 0 | 79.51 | 716.5236 | 0
3016 | 734.83 | 636.863 | 29.4 | 126.922 | 126.922 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19.0375 | 607.908 | 0 | 0.05921 | 5.0066 | 0 | 0 | 127.6195 | 126.922 | off_peak | 607.908 |  |  | 17.27 | 0 | 82.73 | 635.4484 | 0
3017 | 761.54 | 383.358 | 29.1 | 76.4842 | 76.4842 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19.0375 | 685.0558 | 0 | 0.05921 | 5.3898 | 0 | 0 | 127.6195 | 76.4842 | off_peak | 685.0558 |  |  | 10.04 | 0 | 89.96 | 412.234 | 0
3018 | 653.2 | 63.6235 | 28.4 | 12.7261 | 0.32712 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 0 | 30.6357 | 652.8729 | 0 | 0.05921 | 5.7765 | 0 | 0 | 139.2177 | 0.32712 | off_peak | 652.8729 | 100 | 0 | 0.05 | 0 | 99.95 | 1.8896 | 0
3019 | 585.11 | 19 | 28 | 3.8059 | 0 | 0 | 3.8059 | 3.8059 | 0 | 0 | 0 | 0 | 34.1958 | 585.11 | 0 | 0.05921 | 6.1393 | 0 | 0 | 142.7778 | 0 | off_peak | 585.11 | 100 | 0 | 0 | 0 | 100 | 0 | 0
3020 | 602.65 | 0 | 26.7 | 0 | 0 | 0 | 0 | 11.8227 | 11.8227 | 0 | 0 | 0 | 45.255 | 614.4727 | 0 | 0.05921 | 6.4132 | 0 | 0 | 142.7778 | 0 | off_peak | 602.65 | 0 | 100 | 0 | 0 | 100 | 0 | 0
3021 | 596.96 | 0 | 26.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 45.255 | 596.96 | 0 | 0.05921 | 6.614 | 0 | 0 | 142.7778 | 0 | off_peak | 596.96 |  |  | 0 | 0 | 100 | 0 | 0
3022 | 578.77 | 0 | 25.8 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 56.8531 | 591.1689 | 0 | 0.05921 | 6.6928 | 0 | 0 | 142.7778 | 0 | off_peak | 578.77 | 0 | 100 | 0 | 0 | 100 | 0 | 0
3023 | 620.27 | 0 | 25.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 56.8531 | 620.27 | 0 | 0.05921 | 6.7481 | 0 | 0 | 142.7778 | 0 | off_peak | 620.27 |  |  | 0 | 0 | 100 | 0 | 0
3024 | 556.98 | 0 | 25.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 56.8531 | 556.98 | 0 | 0.05921 | 6.6628 | 0 | 0 | 142.7778 | 0 | off_peak | 556.98 |  |  | 0 | 0 | 100 | 0 | 0
3025 | 589.16 | 0 | 24.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 56.8531 | 589.16 | 0 | 0.05921 | 6.5371 | 0 | 0 | 142.7778 | 0 | off_peak | 589.16 |  |  | 0 | 0 | 100 | 0 | 0
3026 | 577.93 | 0 | 24.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 56.8531 | 577.93 | 0 | 0.05921 | 6.5512 | 0 | 0 | 142.7778 | 0 | off_peak | 577.93 |  |  | 0 | 0 | 100 | 0 | 0
3027 | 577.3 | 0 | 24.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 56.8531 | 577.3 | 0 | 0.05921 | 6.1563 | 0 | 0 | 142.7778 | 0 | off_peak | 577.3 |  |  | 0 | 0 | 100 | 0 | 0
3028 | 576.62 | 0 | 24.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 56.8531 | 576.62 | 0 | 0.05921 | 5.6545 | 0 | 0 | 142.7778 | 0 | off_peak | 576.62 |  |  | 0 | 0 | 100 | 0 | 0
3029 | 571.71 | 0 | 24.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 56.8531 | 571.71 | 0 | 0.05921 | 4.9942 | 0 | 0 | 142.7778 | 0 | off_peak | 571.71 |  |  | 0 | 0 | 100 | 0 | 0
3030 | 677.93 | 0 | 24.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 56.8531 | 677.93 | 0 | 0.05921 | 4.3806 | 0 | 0 | 142.7778 | 0 | off_peak | 677.93 |  |  | 0 | 0 | 100 | 0 | 0
3031 | 716.43 | 100.462 | 25.5 | 20.3069 | 20.3069 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 56.8531 | 696.1231 | 0 | 0.05921 | 4.0057 | 0 | 0 | 142.7778 | 20.3069 | off_peak | 696.1231 |  |  | 2.83 | 0 | 97.17 | 81.3441 | 0
3032 | 738.98 | 312.014 | 26.2 | 62.9099 | 62.9099 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 56.8531 | 676.0701 | 0 | 0.05921 | 3.8515 | 0 | 0 | 142.7778 | 62.9099 | off_peak | 676.0701 |  |  | 8.51 | 0 | 91.49 | 242.2974 | 0
3033 | 710.6 | 525.425 | 26.9 | 105.6708 | 105.6708 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 56.8531 | 604.9292 | 0 | 0.05921 | 3.6551 | 0 | 0 | 142.7778 | 105.6708 | off_peak | 604.9292 |  |  | 14.87 | 0 | 85.13 | 386.2377 | 0
3034 | 783.49 | 708.44 | 27.6 | 142.1163 | 142.1163 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 56.8531 | 641.3737 | 0 | 0.05921 | 3.5354 | 0 | 0 | 142.7778 | 142.1163 | off_peak | 641.3737 |  |  | 18.14 | 0 | 81.86 | 502.4328 | 0
3035 | 781.68 | 847.93 | 28.2 | 169.7278 | 169.7278 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 56.8531 | 611.9522 | 0 | 0.05921 | 3.5062 | 0 | 0 | 142.7778 | 169.7278 | off_peak | 611.9522 |  |  | 21.71 | 0 | 78.29 | 595.1076 | 0
3036 | 733.25 | 929.647 | 28.7 | 185.746 | 185.746 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 56.8531 | 547.504 | 0 | 0.05921 | 3.5623 | 0 | 0 | 142.7778 | 185.746 | off_peak | 547.504 |  |  | 25.33 | 0 | 74.67 | 661.6913 | 0
3037 | 781.51 | 945.985 | 29 | 188.8035 | 188.8035 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 56.8531 | 592.7065 | 0 | 0.05921 | 3.6659 | 0 | 0 | 142.7778 | 188.8035 | off_peak | 592.7065 |  |  | 24.16 | 0 | 75.84 | 692.1401 | 0
3038 | 736.93 | 842.973 | 29.1 | 168.1825 | 168.1825 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 68.4513 | 581.1465 | 0 | 0.05921 | 3.9282 | 0 | 0 | 142.7778 | 168.1825 | off_peak | 568.7475 | 0 | 100 | 22.82 | 0 | 77.18 | 660.6618 | 0
3039 | 776.11 | 568.986 | 29 | 113.5605 | 113.5605 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 68.4513 | 662.5495 | 0 | 0.05921 | 4.2488 | 0 | 0 | 142.7778 | 113.5605 | off_peak | 662.5495 |  |  | 14.63 | 0 | 85.37 | 482.4922 | 0
3040 | 724.67 | 289.65 | 28.7 | 57.8729 | 57.8729 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 68.4513 | 666.7971 | 0 | 0.05921 | 4.5 | 0 | 0 | 142.7778 | 57.8729 | off_peak | 666.7971 |  |  | 7.99 | 0 | 92.01 | 260.4278 | 0
3041 | 690.2 | 327.692 | 28.3 | 65.5693 | 65.5693 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 68.4513 | 624.6307 | 0 | 0.05921 | 4.822 | 0 | 0 | 142.7778 | 65.5693 | off_peak | 624.6307 |  |  | 9.5 | 0 | 90.5 | 316.1757 | 0
3042 | 641.18 | 129.315 | 27.6 | 25.9412 | 25.9412 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 68.4513 | 615.2388 | 0 | 0.05921 | 5.2387 | 0 | 0 | 142.7778 | 25.9412 | off_peak | 615.2388 |  |  | 4.05 | 0 | 95.95 | 135.8992 | 0
3043 | 591.15 | 29.5794 | 27.2 | 5.9424 | 0 | 0 | 5.9424 | 5.9424 | 0 | 0 | 0 | 0 | 74.0099 | 591.15 | 0 | 0.05921 | 5.5362 | 0 | 0 | 148.3364 | 0 | off_peak | 591.15 | 100 | 0 | 0 | 0 | 100 | 0 | 0
3044 | 585.28 | 0 | 26.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.0099 | 585.28 | 0 | 0.05921 | 5.7493 | 0 | 0 | 148.3364 | 0 | off_peak | 585.28 |  |  | 0 | 0 | 100 | 0 | 0
3045 | 599.58 | 0 | 25.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.0099 | 599.58 | 0 | 0.05921 | 5.9013 | 0 | 0 | 148.3364 | 0 | off_peak | 599.58 |  |  | 0 | 0 | 100 | 0 | 0
3046 | 569.16 | 0 | 25.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.0099 | 569.16 | 0 | 0.05921 | 6.0488 | 0 | 0 | 148.3364 | 0 | off_peak | 569.16 |  |  | 0 | 0 | 100 | 0 | 0
3047 | 552.43 | 0 | 25.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.0099 | 552.43 | 0 | 0.05921 | 6.3181 | 0 | 0 | 148.3364 | 0 | off_peak | 552.43 |  |  | 0 | 0 | 100 | 0 | 0
3048 | 561.77 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.0099 | 561.77 | 0 | 0.05921 | 6.4242 | 0 | 0 | 148.3364 | 0 | off_peak | 561.77 |  |  | 0 | 0 | 100 | 0 | 0
3049 | 581.54 | 0 | 24.9 | 0 | 0 | 0 | 0 | 0.38379 | 0.38379 | 0 | 0 | 0 | 74.3689 | 581.9238 | 0 | 0.05921 | 6.4903 | 0 | 0 | 148.3364 | 0 | off_peak | 581.54 | 0 | 100 | 0 | 0 | 100 | 0 | 0
3050 | 547.8 | 0 | 24.9 | 0 | 0 | 0 | 0 | 0.024788 | 0.024788 | 0 | 0 | 0 | 74.392 | 547.8248 | 0 | 0.05921 | 6.4485 | 0 | 0 | 148.3364 | 0 | off_peak | 547.8 | 0 | 100 | 0 | 0 | 100 | 0 | 0
3051 | 557.4 | 0 | 24.8 | 0 | 0 | 0 | 0 | 0.0016009 | 0.0016009 | 0 | 0 | 0 | 74.3935 | 557.4016 | 0 | 0.05921 | 6.0565 | 0 | 0 | 148.3364 | 0 | off_peak | 557.4 | 0 | 100 | 0 | 0 | 100 | 0 | 0
3052 | 590.22 | 0 | 24.8 | 0 | 0 | 0 | 0 | 0.00011054 | 0.00011054 | 0 | 0 | 0 | 74.3936 | 590.2201 | 0 | 0.05921 | 5.3915 | 0 | 0 | 148.3364 | 0 | off_peak | 590.22 | 0 | 100 | 0 | 0 | 100 | 0 | 0
3053 | 599.15 | 0 | 24.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 599.15 | 0 | 0.05921 | 4.5704 | 0 | 0 | 148.3364 | 0 | off_peak | 599.15 |  |  | 0 | 0 | 100 | 0 | 0
3054 | 659.13 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 659.13 | 0 | 0.05921 | 3.8864 | 0 | 0 | 148.3364 | 0 | off_peak | 659.13 |  |  | 0 | 0 | 100 | 0 | 0
3055 | 715.43 | 107.902 | 25.8 | 21.7872 | 21.7872 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 693.6428 | 0 | 0.05921 | 3.4944 | 0 | 0 | 148.3364 | 21.7872 | off_peak | 693.6428 |  |  | 3.05 | 0 | 96.95 | 76.1325 | 0
3056 | 821.23 | 311.842 | 26.5 | 62.807 | 62.807 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 758.423 | 0 | 0.05921 | 3.268 | 0 | 0 | 148.3364 | 62.807 | off_peak | 758.423 |  |  | 7.65 | 0 | 92.35 | 205.2555 | 0
3057 | 832.76 | 499.455 | 27.1 | 100.375 | 100.375 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 732.385 | 0 | 0.05921 | 3.1113 | 0 | 0 | 148.3364 | 100.375 | off_peak | 732.385 |  |  | 12.05 | 0 | 87.95 | 312.2966 | 0
3058 | 813.33 | 619.099 | 27.7 | 124.149 | 124.149 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 689.181 | 0 | 0.05921 | 3.0763 | 0 | 0 | 148.3364 | 124.149 | off_peak | 689.181 |  |  | 15.26 | 0 | 84.74 | 381.9198 | 0
3059 | 806.04 | 537.056 | 28.3 | 107.4618 | 107.4618 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 698.5782 | 0 | 0.05921 | 3.218 | 0 | 0 | 148.3364 | 107.4618 | off_peak | 698.5782 |  |  | 13.33 | 0 | 86.67 | 345.8113 | 0
3060 | 865.8 | 493.023 | 28.8 | 98.4714 | 98.4714 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 767.3286 | 0 | 0.05921 | 3.5404 | 0 | 0 | 148.3364 | 98.4714 | off_peak | 767.3286 |  |  | 11.37 | 0 | 88.63 | 348.6248 | 0
3061 | 804.08 | 948.683 | 29.1 | 189.2728 | 189.2728 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 614.8072 | 0 | 0.088511 | 3.7862 | 0 | 0 | 148.3364 | 189.2728 | on_peak | 614.8072 |  |  | 23.54 | 0 | 76.46 | 716.6234 | 0
3062 | 834.9 | 809.335 | 29.4 | 161.2943 | 161.2943 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 673.6057 | 0 | 0.088511 | 3.957 | 0 | 0 | 148.3364 | 161.2943 | on_peak | 673.6057 |  |  | 19.32 | 0 | 80.68 | 638.2453 | 0
3063 | 885.79 | 793.958 | 29.4 | 158.2298 | 158.2298 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 727.5602 | 0 | 0.088511 | 4.0983 | 0 | 0 | 148.3364 | 158.2298 | on_peak | 727.5602 |  |  | 17.86 | 0 | 82.14 | 648.4781 | 0
3064 | 878.53 | 418.909 | 29.2 | 83.5465 | 83.5465 | 0 | 0 | 0 | 0 | 62.63 | 62.63 | 0 | 7.4394 | 732.3535 | 0 | 0.088511 | 4.2597 | 0 | 0 | 148.3364 | 83.5465 | on_peak | 732.3535 |  |  | 9.51 | 7.13 | 83.36 | 355.8802 | 0
3065 | 842.72 | 443.04 | 28.8 | 88.4883 | 88.4883 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 754.2317 | 0 | 0.088511 | 4.4727 | 0 | 0 | 148.3364 | 88.4883 | on_peak | 754.2317 |  |  | 10.5 | 0 | 89.5 | 395.7834 | 0
3066 | 848.51 | 229.848 | 28.1 | 46.0248 | 46.0248 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 802.4852 | 0 | 0.088511 | 4.8666 | 0 | 0 | 148.3364 | 46.0248 | on_peak | 802.4852 |  |  | 5.42 | 0 | 94.58 | 223.9842 | 0
3067 | 808.26 | 45.4202 | 27.7 | 9.1082 | 9.1082 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 799.1518 | 0 | 0.088511 | 5.4553 | 0 | 0 | 148.3364 | 9.1082 | on_peak | 799.1518 |  |  | 1.13 | 0 | 98.87 | 49.6882 | 0
3068 | 810.31 | 0 | 26.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 810.31 | 0 | 0.088511 | 5.8826 | 0 | 0 | 148.3364 | 0 | on_peak | 810.31 |  |  | 0 | 0 | 100 | 0 | 0
3069 | 811.56 | 0 | 26.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 811.56 | 0 | 0.088511 | 6.185 | 0 | 0 | 148.3364 | 0 | on_peak | 811.56 |  |  | 0 | 0 | 100 | 0 | 0
3070 | 779.3 | 0 | 26 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 19.0375 | 791.6989 | 0 | 0.05921 | 6.6534 | 0 | 0 | 148.3364 | 0 | off_peak | 779.3 | 0 | 100 | 0 | 0 | 100 | 0 | 0
3071 | 801.42 | 0 | 25.7 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 30.6357 | 813.8189 | 0 | 0.05921 | 6.8498 | 0 | 0 | 148.3364 | 0 | off_peak | 801.42 | 0 | 100 | 0 | 0 | 100 | 0 | 0
3072 | 803.55 | 0 | 25.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30.6357 | 803.55 | 0 | 0.05921 | 7.0903 | 0 | 0 | 148.3364 | 0 | off_peak | 803.55 |  |  | 0 | 0 | 100 | 0 | 0
3073 | 760.57 | 0 | 25.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30.6357 | 760.57 | 0 | 0.05921 | 7.1266 | 0 | 0 | 148.3364 | 0 | off_peak | 760.57 |  |  | 0 | 0 | 100 | 0 | 0
3074 | 677.38 | 0 | 25.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30.6357 | 677.38 | 0 | 0.05921 | 6.8506 | 0 | 0 | 148.3364 | 0 | off_peak | 677.38 |  |  | 0 | 0 | 100 | 0 | 0
3075 | 604.95 | 0 | 25.1 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 42.2338 | 617.3489 | 0 | 0.05921 | 6.3781 | 0 | 0 | 148.3364 | 0 | off_peak | 604.95 | 0 | 100 | 0 | 0 | 100 | 0 | 0
3076 | 604.77 | 0 | 25.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 42.2338 | 604.77 | 0 | 0.05921 | 5.6298 | 0 | 0 | 148.3364 | 0 | off_peak | 604.77 |  |  | 0 | 0 | 100 | 0 | 0
3077 | 610.84 | 0 | 25.1 | 0 | 0 | 0 | 0 | 8.7263 | 8.7263 | 0 | 0 | 0 | 50.3966 | 619.5663 | 0 | 0.05921 | 4.8066 | 0 | 0 | 148.3364 | 0 | off_peak | 610.84 | 0 | 100 | 0 | 0 | 100 | 0 | 0
3078 | 692.31 | 0 | 25.4 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 61.9947 | 704.7089 | 0 | 0.05921 | 4.1204 | 0 | 0 | 148.3364 | 0 | off_peak | 692.31 | 0 | 100 | 0 | 0 | 100 | 0 | 0
3079 | 705.59 | 113.221 | 25.9 | 22.853 | 22.853 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 61.9947 | 682.737 | 0 | 0.05921 | 3.7362 | 0 | 0 | 148.3364 | 22.853 | off_peak | 682.737 |  |  | 3.24 | 0 | 96.76 | 85.3833 | 0
3080 | 808.87 | 317.419 | 26.4 | 63.9534 | 63.9534 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 73.5928 | 757.3156 | 0 | 0.05921 | 3.4319 | 0 | 0 | 148.3364 | 63.9534 | off_peak | 744.9166 | 0 | 100 | 7.91 | 0 | 92.09 | 219.4813 | 0
3081 | 793.31 | 498.186 | 26.9 | 100.1926 | 100.1926 | 0 | 0 | 0.80079 | 0.80079 | 0 | 0 | 0 | 74.3419 | 693.9182 | 0 | 0.05921 | 3.2181 | 0 | 0 | 148.3364 | 100.1926 | off_peak | 693.1174 | 0 | 100 | 12.63 | 0 | 87.37 | 322.4268 | 0
3082 | 807.97 | 426.635 | 27.4 | 85.6471 | 85.6471 | 0 | 0 | 0.05172 | 0.05172 | 0 | 0 | 0 | 74.3903 | 722.3746 | 0 | 0.05921 | 3.1675 | 0 | 0 | 148.3364 | 85.6471 | off_peak | 722.3229 | 0 | 100 | 10.6 | 0 | 89.4 | 271.2839 | 0
3083 | 825.51 | 299.939 | 28.1 | 60.0598 | 60.0598 | 0 | 0 | 0.0033404 | 0.0033404 | 0 | 0 | 0 | 74.3934 | 765.4535 | 0 | 0.05921 | 3.3431 | 0 | 0 | 148.3364 | 60.0598 | off_peak | 765.4502 | 0 | 100 | 7.28 | 0 | 92.72 | 200.7838 | 0
3084 | 864.05 | 769.861 | 28.6 | 153.8764 | 153.8764 | 0 | 0 | 0.00021574 | 0.00021574 | 0 | 0 | 0 | 74.3936 | 710.1738 | 0 | 0.05921 | 3.7174 | 0 | 0 | 148.3364 | 153.8764 | off_peak | 710.1736 | 0 | 100 | 17.81 | 0 | 82.19 | 572.0187 | 0
3085 | 823.56 | 814.632 | 29 | 162.5875 | 162.5875 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 660.9725 | 0 | 0.088511 | 4.0246 | 0 | 0 | 148.3364 | 162.5875 | on_peak | 660.9725 |  |  | 19.74 | 0 | 80.26 | 654.3557 | 0
3086 | 810.31 | 652.121 | 29.2 | 130.0578 | 130.0578 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 680.2522 | 0 | 0.088511 | 4.3275 | 0 | 0 | 148.3364 | 130.0578 | on_peak | 680.2522 |  |  | 16.05 | 0 | 83.95 | 562.8211 | 0
3087 | 883.05 | 537.774 | 29.2 | 107.2527 | 107.2527 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 775.7973 | 0 | 0.088511 | 4.6727 | 0 | 0 | 148.3364 | 107.2527 | on_peak | 775.7973 |  |  | 12.15 | 0 | 87.85 | 501.1586 | 0
3088 | 860.82 | 488.815 | 29.1 | 97.524 | 97.524 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 763.296 | 0 | 0.088511 | 4.9042 | 0 | 0 | 148.3364 | 97.524 | on_peak | 763.296 |  |  | 11.33 | 0 | 88.67 | 478.2741 | 0
3089 | 822.32 | 430.675 | 28.9 | 85.9872 | 85.9872 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 736.3328 | 0 | 0.088511 | 5.2349 | 0 | 0 | 148.3364 | 85.9872 | on_peak | 736.3328 |  |  | 10.46 | 0 | 89.54 | 450.137 | 0
3090 | 831.33 | 209.846 | 28.6 | 41.9431 | 41.9431 | 0 | 0 | 0 | 0 | 62.63 | 62.63 | 0 | 7.4394 | 726.7569 | 0 | 0.088511 | 5.5838 | 0 | 0 | 148.3364 | 41.9431 | on_peak | 726.7569 |  |  | 5.05 | 7.53 | 87.42 | 234.2009 | 0
3091 | 779.06 | 34.5359 | 28.4 | 6.9079 | 6.9079 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 772.1521 | 0 | 0.088511 | 6.0599 | 0 | 0 | 148.3364 | 6.9079 | on_peak | 772.1521 |  |  | 0.89 | 0 | 99.11 | 41.8611 | 0
3092 | 785.8 | 0 | 27.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 785.8 | 0 | 0.088511 | 6.4529 | 0 | 0 | 148.3364 | 0 | on_peak | 785.8 |  |  | 0 | 0 | 100 | 0 | 0
3093 | 783.26 | 0 | 27.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 783.26 | 0 | 0.088511 | 6.7584 | 0 | 0 | 148.3364 | 0 | on_peak | 783.26 |  |  | 0 | 0 | 100 | 0 | 0
3094 | 763.48 | 0 | 26.9 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 19.0375 | 775.8789 | 0 | 0.05921 | 7.0715 | 0 | 0 | 148.3364 | 0 | off_peak | 763.48 | 0 | 100 | 0 | 0 | 100 | 0 | 0
3095 | 751.54 | 0 | 26.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19.0375 | 751.54 | 0 | 0.05921 | 7.3269 | 0 | 0 | 148.3364 | 0 | off_peak | 751.54 |  |  | 0 | 0 | 100 | 0 | 0
3096 | 789.39 | 0 | 26.2 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 30.6357 | 801.7889 | 0 | 0.05921 | 7.4564 | 0 | 0 | 148.3364 | 0 | off_peak | 789.39 | 0 | 100 | 0 | 0 | 100 | 0 | 0
3097 | 773.6 | 0 | 25.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30.6357 | 773.6 | 0 | 0.05921 | 7.4158 | 0 | 0 | 148.3364 | 0 | off_peak | 773.6 |  |  | 0 | 0 | 100 | 0 | 0
3098 | 633.02 | 0 | 25.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30.6357 | 633.02 | 0 | 0.05921 | 7.1857 | 0 | 0 | 148.3364 | 0 | off_peak | 633.02 |  |  | 0 | 0 | 100 | 0 | 0
3099 | 578.89 | 0 | 25.5 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 42.2338 | 591.2889 | 0 | 0.05921 | 6.8539 | 0 | 0 | 148.3364 | 0 | off_peak | 578.89 | 0 | 100 | 0 | 0 | 100 | 0 | 0
3100 | 581.62 | 0 | 25.4 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 53.832 | 594.0189 | 0 | 0.05921 | 6.0099 | 0 | 0 | 148.3364 | 0 | off_peak | 581.62 | 0 | 100 | 0 | 0 | 100 | 0 | 0
3101 | 605.42 | 0 | 25.3 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 65.4301 | 617.8189 | 0 | 0.05921 | 5.1828 | 0 | 0 | 148.3364 | 0 | off_peak | 605.42 | 0 | 100 | 0 | 0 | 100 | 0 | 0
3102 | 667.53 | 0 | 25.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 65.4301 | 667.53 | 0 | 0.05921 | 4.5311 | 0 | 0 | 148.3364 | 0 | off_peak | 667.53 |  |  | 0 | 0 | 100 | 0 | 0
3103 | 722.03 | 116.521 | 26 | 23.5106 | 23.5106 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 65.4301 | 698.5194 | 0 | 0.05921 | 3.9765 | 0 | 0 | 148.3364 | 23.5106 | off_peak | 698.5194 |  |  | 3.26 | 0 | 96.74 | 93.4894 | 0
3104 | 792.69 | 188.85 | 26.9 | 37.9805 | 29.017 | 0 | 8.9635 | 8.9635 | 0 | 0 | 0 | 0 | 73.8147 | 763.673 | 0 | 0.05921 | 3.6781 | 0 | 0 | 156.7211 | 29.017 | off_peak | 763.673 | 100 | 0 | 3.66 | 0 | 96.34 | 106.7264 | 0
3105 | 793.79 | 215.098 | 27.7 | 43.134 | 42.5551 | 0 | 0.57892 | 0.57892 | 0 | 0 | 0 | 0 | 74.3563 | 751.2349 | 0 | 0.05921 | 3.483 | 0 | 0 | 157.2626 | 42.5551 | off_peak | 751.2349 | 100 | 0 | 5.36 | 0 | 94.64 | 148.2208 | 0
3106 | 823.73 | 714.609 | 28.4 | 142.9371 | 142.9371 | 0 | 0 | 0.03739 | 0.03739 | 0 | 0 | 0 | 74.3912 | 680.8303 | 0 | 0.05921 | 3.3999 | 0 | 0 | 157.2626 | 142.9371 | off_peak | 680.7929 | 0 | 100 | 17.35 | 0 | 82.65 | 485.9684 | 0
3107 | 802.2 | 565.18 | 28.9 | 112.8421 | 112.8421 | 0 | 0 | 0.0024148 | 0.0024148 | 0 | 0 | 0 | 74.3935 | 689.3603 | 0 | 0.05921 | 3.5434 | 0 | 0 | 157.2626 | 112.8421 | off_peak | 689.3579 | 0 | 100 | 14.07 | 0 | 85.93 | 399.8411 | 0
3108 | 880.82 | 934.248 | 29.4 | 186.1885 | 186.1885 | 0 | 0 | 0.00015596 | 0.00015596 | 0 | 0 | 0 | 74.3936 | 694.6316 | 0 | 0.05921 | 3.9172 | 0 | 0 | 157.2626 | 186.1885 | off_peak | 694.6315 | 0 | 100 | 21.14 | 0 | 78.86 | 729.3351 | 0
3109 | 828.43 | 952.211 | 29.8 | 189.4908 | 189.4908 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 638.9392 | 0 | 0.088511 | 4.1201 | 0 | 0 | 157.2626 | 189.4908 | on_peak | 638.9392 |  |  | 22.87 | 0 | 77.13 | 780.7148 | 0
3110 | 816.89 | 875.768 | 30.2 | 174.0232 | 174.0232 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 642.8668 | 0 | 0.088511 | 4.3545 | 0 | 0 | 157.2626 | 174.0232 | on_peak | 642.8668 |  |  | 21.3 | 0 | 78.7 | 757.7818 | 0
3111 | 849.42 | 636.069 | 30.5 | 126.2537 | 126.2537 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 723.1663 | 0 | 0.088511 | 4.55 | 0 | 0 | 157.2626 | 126.2537 | on_peak | 723.1663 |  |  | 14.86 | 0 | 85.14 | 574.4554 | 0
3112 | 841.9 | 631.052 | 30.5 | 125.2578 | 125.2578 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 716.6422 | 0 | 0.088511 | 4.9059 | 0 | 0 | 157.2626 | 125.2578 | on_peak | 716.6422 |  |  | 14.88 | 0 | 85.12 | 614.5035 | 0
3113 | 892.25 | 320.132 | 30.2 | 63.6132 | 63.6132 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 828.6368 | 0 | 0.088511 | 5.4429 | 0 | 0 | 157.2626 | 63.6132 | on_peak | 828.6368 |  |  | 7.13 | 0 | 92.87 | 346.2381 | 0
3114 | 840.81 | 232.563 | 29.6 | 46.3141 | 46.3141 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 794.4959 | 0 | 0.088511 | 6.0953 | 0 | 0 | 157.2626 | 46.3141 | on_peak | 794.4959 |  |  | 5.51 | 0 | 94.49 | 282.299 | 0
3115 | 826.33 | 44.0601 | 29.2 | 8.7873 | 8.7873 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 817.5427 | 0 | 0.088511 | 6.6444 | 0 | 0 | 157.2626 | 8.7873 | on_peak | 817.5427 |  |  | 1.06 | 0 | 98.94 | 58.3861 | 0
3116 | 810.17 | 0 | 28.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 810.17 | 0 | 0.088511 | 6.9942 | 0 | 0 | 157.2626 | 0 | on_peak | 810.17 |  |  | 0 | 0 | 100 | 0 | 0
3117 | 818.4 | 0 | 27.6 | 0 | 0 | 0 | 0 | 0 | 0 | 62.63 | 62.63 | 0 | 7.4394 | 755.77 | 0 | 0.088511 | 7.3363 | 0 | 0 | 157.2626 | 0 | on_peak | 755.77 |  |  | 0 | 7.65 | 92.35 | 0 | 0
3118 | 775.87 | 0 | 27.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 775.87 | 0 | 0.05921 | 7.5276 | 0 | 0 | 157.2626 | 0 | off_peak | 775.87 |  |  | 0 | 0 | 100 | 0 | 0
3119 | 814.46 | 0 | 26.9 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 19.0375 | 826.8589 | 0 | 0.05921 | 7.7264 | 0 | 0 | 157.2626 | 0 | off_peak | 814.46 | 0 | 100 | 0 | 0 | 100 | 0 | 0
3120 | 764.3 | 0 | 26.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19.0375 | 764.3 | 0 | 0.05921 | 7.8292 | 0 | 0 | 157.2626 | 0 | off_peak | 764.3 |  |  | 0 | 0 | 100 | 0 | 0
3121 | 747.01 | 0 | 26.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19.0375 | 747.01 | 0 | 0.05921 | 7.6548 | 0 | 0 | 157.2626 | 0 | off_peak | 747.01 |  |  | 0 | 0 | 100 | 0 | 0
3122 | 653.94 | 0 | 26.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19.0375 | 653.94 | 0 | 0.05921 | 7.473 | 0 | 0 | 157.2626 | 0 | off_peak | 653.94 |  |  | 0 | 0 | 100 | 0 | 0
3123 | 592.12 | 0 | 26.1 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 30.6357 | 604.5189 | 0 | 0.05921 | 6.9423 | 0 | 0 | 157.2626 | 0 | off_peak | 592.12 | 0 | 100 | 0 | 0 | 100 | 0 | 0
3124 | 615.67 | 0 | 26 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 42.2338 | 628.0689 | 0 | 0.05921 | 6.3365 | 0 | 0 | 157.2626 | 0 | off_peak | 615.67 | 0 | 100 | 0 | 0 | 100 | 0 | 0
3125 | 614.44 | 0 | 26 | 0 | 0 | 0 | 0 | 8.7263 | 8.7263 | 0 | 0 | 0 | 50.3966 | 623.1663 | 0 | 0.05921 | 5.5598 | 0 | 0 | 157.2626 | 0 | off_peak | 614.44 | 0 | 100 | 0 | 0 | 100 | 0 | 0
3126 | 727.85 | 0 | 26.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50.3966 | 727.85 | 0 | 0.05921 | 4.8132 | 0 | 0 | 157.2626 | 0 | off_peak | 727.85 |  |  | 0 | 0 | 100 | 0 | 0
3127 | 750.08 | 120.14 | 26.7 | 24.1795 | 24.1795 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 61.9947 | 738.2995 | 0 | 0.05921 | 4.3613 | 0 | 0 | 157.2626 | 24.1795 | off_peak | 725.9005 | 0 | 100 | 3.22 | 0 | 96.78 | 105.4546 | 0
3128 | 790.6 | 325.928 | 27.2 | 65.4777 | 65.4777 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 73.5928 | 737.5212 | 0 | 0.05921 | 3.9752 | 0 | 0 | 157.2626 | 65.4777 | off_peak | 725.1223 | 0 | 100 | 8.28 | 0 | 91.72 | 260.286 | 0
3129 | 859.95 | 534.848 | 27.8 | 107.215 | 107.215 | 0 | 0 | 0.80079 | 0.80079 | 0 | 0 | 0 | 74.3419 | 753.5358 | 0 | 0.05921 | 3.7506 | 0 | 0 | 157.2626 | 107.215 | off_peak | 752.735 | 0 | 100 | 12.47 | 0 | 87.53 | 402.1191 | 0
3130 | 829.84 | 716.884 | 28.3 | 143.4444 | 143.4444 | 0 | 0 | 0.05172 | 0.05172 | 0 | 0 | 0 | 74.3903 | 686.4473 | 0 | 0.05921 | 3.63 | 0 | 0 | 157.2626 | 143.4444 | off_peak | 686.3956 | 0 | 100 | 17.29 | 0 | 82.71 | 520.7036 | 0
3131 | 780.51 | 818.386 | 28.8 | 163.4561 | 163.4561 | 0 | 0 | 0.0033404 | 0.0033404 | 0 | 0 | 0 | 74.3934 | 617.0573 | 0 | 0.05921 | 3.8043 | 0 | 0 | 157.2626 | 163.4561 | off_peak | 617.0539 | 0 | 100 | 20.94 | 0 | 79.06 | 621.8352 | 0
3132 | 859.91 | 934.741 | 29.3 | 186.3549 | 186.3549 | 0 | 0 | 0.00021574 | 0.00021574 | 0 | 0 | 0 | 74.3936 | 673.5553 | 0 | 0.05921 | 4.247 | 0 | 0 | 157.2626 | 186.3549 | off_peak | 673.5551 | 0 | 100 | 21.67 | 0 | 78.33 | 791.4517 | 0
3133 | 813.66 | 952.708 | 29.7 | 189.6591 | 189.6591 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 624.0009 | 0 | 0.088511 | 4.3808 | 0 | 0 | 157.2626 | 189.6591 | on_peak | 624.0009 |  |  | 23.31 | 0 | 76.69 | 830.8519 | 0
3134 | 856.74 | 904.511 | 30 | 179.8665 | 179.8665 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 676.8735 | 0 | 0.088511 | 4.728 | 0 | 0 | 157.2626 | 179.8665 | on_peak | 676.8735 |  |  | 20.99 | 0 | 79.01 | 850.4127 | 0
3135 | 917.17 | 797.293 | 30.2 | 158.4295 | 158.4295 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 758.7405 | 0 | 0.088511 | 4.9848 | 0 | 0 | 157.2626 | 158.4295 | on_peak | 758.7405 |  |  | 17.27 | 0 | 82.73 | 789.7368 | 0
3136 | 871.77 | 626.299 | 30.2 | 124.4514 | 124.4514 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 747.3186 | 0 | 0.088511 | 5.3188 | 0 | 0 | 157.2626 | 124.4514 | on_peak | 747.3186 |  |  | 14.28 | 0 | 85.72 | 661.9319 | 0
3137 | 829.59 | 376.658 | 30 | 74.9003 | 74.9003 | 0 | 0 | 0 | 0 | 62.63 | 62.63 | 0 | 7.4394 | 692.0597 | 0 | 0.088511 | 5.5586 | 0 | 0 | 157.2626 | 74.9003 | on_peak | 692.0597 |  |  | 9.03 | 7.55 | 83.42 | 416.3433 | 0
3138 | 821.53 | 149.775 | 29.6 | 29.8272 | 29.8272 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 791.7028 | 0 | 0.088511 | 5.9492 | 0 | 0 | 157.2626 | 29.8272 | on_peak | 791.7028 |  |  | 3.63 | 0 | 96.37 | 177.4471 | 0
3139 | 774.75 | 43.4611 | 29.4 | 8.6615 | 8.6615 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 766.0885 | 0 | 0.088511 | 6.3228 | 0 | 0 | 157.2626 | 8.6615 | on_peak | 766.0885 |  |  | 1.12 | 0 | 98.88 | 54.7646 | 0
3140 | 796.11 | 0 | 28.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 796.11 | 0 | 0.088511 | 6.703 | 0 | 0 | 157.2626 | 0 | on_peak | 796.11 |  |  | 0 | 0 | 100 | 0 | 0
3141 | 812.82 | 0 | 27.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 812.82 | 0 | 0.088511 | 6.9743 | 0 | 0 | 157.2626 | 0 | on_peak | 812.82 |  |  | 0 | 0 | 100 | 0 | 0
3142 | 762.3 | 0 | 27.4 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 19.0375 | 774.6989 | 0 | 0.05921 | 7.2672 | 0 | 0 | 157.2626 | 0 | off_peak | 762.3 | 0 | 100 | 0 | 0 | 100 | 0 | 0
3143 | 793.54 | 0 | 26.9 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 30.6357 | 805.9389 | 0 | 0.05921 | 7.518 | 0 | 0 | 157.2626 | 0 | off_peak | 793.54 | 0 | 100 | 0 | 0 | 100 | 0 | 0
3144 | 768.32 | 0 | 26.5 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 42.2338 | 780.7189 | 0 | 0.05921 | 7.6716 | 0 | 0 | 157.2626 | 0 | off_peak | 768.32 | 0 | 100 | 0 | 0 | 100 | 0 | 0
3145 | 707.53 | 0 | 26.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 42.2338 | 707.53 | 0 | 0.05921 | 7.594 | 0 | 0 | 157.2626 | 0 | off_peak | 707.53 |  |  | 0 | 0 | 100 | 0 | 0
3146 | 677.94 | 0 | 26 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 53.832 | 690.3389 | 0 | 0.05921 | 7.3961 | 0 | 0 | 157.2626 | 0 | off_peak | 677.94 | 0 | 100 | 0 | 0 | 100 | 0 | 0
3147 | 608.93 | 0 | 25.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 53.832 | 608.93 | 0 | 0.05921 | 6.9099 | 0 | 0 | 157.2626 | 0 | off_peak | 608.93 |  |  | 0 | 0 | 100 | 0 | 0
3148 | 600.99 | 0 | 25.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 53.832 | 600.99 | 0 | 0.05921 | 6.1808 | 0 | 0 | 157.2626 | 0 | off_peak | 600.99 |  |  | 0 | 0 | 100 | 0 | 0
3149 | 579.14 | 0 | 25.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 53.832 | 579.14 | 0 | 0.05921 | 5.4181 | 0 | 0 | 157.2626 | 0 | off_peak | 579.14 |  |  | 0 | 0 | 100 | 0 | 0
3150 | 708.65 | 0 | 25.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 53.832 | 708.65 | 0 | 0.05921 | 4.648 | 0 | 0 | 157.2626 | 0 | off_peak | 708.65 |  |  | 0 | 0 | 100 | 0 | 0
3151 | 763.87 | 116.632 | 25.7 | 23.5585 | 11.1595 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 0 | 65.4301 | 752.7105 | 0 | 0.05921 | 4.2697 | 0 | 0 | 168.8607 | 11.1595 | off_peak | 752.7105 | 100 | 0 | 1.46 | 0 | 98.54 | 47.6482 | 0
3152 | 817.54 | 322.76 | 25.9 | 65.1471 | 65.1471 | 0 | 0 | 8.9635 | 8.9635 | 0 | 0 | 0 | 73.8147 | 761.3564 | 0 | 0.05921 | 4.0205 | 0 | 0 | 168.8607 | 65.1471 | off_peak | 752.3929 | 0 | 100 | 7.97 | 0 | 92.03 | 261.9233 | 0
3153 | 848.27 | 527.977 | 26.3 | 106.415 | 106.415 | 0 | 0 | 0.57892 | 0.57892 | 0 | 0 | 0 | 74.3563 | 742.4339 | 0 | 0.05921 | 3.7666 | 0 | 0 | 168.8607 | 106.415 | off_peak | 741.855 | 0 | 100 | 12.54 | 0 | 87.46 | 400.8195 | 0
3154 | 818.81 | 704.999 | 26.9 | 141.7858 | 141.7484 | 0 | 0.03739 | 0.03739 | 0 | 0 | 0 | 0 | 74.3912 | 677.0616 | 0 | 0.05921 | 3.6701 | 0 | 0 | 168.8957 | 141.7484 | off_peak | 677.0616 | 100 | 0 | 17.31 | 0 | 82.69 | 520.2269 | 0
3155 | 770.36 | 790.895 | 27.5 | 158.7148 | 158.7148 | 0 | 0 | 0.0024148 | 0.0024148 | 0 | 0 | 0 | 74.3935 | 611.6476 | 0 | 0.05921 | 3.8514 | 0 | 0 | 168.8957 | 158.7148 | off_peak | 611.6452 | 0 | 100 | 20.6 | 0 | 79.4 | 611.2753 | 0
3156 | 853.49 | 756.919 | 28.1 | 151.5655 | 151.5655 | 0 | 0 | 0.00015596 | 0.00015596 | 0 | 0 | 0 | 74.3936 | 701.9246 | 0 | 0.05921 | 4.1596 | 0 | 0 | 168.8957 | 151.5655 | off_peak | 701.9245 | 0 | 100 | 17.76 | 0 | 82.24 | 630.4593 | 0
3157 | 815.1 | 446.662 | 28.7 | 89.2443 | 89.2443 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 725.8557 | 0 | 0.088511 | 4.3509 | 0 | 0 | 168.8957 | 89.2443 | on_peak | 725.8557 |  |  | 10.95 | 0 | 89.05 | 388.2913 | 0
3158 | 819.36 | 855.975 | 29.1 | 170.7765 | 170.7765 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 648.5835 | 0 | 0.088511 | 4.6399 | 0 | 0 | 168.8957 | 170.7765 | on_peak | 648.5835 |  |  | 20.84 | 0 | 79.16 | 792.3905 | 0
3159 | 926.8 | 788.245 | 29.4 | 157.0912 | 157.0912 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 769.7088 | 0 | 0.088511 | 4.9864 | 0 | 0 | 168.8957 | 157.0912 | on_peak | 769.7088 |  |  | 16.95 | 0 | 83.05 | 783.325 | 0
3160 | 911.15 | 606.054 | 29.5 | 120.7378 | 120.7378 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 790.4122 | 0 | 0.088511 | 5.3195 | 0 | 0 | 168.8957 | 120.7378 | on_peak | 790.4122 |  |  | 13.25 | 0 | 86.75 | 642.2702 | 0
3161 | 882.26 | 387.262 | 29.1 | 77.2631 | 77.2631 | 0 | 0 | 0 | 0 | 53.0392 | 53.0392 | 0 | 17.6923 | 751.9577 | 0 | 0.088511 | 5.6543 | 0 | 0 | 168.8957 | 77.2631 | on_peak | 751.9577 |  |  | 8.76 | 6.01 | 85.23 | 436.8668 | 0
3162 | 888.38 | 179.987 | 28.4 | 36.0013 | 36.0013 | 0 | 0 | 0 | 0 | 9.5908 | 9.5908 | 0 | 7.4394 | 842.788 | 0 | 0.088511 | 5.9544 | 0 | 0 | 168.8957 | 36.0013 | on_peak | 842.788 |  |  | 4.05 | 1.08 | 94.87 | 214.3654 | 0
3163 | 839.94 | 42.3043 | 27.9 | 8.4772 | 8.4772 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 831.4628 | 0 | 0.088511 | 6.4551 | 0 | 0 | 168.8957 | 8.4772 | on_peak | 831.4628 |  |  | 1.01 | 0 | 98.99 | 54.7212 | 0
3164 | 832.61 | 0 | 26.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 832.61 | 0 | 0.088511 | 6.8037 | 0 | 0 | 168.8957 | 0 | on_peak | 832.61 |  |  | 0 | 0 | 100 | 0 | 0
3165 | 831.52 | 0 | 25.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 831.52 | 0 | 0.088511 | 7.0781 | 0 | 0 | 168.8957 | 0 | on_peak | 831.52 |  |  | 0 | 0 | 100 | 0 | 0
3166 | 784.49 | 0 | 25.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 784.49 | 0 | 0.05921 | 7.3085 | 0 | 0 | 168.8957 | 0 | off_peak | 784.49 |  |  | 0 | 0 | 100 | 0 | 0
3167 | 771.24 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 771.24 | 0 | 0.05921 | 7.4673 | 0 | 0 | 168.8957 | 0 | off_peak | 771.24 |  |  | 0 | 0 | 100 | 0 | 0
3168 | 776.62 | 0 | 24.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 776.62 | 0 | 0.05921 | 7.5392 | 0 | 0 | 168.8957 | 0 | off_peak | 776.62 |  |  | 0 | 0 | 100 | 0 | 0
3169 | 768.33 | 0 | 24.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 768.33 | 0 | 0.05921 | 7.5204 | 0 | 0 | 168.8957 | 0 | off_peak | 768.33 |  |  | 0 | 0 | 100 | 0 | 0
3170 | 637.9 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 637.9 | 0 | 0.05921 | 7.143 | 0 | 0 | 168.8957 | 0 | off_peak | 637.9 |  |  | 0 | 0 | 100 | 0 | 0
3171 | 601.46 | 0 | 23.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 601.46 | 0 | 0.05921 | 6.7156 | 0 | 0 | 168.8957 | 0 | off_peak | 601.46 |  |  | 0 | 0 | 100 | 0 | 0
3172 | 613.2 | 0 | 23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 613.2 | 0 | 0.05921 | 6.0881 | 0 | 0 | 168.8957 | 0 | off_peak | 613.2 |  |  | 0 | 0 | 100 | 0 | 0
3173 | 586.36 | 0 | 22.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 586.36 | 0 | 0.05921 | 5.4843 | 0 | 0 | 168.8957 | 0 | off_peak | 586.36 |  |  | 0 | 0 | 100 | 0 | 0
3174 | 794.43 | 0 | 22.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 794.43 | 0 | 0.05921 | 4.8979 | 0 | 0 | 168.8957 | 0 | off_peak | 794.43 |  |  | 0 | 0 | 100 | 0 | 0
3175 | 799.59 | 69.3941 | 22.7 | 14.1687 | 14.1687 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 785.4213 | 0 | 0.05921 | 4.3954 | 0 | 0 | 168.8957 | 14.1687 | off_peak | 785.4213 |  |  | 1.77 | 0 | 98.23 | 62.2776 | 0
3176 | 775.71 | 312.03 | 23.6 | 63.5045 | 63.5045 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 712.2055 | 0 | 0.05921 | 4.0617 | 0 | 0 | 168.8957 | 63.5045 | off_peak | 712.2055 |  |  | 8.19 | 0 | 91.81 | 257.9361 | 0
3177 | 859.94 | 491.562 | 24.6 | 99.6846 | 99.6846 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 760.2554 | 0 | 0.05921 | 3.7043 | 0 | 0 | 168.8957 | 99.6846 | off_peak | 760.2554 |  |  | 11.59 | 0 | 88.41 | 369.2663 | 0
3178 | 805.74 | 549.061 | 25.6 | 110.9447 | 110.9447 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 694.7953 | 0 | 0.05921 | 3.5409 | 0 | 0 | 168.8957 | 110.9447 | off_peak | 694.7953 |  |  | 13.77 | 0 | 86.23 | 392.8459 | 0
3179 | 760.67 | 727.148 | 26.5 | 146.4523 | 146.4523 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 614.2177 | 0 | 0.05921 | 3.5137 | 0 | 0 | 168.8957 | 146.4523 | off_peak | 614.2177 |  |  | 19.25 | 0 | 80.75 | 514.5862 | 0
3180 | 810.78 | 870.699 | 27.1 | 174.9836 | 174.9836 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 635.7964 | 0 | 0.05921 | 3.5294 | 0 | 0 | 168.8957 | 174.9836 | off_peak | 635.7964 |  |  | 21.58 | 0 | 78.42 | 617.5889 | 0
3181 | 772.58 | 884.475 | 27.6 | 177.4298 | 177.4298 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 595.1502 | 0 | 0.05921 | 3.7185 | 0 | 0 | 168.8957 | 177.4298 | off_peak | 595.1502 |  |  | 22.97 | 0 | 77.03 | 659.7653 | 0
3182 | 708.3 | 696.861 | 28 | 139.5903 | 139.5903 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 568.7097 | 0 | 0.05921 | 4.1838 | 0 | 0 | 168.8957 | 139.5903 | off_peak | 568.7097 |  |  | 19.71 | 0 | 80.29 | 584.0145 | 0
3183 | 696.42 | 529.86 | 28.2 | 106.0606 | 106.0606 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 590.3594 | 0 | 0.05921 | 4.4757 | 0 | 0 | 168.8957 | 106.0606 | off_peak | 590.3594 |  |  | 15.23 | 0 | 84.77 | 474.7003 | 0
3184 | 709.2 | 344.623 | 28.2 | 68.9822 | 68.9822 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 640.2178 | 0 | 0.05921 | 4.6931 | 0 | 0 | 168.8957 | 68.9822 | off_peak | 640.2178 |  |  | 9.73 | 0 | 90.27 | 323.7437 | 0
3185 | 701.78 | 225.986 | 28 | 45.2679 | 45.2679 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 656.5121 | 0 | 0.05921 | 5.1422 | 0 | 0 | 168.8957 | 45.2679 | off_peak | 656.5121 |  |  | 6.45 | 0 | 93.55 | 232.7784 | 0
3186 | 611.8 | 97.192 | 27.4 | 19.5113 | 19.5113 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 592.2887 | 0 | 0.05921 | 5.6311 | 0 | 0 | 168.8957 | 19.5113 | off_peak | 592.2887 |  |  | 3.19 | 0 | 96.81 | 109.8712 | 0
3187 | 594.32 | 19 | 26.9 | 3.8212 | 0 | 0 | 3.8212 | 12.3989 | 8.5778 | 0 | 0 | 0 | 19.0375 | 602.8978 | 0 | 0.05921 | 6.0481 | 0 | 0 | 172.4701 | 0 | off_peak | 594.32 | 30.82 | 69.18 | 0 | 0 | 100 | 0 | 0
3188 | 564.94 | 0 | 25.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19.0375 | 564.94 | 0 | 0.05921 | 6.216 | 0 | 0 | 172.4701 | 0 | off_peak | 564.94 |  |  | 0 | 0 | 100 | 0 | 0
3189 | 578.34 | 0 | 25.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19.0375 | 578.34 | 0 | 0.05921 | 6.3832 | 0 | 0 | 172.4701 | 0 | off_peak | 578.34 |  |  | 0 | 0 | 100 | 0 | 0
3190 | 550.18 | 0 | 25.1 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 30.6357 | 562.5789 | 0 | 0.05921 | 6.638 | 0 | 0 | 172.4701 | 0 | off_peak | 550.18 | 0 | 100 | 0 | 0 | 100 | 0 | 0
3191 | 566.25 | 0 | 24.9 | 0 | 0 | 0 | 0 | 8.7263 | 8.7263 | 0 | 0 | 0 | 38.7984 | 574.9763 | 0 | 0.05921 | 6.8704 | 0 | 0 | 172.4701 | 0 | off_peak | 566.25 | 0 | 100 | 0 | 0 | 100 | 0 | 0
3192 | 515.95 | 0 | 24.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 38.7984 | 515.95 | 0 | 0.05921 | 6.9215 | 0 | 0 | 172.4701 | 0 | off_peak | 515.95 |  |  | 0 | 0 | 100 | 0 | 0
3193 | 564.58 | 0 | 24.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 38.7984 | 564.58 | 0 | 0.05921 | 6.7709 | 0 | 0 | 172.4701 | 0 | off_peak | 564.58 |  |  | 0 | 0 | 100 | 0 | 0
3194 | 554.47 | 0 | 24.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 38.7984 | 554.47 | 0 | 0.05921 | 6.683 | 0 | 0 | 172.4701 | 0 | off_peak | 554.47 |  |  | 0 | 0 | 100 | 0 | 0
3195 | 538.81 | 0 | 24.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 38.7984 | 538.81 | 0 | 0.05921 | 6.3035 | 0 | 0 | 172.4701 | 0 | off_peak | 538.81 |  |  | 0 | 0 | 100 | 0 | 0
3196 | 537.76 | 0 | 24.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 38.7984 | 537.76 | 0 | 0.05921 | 5.6367 | 0 | 0 | 172.4701 | 0 | off_peak | 537.76 |  |  | 0 | 0 | 100 | 0 | 0
3197 | 569.54 | 0 | 24.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 38.7984 | 569.54 | 0 | 0.05921 | 5.0146 | 0 | 0 | 172.4701 | 0 | off_peak | 569.54 |  |  | 0 | 0 | 100 | 0 | 0
3198 | 689.26 | 0 | 24.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 38.7984 | 689.26 | 0 | 0.05921 | 4.4131 | 0 | 0 | 172.4701 | 0 | off_peak | 689.26 |  |  | 0 | 0 | 100 | 0 | 0
3199 | 717.35 | 69.0549 | 25 | 13.9836 | 13.9836 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 38.7984 | 703.3664 | 0 | 0.05921 | 3.9587 | 0 | 0 | 172.4701 | 13.9836 | off_peak | 703.3664 |  |  | 1.95 | 0 | 98.05 | 55.3564 | 0
3200 | 775.4 | 141.863 | 25.7 | 28.6549 | 28.6549 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 38.7984 | 746.7451 | 0 | 0.05921 | 3.5879 | 0 | 0 | 172.4701 | 28.6549 | off_peak | 746.7451 |  |  | 3.7 | 0 | 96.3 | 102.8116 | 0
3201 | 760.49 | 260.037 | 26.6 | 52.3542 | 52.3542 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 38.7984 | 708.1358 | 0 | 0.05921 | 3.3254 | 0 | 0 | 172.4701 | 52.3542 | off_peak | 708.1358 |  |  | 6.88 | 0 | 93.12 | 174.0996 | 0
3202 | 775.4 | 352.243 | 27.3 | 70.7386 | 70.7386 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 38.7984 | 704.6614 | 0 | 0.05921 | 3.1818 | 0 | 0 | 172.4701 | 70.7386 | off_peak | 704.6614 |  |  | 9.12 | 0 | 90.88 | 225.0767 | 0
3203 | 749.61 | 395.31 | 27.9 | 79.2146 | 79.2146 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 38.7984 | 670.3954 | 0 | 0.05921 | 3.1479 | 0 | 0 | 172.4701 | 79.2146 | off_peak | 670.3954 |  |  | 10.57 | 0 | 89.43 | 249.3556 | 0
3204 | 756.77 | 612.803 | 28.4 | 122.5737 | 122.5737 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 38.7984 | 634.1963 | 0 | 0.05921 | 3.159 | 0 | 0 | 172.4701 | 122.5737 | off_peak | 634.1963 |  |  | 16.2 | 0 | 83.8 | 387.2106 | 0
3205 | 728.74 | 652.285 | 28.8 | 130.2808 | 130.2808 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 38.7984 | 598.4592 | 0 | 0.05921 | 3.3331 | 0 | 0 | 172.4701 | 130.2808 | off_peak | 598.4592 |  |  | 17.88 | 0 | 82.12 | 434.2412 | 0
3206 | 681.22 | 661.631 | 28.9 | 132.0992 | 132.0992 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 38.7984 | 549.1208 | 0 | 0.05921 | 3.6926 | 0 | 0 | 172.4701 | 132.0992 | off_peak | 549.1208 |  |  | 19.39 | 0 | 80.61 | 487.7912 | 0
3207 | 741.41 | 530.324 | 28.8 | 105.9215 | 105.9215 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 50.3966 | 647.8874 | 0 | 0.05921 | 4.0849 | 0 | 0 | 172.4701 | 105.9215 | off_peak | 635.4885 | 0 | 100 | 14.29 | 0 | 85.71 | 432.6813 | 0
3208 | 732.99 | 350.951 | 28.6 | 70.1465 | 70.1465 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50.3966 | 662.8435 | 0 | 0.05921 | 4.4426 | 0 | 0 | 172.4701 | 70.1465 | off_peak | 662.8435 |  |  | 9.57 | 0 | 90.43 | 311.6319 | 0
3209 | 716.79 | 354.204 | 28.2 | 70.9 | 70.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50.3966 | 645.89 | 0 | 0.05921 | 4.9397 | 0 | 0 | 172.4701 | 70.9 | off_peak | 645.89 |  |  | 9.89 | 0 | 90.11 | 350.2246 | 0
3210 | 653.94 | 199.799 | 27.6 | 40.0806 | 40.0806 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50.3966 | 613.8594 | 0 | 0.05921 | 5.4746 | 0 | 0 | 172.4701 | 40.0806 | off_peak | 613.8594 |  |  | 6.13 | 0 | 93.87 | 219.4256 | 0
3211 | 591.24 | 46.4542 | 27.3 | 9.3291 | 9.3291 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50.3966 | 581.9109 | 0 | 0.05921 | 5.8204 | 0 | 0 | 172.4701 | 9.3291 | off_peak | 581.9109 |  |  | 1.58 | 0 | 98.42 | 54.2995 | 0
3212 | 583.75 | 0 | 26.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50.3966 | 583.75 | 0 | 0.05921 | 6.1442 | 0 | 0 | 172.4701 | 0 | off_peak | 583.75 |  |  | 0 | 0 | 100 | 0 | 0
3213 | 566.98 | 0 | 26 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 61.9947 | 579.3789 | 0 | 0.05921 | 6.3077 | 0 | 0 | 172.4701 | 0 | off_peak | 566.98 | 0 | 100 | 0 | 0 | 100 | 0 | 0
3214 | 588.04 | 0 | 25.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 61.9947 | 588.04 | 0 | 0.05921 | 6.4769 | 0 | 0 | 172.4701 | 0 | off_peak | 588.04 |  |  | 0 | 0 | 100 | 0 | 0
3215 | 591.02 | 0 | 25.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 61.9947 | 591.02 | 0 | 0.05921 | 6.5172 | 0 | 0 | 172.4701 | 0 | off_peak | 591.02 |  |  | 0 | 0 | 100 | 0 | 0
3216 | 573.8 | 0 | 25.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 61.9947 | 573.8 | 0 | 0.05921 | 6.6471 | 0 | 0 | 172.4701 | 0 | off_peak | 573.8 |  |  | 0 | 0 | 100 | 0 | 0
3217 | 574.56 | 0 | 25.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 61.9947 | 574.56 | 0 | 0.05921 | 6.7959 | 0 | 0 | 172.4701 | 0 | off_peak | 574.56 |  |  | 0 | 0 | 100 | 0 | 0
3218 | 572.23 | 0 | 25.2 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 73.5928 | 584.6289 | 0 | 0.05921 | 6.7883 | 0 | 0 | 172.4701 | 0 | off_peak | 572.23 | 0 | 100 | 0 | 0 | 100 | 0 | 0
3219 | 587.2 | 0 | 25.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 73.5928 | 587.2 | 0 | 0.05921 | 6.4403 | 0 | 0 | 172.4701 | 0 | off_peak | 587.2 |  |  | 0 | 0 | 100 | 0 | 0
3220 | 574.87 | 0 | 25.2 | 0 | 0 | 0 | 0 | 0.80079 | 0.80079 | 0 | 0 | 0 | 74.3419 | 575.6708 | 0 | 0.05921 | 5.8736 | 0 | 0 | 172.4701 | 0 | off_peak | 574.87 | 0 | 100 | 0 | 0 | 100 | 0 | 0
3221 | 604.49 | 0 | 25.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3419 | 604.49 | 0 | 0.05921 | 4.9454 | 0 | 0 | 172.4701 | 0 | off_peak | 604.49 |  |  | 0 | 0 | 100 | 0 | 0
3222 | 700.51 | 0 | 25.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3419 | 700.51 | 0 | 0.05921 | 4.3177 | 0 | 0 | 172.4701 | 0 | off_peak | 700.51 |  |  | 0 | 0 | 100 | 0 | 0
3223 | 773.2 | 124.281 | 26.2 | 25.0582 | 25.0582 | 0 | 0 | 0.05172 | 0.05172 | 0 | 0 | 0 | 74.3903 | 748.1935 | 0 | 0.05921 | 3.8618 | 0 | 0 | 172.4701 | 25.0582 | off_peak | 748.1418 | 0 | 100 | 3.24 | 0 | 96.76 | 96.7695 | 0
3224 | 784.6 | 330.047 | 26.8 | 66.4014 | 66.4014 | 0 | 0 | 0.0033404 | 0.0033404 | 0 | 0 | 0 | 74.3934 | 718.2019 | 0 | 0.05921 | 3.5801 | 0 | 0 | 172.4701 | 66.4014 | off_peak | 718.1986 | 0 | 100 | 8.46 | 0 | 91.54 | 237.7237 | 0
3225 | 815.65 | 539.728 | 27.1 | 108.4687 | 108.4687 | 0 | 0 | 0.00021574 | 0.00021574 | 0 | 0 | 0 | 74.3936 | 707.1816 | 0 | 0.05921 | 3.4029 | 0 | 0 | 172.4701 | 108.4687 | off_peak | 707.1813 | 0 | 100 | 13.3 | 0 | 86.7 | 369.1082 | 0
3226 | 813.52 | 723.598 | 27.3 | 145.3153 | 145.3153 | 0 | 0 | 1.3934e-05 | 1.3934e-05 | 0 | 0 | 0 | 74.3936 | 668.2047 | 0 | 0.05921 | 3.3682 | 0 | 0 | 172.4701 | 145.3153 | off_peak | 668.2047 | 0 | 100 | 17.86 | 0 | 82.14 | 489.4561 | 0
3227 | 827.52 | 561.389 | 27.5 | 112.6581 | 112.6581 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 714.8619 | 0 | 0.05921 | 3.5185 | 0 | 0 | 172.4701 | 112.6581 | off_peak | 714.8619 |  |  | 13.61 | 0 | 86.39 | 396.3894 | 0
3228 | 872.93 | 654.762 | 27.7 | 131.3005 | 131.3005 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 741.6295 | 0 | 0.05921 | 3.8564 | 0 | 0 | 172.4701 | 131.3005 | off_peak | 741.6295 |  |  | 15.04 | 0 | 84.96 | 506.3523 | 0
3229 | 827.42 | 553.144 | 27.7 | 110.9229 | 110.9229 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 716.4971 | 0 | 0.088511 | 4.0819 | 0 | 0 | 172.4701 | 110.9229 | on_peak | 716.4971 |  |  | 13.41 | 0 | 86.59 | 452.7768 | 0
3230 | 860.59 | 881.909 | 27.7 | 176.8507 | 176.8507 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 683.7393 | 0 | 0.088511 | 4.2781 | 0 | 0 | 172.4701 | 176.8507 | on_peak | 683.7393 |  |  | 20.55 | 0 | 79.45 | 756.5826 | 0
3231 | 862.61 | 806.497 | 27.6 | 161.787 | 161.787 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 700.823 | 0 | 0.088511 | 4.4802 | 0 | 0 | 172.4701 | 161.787 | on_peak | 700.823 |  |  | 18.76 | 0 | 81.24 | 724.8325 | 0
3232 | 878.08 | 512.044 | 27.4 | 102.793 | 102.793 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 775.287 | 0 | 0.088511 | 4.8492 | 0 | 0 | 172.4701 | 102.793 | on_peak | 775.287 |  |  | 11.71 | 0 | 88.29 | 498.4611 | 0
3233 | 826.23 | 448.611 | 27.1 | 90.1569 | 90.1569 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 736.0731 | 0 | 0.088511 | 5.246 | 0 | 0 | 172.4701 | 90.1569 | on_peak | 736.0731 |  |  | 10.91 | 0 | 89.09 | 472.9649 | 0
3234 | 882.47 | 234.403 | 26.7 | 47.1761 | 47.1761 | 0 | 0 | 0 | 0 | 62.63 | 62.63 | 0 | 7.4394 | 772.6639 | 0 | 0.088511 | 5.7726 | 0 | 0 | 172.4701 | 47.1761 | on_peak | 772.6639 |  |  | 5.35 | 7.1 | 87.56 | 272.3269 | 0
3235 | 781.5 | 44.8892 | 26.4 | 9.0442 | 9.0442 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 772.4558 | 0 | 0.088511 | 6.2002 | 0 | 0 | 172.4701 | 9.0442 | on_peak | 772.4558 |  |  | 1.16 | 0 | 98.84 | 56.0763 | 0
3236 | 807.07 | 0 | 26 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 807.07 | 0 | 0.088511 | 6.5536 | 0 | 0 | 172.4701 | 0 | on_peak | 807.07 |  |  | 0 | 0 | 100 | 0 | 0
3237 | 809.11 | 0 | 26 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 809.11 | 0 | 0.088511 | 6.9193 | 0 | 0 | 172.4701 | 0 | on_peak | 809.11 |  |  | 0 | 0 | 100 | 0 | 0
3238 | 792.48 | 0 | 26 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 792.48 | 0 | 0.05921 | 7.2747 | 0 | 0 | 172.4701 | 0 | off_peak | 792.48 |  |  | 0 | 0 | 100 | 0 | 0
3239 | 772.9 | 0 | 26.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 772.9 | 0 | 0.05921 | 7.4464 | 0 | 0 | 172.4701 | 0 | off_peak | 772.9 |  |  | 0 | 0 | 100 | 0 | 0
3240 | 755.06 | 0 | 26 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 755.06 | 0 | 0.05921 | 7.6134 | 0 | 0 | 172.4701 | 0 | off_peak | 755.06 |  |  | 0 | 0 | 100 | 0 | 0
3241 | 738.31 | 0 | 25.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 738.31 | 0 | 0.05921 | 7.5055 | 0 | 0 | 172.4701 | 0 | off_peak | 738.31 |  |  | 0 | 0 | 100 | 0 | 0
3242 | 685.73 | 0 | 25.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 685.73 | 0 | 0.05921 | 7.2608 | 0 | 0 | 172.4701 | 0 | off_peak | 685.73 |  |  | 0 | 0 | 100 | 0 | 0
3243 | 641.41 | 0 | 25.5 | 0 | 0 | 0 | 0 | 8.7263 | 8.7263 | 0 | 0 | 0 | 15.6021 | 650.1363 | 0 | 0.05921 | 6.8057 | 0 | 0 | 172.4701 | 0 | off_peak | 641.41 | 0 | 100 | 0 | 0 | 100 | 0 | 0
3244 | 621.9 | 0 | 25.4 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 27.2003 | 634.2989 | 0 | 0.05921 | 6.0598 | 0 | 0 | 172.4701 | 0 | off_peak | 621.9 | 0 | 100 | 0 | 0 | 100 | 0 | 0
3245 | 639.71 | 0 | 25.4 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 38.7984 | 652.1089 | 0 | 0.05921 | 5.126 | 0 | 0 | 172.4701 | 0 | off_peak | 639.71 | 0 | 100 | 0 | 0 | 100 | 0 | 0
3246 | 693.6 | 0 | 25.6 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 50.3966 | 705.9989 | 0 | 0.05921 | 4.376 | 0 | 0 | 172.4701 | 0 | off_peak | 693.6 | 0 | 100 | 0 | 0 | 100 | 0 | 0
3247 | 759.21 | 102.977 | 25.7 | 20.8003 | 20.8003 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 61.9947 | 750.8086 | 0 | 0.05921 | 3.9259 | 0 | 0 | 172.4701 | 20.8003 | off_peak | 738.4097 | 0 | 100 | 2.74 | 0 | 97.26 | 81.6608 | 0
3248 | 854.01 | 290.878 | 25.7 | 58.7544 | 58.7544 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 73.5928 | 807.6546 | 0 | 0.05921 | 3.5722 | 0 | 0 | 172.4701 | 58.7544 | off_peak | 795.2556 | 0 | 100 | 6.88 | 0 | 93.12 | 209.8825 | 0
3249 | 864.2 | 460.606 | 25.5 | 93.1048 | 93.1048 | 0 | 0 | 0.80079 | 0.80079 | 0 | 0 | 0 | 74.3419 | 771.896 | 0 | 0.05921 | 3.3685 | 0 | 0 | 172.4701 | 93.1048 | off_peak | 771.0952 | 0 | 100 | 10.77 | 0 | 89.23 | 313.6221 | 0
3250 | 814.51 | 642.421 | 25.3 | 129.9498 | 129.9498 | 0 | 0 | 0.05172 | 0.05172 | 0 | 0 | 0 | 74.3903 | 684.612 | 0 | 0.05921 | 3.2834 | 0 | 0 | 172.4701 | 129.9498 | off_peak | 684.5602 | 0 | 100 | 15.95 | 0 | 84.05 | 426.6743 | 0
3251 | 819.71 | 759.138 | 25 | 153.7254 | 153.7254 | 0 | 0 | 0.0033404 | 0.0033404 | 0 | 0 | 0 | 74.3934 | 665.9879 | 0 | 0.05921 | 3.4161 | 0 | 0 | 172.4701 | 153.7254 | off_peak | 665.9846 | 0 | 100 | 18.75 | 0 | 81.25 | 525.1478 | 0
3252 | 873.82 | 897.594 | 24.6 | 182.0245 | 182.0245 | 0 | 0 | 0.00021574 | 0.00021574 | 0 | 0 | 0 | 74.3936 | 691.7957 | 0 | 0.05921 | 3.8073 | 0 | 0 | 172.4701 | 182.0245 | off_peak | 691.7955 | 0 | 100 | 20.83 | 0 | 79.17 | 693.0209 | 0
3253 | 880.4 | 867.342 | 24.4 | 176.0161 | 176.0161 | 0 | 0 | 1.4896e-05 | 1.4896e-05 | 0 | 0 | 0 | 74.3936 | 704.3839 | 0 | 0.088511 | 4.1348 | 0 | 0 | 172.4701 | 176.0161 | on_peak | 704.3839 | 0 | 100 | 19.99 | 0 | 80.01 | 727.7854 | 0
3254 | 897.78 | 830.755 | 24.1 | 168.7729 | 168.7729 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 729.0071 | 0 | 0.088511 | 4.4151 | 0 | 0 | 172.4701 | 168.7729 | on_peak | 729.0071 |  |  | 18.8 | 0 | 81.2 | 745.1492 | 0
3255 | 911.92 | 735.43 | 23.7 | 149.6215 | 149.6215 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 762.2985 | 0 | 0.088511 | 4.688 | 0 | 0 | 172.4701 | 149.6215 | on_peak | 762.2985 |  |  | 16.41 | 0 | 83.59 | 701.4223 | 0
3256 | 939.3 | 341.564 | 23.4 | 69.5651 | 69.5651 | 0 | 0 | 0 | 0 | 26.9469 | 26.9469 | 0 | 45.5862 | 842.788 | 0 | 0.088511 | 4.9597 | 0 | 0 | 172.4701 | 69.5651 | on_peak | 842.788 |  |  | 7.41 | 2.87 | 89.73 | 345.0189 | 0
3257 | 912.97 | 376.172 | 23.3 | 76.641 | 76.641 | 0 | 0 | 6.459 | 6.459 | 0 | 0 | 0 | 51.628 | 842.788 | 0 | 0.088511 | 5.4232 | 0 | 0 | 172.4701 | 76.641 | on_peak | 836.329 | 0 | 100 | 8.39 | 0 | 91.61 | 415.6373 | 0
3258 | 921.29 | 182.491 | 23.4 | 37.1673 | 37.1673 | 0 | 0 | 0 | 0 | 41.3347 | 41.3347 | 0 | 7.4394 | 842.788 | 0 | 0.088511 | 6.0307 | 0 | 0 | 172.4701 | 37.1673 | on_peak | 842.788 |  |  | 4.03 | 4.49 | 91.48 | 224.1464 | 0
3259 | 827.41 | 54.3843 | 23.4 | 11.0763 | 11.0763 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 816.3337 | 0 | 0.088511 | 6.6201 | 0 | 0 | 172.4701 | 11.0763 | on_peak | 816.3337 |  |  | 1.34 | 0 | 98.66 | 73.3262 | 0
3260 | 841.05 | 0 | 23.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 841.05 | 0 | 0.088511 | 7.2021 | 0 | 0 | 172.4701 | 0 | on_peak | 841.05 |  |  | 0 | 0 | 100 | 0 | 0
3261 | 825.89 | 0 | 23.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 825.89 | 0 | 0.088511 | 7.5088 | 0 | 0 | 172.4701 | 0 | on_peak | 825.89 |  |  | 0 | 0 | 100 | 0 | 0
3262 | 802.35 | 0 | 23.5 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 19.0375 | 814.7489 | 0 | 0.05921 | 7.5994 | 0 | 0 | 172.4701 | 0 | off_peak | 802.35 | 0 | 100 | 0 | 0 | 100 | 0 | 0
3263 | 812.43 | 0 | 23.4 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 30.6357 | 824.8289 | 0 | 0.05921 | 7.6903 | 0 | 0 | 172.4701 | 0 | off_peak | 812.43 | 0 | 100 | 0 | 0 | 100 | 0 | 0
3264 | 794.01 | 0 | 23.4 | 0 | 0 | 0 | 0 | 8.7263 | 8.7263 | 0 | 0 | 0 | 38.7984 | 802.7363 | 0 | 0.05921 | 7.8245 | 0 | 0 | 172.4701 | 0 | off_peak | 794.01 | 0 | 100 | 0 | 0 | 100 | 0 | 0
3265 | 735.42 | 0 | 23.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 38.7984 | 735.42 | 0 | 0.05921 | 7.7372 | 0 | 0 | 172.4701 | 0 | off_peak | 735.42 |  |  | 0 | 0 | 100 | 0 | 0
3266 | 694.08 | 0 | 23.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 38.7984 | 694.08 | 0 | 0.05921 | 7.6534 | 0 | 0 | 172.4701 | 0 | off_peak | 694.08 |  |  | 0 | 0 | 100 | 0 | 0
3267 | 558.46 | 0 | 23.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 38.7984 | 558.46 | 0 | 0.05921 | 7.2368 | 0 | 0 | 172.4701 | 0 | off_peak | 558.46 |  |  | 0 | 0 | 100 | 0 | 0
3268 | 493.17 | 0 | 23.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 38.7984 | 493.17 | 0 | 0.05921 | 6.3683 | 0 | 0 | 172.4701 | 0 | off_peak | 493.17 |  |  | 0 | 0 | 100 | 0 | 0
3269 | 523.08 | 0 | 23.1 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 50.3966 | 535.4789 | 0 | 0.05921 | 5.4233 | 0 | 0 | 172.4701 | 0 | off_peak | 523.08 | 0 | 100 | 0 | 0 | 100 | 0 | 0
3270 | 738.02 | 0 | 23.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50.3966 | 738.02 | 0 | 0.05921 | 4.7337 | 0 | 0 | 172.4701 | 0 | off_peak | 738.02 |  |  | 0 | 0 | 100 | 0 | 0
3271 | 773.11 | 130.889 | 23.1 | 26.6863 | 26.6863 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 61.9947 | 758.8226 | 0 | 0.05921 | 4.3251 | 0 | 0 | 172.4701 | 26.6863 | off_peak | 746.4237 | 0 | 100 | 3.45 | 0 | 96.55 | 115.4204 | 0
3272 | 819.62 | 341.374 | 23.3 | 69.5513 | 69.5513 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 73.5928 | 762.4676 | 0 | 0.05921 | 3.9711 | 0 | 0 | 172.4701 | 69.5513 | off_peak | 750.0687 | 0 | 100 | 8.49 | 0 | 91.51 | 276.1917 | 0
3273 | 887.25 | 552.782 | 23.6 | 112.5025 | 112.5025 | 0 | 0 | 0.80079 | 0.80079 | 0 | 0 | 0 | 74.3419 | 775.5483 | 0 | 0.05921 | 3.7407 | 0 | 0 | 172.4701 | 112.5025 | off_peak | 774.7475 | 0 | 100 | 12.68 | 0 | 87.32 | 420.835 | 0
3274 | 861.1 | 736.821 | 24.1 | 149.6897 | 149.6897 | 0 | 0 | 0.05172 | 0.05172 | 0 | 0 | 0 | 74.3903 | 711.462 | 0 | 0.05921 | 3.6527 | 0 | 0 | 172.4701 | 149.6897 | off_peak | 711.4103 | 0 | 100 | 17.38 | 0 | 82.62 | 546.7739 | 0
3275 | 810.65 | 769.51 | 24.7 | 155.9941 | 155.9941 | 0 | 0 | 0.0033404 | 0.0033404 | 0 | 0 | 0 | 74.3934 | 654.6593 | 0 | 0.05921 | 3.7985 | 0 | 0 | 172.4701 | 155.9941 | off_peak | 654.6559 | 0 | 100 | 19.24 | 0 | 80.76 | 592.5489 | 0
3276 | 867.37 | 864.138 | 25.2 | 174.862 | 174.862 | 0 | 0 | 0.00021574 | 0.00021574 | 0 | 0 | 0 | 74.3936 | 692.5083 | 0 | 0.05921 | 4.2177 | 0 | 0 | 172.4701 | 174.862 | off_peak | 692.508 | 0 | 100 | 20.16 | 0 | 79.84 | 737.523 | 0
3277 | 860.53 | 639.379 | 25.5 | 129.2412 | 129.2412 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 731.2888 | 0 | 0.088511 | 4.4452 | 0 | 0 | 172.4701 | 129.2412 | on_peak | 731.2888 |  |  | 15.02 | 0 | 84.98 | 574.5031 | 0
3278 | 881.81 | 573.389 | 25.8 | 115.7769 | 115.7769 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 766.0331 | 0 | 0.088511 | 4.6832 | 0 | 0 | 172.4701 | 115.7769 | on_peak | 766.0331 |  |  | 13.13 | 0 | 86.87 | 542.2069 | 0
3279 | 938.44 | 730.112 | 26.1 | 147.2622 | 147.2622 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 791.1778 | 0 | 0.088511 | 5.0405 | 0 | 0 | 172.4701 | 147.2622 | on_peak | 791.1778 |  |  | 15.69 | 0 | 84.31 | 742.2785 | 0
3280 | 900.67 | 644.72 | 26.2 | 129.9918 | 129.9918 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 770.6782 | 0 | 0.088511 | 5.4407 | 0 | 0 | 172.4701 | 129.9918 | on_peak | 770.6782 |  |  | 14.43 | 0 | 85.57 | 707.2525 | 0
3281 | 867.92 | 461.775 | 26.2 | 93.1055 | 93.1055 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 774.8145 | 0 | 0.088511 | 5.9824 | 0 | 0 | 172.4701 | 93.1055 | on_peak | 774.8145 |  |  | 10.73 | 0 | 89.27 | 556.9928 | 0
3282 | 861.94 | 225.962 | 25.8 | 45.6255 | 45.6255 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 816.3145 | 0 | 0.088511 | 6.5351 | 0 | 0 | 172.4701 | 45.6255 | on_peak | 816.3145 |  |  | 5.29 | 0 | 94.71 | 298.1651 | 0
3283 | 814.91 | 53.5205 | 25.4 | 10.8223 | 10.8223 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 804.0877 | 0 | 0.088511 | 7.0378 | 0 | 0 | 172.4701 | 10.8223 | on_peak | 804.0877 |  |  | 1.33 | 0 | 98.67 | 76.1647 | 0
3284 | 836.23 | 0 | 24.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 836.23 | 0 | 0.088511 | 7.1889 | 0 | 0 | 172.4701 | 0 | on_peak | 836.23 |  |  | 0 | 0 | 100 | 0 | 0
3285 | 814.57 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 62.63 | 62.63 | 0 | 7.4394 | 751.94 | 0 | 0.088511 | 7.0405 | 62.63 | 0 | 105.5158 | 62.63 | on_peak | 751.94 |  |  | 0 | 7.69 | 92.31 | 440.9435 | 0
3286 | 786.05 | 0 | 23.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 786.05 | 0 | 0.05921 | 6.9926 | 0 | 0 | 105.5158 | 0 | off_peak | 786.05 |  |  | 0 | 0 | 100 | 0 | 0
3287 | 776.26 | 0 | 23.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 776.26 | 0 | 0.05921 | 7.1452 | 0 | 0 | 105.5158 | 0 | off_peak | 776.26 |  |  | 0 | 0 | 100 | 0 | 0
3288 | 796.71 | 0 | 23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 796.71 | 0 | 0.05921 | 7.2513 | 0 | 0 | 105.5158 | 0 | off_peak | 796.71 |  |  | 0 | 0 | 100 | 0 | 0
3289 | 704.24 | 0 | 22.7 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 19.0375 | 716.6389 | 0 | 0.05921 | 7.2244 | 0 | 0 | 105.5158 | 0 | off_peak | 704.24 | 0 | 100 | 0 | 0 | 100 | 0 | 0
3290 | 717.82 | 0 | 22.4 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 30.6357 | 730.2189 | 0 | 0.05921 | 7.0584 | 0 | 0 | 105.5158 | 0 | off_peak | 717.82 | 0 | 100 | 0 | 0 | 100 | 0 | 0
3291 | 645.35 | 0 | 22.1 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 42.2338 | 657.7489 | 0 | 0.05921 | 6.7285 | 0 | 0 | 105.5158 | 0 | off_peak | 645.35 | 0 | 100 | 0 | 0 | 100 | 0 | 0
3292 | 618.02 | 0 | 21.8 | 0 | 0 | 0 | 0 | 8.7263 | 8.7263 | 0 | 0 | 0 | 50.3966 | 626.7463 | 0 | 0.05921 | 6.0259 | 0 | 0 | 105.5158 | 0 | off_peak | 618.02 | 0 | 100 | 0 | 0 | 100 | 0 | 0
3293 | 618.91 | 0 | 21.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50.3966 | 618.91 | 0 | 0.05921 | 5.2332 | 0 | 0 | 105.5158 | 0 | off_peak | 618.91 |  |  | 0 | 0 | 100 | 0 | 0
3294 | 671.69 | 0 | 21.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50.3966 | 671.69 | 0 | 0.05921 | 4.4288 | 0 | 0 | 105.5158 | 0 | off_peak | 671.69 |  |  | 0 | 0 | 100 | 0 | 0
3295 | 784.43 | 109.714 | 22.2 | 22.441 | 22.441 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 61.9947 | 774.3879 | 0 | 0.05921 | 3.9549 | 0 | 0 | 105.5158 | 22.441 | off_peak | 761.989 | 0 | 100 | 2.86 | 0 | 97.14 | 88.7529 | 0
3296 | 872.93 | 205.622 | 23.1 | 41.9233 | 41.9233 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 73.5928 | 843.4057 | 0 | 0.05921 | 3.5938 | 0 | 0 | 105.5158 | 41.9233 | off_peak | 831.0067 | 0 | 100 | 4.8 | 0 | 95.2 | 150.6627 | 0
3297 | 885.68 | 469.36 | 24 | 95.3876 | 95.3876 | 0 | 0 | 0.80079 | 0.80079 | 0 | 0 | 0 | 74.3419 | 791.0932 | 0 | 0.05921 | 3.3528 | 0 | 0 | 105.5158 | 95.3876 | off_peak | 790.2924 | 0 | 100 | 10.77 | 0 | 89.23 | 319.8177 | 0
3298 | 869.43 | 462.377 | 24.8 | 93.6988 | 93.6988 | 0 | 0 | 0.05172 | 0.05172 | 0 | 0 | 0 | 74.3903 | 775.783 | 0 | 0.05921 | 3.2637 | 0 | 0 | 105.5158 | 93.6988 | off_peak | 775.7312 | 0 | 100 | 10.78 | 0 | 89.22 | 305.8077 | 0
3299 | 823.32 | 659.436 | 25.5 | 133.2954 | 133.2954 | 0 | 0 | 0.0033404 | 0.0033404 | 0 | 0 | 0 | 74.3934 | 690.0279 | 0 | 0.05921 | 3.4273 | 0 | 0 | 105.5158 | 133.2954 | off_peak | 690.0246 | 0 | 100 | 16.19 | 0 | 83.81 | 456.8405 | 0
3300 | 896.5 | 672.264 | 26.1 | 135.5944 | 135.5944 | 0 | 0 | 0.00021574 | 0.00021574 | 0 | 0 | 0 | 74.3936 | 760.9058 | 0 | 0.05921 | 3.8278 | 0 | 0 | 105.5158 | 135.5944 | off_peak | 760.9056 | 0 | 100 | 15.12 | 0 | 84.88 | 519.0288 | 0
3301 | 859.19 | 563.461 | 26.6 | 113.4436 | 113.4436 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 745.7464 | 0 | 0.088511 | 4.1254 | 0 | 0 | 105.5158 | 113.4436 | on_peak | 745.7464 |  |  | 13.2 | 0 | 86.8 | 467.9967 | 0
3302 | 922.67 | 761.769 | 27 | 153.1476 | 153.1476 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 769.5224 | 0 | 0.088511 | 4.4173 | 0 | 0 | 105.5158 | 153.1476 | on_peak | 769.5224 |  |  | 16.6 | 0 | 83.4 | 676.4968 | 0
3303 | 956.16 | 811.39 | 27.2 | 163.0052 | 163.0052 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 793.1548 | 0 | 0.088511 | 4.6711 | 0 | 0 | 105.5158 | 163.0052 | on_peak | 793.1548 |  |  | 17.05 | 0 | 82.95 | 761.4101 | 0
3304 | 875.11 | 653.602 | 27.1 | 131.3538 | 131.3538 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 743.7562 | 0 | 0.088511 | 5.1159 | 0 | 0 | 105.5158 | 131.3538 | on_peak | 743.7562 |  |  | 15.01 | 0 | 84.99 | 671.9984 | 0
3305 | 933.87 | 457.75 | 26.9 | 92.0603 | 92.0603 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 841.8097 | 0 | 0.088511 | 5.6353 | 0 | 0 | 105.5158 | 92.0603 | on_peak | 841.8097 |  |  | 9.86 | 0 | 90.14 | 518.7831 | 0
3306 | 888.69 | 240.927 | 26.5 | 48.5243 | 48.5243 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 840.1657 | 0 | 0.088511 | 6.1492 | 0 | 0 | 105.5158 | 48.5243 | on_peak | 840.1657 |  |  | 5.46 | 0 | 94.54 | 298.3848 | 0
3307 | 830.48 | 58.1645 | 26.2 | 11.7274 | 11.7274 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 818.7526 | 0 | 0.088511 | 6.696 | 0 | 0 | 105.5158 | 11.7274 | on_peak | 818.7526 |  |  | 1.41 | 0 | 98.59 | 78.5265 | 0
3308 | 857.11 | 0 | 25.3 | 0 | 0 | 0 | 0 | 0 | 0 | 61.118 | 61.118 | 0 | 9.0558 | 795.992 | 0 | 0.088511 | 7.08 | 0 | 0 | 105.5158 | 0 | on_peak | 795.992 |  |  | 0 | 7.13 | 92.87 | 0 | 0
3309 | 844.3 | 0 | 24.9 | 0 | 0 | 0 | 0 | 0 | 0 | 1.512 | 1.512 | 0 | 7.4394 | 842.788 | 0 | 0.088511 | 7.3036 | 0 | 0 | 105.5158 | 0 | on_peak | 842.788 |  |  | 0 | 0.18 | 99.82 | 0 | 0
3310 | 796.8 | 0 | 24.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 796.8 | 0 | 0.05921 | 7.4434 | 0 | 0 | 105.5158 | 0 | off_peak | 796.8 |  |  | 0 | 0 | 100 | 0 | 0
3311 | 832.99 | 0 | 24.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 832.99 | 0 | 0.05921 | 7.4157 | 0 | 0 | 105.5158 | 0 | off_peak | 832.99 |  |  | 0 | 0 | 100 | 0 | 0
3312 | 803.42 | 0 | 23.8 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 19.0375 | 815.8189 | 0 | 0.05921 | 7.1216 | 0 | 0 | 105.5158 | 0 | off_peak | 803.42 | 0 | 100 | 0 | 0 | 100 | 0 | 0
3313 | 787.96 | 0 | 23.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19.0375 | 787.96 | 0 | 0.05921 | 6.9501 | 0 | 0 | 105.5158 | 0 | off_peak | 787.96 |  |  | 0 | 0 | 100 | 0 | 0
3314 | 742.77 | 0 | 23 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 30.6357 | 755.1689 | 0 | 0.05921 | 6.8523 | 0 | 0 | 105.5158 | 0 | off_peak | 742.77 | 0 | 100 | 0 | 0 | 100 | 0 | 0
3315 | 703 | 0 | 22.7 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 42.2338 | 715.3989 | 0 | 0.05921 | 6.5009 | 0 | 0 | 105.5158 | 0 | off_peak | 703 | 0 | 100 | 0 | 0 | 100 | 0 | 0
3316 | 675.56 | 0 | 22.4 | 0 | 0 | 0 | 0 | 8.7263 | 8.7263 | 0 | 0 | 0 | 50.3966 | 684.2863 | 0 | 0.05921 | 5.8855 | 0 | 0 | 105.5158 | 0 | off_peak | 675.56 | 0 | 100 | 0 | 0 | 100 | 0 | 0
3317 | 682.35 | 0 | 22.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50.3966 | 682.35 | 0 | 0.05921 | 5.1289 | 0 | 0 | 105.5158 | 0 | off_peak | 682.35 |  |  | 0 | 0 | 100 | 0 | 0
3318 | 735.75 | 0 | 22.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50.3966 | 735.75 | 0 | 0.05921 | 4.4101 | 0 | 0 | 105.5158 | 0 | off_peak | 735.75 |  |  | 0 | 0 | 100 | 0 | 0
3319 | 771.7 | 76.7798 | 23 | 15.6599 | 15.6599 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 61.9947 | 768.4391 | 0 | 0.05921 | 4.0476 | 0 | 0 | 105.5158 | 15.6599 | off_peak | 756.0401 | 0 | 100 | 2.03 | 0 | 97.97 | 63.3842 | 0
3320 | 849.08 | 179.361 | 23.8 | 36.4775 | 36.4775 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 73.5928 | 825.0014 | 0 | 0.05921 | 3.7282 | 0 | 0 | 105.5158 | 36.4775 | off_peak | 812.6025 | 0 | 100 | 4.3 | 0 | 95.7 | 135.9937 | 0
3321 | 873.15 | 364.468 | 24.6 | 73.911 | 73.911 | 0 | 0 | 0.80079 | 0.80079 | 0 | 0 | 0 | 74.3419 | 800.0397 | 0 | 0.05921 | 3.5345 | 0 | 0 | 105.5158 | 73.911 | off_peak | 799.239 | 0 | 100 | 8.46 | 0 | 91.54 | 261.2361 | 0
3322 | 856.91 | 494.172 | 25.3 | 99.9618 | 99.9618 | 0 | 0 | 0.05172 | 0.05172 | 0 | 0 | 0 | 74.3903 | 757 | 0 | 0.05921 | 3.4825 | 0 | 0 | 105.5158 | 99.9618 | off_peak | 756.9482 | 0 | 100 | 11.67 | 0 | 88.33 | 348.113 | 0
3323 | 775.74 | 635.302 | 26 | 128.1855 | 128.1855 | 0 | 0 | 0.0033404 | 0.0033404 | 0 | 0 | 0 | 74.3934 | 647.5578 | 0 | 0.05921 | 3.6573 | 0 | 0 | 105.5158 | 128.1855 | off_peak | 647.5545 | 0 | 100 | 16.52 | 0 | 83.48 | 468.8098 | 0
3324 | 820.78 | 717.436 | 26.7 | 144.3917 | 144.3917 | 0 | 0 | 0.00021574 | 0.00021574 | 0 | 0 | 0 | 74.3936 | 676.3885 | 0 | 0.05921 | 4.0319 | 0 | 0 | 105.5158 | 144.3917 | off_peak | 676.3883 | 0 | 100 | 17.59 | 0 | 82.41 | 582.167 | 0
3325 | 870.95 | 627.363 | 27.3 | 125.9891 | 125.9891 | 0 | 0 | 0 | 0 | 62.63 | 62.63 | 0 | 7.4394 | 682.3309 | 0 | 0.088511 | 4.2978 | 0 | 0 | 105.5158 | 125.9891 | on_peak | 682.3309 |  |  | 14.47 | 7.19 | 78.34 | 541.47 | 0
3326 | 914.74 | 761.073 | 27.7 | 152.6193 | 152.6193 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 762.1207 | 0 | 0.088511 | 4.6578 | 0 | 0 | 105.5158 | 152.6193 | on_peak | 762.1207 |  |  | 16.68 | 0 | 83.32 | 710.8638 | 0
3327 | 914.26 | 657.007 | 28.1 | 131.5591 | 131.5591 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 782.7009 | 0 | 0.088511 | 5.0006 | 0 | 0 | 105.5158 | 131.5591 | on_peak | 782.7009 |  |  | 14.39 | 0 | 85.61 | 657.8765 | 0
3328 | 908.19 | 498.612 | 28.2 | 99.8058 | 99.8058 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 808.3842 | 0 | 0.088511 | 5.3841 | 0 | 0 | 105.5158 | 99.8058 | on_peak | 808.3842 |  |  | 10.99 | 0 | 89.01 | 537.3687 | 0
3329 | 873.57 | 251.695 | 27.9 | 50.4361 | 50.4361 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 823.1339 | 0 | 0.088511 | 5.8028 | 0 | 0 | 105.5158 | 50.4361 | on_peak | 823.1339 |  |  | 5.77 | 0 | 94.23 | 292.6707 | 0
3330 | 832.89 | 125.559 | 27.3 | 25.2152 | 25.2152 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 807.6748 | 0 | 0.088511 | 6.3086 | 0 | 0 | 105.5158 | 25.2152 | on_peak | 807.6748 |  |  | 3.03 | 0 | 96.97 | 159.073 | 0
3331 | 836.84 | 45.831 | 26.8 | 9.2206 | 9.2206 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 827.6194 | 0 | 0.088511 | 6.675 | 0 | 0 | 105.5158 | 9.2206 | on_peak | 827.6194 |  |  | 1.1 | 0 | 98.9 | 61.5478 | 0
3332 | 828.58 | 0 | 25.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 828.58 | 0 | 0.088511 | 6.8366 | 0 | 0 | 105.5158 | 0 | on_peak | 828.58 |  |  | 0 | 0 | 100 | 0 | 0
3333 | 842.14 | 0 | 25.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 842.14 | 0 | 0.088511 | 6.7662 | 0 | 0 | 105.5158 | 0 | on_peak | 842.14 |  |  | 0 | 0 | 100 | 0 | 0
3334 | 803.54 | 0 | 25.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 803.54 | 0 | 0.05921 | 7.0882 | 0 | 0 | 105.5158 | 0 | off_peak | 803.54 |  |  | 0 | 0 | 100 | 0 | 0
3335 | 800.54 | 0 | 24.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 800.54 | 0 | 0.05921 | 7.3244 | 0 | 0 | 105.5158 | 0 | off_peak | 800.54 |  |  | 0 | 0 | 100 | 0 | 0
3336 | 776.8 | 0 | 24.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 776.8 | 0 | 0.05921 | 7.3211 | 0 | 0 | 105.5158 | 0 | off_peak | 776.8 |  |  | 0 | 0 | 100 | 0 | 0
3337 | 776.24 | 0 | 24.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 776.24 | 0 | 0.05921 | 7.3005 | 0 | 0 | 105.5158 | 0 | off_peak | 776.24 |  |  | 0 | 0 | 100 | 0 | 0
3338 | 698.46 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 698.46 | 0 | 0.05921 | 7.0806 | 0 | 0 | 105.5158 | 0 | off_peak | 698.46 |  |  | 0 | 0 | 100 | 0 | 0
3339 | 634.08 | 0 | 23.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 634.08 | 0 | 0.05921 | 6.7695 | 0 | 0 | 105.5158 | 0 | off_peak | 634.08 |  |  | 0 | 0 | 100 | 0 | 0
3340 | 646.48 | 0 | 23.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 646.48 | 0 | 0.05921 | 6.0665 | 0 | 0 | 105.5158 | 0 | off_peak | 646.48 |  |  | 0 | 0 | 100 | 0 | 0
3341 | 681.43 | 0 | 23.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 681.43 | 0 | 0.05921 | 5.4649 | 0 | 0 | 105.5158 | 0 | off_peak | 681.43 |  |  | 0 | 0 | 100 | 0 | 0
3342 | 730.1 | 0 | 23.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 730.1 | 0 | 0.05921 | 4.6988 | 0 | 0 | 105.5158 | 0 | off_peak | 730.1 |  |  | 0 | 0 | 100 | 0 | 0
3343 | 800.89 | 102.248 | 24.1 | 20.7723 | 20.7723 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 780.1177 | 0 | 0.05921 | 4.2965 | 0 | 0 | 105.5158 | 20.7723 | off_peak | 780.1177 |  |  | 2.59 | 0 | 97.41 | 89.2484 | 0
3344 | 876.51 | 241.294 | 24.9 | 48.8796 | 48.8796 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 827.6304 | 0 | 0.05921 | 3.9487 | 0 | 0 | 105.5158 | 48.8796 | off_peak | 827.6304 |  |  | 5.58 | 0 | 94.42 | 193.0111 | 0
3345 | 879.14 | 359.783 | 25.7 | 72.6725 | 72.6725 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 806.4675 | 0 | 0.05921 | 3.7028 | 0 | 0 | 105.5158 | 72.6725 | off_peak | 806.4675 |  |  | 8.27 | 0 | 91.73 | 269.0925 | 0
3346 | 867.28 | 478.481 | 26.5 | 96.3692 | 96.3692 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 770.9108 | 0 | 0.05921 | 3.5643 | 0 | 0 | 105.5158 | 96.3692 | off_peak | 770.9108 |  |  | 11.11 | 0 | 88.89 | 343.4933 | 0
3347 | 835.95 | 536.765 | 27.3 | 107.7949 | 107.7949 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 728.1551 | 0 | 0.05921 | 3.5375 | 0 | 0 | 105.5158 | 107.7949 | off_peak | 728.1551 |  |  | 12.89 | 0 | 87.11 | 381.3228 | 0
3348 | 872.72 | 737.035 | 28 | 147.6377 | 135.2388 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 0 | 19.0375 | 737.4812 | 0 | 0.05921 | 3.5873 | 0 | 0 | 117.114 | 135.2388 | off_peak | 737.4812 | 100 | 0 | 15.5 | 0 | 84.5 | 485.1478 | 0
3349 | 831.02 | 775.165 | 28.4 | 155.0496 | 155.0496 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19.0375 | 675.9704 | 0 | 0.05921 | 3.8259 | 0 | 0 | 117.114 | 155.0496 | off_peak | 675.9704 |  |  | 18.66 | 0 | 81.34 | 593.2072 | 0
3350 | 869.03 | 742.01 | 28.7 | 148.2556 | 148.2556 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 30.6357 | 733.1733 | 0 | 0.05921 | 4.3016 | 0 | 0 | 117.114 | 148.2556 | off_peak | 720.7744 | 0 | 100 | 17.06 | 0 | 82.94 | 637.7423 | 0
3351 | 855.87 | 562.194 | 28.8 | 112.2869 | 112.2869 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30.6357 | 743.5831 | 0 | 0.05921 | 4.6258 | 0 | 0 | 117.114 | 112.2869 | off_peak | 743.5831 |  |  | 13.12 | 0 | 86.88 | 519.4136 | 0
3352 | 843.28 | 481.64 | 28.7 | 96.233 | 96.233 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 42.2338 | 759.446 | 0 | 0.05921 | 5.0917 | 0 | 0 | 117.114 | 96.233 | off_peak | 747.047 | 0 | 100 | 11.41 | 0 | 88.59 | 489.9848 | 0
3353 | 811.47 | 396.871 | 28.2 | 79.4406 | 79.4406 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 42.2338 | 732.0294 | 0 | 0.05921 | 5.7471 | 0 | 0 | 117.114 | 79.4406 | off_peak | 732.0294 |  |  | 9.79 | 0 | 90.21 | 456.5548 | 0
3354 | 788.53 | 142.993 | 27.4 | 28.7059 | 28.7059 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 42.2338 | 759.8241 | 0 | 0.05921 | 6.5803 | 0 | 0 | 117.114 | 28.7059 | off_peak | 759.8241 |  |  | 3.64 | 0 | 96.36 | 188.8927 | 0
3355 | 730.12 | 49.0363 | 27 | 9.8584 | 9.8584 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 42.2338 | 720.2616 | 0 | 0.05921 | 7.0998 | 0 | 0 | 117.114 | 9.8584 | off_peak | 720.2616 |  |  | 1.35 | 0 | 98.65 | 69.9928 | 0
3356 | 663.54 | 0 | 26 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 42.2338 | 663.54 | 0 | 0.05921 | 7.3812 | 0 | 0 | 117.114 | 0 | off_peak | 663.54 |  |  | 0 | 0 | 100 | 0 | 0
3357 | 674.58 | 0 | 25.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 42.2338 | 674.58 | 0 | 0.05921 | 7.5025 | 0 | 0 | 117.114 | 0 | off_peak | 674.58 |  |  | 0 | 0 | 100 | 0 | 0
3358 | 683.56 | 0 | 25.8 | 0 | 0 | 0 | 0 | 8.7263 | 8.7263 | 0 | 0 | 0 | 50.3966 | 692.2863 | 0 | 0.05921 | 7.4856 | 0 | 0 | 117.114 | 0 | off_peak | 683.56 | 0 | 100 | 0 | 0 | 100 | 0 | 0
3359 | 664.14 | 0 | 25.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50.3966 | 664.14 | 0 | 0.05921 | 7.4037 | 0 | 0 | 117.114 | 0 | off_peak | 664.14 |  |  | 0 | 0 | 100 | 0 | 0
3360 | 655.91 | 0 | 25.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50.3966 | 655.91 | 0 | 0.05921 | 7.4058 | 0 | 0 | 117.114 | 0 | off_peak | 655.91 |  |  | 0 | 0 | 100 | 0 | 0
3361 | 670.9 | 0 | 25.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50.3966 | 670.9 | 0 | 0.05921 | 7.219 | 0 | 0 | 117.114 | 0 | off_peak | 670.9 |  |  | 0 | 0 | 100 | 0 | 0
3362 | 641.03 | 0 | 25.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50.3966 | 641.03 | 0 | 0.05921 | 7.0103 | 0 | 0 | 117.114 | 0 | off_peak | 641.03 |  |  | 0 | 0 | 100 | 0 | 0
3363 | 689.16 | 0 | 25.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50.3966 | 689.16 | 0 | 0.05921 | 6.6193 | 0 | 0 | 117.114 | 0 | off_peak | 689.16 |  |  | 0 | 0 | 100 | 0 | 0
3364 | 678.85 | 0 | 25.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50.3966 | 678.85 | 0 | 0.05921 | 5.96 | 0 | 0 | 117.114 | 0 | off_peak | 678.85 |  |  | 0 | 0 | 100 | 0 | 0
3365 | 677.34 | 0 | 25.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50.3966 | 677.34 | 0 | 0.05921 | 5.3067 | 0 | 0 | 117.114 | 0 | off_peak | 677.34 |  |  | 0 | 0 | 100 | 0 | 0
3366 | 713.12 | 0 | 25.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50.3966 | 713.12 | 0 | 0.05921 | 4.7275 | 0 | 0 | 117.114 | 0 | off_peak | 713.12 |  |  | 0 | 0 | 100 | 0 | 0
3367 | 788.01 | 124.203 | 25.7 | 25.0877 | 25.0877 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50.3966 | 762.9223 | 0 | 0.05921 | 4.3646 | 0 | 0 | 117.114 | 25.0877 | off_peak | 762.9223 |  |  | 3.18 | 0 | 96.82 | 109.4974 | 0
3368 | 783.02 | 326.475 | 26.2 | 65.8256 | 65.8256 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50.3966 | 717.1944 | 0 | 0.05921 | 4.0453 | 0 | 0 | 117.114 | 65.8256 | off_peak | 717.1944 |  |  | 8.41 | 0 | 91.59 | 266.2824 | 0
3369 | 762.29 | 547.419 | 26.7 | 110.1739 | 110.1739 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50.3966 | 652.1161 | 0 | 0.05921 | 3.7421 | 0 | 0 | 117.114 | 110.1739 | off_peak | 652.1161 |  |  | 14.45 | 0 | 85.55 | 412.2792 | 0
3370 | 787.61 | 571.422 | 27.2 | 114.7965 | 114.7965 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50.3966 | 672.8135 | 0 | 0.05921 | 3.5877 | 0 | 0 | 117.114 | 114.7965 | off_peak | 672.8135 |  |  | 14.58 | 0 | 85.42 | 411.8551 | 0
3371 | 772.71 | 530.051 | 27.8 | 106.2534 | 106.2534 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50.3966 | 666.4566 | 0 | 0.05921 | 3.5149 | 0 | 0 | 117.114 | 106.2534 | off_peak | 666.4566 |  |  | 13.75 | 0 | 86.25 | 373.4681 | 0
3372 | 783.34 | 837.414 | 28.3 | 167.5618 | 167.5618 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50.3966 | 615.7782 | 0 | 0.05921 | 3.476 | 0 | 0 | 117.114 | 167.5618 | off_peak | 615.7782 |  |  | 21.39 | 0 | 78.61 | 582.4527 | 0
3373 | 757.18 | 939.12 | 28.6 | 187.7072 | 187.7072 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50.3966 | 569.4728 | 0 | 0.05921 | 3.662 | 0 | 0 | 117.114 | 187.7072 | off_peak | 569.4728 |  |  | 24.79 | 0 | 75.21 | 687.3779 | 0
3374 | 773.26 | 899.931 | 28.8 | 179.743 | 179.743 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 61.9947 | 605.9159 | 0 | 0.05921 | 4.1339 | 0 | 0 | 117.114 | 179.743 | off_peak | 593.517 | 0 | 100 | 23.24 | 0 | 76.76 | 743.0406 | 0
3375 | 785.2 | 756.523 | 28.8 | 151.1002 | 151.1002 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 61.9947 | 634.0998 | 0 | 0.05921 | 4.6883 | 0 | 0 | 117.114 | 151.1002 | off_peak | 634.0998 |  |  | 19.24 | 0 | 80.76 | 708.4021 | 0
3376 | 783.58 | 493.84 | 28.7 | 98.6706 | 98.6706 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 61.9947 | 684.9094 | 0 | 0.05921 | 5.3011 | 0 | 0 | 117.114 | 98.6706 | off_peak | 684.9094 |  |  | 12.59 | 0 | 87.41 | 523.0642 | 0
3377 | 747.64 | 456.463 | 28.3 | 91.3356 | 91.3356 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 61.9947 | 656.3044 | 0 | 0.05921 | 5.8957 | 0 | 0 | 117.114 | 91.3356 | off_peak | 656.3044 |  |  | 12.22 | 0 | 87.78 | 538.4905 | 0
3378 | 692.5 | 249.625 | 27.8 | 50.0395 | 50.0395 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 61.9947 | 642.4605 | 0 | 0.05921 | 6.4259 | 0 | 0 | 117.114 | 50.0395 | off_peak | 642.4605 |  |  | 7.23 | 0 | 92.77 | 321.5472 | 0
3379 | 613.63 | 59.7095 | 27.4 | 11.9867 | 11.9867 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 61.9947 | 601.6433 | 0 | 0.05921 | 6.7343 | 0 | 0 | 117.114 | 11.9867 | off_peak | 601.6433 |  |  | 1.95 | 0 | 98.05 | 80.7218 | 0
3380 | 590.53 | 0 | 26.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 61.9947 | 590.53 | 0 | 0.05921 | 6.8842 | 0 | 0 | 117.114 | 0 | off_peak | 590.53 |  |  | 0 | 0 | 100 | 0 | 0
3381 | 562.98 | 0 | 26.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 61.9947 | 562.98 | 0 | 0.05921 | 7.0257 | 0 | 0 | 117.114 | 0 | off_peak | 562.98 |  |  | 0 | 0 | 100 | 0 | 0
3382 | 550.14 | 0 | 26.1 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 73.5928 | 562.5389 | 0 | 0.05921 | 7.2506 | 0 | 0 | 117.114 | 0 | off_peak | 550.14 | 0 | 100 | 0 | 0 | 100 | 0 | 0
3383 | 588.76 | 0 | 26 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 73.5928 | 588.76 | 0 | 0.05921 | 7.2369 | 0 | 0 | 117.114 | 0 | off_peak | 588.76 |  |  | 0 | 0 | 100 | 0 | 0
3384 | 523.32 | 0 | 26 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 73.5928 | 523.32 | 0 | 0.05921 | 7.2617 | 0 | 0 | 117.114 | 0 | off_peak | 523.32 |  |  | 0 | 0 | 100 | 0 | 0
3385 | 565.13 | 0 | 25.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 73.5928 | 565.13 | 0 | 0.05921 | 7.2396 | 0 | 0 | 117.114 | 0 | off_peak | 565.13 |  |  | 0 | 0 | 100 | 0 | 0
3386 | 561.79 | 0 | 26 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 73.5928 | 561.79 | 0 | 0.05921 | 7.1485 | 0 | 0 | 117.114 | 0 | off_peak | 561.79 |  |  | 0 | 0 | 100 | 0 | 0
3387 | 536.84 | 0 | 26.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 73.5928 | 536.84 | 0 | 0.05921 | 6.7468 | 0 | 0 | 117.114 | 0 | off_peak | 536.84 |  |  | 0 | 0 | 100 | 0 | 0
3388 | 551.46 | 0 | 26.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 73.5928 | 551.46 | 0 | 0.05921 | 5.9773 | 0 | 0 | 117.114 | 0 | off_peak | 551.46 |  |  | 0 | 0 | 100 | 0 | 0
3389 | 557.28 | 0 | 26.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 73.5928 | 557.28 | 0 | 0.05921 | 5.2884 | 0 | 0 | 117.114 | 0 | off_peak | 557.28 |  |  | 0 | 0 | 100 | 0 | 0
3390 | 689.76 | 0 | 26.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 73.5928 | 689.76 | 0 | 0.05921 | 4.6806 | 0 | 0 | 117.114 | 0 | off_peak | 689.76 |  |  | 0 | 0 | 100 | 0 | 0
3391 | 833.03 | 134.443 | 26.6 | 27.0679 | 27.0679 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 73.5928 | 805.9621 | 0 | 0.05921 | 4.2597 | 0 | 0 | 117.114 | 27.0679 | off_peak | 805.9621 |  |  | 3.25 | 0 | 96.75 | 115.3009 | 0
3392 | 888.92 | 343.427 | 26.9 | 69.0683 | 69.0683 | 0 | 0 | 0.80079 | 0.80079 | 0 | 0 | 0 | 74.3419 | 820.6525 | 0 | 0.05921 | 3.9445 | 0 | 0 | 117.114 | 69.0683 | off_peak | 819.8517 | 0 | 100 | 7.77 | 0 | 92.23 | 272.443 | 0
3393 | 865.2 | 410.059 | 27.2 | 82.3793 | 82.3793 | 0 | 0 | 0.05172 | 0.05172 | 0 | 0 | 0 | 74.3903 | 782.8724 | 0 | 0.05921 | 3.7716 | 0 | 0 | 117.114 | 82.3793 | off_peak | 782.8207 | 0 | 100 | 9.52 | 0 | 90.48 | 310.6987 | 0
3394 | 871.98 | 611.709 | 27.5 | 122.7562 | 122.7562 | 0 | 0 | 0.0033404 | 0.0033404 | 0 | 0 | 0 | 74.3934 | 749.2271 | 0 | 0.05921 | 3.7059 | 0 | 0 | 117.114 | 122.7562 | off_peak | 749.2238 | 0 | 100 | 14.08 | 0 | 85.92 | 454.9165 | 0
3395 | 849.16 | 876.834 | 27.9 | 175.7052 | 175.7052 | 0 | 0 | 0.00021574 | 0.00021574 | 0 | 0 | 0 | 74.3936 | 673.455 | 0 | 0.05921 | 3.8708 | 0 | 0 | 117.114 | 175.7052 | off_peak | 673.4548 | 0 | 100 | 20.69 | 0 | 79.31 | 680.1269 | 0
3396 | 899.45 | 880.754 | 28.3 | 176.2339 | 176.2339 | 0 | 0 | 1.3934e-05 | 1.3934e-05 | 0 | 0 | 0 | 74.3936 | 723.2162 | 0 | 0.05921 | 4.2025 | 0 | 0 | 117.114 | 176.2339 | off_peak | 723.2161 | 0 | 100 | 19.59 | 0 | 80.41 | 740.618 | 0
3397 | 911.92 | 967.351 | 28.6 | 193.3499 | 193.3499 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 718.5701 | 0 | 0.088511 | 4.4399 | 0 | 0 | 117.114 | 193.3499 | on_peak | 718.5701 |  |  | 21.2 | 0 | 78.8 | 858.4555 | 0
3398 | 923.53 | 907.744 | 28.8 | 181.3035 | 181.3035 | 0 | 0 | 0 | 0 | 2.8707 | 2.8707 | 0 | 71.3248 | 739.3558 | 0 | 0.088511 | 4.7563 | 0 | 0 | 117.114 | 181.3035 | on_peak | 739.3558 |  |  | 19.63 | 0.31 | 80.06 | 862.3424 | 0
3399 | 929.8 | 823.275 | 28.9 | 164.3725 | 164.3725 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 71.3248 | 765.4275 | 0 | 0.088511 | 5.1111 | 0 | 0 | 117.114 | 164.3725 | on_peak | 765.4275 |  |  | 17.68 | 0 | 82.32 | 840.1271 | 0
3400 | 918.92 | 661.838 | 28.9 | 132.1405 | 132.1405 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 71.3248 | 786.7795 | 0 | 0.088511 | 5.5495 | 0 | 0 | 117.114 | 132.1405 | on_peak | 786.7795 |  |  | 14.38 | 0 | 85.62 | 733.3165 | 0
3401 | 918.74 | 465.899 | 28.7 | 93.0879 | 93.0879 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 71.3248 | 825.6521 | 0 | 0.088511 | 5.9481 | 0 | 0 | 117.114 | 93.0879 | on_peak | 825.6521 |  |  | 10.13 | 0 | 89.87 | 553.6997 | 0
3402 | 892.26 | 251.453 | 28.3 | 50.3143 | 50.3143 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 71.3248 | 841.9457 | 0 | 0.088511 | 6.6276 | 0 | 0 | 117.114 | 50.3143 | on_peak | 841.9457 |  |  | 5.64 | 0 | 94.36 | 333.4648 | 0
3403 | 888.08 | 61.7687 | 27.9 | 12.3776 | 12.3776 | 0 | 0 | 0 | 0 | 32.9144 | 32.9144 | 0 | 36.1377 | 842.788 | 0 | 0.088511 | 6.8956 | 0 | 0 | 117.114 | 12.3776 | on_peak | 842.788 |  |  | 1.39 | 3.71 | 94.9 | 85.3507 | 0
3404 | 841.99 | 0 | 27.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 36.1377 | 841.99 | 0 | 0.088511 | 7.1702 | 0 | 0 | 117.114 | 0 | on_peak | 841.99 |  |  | 0 | 0 | 100 | 0 | 0
3405 | 862.8 | 0 | 26.9 | 0 | 0 | 0 | 0 | 0 | 0 | 20.012 | 20.012 | 0 | 14.744 | 842.788 | 0 | 0.088511 | 7.58 | 0 | 0 | 117.114 | 0 | on_peak | 842.788 |  |  | 0 | 2.32 | 97.68 | 0 | 0
3406 | 813.2 | 0 | 26.7 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 26.3422 | 825.5989 | 0 | 0.05921 | 7.8608 | 0 | 0 | 117.114 | 0 | off_peak | 813.2 | 0 | 100 | 0 | 0 | 100 | 0 | 0
3407 | 869.11 | 0 | 26.6 | 0 | 0 | 0 | 0 | 0 | 0 | 4.586 | 4.586 | 0 | 21.4395 | 864.524 | 0 | 0.05921 | 7.9315 | 0 | 0 | 117.114 | 0 | off_peak | 864.524 |  |  | 0 | 0.53 | 99.47 | 0 | 0
3408 | 877.62 | 0 | 26.6 | 0 | 0 | 0 | 0 | 0 | 0 | 13.096 | 13.096 | 0 | 7.4394 | 864.524 | 0 | 0.05921 | 7.8755 | 0 | 0 | 117.114 | 0 | off_peak | 864.524 |  |  | 0 | 1.49 | 98.51 | 0 | 0
3409 | 788.49 | 0 | 26.6 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 19.0375 | 800.8889 | 0 | 0.05921 | 7.6794 | 0 | 0 | 117.114 | 0 | off_peak | 788.49 | 0 | 100 | 0 | 0 | 100 | 0 | 0
3410 | 716.84 | 0 | 26.6 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 30.6357 | 729.2389 | 0 | 0.05921 | 7.4221 | 0 | 0 | 117.114 | 0 | off_peak | 716.84 | 0 | 100 | 0 | 0 | 100 | 0 | 0
3411 | 648.1 | 0 | 26.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30.6357 | 648.1 | 0 | 0.05921 | 6.9525 | 0 | 0 | 117.114 | 0 | off_peak | 648.1 |  |  | 0 | 0 | 100 | 0 | 0
3412 | 638.07 | 0 | 26.6 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 42.2338 | 650.4689 | 0 | 0.05921 | 6.125 | 0 | 0 | 117.114 | 0 | off_peak | 638.07 | 0 | 100 | 0 | 0 | 100 | 0 | 0
3413 | 624.7 | 0 | 26.6 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 53.832 | 637.0989 | 0 | 0.05921 | 5.1729 | 0 | 0 | 117.114 | 0 | off_peak | 624.7 | 0 | 100 | 0 | 0 | 100 | 0 | 0
3414 | 708.63 | 0 | 26.6 | 0 | 0 | 0 | 0 | 8.7263 | 8.7263 | 0 | 0 | 0 | 61.9947 | 717.3563 | 0 | 0.05921 | 4.5369 | 0 | 0 | 117.114 | 0 | off_peak | 708.63 | 0 | 100 | 0 | 0 | 100 | 0 | 0
3415 | 753.25 | 137.846 | 26.8 | 27.7329 | 27.7329 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 73.5928 | 737.916 | 0 | 0.05921 | 4.136 | 0 | 0 | 117.114 | 27.7329 | off_peak | 725.5171 | 0 | 100 | 3.68 | 0 | 96.32 | 114.7043 | 0
3416 | 872.57 | 346.532 | 27.2 | 69.617 | 68.8162 | 0 | 0.80079 | 0.80079 | 0 | 0 | 0 | 0 | 74.3419 | 803.7538 | 0 | 0.05921 | 3.8018 | 0 | 0 | 117.863 | 68.8162 | off_peak | 803.7538 | 100 | 0 | 7.89 | 0 | 92.11 | 261.6262 | 0
3417 | 819.51 | 557.064 | 27.5 | 111.7902 | 111.7902 | 0 | 0 | 0.05172 | 0.05172 | 0 | 0 | 0 | 74.3903 | 707.7715 | 0 | 0.05921 | 3.5966 | 0 | 0 | 117.863 | 111.7902 | off_peak | 707.7198 | 0 | 100 | 13.64 | 0 | 86.36 | 402.0682 | 0
3418 | 863.6 | 613.916 | 28.1 | 122.9306 | 122.9306 | 0 | 0 | 0.0033404 | 0.0033404 | 0 | 0 | 0 | 74.3934 | 740.6727 | 0 | 0.05921 | 3.5182 | 0 | 0 | 117.863 | 122.9306 | off_peak | 740.6694 | 0 | 100 | 14.23 | 0 | 85.77 | 432.4989 | 0
3419 | 844.43 | 747.188 | 28.6 | 149.3446 | 149.3446 | 0 | 0 | 0.00021574 | 0.00021574 | 0 | 0 | 0 | 74.3936 | 695.0856 | 0 | 0.05921 | 3.6814 | 0 | 0 | 117.863 | 149.3446 | off_peak | 695.0854 | 0 | 100 | 17.69 | 0 | 82.31 | 549.8027 | 0
3420 | 921.2 | 950.584 | 29 | 189.7214 | 189.7214 | 0 | 0 | 1.3934e-05 | 1.3934e-05 | 0 | 0 | 0 | 74.3936 | 731.4787 | 0 | 0.05921 | 4.0731 | 0 | 0 | 117.863 | 189.7214 | off_peak | 731.4786 | 0 | 100 | 20.6 | 0 | 79.4 | 772.7577 | 0
3421 | 863.1 | 970.458 | 29.3 | 193.4757 | 193.4757 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 669.6243 | 0 | 0.088511 | 4.3539 | 0 | 0 | 117.863 | 193.4757 | on_peak | 669.6243 |  |  | 22.42 | 0 | 77.58 | 842.3662 | 0
3422 | 911.5 | 923.131 | 29.5 | 183.9057 | 183.9057 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 727.5943 | 0 | 0.088511 | 4.616 | 0 | 0 | 117.863 | 183.9057 | on_peak | 727.5943 |  |  | 20.18 | 0 | 79.82 | 848.9157 | 0
3423 | 953.41 | 819.127 | 29.7 | 163.0666 | 163.0666 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 790.3434 | 0 | 0.088511 | 4.9309 | 0 | 0 | 117.863 | 163.0666 | on_peak | 790.3434 |  |  | 17.1 | 0 | 82.9 | 804.0598 | 0
3424 | 932.26 | 662.762 | 29.8 | 131.8902 | 131.8902 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 800.3698 | 0 | 0.088511 | 5.3028 | 0 | 0 | 117.863 | 131.8902 | on_peak | 800.3698 |  |  | 14.15 | 0 | 85.85 | 699.3868 | 0
3425 | 921.82 | 468.168 | 29.6 | 93.2341 | 93.2341 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 828.5859 | 0 | 0.088511 | 5.7021 | 0 | 0 | 117.863 | 93.2341 | on_peak | 828.5859 |  |  | 10.11 | 0 | 89.89 | 531.626 | 0
3426 | 890.8 | 257.755 | 29 | 51.4438 | 51.4438 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 839.3562 | 0 | 0.088511 | 6.0557 | 0 | 0 | 117.863 | 51.4438 | on_peak | 839.3562 |  |  | 5.78 | 0 | 94.22 | 311.5294 | 0
3427 | 850.67 | 64.905 | 28.6 | 12.9729 | 12.9729 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 837.6971 | 0 | 0.088511 | 6.2829 | 0 | 0 | 117.863 | 12.9729 | on_peak | 837.6971 |  |  | 1.53 | 0 | 98.47 | 81.508 | 0
3428 | 890.81 | 0 | 27.6 | 0 | 0 | 0 | 0 | 0 | 0 | 48.022 | 48.022 | 0 | 23.056 | 842.788 | 0 | 0.088511 | 6.4869 | 0 | 0 | 117.863 | 0 | on_peak | 842.788 |  |  | 0 | 5.39 | 94.61 | 0 | 0
3429 | 854.51 | 0 | 27.1 | 0 | 0 | 0 | 0 | 0 | 0 | 11.722 | 11.722 | 0 | 10.5246 | 842.788 | 0 | 0.088511 | 6.5726 | 0 | 0 | 117.863 | 0 | on_peak | 842.788 |  |  | 0 | 1.37 | 98.63 | 0 | 0
3430 | 867.41 | 0 | 26.8 | 0 | 0 | 0 | 0 | 0 | 0 | 2.886 | 2.886 | 0 | 7.4394 | 864.524 | 0 | 0.05921 | 6.8537 | 0 | 0 | 117.863 | 0 | off_peak | 864.524 |  |  | 0 | 0.33 | 99.67 | 0 | 0
3431 | 861.58 | 0 | 26.5 | 0 | 0 | 0 | 0 | 2.944 | 2.944 | 0 | 0 | 0 | 10.1933 | 864.524 | 0 | 0.05921 | 7.1511 | 0 | 0 | 117.863 | 0 | off_peak | 861.58 | 0 | 100 | 0 | 0 | 100 | 0 | 0
3432 | 824.34 | 0 | 26.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1933 | 824.34 | 0 | 0.05921 | 7.0298 | 0 | 0 | 117.863 | 0 | off_peak | 824.34 |  |  | 0 | 0 | 100 | 0 | 0
3433 | 810.41 | 0 | 26.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1933 | 810.41 | 0 | 0.05921 | 6.7951 | 0 | 0 | 117.863 | 0 | off_peak | 810.41 |  |  | 0 | 0 | 100 | 0 | 0
3434 | 756.85 | 0 | 26.2 | 0 | 0 | 0 | 0 | 5.7823 | 5.7823 | 0 | 0 | 0 | 15.6021 | 762.6323 | 0 | 0.05921 | 6.6942 | 0 | 0 | 117.863 | 0 | off_peak | 756.85 | 0 | 100 | 0 | 0 | 100 | 0 | 0
3435 | 701.69 | 0 | 26.1 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 27.2003 | 714.0889 | 0 | 0.05921 | 6.2757 | 0 | 0 | 117.863 | 0 | off_peak | 701.69 | 0 | 100 | 0 | 0 | 100 | 0 | 0
3436 | 660.69 | 0 | 26.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27.2003 | 660.69 | 0 | 0.05921 | 5.5422 | 0 | 0 | 117.863 | 0 | off_peak | 660.69 |  |  | 0 | 0 | 100 | 0 | 0
3437 | 685.03 | 0 | 26.2 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 38.7984 | 697.4289 | 0 | 0.05921 | 4.839 | 0 | 0 | 117.863 | 0 | off_peak | 685.03 | 0 | 100 | 0 | 0 | 100 | 0 | 0
3438 | 739.38 | 0 | 26.4 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 50.3966 | 751.7789 | 0 | 0.05921 | 4.1093 | 0 | 0 | 117.863 | 0 | off_peak | 739.38 | 0 | 100 | 0 | 0 | 100 | 0 | 0
3439 | 794.19 | 129.657 | 26.8 | 26.0854 | 26.0854 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 61.9947 | 780.5035 | 0 | 0.05921 | 3.7473 | 0 | 0 | 117.863 | 26.0854 | off_peak | 768.1046 | 0 | 100 | 3.28 | 0 | 96.72 | 97.7485 | 0
3440 | 803.83 | 333.711 | 27.1 | 67.0656 | 67.0656 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 73.5928 | 749.1633 | 0 | 0.05921 | 3.4203 | 0 | 0 | 117.863 | 67.0656 | off_peak | 736.7644 | 0 | 100 | 8.34 | 0 | 91.66 | 229.3835 | 0
3441 | 912.91 | 541.942 | 27.5 | 108.7556 | 108.7556 | 0 | 0 | 0.80079 | 0.80079 | 0 | 0 | 0 | 74.3419 | 804.9552 | 0 | 0.05921 | 3.2585 | 0 | 0 | 117.863 | 108.7556 | off_peak | 804.1544 | 0 | 100 | 11.91 | 0 | 88.09 | 354.3833 | 0
3442 | 871.4 | 726.007 | 27.9 | 145.4816 | 145.4816 | 0 | 0 | 0.05172 | 0.05172 | 0 | 0 | 0 | 74.3903 | 725.9702 | 0 | 0.05921 | 3.2357 | 0 | 0 | 117.863 | 145.4816 | off_peak | 725.9184 | 0 | 100 | 16.7 | 0 | 83.3 | 470.7311 | 0
3443 | 858.65 | 865.2 | 28.3 | 173.1216 | 173.1216 | 0 | 0 | 0.0033404 | 0.0033404 | 0 | 0 | 0 | 74.3934 | 685.5318 | 0 | 0.05921 | 3.0643 | 0 | 0 | 117.863 | 173.1216 | off_peak | 685.5284 | 0 | 100 | 20.16 | 0 | 79.84 | 530.5018 | 0
3444 | 936.07 | 948.201 | 28.6 | 189.5222 | 189.5222 | 0 | 0 | 0.00021574 | 0.00021574 | 0 | 0 | 0 | 74.3936 | 746.548 | 0 | 0.05921 | 3.8115 | 0 | 0 | 117.863 | 189.5222 | off_peak | 746.5478 | 0 | 100 | 20.25 | 0 | 79.75 | 722.3563 | 0
3445 | 860.51 | 968.815 | 28.8 | 193.5012 | 193.5012 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 667.0088 | 0 | 0.088511 | 4.1311 | 0 | 0 | 117.863 | 193.5012 | on_peak | 667.0088 |  |  | 22.49 | 0 | 77.51 | 799.3642 | 0
3446 | 902.63 | 926.602 | 28.8 | 185.07 | 185.07 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 717.56 | 0 | 0.088511 | 4.4398 | 0 | 0 | 117.863 | 185.07 | on_peak | 717.56 |  |  | 20.5 | 0 | 79.5 | 821.675 | 0
3447 | 942.38 | 820.202 | 28.6 | 163.9384 | 163.9384 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 778.4416 | 0 | 0.088511 | 4.742 | 0 | 0 | 117.863 | 163.9384 | on_peak | 778.4416 |  |  | 17.4 | 0 | 82.6 | 777.4007 | 0
3448 | 916.42 | 662.612 | 28.3 | 132.5849 | 132.5849 | 0 | 0 | 0 | 0 | 21.888 | 21.888 | 0 | 50.9944 | 761.9471 | 0 | 0.088511 | 5.1431 | 0 | 0 | 117.863 | 132.5849 | on_peak | 761.9471 |  |  | 14.47 | 2.39 | 83.14 | 681.898 | 0
3449 | 890.19 | 467.332 | 28 | 93.6127 | 93.6127 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50.9944 | 796.5773 | 0 | 0.088511 | 5.6107 | 0 | 0 | 117.863 | 93.6127 | on_peak | 796.5773 |  |  | 10.52 | 0 | 89.48 | 525.2319 | 0
3450 | 862.63 | 255.682 | 27.5 | 51.3096 | 51.3096 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50.9944 | 811.3204 | 0 | 0.088511 | 5.9015 | 0 | 0 | 117.863 | 51.3096 | on_peak | 811.3204 |  |  | 5.95 | 0 | 94.05 | 302.8018 | 0
3451 | 852.9 | 64.1992 | 27.3 | 12.8927 | 12.8927 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50.9944 | 840.0073 | 0 | 0.088511 | 6.1622 | 0 | 0 | 117.863 | 12.8927 | on_peak | 840.0073 |  |  | 1.51 | 0 | 98.49 | 79.448 | 0
3452 | 883.53 | 0 | 26.6 | 0 | 0 | 0 | 0 | 0 | 0 | 40.742 | 40.742 | 0 | 7.4394 | 842.788 | 0 | 0.088511 | 6.3552 | 40.742 | 0 | 74.308 | 40.742 | on_peak | 842.788 |  |  | 0 | 4.61 | 95.39 | 258.9251 | 0
3453 | 832.13 | 0 | 26.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 832.13 | 0 | 0.088511 | 6.2093 | 0 | 0 | 74.308 | 0 | on_peak | 832.13 |  |  | 0 | 0 | 100 | 0 | 0
3454 | 831.92 | 0 | 26.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 831.92 | 0 | 0.05921 | 6.1437 | 0 | 0 | 74.308 | 0 | off_peak | 831.92 |  |  | 0 | 0 | 100 | 0 | 0
3455 | 826.21 | 0 | 26.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 826.21 | 0 | 0.05921 | 6.131 | 0 | 0 | 74.308 | 0 | off_peak | 826.21 |  |  | 0 | 0 | 100 | 0 | 0
3456 | 834.01 | 0 | 26.1 | 0 | 0 | 0 | 0 | 8.7263 | 8.7263 | 0 | 0 | 0 | 15.6021 | 842.7363 | 0 | 0.05921 | 5.9685 | 0 | 0 | 74.308 | 0 | off_peak | 834.01 | 0 | 100 | 0 | 0 | 100 | 0 | 0
3457 | 794.47 | 0 | 26 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15.6021 | 794.47 | 0 | 0.05921 | 5.7383 | 0 | 0 | 74.308 | 0 | off_peak | 794.47 |  |  | 0 | 0 | 100 | 0 | 0
3458 | 770.63 | 0 | 26 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15.6021 | 770.63 | 0 | 0.05921 | 5.6328 | 0 | 0 | 74.308 | 0 | off_peak | 770.63 |  |  | 0 | 0 | 100 | 0 | 0
3459 | 685.52 | 0 | 25.9 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 27.2003 | 697.9189 | 0 | 0.05921 | 5.3525 | 0 | 0 | 74.308 | 0 | off_peak | 685.52 | 0 | 100 | 0 | 0 | 100 | 0 | 0
3460 | 688.13 | 0 | 25.9 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 38.7984 | 700.5289 | 0 | 0.05921 | 4.7751 | 0 | 0 | 74.308 | 0 | off_peak | 688.13 | 0 | 100 | 0 | 0 | 100 | 0 | 0
3461 | 660.47 | 0 | 26 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 50.3966 | 672.8689 | 0 | 0.05921 | 4.1437 | 0 | 0 | 74.308 | 0 | off_peak | 660.47 | 0 | 100 | 0 | 0 | 100 | 0 | 0
3462 | 765.51 | 0 | 26.2 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 61.9947 | 777.9089 | 0 | 0.05921 | 3.5905 | 0 | 0 | 74.308 | 0 | off_peak | 765.51 | 0 | 100 | 0 | 0 | 100 | 0 | 0
3463 | 805.67 | 135.309 | 26.7 | 27.2324 | 27.2324 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 73.5928 | 790.8366 | 0 | 0.05921 | 3.428 | 0 | 0 | 74.308 | 27.2324 | off_peak | 778.4376 | 0 | 100 | 3.38 | 0 | 96.62 | 93.3527 | 0
3464 | 837.21 | 341.141 | 27 | 68.5837 | 68.5837 | 0 | 0 | 0.80079 | 0.80079 | 0 | 0 | 0 | 74.3419 | 769.4271 | 0 | 0.05921 | 3.1421 | 0 | 0 | 74.308 | 68.5837 | off_peak | 768.6263 | 0 | 100 | 8.19 | 0 | 91.81 | 215.4997 | 0
3465 | 865.79 | 549.03 | 27.1 | 110.3381 | 110.3381 | 0 | 0 | 0.05172 | 0.05172 | 0 | 0 | 0 | 74.3903 | 755.5037 | 0 | 0.05921 | 2.9964 | 0 | 0 | 74.308 | 110.3381 | off_peak | 755.4519 | 0 | 100 | 12.74 | 0 | 87.26 | 330.6122 | 0
3466 | 872.47 | 729.667 | 26.9 | 146.7469 | 146.7469 | 0 | 0 | 0.0033404 | 0.0033404 | 0 | 0 | 0 | 74.3934 | 725.7264 | 0 | 0.05921 | 2.9951 | 0 | 0 | 74.308 | 146.7469 | off_peak | 725.7231 | 0 | 100 | 16.82 | 0 | 83.18 | 439.5163 | 0
3467 | 838.44 | 865.815 | 26.6 | 174.3177 | 174.3177 | 0 | 0 | 0.00021574 | 0.00021574 | 0 | 0 | 0 | 74.3936 | 664.1226 | 0 | 0.05921 | 2.9154 | 0 | 0 | 74.308 | 174.3177 | off_peak | 664.1223 | 0 | 100 | 20.79 | 0 | 79.21 | 508.199 | 0
3468 | 844.88 | 948.903 | 26.2 | 191.3228 | 191.3228 | 0 | 0 | 1.3934e-05 | 1.3934e-05 | 0 | 0 | 0 | 74.3936 | 653.5573 | 0 | 0.05921 | 3.6139 | 0 | 0 | 74.308 | 191.3228 | off_peak | 653.5572 | 0 | 100 | 22.64 | 0 | 77.36 | 691.4212 | 0
3469 | 844.13 | 967.125 | 25.9 | 195.2083 | 195.2083 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 648.9217 | 0 | 0.088511 | 3.9087 | 0 | 0 | 74.308 | 195.2083 | on_peak | 648.9217 |  |  | 23.13 | 0 | 76.87 | 763.002 | 0
3470 | 902.75 | 920.889 | 25.5 | 186.1444 | 186.1444 | 0 | 0 | 0 | 0 | 62.63 | 62.63 | 0 | 7.4394 | 653.9756 | 0 | 0.088511 | 4.0395 | 0 | 0 | 74.308 | 186.1444 | on_peak | 653.9756 |  |  | 20.62 | 6.94 | 72.44 | 751.9245 | 0
3471 | 916.99 | 818.667 | 25.3 | 165.601 | 165.601 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 751.389 | 0 | 0.088511 | 4.2401 | 0 | 0 | 74.308 | 165.601 | on_peak | 751.389 |  |  | 18.06 | 0 | 81.94 | 702.1651 | 0
3472 | 877.14 | 664.282 | 25.2 | 134.4203 | 134.4203 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 742.7197 | 0 | 0.088511 | 4.6025 | 0 | 0 | 74.308 | 134.4203 | on_peak | 742.7197 |  |  | 15.32 | 0 | 84.68 | 618.6741 | 0
3473 | 859.45 | 472.499 | 25.2 | 95.6122 | 95.6122 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 763.8378 | 0 | 0.088511 | 4.9711 | 0 | 0 | 74.308 | 95.6122 | on_peak | 763.8378 |  |  | 11.12 | 0 | 88.88 | 475.2995 | 0
3474 | 817.32 | 254.529 | 25.3 | 51.4865 | 51.4865 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 765.8335 | 0 | 0.088511 | 5.3698 | 0 | 0 | 74.308 | 51.4865 | on_peak | 765.8335 |  |  | 6.3 | 0 | 93.7 | 276.4743 | 0
3475 | 825.46 | 61.672 | 25.3 | 12.4751 | 12.4751 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 812.9849 | 0 | 0.088511 | 5.4363 | 0 | 0 | 74.308 | 12.4751 | on_peak | 812.9849 |  |  | 1.51 | 0 | 98.49 | 67.8179 | 0
3476 | 834.84 | 0 | 25.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 834.84 | 0 | 0.088511 | 5.4518 | 0 | 0 | 74.308 | 0 | on_peak | 834.84 |  |  | 0 | 0 | 100 | 0 | 0
3477 | 819.6 | 0 | 25.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 819.6 | 0 | 0.088511 | 5.618 | 0 | 0 | 74.308 | 0 | on_peak | 819.6 |  |  | 0 | 0 | 100 | 0 | 0
3478 | 784.14 | 0 | 25.8 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 19.0375 | 796.5389 | 0 | 0.05921 | 5.776 | 0 | 0 | 74.308 | 0 | off_peak | 784.14 | 0 | 100 | 0 | 0 | 100 | 0 | 0
3479 | 842.7 | 0 | 25.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19.0375 | 842.7 | 0 | 0.05921 | 5.9829 | 0 | 0 | 74.308 | 0 | off_peak | 842.7 |  |  | 0 | 0 | 100 | 0 | 0
3480 | 818.29 | 0 | 25.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19.0375 | 818.29 | 0 | 0.05921 | 6.0055 | 0 | 0 | 74.308 | 0 | off_peak | 818.29 |  |  | 0 | 0 | 100 | 0 | 0
3481 | 796.12 | 0 | 25.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19.0375 | 796.12 | 0 | 0.05921 | 6.0313 | 0 | 0 | 74.308 | 0 | off_peak | 796.12 |  |  | 0 | 0 | 100 | 0 | 0
3482 | 724.01 | 0 | 25.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19.0375 | 724.01 | 0 | 0.05921 | 5.9783 | 0 | 0 | 74.308 | 0 | off_peak | 724.01 |  |  | 0 | 0 | 100 | 0 | 0
3483 | 682.21 | 0 | 25.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19.0375 | 682.21 | 0 | 0.05921 | 5.6661 | 0 | 0 | 74.308 | 0 | off_peak | 682.21 |  |  | 0 | 0 | 100 | 0 | 0
3484 | 654.58 | 0 | 25.8 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 30.6357 | 666.9789 | 0 | 0.05921 | 5.1715 | 0 | 0 | 74.308 | 0 | off_peak | 654.58 | 0 | 100 | 0 | 0 | 100 | 0 | 0
3485 | 626.64 | 0 | 25.9 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 42.2338 | 639.0389 | 0 | 0.05921 | 4.4092 | 0 | 0 | 74.308 | 0 | off_peak | 626.64 | 0 | 100 | 0 | 0 | 100 | 0 | 0
3486 | 703.94 | 0 | 26.1 | 0 | 0 | 0 | 0 | 8.7263 | 8.7263 | 0 | 0 | 0 | 50.3966 | 712.6663 | 0 | 0.05921 | 3.8671 | 0 | 0 | 74.308 | 0 | off_peak | 703.94 | 0 | 100 | 0 | 0 | 100 | 0 | 0
3487 | 744.83 | 133.847 | 26.5 | 26.9577 | 26.9577 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 61.9947 | 730.2713 | 0 | 0.05921 | 3.4381 | 0 | 0 | 74.308 | 26.9577 | off_peak | 717.8723 | 0 | 100 | 3.62 | 0 | 96.38 | 92.684 | 0
3488 | 854.82 | 340.997 | 26.8 | 68.6044 | 68.6044 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 73.5928 | 798.6145 | 0 | 0.05921 | 3.1585 | 0 | 0 | 74.308 | 68.6044 | off_peak | 786.2156 | 0 | 100 | 8.03 | 0 | 91.97 | 216.6895 | 0
3489 | 898.57 | 548.639 | 27.1 | 110.2595 | 110.2595 | 0 | 0 | 0.80079 | 0.80079 | 0 | 0 | 0 | 74.3419 | 789.1113 | 0 | 0.05921 | 3.0061 | 0 | 0 | 74.308 | 110.2595 | off_peak | 788.3105 | 0 | 100 | 12.27 | 0 | 87.73 | 331.4483 | 0
3490 | 839.49 | 730.59 | 27.3 | 146.7195 | 146.7195 | 0 | 0 | 0.05172 | 0.05172 | 0 | 0 | 0 | 74.3903 | 692.8222 | 0 | 0.05921 | 2.9923 | 0 | 0 | 74.308 | 146.7195 | off_peak | 692.7705 | 0 | 100 | 17.48 | 0 | 82.52 | 439.0246 | 0
3491 | 838.55 | 868.761 | 27.4 | 174.4041 | 174.4041 | 0 | 0 | 0.0033404 | 0.0033404 | 0 | 0 | 0 | 74.3934 | 664.1492 | 0 | 0.05921 | 3.2064 | 0 | 0 | 74.308 | 174.4041 | off_peak | 664.1459 | 0 | 100 | 20.8 | 0 | 79.2 | 559.2016 | 0
3492 | 890.83 | 953.661 | 27.5 | 191.3783 | 191.3783 | 0 | 0 | 0.00021574 | 0.00021574 | 0 | 0 | 0 | 74.3936 | 699.4519 | 0 | 0.05921 | 3.6104 | 0 | 0 | 74.308 | 191.3783 | off_peak | 699.4517 | 0 | 100 | 21.48 | 0 | 78.52 | 690.9594 | 0
3493 | 858.52 | 974.875 | 27.6 | 195.5644 | 195.5644 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 662.9556 | 0 | 0.088511 | 3.8295 | 0 | 0 | 74.308 | 195.5644 | on_peak | 662.9556 |  |  | 22.78 | 0 | 77.22 | 748.9129 | 0
3494 | 848.29 | 932.239 | 27.5 | 187.0794 | 187.0794 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 661.2106 | 0 | 0.088511 | 4.034 | 0 | 0 | 74.308 | 187.0794 | on_peak | 661.2106 |  |  | 22.05 | 0 | 77.95 | 754.6703 | 0
3495 | 864.62 | 828.76 | 27.4 | 166.3739 | 166.3739 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 698.2461 | 0 | 0.088511 | 4.2522 | 0 | 0 | 74.308 | 166.3739 | on_peak | 698.2461 |  |  | 19.24 | 0 | 80.76 | 707.4519 | 0
3496 | 848.56 | 673.458 | 27.2 | 135.2952 | 135.2952 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 713.2648 | 0 | 0.088511 | 4.5757 | 0 | 0 | 74.308 | 135.2952 | on_peak | 713.2648 |  |  | 15.94 | 0 | 84.06 | 619.0767 | 0
3497 | 868.59 | 479.085 | 26.9 | 96.3511 | 96.3511 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 772.2389 | 0 | 0.088511 | 4.9409 | 0 | 0 | 74.308 | 96.3511 | on_peak | 772.2389 |  |  | 11.09 | 0 | 88.91 | 476.0638 | 0
3498 | 771.2 | 265.766 | 26.5 | 53.527 | 53.527 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 717.673 | 0 | 0.088511 | 5.3112 | 0 | 0 | 74.308 | 53.527 | on_peak | 717.673 |  |  | 6.94 | 0 | 93.06 | 284.2909 | 0
3499 | 780.15 | 71.3606 | 26.3 | 14.3829 | 14.3829 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 765.7671 | 0 | 0.088511 | 5.4478 | 0 | 0 | 74.308 | 14.3829 | on_peak | 765.7671 |  |  | 1.84 | 0 | 98.16 | 78.3553 | 0
3500 | 769.74 | 0 | 26 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 769.74 | 0 | 0.088511 | 5.5862 | 0 | 0 | 74.308 | 0 | on_peak | 769.74 |  |  | 0 | 0 | 100 | 0 | 0
3501 | 793.18 | 0 | 25.9 | 0 | 0 | 0 | 0 | 0 | 0 | 62.63 | 62.63 | 0 | 7.4394 | 730.55 | 0 | 0.088511 | 5.8023 | 0 | 0 | 74.308 | 0 | on_peak | 730.55 |  |  | 0 | 7.9 | 92.1 | 0 | 0
3502 | 756.1 | 0 | 25.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 756.1 | 0 | 0.05921 | 5.8173 | 0 | 0 | 74.308 | 0 | off_peak | 756.1 |  |  | 0 | 0 | 100 | 0 | 0
3503 | 800.02 | 0 | 25.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 800.02 | 0 | 0.05921 | 5.7525 | 0 | 0 | 74.308 | 0 | off_peak | 800.02 |  |  | 0 | 0 | 100 | 0 | 0
3504 | 726.45 | 0 | 25.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 726.45 | 0 | 0.05921 | 5.7299 | 0 | 0 | 74.308 | 0 | off_peak | 726.45 |  |  | 0 | 0 | 100 | 0 | 0
3505 | 754.45 | 0 | 25.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 754.45 | 0 | 0.05921 | 5.61 | 0 | 0 | 74.308 | 0 | off_peak | 754.45 |  |  | 0 | 0 | 100 | 0 | 0
3506 | 660.09 | 0 | 25.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 660.09 | 0 | 0.05921 | 5.5184 | 0 | 0 | 74.308 | 0 | off_peak | 660.09 |  |  | 0 | 0 | 100 | 0 | 0
3507 | 621.26 | 0 | 25.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 621.26 | 0 | 0.05921 | 5.2776 | 0 | 0 | 74.308 | 0 | off_peak | 621.26 |  |  | 0 | 0 | 100 | 0 | 0
3508 | 580.7 | 0 | 25.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 580.7 | 0 | 0.05921 | 4.8366 | 0 | 0 | 74.308 | 0 | off_peak | 580.7 |  |  | 0 | 0 | 100 | 0 | 0
3509 | 610.11 | 0 | 25.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 610.11 | 0 | 0.05921 | 4.2847 | 0 | 0 | 74.308 | 0 | off_peak | 610.11 |  |  | 0 | 0 | 100 | 0 | 0
3510 | 705.83 | 0 | 25.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 705.83 | 0 | 0.05921 | 3.7197 | 0 | 0 | 74.308 | 0 | off_peak | 705.83 |  |  | 0 | 0 | 100 | 0 | 0
3511 | 703.92 | 101.959 | 26.2 | 20.5575 | 20.5575 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 683.3625 | 0 | 0.05921 | 3.2975 | 0 | 0 | 74.308 | 20.5575 | off_peak | 683.3625 |  |  | 2.92 | 0 | 97.08 | 67.7875 | 0
3512 | 764.14 | 338.671 | 26.5 | 68.2105 | 68.2105 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 695.9295 | 0 | 0.05921 | 3.0263 | 0 | 0 | 74.308 | 68.2105 | off_peak | 695.9295 |  |  | 8.93 | 0 | 91.07 | 206.4286 | 0
3513 | 776.81 | 542.954 | 26.6 | 109.3149 | 109.3149 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 667.4951 | 0 | 0.05921 | 2.8734 | 0 | 0 | 74.308 | 109.3149 | off_peak | 667.4951 |  |  | 14.07 | 0 | 85.93 | 314.1036 | 0
3514 | 754.13 | 717.333 | 26.9 | 144.2664 | 144.2664 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 609.8636 | 0 | 0.05921 | 2.7852 | 0 | 0 | 74.308 | 144.2664 | off_peak | 609.8636 |  |  | 19.13 | 0 | 80.87 | 401.8157 | 0
3515 | 741.37 | 849.955 | 27.3 | 170.6908 | 170.6908 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 570.6792 | 0 | 0.05921 | 2.7395 | 0 | 0 | 74.308 | 170.6908 | off_peak | 570.6792 |  |  | 23.02 | 0 | 76.98 | 467.6007 | 0
3516 | 818.03 | 850.717 | 27.8 | 170.5337 | 170.5337 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 647.4963 | 0 | 0.05921 | 2.8225 | 0 | 0 | 74.308 | 170.5337 | off_peak | 647.4963 |  |  | 20.85 | 0 | 79.15 | 481.337 | 0
3517 | 737.56 | 849.707 | 28.3 | 170.0215 | 170.0215 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 567.5385 | 0 | 0.05921 | 2.9493 | 0 | 0 | 74.308 | 170.0215 | off_peak | 567.5385 |  |  | 23.05 | 0 | 76.95 | 501.4483 | 0
3518 | 764.47 | 744.309 | 28.6 | 148.7692 | 148.7692 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 615.7008 | 0 | 0.05921 | 3.2 | 0 | 0 | 74.308 | 148.7692 | off_peak | 615.7008 |  |  | 19.46 | 0 | 80.54 | 476.0594 | 0
3519 | 738.67 | 611.234 | 28.9 | 122.0371 | 122.0371 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 616.6329 | 0 | 0.05921 | 3.458 | 0 | 0 | 74.308 | 122.0371 | off_peak | 616.6329 |  |  | 16.52 | 0 | 83.48 | 422.0049 | 0
3520 | 751.34 | 660.172 | 28.9 | 131.8079 | 131.8079 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 619.5321 | 0 | 0.05921 | 3.6395 | 0 | 0 | 74.308 | 131.8079 | off_peak | 619.5321 |  |  | 17.54 | 0 | 82.46 | 479.7106 | 0
3521 | 746.61 | 470.426 | 28.8 | 93.9581 | 93.9581 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 652.6519 | 0 | 0.05921 | 3.8943 | 0 | 0 | 74.308 | 93.9581 | off_peak | 652.6519 |  |  | 12.58 | 0 | 87.42 | 365.9057 | 0
3522 | 666.68 | 261.737 | 28.5 | 52.3339 | 52.3339 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 614.3461 | 0 | 0.05921 | 4.278 | 0 | 0 | 74.308 | 52.3339 | off_peak | 614.3461 |  |  | 7.85 | 0 | 92.15 | 223.8847 | 0
3523 | 606.79 | 62.9168 | 28.4 | 12.5847 | 12.5847 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 594.2053 | 0 | 0.05921 | 4.6191 | 0 | 0 | 74.308 | 12.5847 | off_peak | 594.2053 |  |  | 2.07 | 0 | 97.93 | 58.1296 | 0
3524 | 601.01 | 0 | 27.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 601.01 | 0 | 0.05921 | 4.9398 | 0 | 0 | 74.308 | 0 | off_peak | 601.01 |  |  | 0 | 0 | 100 | 0 | 0
3525 | 618.7 | 0 | 27.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 618.7 | 0 | 0.05921 | 5.2398 | 0 | 0 | 74.308 | 0 | off_peak | 618.7 |  |  | 0 | 0 | 100 | 0 | 0
3526 | 577.71 | 0 | 27 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 577.71 | 0 | 0.05921 | 5.685 | 0 | 0 | 74.308 | 0 | off_peak | 577.71 |  |  | 0 | 0 | 100 | 0 | 0
3527 | 598.15 | 0 | 26.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 598.15 | 0 | 0.05921 | 6.0608 | 0 | 0 | 74.308 | 0 | off_peak | 598.15 |  |  | 0 | 0 | 100 | 0 | 0
3528 | 597.49 | 0 | 26.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 597.49 | 0 | 0.05921 | 6.2563 | 0 | 0 | 74.308 | 0 | off_peak | 597.49 |  |  | 0 | 0 | 100 | 0 | 0
3529 | 589.85 | 0 | 26.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 589.85 | 0 | 0.05921 | 6.3699 | 0 | 0 | 74.308 | 0 | off_peak | 589.85 |  |  | 0 | 0 | 100 | 0 | 0
3530 | 603.8 | 0 | 26.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 603.8 | 0 | 0.05921 | 6.1583 | 0 | 0 | 74.308 | 0 | off_peak | 603.8 |  |  | 0 | 0 | 100 | 0 | 0
3531 | 607.58 | 0 | 25.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 607.58 | 0 | 0.05921 | 5.7943 | 0 | 0 | 74.308 | 0 | off_peak | 607.58 |  |  | 0 | 0 | 100 | 0 | 0
3532 | 582.93 | 0 | 25.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 582.93 | 0 | 0.05921 | 5.2526 | 0 | 0 | 74.308 | 0 | off_peak | 582.93 |  |  | 0 | 0 | 100 | 0 | 0
3533 | 609.03 | 0 | 25.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 609.03 | 0 | 0.05921 | 4.7162 | 0 | 0 | 74.308 | 0 | off_peak | 609.03 |  |  | 0 | 0 | 100 | 0 | 0
3534 | 690.29 | 0 | 25.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 690.29 | 0 | 0.05921 | 4.2062 | 0 | 0 | 74.308 | 0 | off_peak | 690.29 |  |  | 0 | 0 | 100 | 0 | 0
3535 | 753.99 | 138.139 | 25.9 | 27.8825 | 27.8825 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 726.1075 | 0 | 0.05921 | 3.7238 | 0 | 0 | 74.308 | 27.8825 | off_peak | 726.1075 |  |  | 3.7 | 0 | 96.3 | 103.8287 | 0
3536 | 730.72 | 343.947 | 26.6 | 69.2481 | 69.2481 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 661.4719 | 0 | 0.05921 | 3.3215 | 0 | 0 | 74.308 | 69.2481 | off_peak | 661.4719 |  |  | 9.48 | 0 | 90.52 | 230.0092 | 0
3537 | 798.56 | 550.113 | 27.6 | 110.3552 | 110.3552 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 688.2048 | 0 | 0.05921 | 3.1614 | 0 | 0 | 74.308 | 110.3552 | off_peak | 688.2048 |  |  | 13.82 | 0 | 86.18 | 348.875 | 0
3538 | 777.42 | 720.168 | 28.5 | 143.9965 | 143.9965 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 633.4235 | 0 | 0.05921 | 3.0294 | 0 | 0 | 74.308 | 143.9965 | off_peak | 633.4235 |  |  | 18.52 | 0 | 81.48 | 436.2272 | 0
3539 | 765.15 | 827.584 | 29.2 | 165.0519 | 165.0519 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 600.0981 | 0 | 0.05921 | 2.9863 | 0 | 0 | 74.308 | 165.0519 | off_peak | 600.0981 |  |  | 21.57 | 0 | 78.43 | 492.892 | 0
3540 | 769.75 | 904.609 | 29.7 | 180.0839 | 180.0839 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 589.6661 | 0 | 0.05921 | 2.9861 | 0 | 0 | 74.308 | 180.0839 | off_peak | 589.6661 |  |  | 23.4 | 0 | 76.6 | 537.7555 | 0
3541 | 758.31 | 921.496 | 30 | 183.2441 | 183.2441 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 575.0659 | 0 | 0.05921 | 3.1506 | 0 | 0 | 74.308 | 183.2441 | off_peak | 575.0659 |  |  | 24.16 | 0 | 75.84 | 577.3348 | 0
3542 | 759.32 | 925.225 | 30.1 | 183.9182 | 183.9182 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 575.4018 | 0 | 0.05921 | 3.5258 | 0 | 0 | 74.308 | 183.9182 | off_peak | 575.4018 |  |  | 24.22 | 0 | 75.78 | 648.4501 | 0
3543 | 708.82 | 821.201 | 30.1 | 163.2401 | 163.2401 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 545.5799 | 0 | 0.05921 | 3.8517 | 0 | 0 | 74.308 | 163.2401 | off_peak | 545.5799 |  |  | 23.03 | 0 | 76.97 | 628.7501 | 0
3544 | 755.72 | 666.607 | 29.9 | 132.6067 | 132.6067 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 623.1133 | 0 | 0.05921 | 4.2187 | 0 | 0 | 74.308 | 132.6067 | off_peak | 623.1133 |  |  | 17.55 | 0 | 82.45 | 559.4288 | 0
3545 | 730.21 | 474.728 | 29.6 | 94.5405 | 94.5405 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 635.6695 | 0 | 0.05921 | 4.6675 | 0 | 0 | 74.308 | 94.5405 | off_peak | 635.6695 |  |  | 12.95 | 0 | 87.05 | 441.2639 | 0
3546 | 704.49 | 265.14 | 29 | 52.9177 | 52.9177 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 651.5723 | 0 | 0.05921 | 5.1781 | 0 | 0 | 74.308 | 52.9177 | off_peak | 651.5723 |  |  | 7.51 | 0 | 92.49 | 274.0136 | 0
3547 | 651.05 | 72.5796 | 28.7 | 14.5016 | 14.5016 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 636.5484 | 0 | 0.05921 | 5.53 | 0 | 0 | 74.308 | 14.5016 | off_peak | 636.5484 |  |  | 2.23 | 0 | 97.77 | 80.1945 | 0
3548 | 614.49 | 0 | 27.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 614.49 | 0 | 0.05921 | 5.8919 | 0 | 0 | 74.308 | 0 | off_peak | 614.49 |  |  | 0 | 0 | 100 | 0 | 0
3549 | 597.85 | 0 | 27.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 597.85 | 0 | 0.05921 | 6.271 | 0 | 0 | 74.308 | 0 | off_peak | 597.85 |  |  | 0 | 0 | 100 | 0 | 0
3550 | 617.29 | 0 | 27.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 617.29 | 0 | 0.05921 | 6.5476 | 0 | 0 | 74.308 | 0 | off_peak | 617.29 |  |  | 0 | 0 | 100 | 0 | 0
3551 | 596.92 | 0 | 27.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 596.92 | 0 | 0.05921 | 6.8445 | 0 | 0 | 74.308 | 0 | off_peak | 596.92 |  |  | 0 | 0 | 100 | 0 | 0
3552 | 599.48 | 0 | 27.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 599.48 | 0 | 0.05921 | 6.9166 | 0 | 0 | 74.308 | 0 | off_peak | 599.48 |  |  | 0 | 0 | 100 | 0 | 0
3553 | 586.87 | 0 | 26.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 586.87 | 0 | 0.05921 | 6.9498 | 0 | 0 | 74.308 | 0 | off_peak | 586.87 |  |  | 0 | 0 | 100 | 0 | 0
3554 | 595.96 | 0 | 26.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 595.96 | 0 | 0.05921 | 6.7833 | 0 | 0 | 74.308 | 0 | off_peak | 595.96 |  |  | 0 | 0 | 100 | 0 | 0
3555 | 579.89 | 0 | 26.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 579.89 | 0 | 0.05921 | 6.3995 | 0 | 0 | 74.308 | 0 | off_peak | 579.89 |  |  | 0 | 0 | 100 | 0 | 0
3556 | 623.13 | 0 | 26.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 623.13 | 0 | 0.05921 | 5.8089 | 0 | 0 | 74.308 | 0 | off_peak | 623.13 |  |  | 0 | 0 | 100 | 0 | 0
3557 | 591.54 | 0 | 26.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 591.54 | 0 | 0.05921 | 5.1101 | 0 | 0 | 74.308 | 0 | off_peak | 591.54 |  |  | 0 | 0 | 100 | 0 | 0
3558 | 685.61 | 0 | 26.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 685.61 | 0 | 0.05921 | 4.4805 | 0 | 0 | 74.308 | 0 | off_peak | 685.61 |  |  | 0 | 0 | 100 | 0 | 0
3559 | 733.2 | 141.738 | 26.8 | 28.516 | 28.516 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 704.684 | 0 | 0.05921 | 3.9823 | 0 | 0 | 74.308 | 28.516 | off_peak | 704.684 |  |  | 3.89 | 0 | 96.11 | 113.5581 | 0
3560 | 772.36 | 349.834 | 27.2 | 70.2803 | 70.2803 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 702.0797 | 0 | 0.05921 | 3.5608 | 0 | 0 | 74.308 | 70.2803 | off_peak | 702.0797 |  |  | 9.1 | 0 | 90.9 | 250.253 | 0
3561 | 807.06 | 556.32 | 27.9 | 111.4787 | 111.4787 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 695.5813 | 0 | 0.05921 | 3.2833 | 0 | 0 | 74.308 | 111.4787 | off_peak | 695.5813 |  |  | 13.81 | 0 | 86.19 | 366.0191 | 0
3562 | 797.73 | 737.523 | 28.6 | 147.4129 | 147.4129 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 650.3171 | 0 | 0.05921 | 3.1506 | 0 | 0 | 74.308 | 147.4129 | off_peak | 650.3171 |  |  | 18.48 | 0 | 81.52 | 464.4414 | 0
3563 | 773.62 | 875.283 | 29.2 | 174.5649 | 174.5649 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 599.0551 | 0 | 0.05921 | 3.1377 | 0 | 0 | 74.308 | 174.5649 | off_peak | 599.0551 |  |  | 22.56 | 0 | 77.44 | 547.7271 | 0
3564 | 801.33 | 687.401 | 29.5 | 136.9437 | 136.9437 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 664.3863 | 0 | 0.05921 | 3.188 | 0 | 0 | 74.308 | 136.9437 | off_peak | 664.3863 |  |  | 17.09 | 0 | 82.91 | 436.5727 | 0
3565 | 773.07 | 971.614 | 29.7 | 193.4228 | 193.4228 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 579.6472 | 0 | 0.05921 | 3.2653 | 0 | 0 | 74.308 | 193.4228 | on_peak | 579.6472 |  |  | 25.02 | 0 | 74.98 | 631.5753 | 0
3566 | 791.84 | 923.185 | 29.8 | 183.7146 | 183.7146 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 608.1254 | 0 | 0.05921 | 3.5606 | 0 | 0 | 74.308 | 183.7146 | on_peak | 608.1254 |  |  | 23.2 | 0 | 76.8 | 654.1331 | 0
3567 | 829.65 | 819.181 | 29.7 | 163.0774 | 163.0774 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 666.5726 | 0 | 0.05921 | 4.0209 | 0 | 0 | 74.308 | 163.0774 | on_peak | 666.5726 |  |  | 19.66 | 0 | 80.34 | 655.7129 | 0
3568 | 808.16 | 662.921 | 29.5 | 132.0668 | 132.0668 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 676.0932 | 0 | 0.05921 | 4.5024 | 0 | 0 | 74.308 | 132.0668 | on_peak | 676.0932 |  |  | 16.34 | 0 | 83.66 | 594.6224 | 0
3569 | 805.14 | 470.11 | 29.1 | 93.7922 | 93.7922 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 711.3478 | 0 | 0.05921 | 4.9985 | 0 | 0 | 74.308 | 93.7922 | on_peak | 711.3478 |  |  | 11.65 | 0 | 88.35 | 468.8179 | 0
3570 | 778.15 | 260.945 | 28.5 | 52.1756 | 52.1756 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 725.9744 | 0 | 0.05921 | 5.3999 | 0 | 0 | 74.308 | 52.1756 | on_peak | 725.9744 |  |  | 6.71 | 0 | 93.29 | 281.7425 | 0
3571 | 784.37 | 69.9687 | 28.1 | 14.0105 | 1.6116 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 0 | 19.0375 | 782.7584 | 0 | 0.05921 | 5.9129 | 0 | 0 | 85.9062 | 1.6116 | on_peak | 782.7584 | 100 | 0 | 0.21 | 0 | 99.79 | 9.5293 | 0
3572 | 733.26 | 0 | 27.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19.0375 | 733.26 | 0 | 0.05921 | 6.1526 | 0 | 0 | 85.9062 | 0 | on_peak | 733.26 |  |  | 0 | 0 | 100 | 0 | 0
3573 | 679.45 | 0 | 26.7 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 30.6357 | 691.8489 | 0 | 0.05921 | 6.4859 | 0 | 0 | 85.9062 | 0 | on_peak | 679.45 | 0 | 100 | 0 | 0 | 100 | 0 | 0
3574 | 597.01 | 0 | 26.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30.6357 | 597.01 | 0 | 0.05921 | 6.7407 | 0 | 0 | 85.9062 | 0 | off_peak | 597.01 |  |  | 0 | 0 | 100 | 0 | 0
3575 | 643.05 | 0 | 26 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30.6357 | 643.05 | 0 | 0.05921 | 7.0471 | 0 | 0 | 85.9062 | 0 | off_peak | 643.05 |  |  | 0 | 0 | 100 | 0 | 0
3576 | 623.04 | 0 | 25.8 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 42.2338 | 635.4389 | 0 | 0.05921 | 7.074 | 0 | 0 | 85.9062 | 0 | off_peak | 623.04 | 0 | 100 | 0 | 0 | 100 | 0 | 0
3577 | 571.95 | 0 | 25.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 42.2338 | 571.95 | 0 | 0.05921 | 7.165 | 0 | 0 | 85.9062 | 0 | off_peak | 571.95 |  |  | 0 | 0 | 100 | 0 | 0
3578 | 541.23 | 0 | 25.3 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 53.832 | 553.6289 | 0 | 0.05921 | 6.9613 | 0 | 0 | 85.9062 | 0 | off_peak | 541.23 | 0 | 100 | 0 | 0 | 100 | 0 | 0
3579 | 544.05 | 0 | 25.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 53.832 | 544.05 | 0 | 0.05921 | 6.5482 | 0 | 0 | 85.9062 | 0 | off_peak | 544.05 |  |  | 0 | 0 | 100 | 0 | 0
3580 | 562.73 | 0 | 25.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 53.832 | 562.73 | 0 | 0.05921 | 5.8867 | 0 | 0 | 85.9062 | 0 | off_peak | 562.73 |  |  | 0 | 0 | 100 | 0 | 0
3581 | 587.01 | 0 | 25.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 53.832 | 587.01 | 0 | 0.05921 | 5.1819 | 0 | 0 | 85.9062 | 0 | off_peak | 587.01 |  |  | 0 | 0 | 100 | 0 | 0
3582 | 687.86 | 4.75 | 25.3 | 0.96084 | 0.96084 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 65.4301 | 699.2981 | 0 | 0.05921 | 4.5045 | 0 | 0 | 85.9062 | 0.96084 | off_peak | 686.8992 | 0 | 100 | 0.14 | 0 | 99.86 | 4.3281 | 0
3583 | 752.44 | 136.406 | 25.9 | 27.5327 | 27.5327 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 65.4301 | 724.9073 | 0 | 0.05921 | 4.0015 | 0 | 0 | 85.9062 | 27.5327 | off_peak | 724.9073 |  |  | 3.66 | 0 | 96.34 | 110.1719 | 0
3584 | 821.02 | 338.637 | 26.5 | 68.2037 | 68.2037 | 0 | 0 | 8.9635 | 8.9635 | 0 | 0 | 0 | 73.8147 | 761.7799 | 0 | 0.05921 | 3.6696 | 0 | 0 | 85.9062 | 68.2037 | off_peak | 752.8163 | 0 | 100 | 8.31 | 0 | 91.69 | 250.2786 | 0
3585 | 850.37 | 454.188 | 27.3 | 91.2115 | 91.2115 | 0 | 0 | 0.57892 | 0.57892 | 0 | 0 | 0 | 74.3563 | 759.7374 | 0 | 0.05921 | 3.4606 | 0 | 0 | 85.9062 | 91.2115 | off_peak | 759.1585 | 0 | 100 | 10.73 | 0 | 89.27 | 315.6452 | 0
3586 | 883.26 | 638.909 | 27.9 | 128.0284 | 127.991 | 0 | 0.03739 | 0.03739 | 0 | 0 | 0 | 0 | 74.3912 | 755.269 | 0 | 0.05921 | 3.4011 | 0 | 0 | 85.9411 | 127.991 | off_peak | 755.269 | 100 | 0 | 14.49 | 0 | 85.51 | 435.3119 | 0
3587 | 871.78 | 528.168 | 28.5 | 105.6064 | 105.6064 | 0 | 0 | 0.0024148 | 0.0024148 | 0 | 0 | 0 | 74.3935 | 766.176 | 0 | 0.05921 | 3.5626 | 0 | 0 | 85.9411 | 105.6064 | off_peak | 766.1736 | 0 | 100 | 12.11 | 0 | 87.89 | 376.2373 | 0
3588 | 944.99 | 857.002 | 29 | 171.0439 | 171.0439 | 0 | 0 | 0.00015596 | 0.00015596 | 0 | 0 | 0 | 74.3936 | 773.9463 | 0 | 0.05921 | 3.9201 | 0 | 0 | 85.9411 | 171.0439 | off_peak | 773.9461 | 0 | 100 | 18.1 | 0 | 81.9 | 670.5107 | 0
3589 | 872.33 | 942.567 | 29.3 | 187.9152 | 187.9152 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 684.4148 | 0 | 0.088511 | 4.071 | 0 | 0 | 85.9411 | 187.9152 | on_peak | 684.4148 |  |  | 21.54 | 0 | 78.46 | 765.0059 | 0
3590 | 929.27 | 802.487 | 29.4 | 159.9296 | 159.9296 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 769.3404 | 0 | 0.088511 | 4.2211 | 0 | 0 | 85.9411 | 159.9296 | on_peak | 769.3404 |  |  | 17.21 | 0 | 82.79 | 675.0828 | 0
3591 | 923.71 | 793.047 | 29.4 | 158.0482 | 158.0482 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 765.6618 | 0 | 0.088511 | 4.4761 | 0 | 0 | 85.9411 | 158.0482 | on_peak | 765.6618 |  |  | 17.11 | 0 | 82.89 | 707.4426 | 0
3592 | 934.4 | 622.359 | 29.2 | 124.1222 | 124.1222 | 0 | 0 | 0 | 0 | 58.6428 | 58.6428 | 0 | 11.7019 | 751.6351 | 0 | 0.088511 | 4.8112 | 0 | 0 | 85.9411 | 124.1222 | on_peak | 751.6351 |  |  | 13.28 | 6.28 | 80.44 | 597.1799 | 0
3593 | 905.25 | 392.65 | 28.8 | 78.4239 | 78.4239 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11.7019 | 826.8261 | 0 | 0.088511 | 5.3192 | 0 | 0 | 85.9411 | 78.4239 | on_peak | 826.8261 |  |  | 8.66 | 0 | 91.34 | 417.1546 | 0
3594 | 888.28 | 247.108 | 28.2 | 49.4629 | 49.4629 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11.7019 | 838.8171 | 0 | 0.088511 | 5.8098 | 0 | 0 | 85.9411 | 49.4629 | on_peak | 838.8171 |  |  | 5.57 | 0 | 94.43 | 287.3693 | 0
3595 | 854.13 | 36.6898 | 27.8 | 7.3548 | 7.3548 | 0 | 0 | 0 | 0 | 3.9872 | 3.9872 | 0 | 7.4394 | 842.788 | 0 | 0.088511 | 6.3183 | 0 | 0 | 85.9411 | 7.3548 | on_peak | 842.788 |  |  | 0.86 | 0.47 | 98.67 | 46.47 | 0
3596 | 813.02 | 0 | 26.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 813.02 | 0 | 0.088511 | 6.6594 | 0 | 0 | 85.9411 | 0 | on_peak | 813.02 |  |  | 0 | 0 | 100 | 0 | 0
3597 | 825.02 | 0 | 26.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 825.02 | 0 | 0.088511 | 7.0662 | 0 | 0 | 85.9411 | 0 | on_peak | 825.02 |  |  | 0 | 0 | 100 | 0 | 0
3598 | 795.93 | 0 | 26.1 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 19.0375 | 808.3289 | 0 | 0.05921 | 7.2387 | 0 | 0 | 85.9411 | 0 | off_peak | 795.93 | 0 | 100 | 0 | 0 | 100 | 0 | 0
3599 | 826.98 | 0 | 25.9 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 30.6357 | 839.3789 | 0 | 0.05921 | 7.5352 | 0 | 0 | 85.9411 | 0 | off_peak | 826.98 | 0 | 100 | 0 | 0 | 100 | 0 | 0
3600 | 813.89 | 0 | 25.8 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 42.2338 | 826.2889 | 0 | 0.05921 | 7.4436 | 0 | 0 | 85.9411 | 0 | off_peak | 813.89 | 0 | 100 | 0 | 0 | 100 | 0 | 0
3601 | 781.26 | 0 | 25.7 | 0 | 0 | 0 | 0 | 8.7263 | 8.7263 | 0 | 0 | 0 | 50.3966 | 789.9863 | 0 | 0.05921 | 7.3879 | 0 | 0 | 85.9411 | 0 | off_peak | 781.26 | 0 | 100 | 0 | 0 | 100 | 0 | 0
3602 | 715.07 | 0 | 25.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50.3966 | 715.07 | 0 | 0.05921 | 7.0155 | 0 | 0 | 85.9411 | 0 | off_peak | 715.07 |  |  | 0 | 0 | 100 | 0 | 0
3603 | 677.57 | 0 | 25.5 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 61.9947 | 689.9689 | 0 | 0.05921 | 6.3577 | 0 | 0 | 85.9411 | 0 | off_peak | 677.57 | 0 | 100 | 0 | 0 | 100 | 0 | 0
3604 | 657.97 | 0 | 25.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 61.9947 | 657.97 | 0 | 0.05921 | 5.7221 | 0 | 0 | 85.9411 | 0 | off_peak | 657.97 |  |  | 0 | 0 | 100 | 0 | 0
3605 | 697.97 | 0 | 25.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 61.9947 | 697.97 | 0 | 0.05921 | 5.0225 | 0 | 0 | 85.9411 | 0 | off_peak | 697.97 |  |  | 0 | 0 | 100 | 0 | 0
3606 | 764.41 | 4.75 | 25.7 | 0.95945 | 0.95945 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 61.9947 | 763.4505 | 0 | 0.05921 | 4.4482 | 0 | 0 | 85.9411 | 0.95945 | off_peak | 763.4505 |  |  | 0.13 | 0 | 99.87 | 4.2679 | 0
3607 | 778.98 | 134.633 | 26.3 | 27.1356 | 27.1356 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 61.9947 | 751.8444 | 0 | 0.05921 | 4.0687 | 0 | 0 | 85.9411 | 27.1356 | off_peak | 751.8444 |  |  | 3.48 | 0 | 96.52 | 110.4067 | 0
3608 | 825.82 | 333.93 | 26.9 | 67.1583 | 67.1583 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 73.5928 | 771.0606 | 0 | 0.05921 | 3.7806 | 0 | 0 | 85.9411 | 67.1583 | off_peak | 758.6617 | 0 | 100 | 8.13 | 0 | 91.87 | 253.9004 | 0
3609 | 870.9 | 468.729 | 27.5 | 94.0634 | 93.2626 | 0 | 0.80079 | 0.80079 | 0 | 0 | 0 | 0 | 74.3419 | 777.6374 | 0 | 0.05921 | 3.5867 | 0 | 0 | 86.6902 | 93.2626 | off_peak | 777.6374 | 100 | 0 | 10.71 | 0 | 89.29 | 334.509 | 0
3610 | 828.15 | 544.225 | 28.2 | 108.936 | 108.936 | 0 | 0 | 0.05172 | 0.05172 | 0 | 0 | 0 | 74.3903 | 719.2657 | 0 | 0.05921 | 3.5604 | 0 | 0 | 86.6902 | 108.936 | off_peak | 719.214 | 0 | 100 | 13.15 | 0 | 86.85 | 387.8511 | 0
3611 | 838.56 | 841.647 | 28.7 | 168.1633 | 168.1633 | 0 | 0 | 0.0033404 | 0.0033404 | 0 | 0 | 0 | 74.3934 | 670.4 | 0 | 0.05921 | 3.7316 | 0 | 0 | 86.6902 | 168.1633 | off_peak | 670.3967 | 0 | 100 | 20.05 | 0 | 79.95 | 627.5244 | 0
3612 | 886.94 | 925.34 | 29.1 | 184.6156 | 184.6156 | 0 | 0 | 0.00021574 | 0.00021574 | 0 | 0 | 0 | 74.3936 | 702.3246 | 0 | 0.05921 | 4.0617 | 0 | 0 | 86.6902 | 184.6156 | off_peak | 702.3244 | 0 | 100 | 20.81 | 0 | 79.19 | 749.8499 | 0
3613 | 868.76 | 919.99 | 29.4 | 183.347 | 183.347 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 685.413 | 0 | 0.088511 | 4.2484 | 0 | 0 | 86.6902 | 183.347 | on_peak | 685.413 |  |  | 21.1 | 0 | 78.9 | 778.9287 | 0
3614 | 959.07 | 553.726 | 29.6 | 110.2727 | 110.2727 | 0 | 0 | 0 | 0 | 6.0094 | 6.0094 | 0 | 67.9694 | 842.788 | 0 | 0.088511 | 4.4749 | 0 | 0 | 86.6902 | 110.2727 | on_peak | 842.788 |  |  | 11.5 | 0.63 | 87.88 | 493.4638 | 0
3615 | 916.97 | 538.831 | 29.6 | 107.3064 | 107.3064 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 67.9694 | 809.6636 | 0 | 0.088511 | 4.6421 | 0 | 0 | 86.6902 | 107.3064 | on_peak | 809.6636 |  |  | 11.7 | 0 | 88.3 | 498.1247 | 0
3616 | 877.31 | 615.153 | 29.4 | 122.5953 | 122.5953 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 67.9694 | 754.7147 | 0 | 0.088511 | 4.9827 | 0 | 0 | 86.6902 | 122.5953 | on_peak | 754.7147 |  |  | 13.97 | 0 | 86.03 | 610.8592 | 0
3617 | 862.78 | 452.995 | 29 | 90.4106 | 90.4106 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 67.9694 | 772.3694 | 0 | 0.088511 | 5.3239 | 0 | 0 | 86.6902 | 90.4106 | on_peak | 772.3694 |  |  | 10.48 | 0 | 89.52 | 481.3356 | 0
3618 | 879.43 | 218.154 | 28.5 | 43.6196 | 43.6196 | 0 | 0 | 0 | 0 | 56.6206 | 56.6206 | 0 | 7.4394 | 779.1898 | 0 | 0.088511 | 5.8428 | 0 | 0 | 86.6902 | 43.6196 | on_peak | 779.1898 |  |  | 4.96 | 6.44 | 88.6 | 254.8598 | 0
3619 | 829.04 | 60.263 | 28.2 | 12.0627 | 12.0627 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 816.9773 | 0 | 0.088511 | 6.312 | 0 | 0 | 86.6902 | 12.0627 | on_peak | 816.9773 |  |  | 1.46 | 0 | 98.54 | 76.1399 | 0
3620 | 830.43 | 0 | 27.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 830.43 | 0 | 0.088511 | 6.4873 | 0 | 0 | 86.6902 | 0 | on_peak | 830.43 |  |  | 0 | 0 | 100 | 0 | 0
3621 | 784.21 | 0 | 27.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 784.21 | 0 | 0.088511 | 6.6362 | 0 | 0 | 86.6902 | 0 | on_peak | 784.21 |  |  | 0 | 0 | 100 | 0 | 0
3622 | 806.39 | 0 | 27.1 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 19.0375 | 818.7889 | 0 | 0.05921 | 6.7249 | 0 | 0 | 86.6902 | 0 | off_peak | 806.39 | 0 | 100 | 0 | 0 | 100 | 0 | 0
3623 | 819.64 | 0 | 27 | 0 | 0 | 0 | 0 | 8.7263 | 8.7263 | 0 | 0 | 0 | 27.2003 | 828.3663 | 0 | 0.05921 | 6.6567 | 0 | 0 | 86.6902 | 0 | off_peak | 819.64 | 0 | 100 | 0 | 0 | 100 | 0 | 0
3624 | 792.15 | 0 | 27 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27.2003 | 792.15 | 0 | 0.05921 | 6.5924 | 0 | 0 | 86.6902 | 0 | off_peak | 792.15 |  |  | 0 | 0 | 100 | 0 | 0
3625 | 765.11 | 0 | 26.9 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 38.7984 | 777.5089 | 0 | 0.05921 | 6.3338 | 0 | 0 | 86.6902 | 0 | off_peak | 765.11 | 0 | 100 | 0 | 0 | 100 | 0 | 0
3626 | 736.6 | 0 | 26.8 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 50.3966 | 748.9989 | 0 | 0.05921 | 6.2483 | 0 | 0 | 86.6902 | 0 | off_peak | 736.6 | 0 | 100 | 0 | 0 | 100 | 0 | 0
3627 | 664.73 | 0 | 26.8 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 61.9947 | 677.1289 | 0 | 0.05921 | 5.927 | 0 | 0 | 86.6902 | 0 | off_peak | 664.73 | 0 | 100 | 0 | 0 | 100 | 0 | 0
3628 | 659.95 | 0 | 26.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 61.9947 | 659.95 | 0 | 0.05921 | 5.3999 | 0 | 0 | 86.6902 | 0 | off_peak | 659.95 |  |  | 0 | 0 | 100 | 0 | 0
3629 | 665.67 | 0 | 26.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 61.9947 | 665.67 | 0 | 0.05921 | 4.7657 | 0 | 0 | 86.6902 | 0 | off_peak | 665.67 |  |  | 0 | 0 | 100 | 0 | 0
3630 | 701.04 | 3.8 | 27 | 0.76396 | 0.76396 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 61.9947 | 700.276 | 0 | 0.05921 | 4.2488 | 0 | 0 | 86.6902 | 0.76396 | off_peak | 700.276 |  |  | 0.11 | 0 | 99.89 | 3.2459 | 0
3631 | 795.67 | 117.29 | 27.6 | 23.5289 | 11.13 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 0 | 73.5928 | 784.54 | 0 | 0.05921 | 3.8224 | 0 | 0 | 98.2884 | 11.13 | off_peak | 784.54 | 100 | 0 | 1.4 | 0 | 98.6 | 42.543 | 0
3632 | 848.38 | 323.76 | 28.1 | 64.8297 | 64.8297 | 0 | 0 | 0.80079 | 0.80079 | 0 | 0 | 0 | 74.3419 | 784.3511 | 0 | 0.05921 | 3.5457 | 0 | 0 | 98.2884 | 64.8297 | off_peak | 783.5503 | 0 | 100 | 7.64 | 0 | 92.36 | 229.8681 | 0
3633 | 899 | 106.619 | 28.6 | 21.3105 | 21.3105 | 0 | 0 | 0.05172 | 0.05172 | 0 | 0 | 0 | 74.3903 | 877.7412 | 0 | 0.05921 | 3.4006 | 0 | 0 | 98.2884 | 21.3105 | off_peak | 877.6895 | 0 | 100 | 2.37 | 0 | 97.63 | 72.4692 | 0
3634 | 889.85 | 501.059 | 29 | 100.0034 | 100.0034 | 0 | 0 | 0.0033404 | 0.0033404 | 0 | 0 | 0 | 74.3934 | 789.85 | 0 | 0.05921 | 3.3751 | 0 | 0 | 98.2884 | 100.0034 | off_peak | 789.8466 | 0 | 100 | 11.24 | 0 | 88.76 | 337.5221 | 0
3635 | 883.99 | 709.841 | 29.4 | 141.4659 | 141.4659 | 0 | 0 | 0.00021574 | 0.00021574 | 0 | 0 | 0 | 74.3936 | 742.5243 | 0 | 0.05921 | 3.5782 | 0 | 0 | 98.2884 | 141.4659 | off_peak | 742.5241 | 0 | 100 | 16 | 0 | 84 | 506.1948 | 0
3636 | 905.87 | 780.594 | 29.8 | 155.3388 | 155.3388 | 0 | 0 | 1.3934e-05 | 1.3934e-05 | 0 | 0 | 0 | 74.3936 | 750.5312 | 0 | 0.05921 | 3.9483 | 0 | 0 | 98.2884 | 155.3388 | off_peak | 750.5312 | 0 | 100 | 17.15 | 0 | 82.85 | 613.324 | 0
3637 | 900.65 | 835.072 | 29.9 | 166.1191 | 166.1191 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 734.5309 | 0 | 0.088511 | 4.3651 | 0 | 0 | 98.2884 | 166.1191 | on_peak | 734.5309 |  |  | 18.44 | 0 | 81.56 | 725.1342 | 0
3638 | 880.37 | 891.955 | 30 | 177.3697 | 177.3697 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 703.0003 | 0 | 0.088511 | 4.6431 | 0 | 0 | 98.2884 | 177.3697 | on_peak | 703.0003 |  |  | 20.15 | 0 | 79.85 | 823.5375 | 0
3639 | 916.98 | 703.133 | 29.9 | 139.8728 | 139.8728 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 777.1072 | 0 | 0.088511 | 4.888 | 0 | 0 | 98.2884 | 139.8728 | on_peak | 777.1072 |  |  | 15.25 | 0 | 84.75 | 683.6965 | 0
3640 | 866.67 | 592.298 | 29.7 | 117.911 | 117.911 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 748.759 | 0 | 0.088511 | 5.241 | 0 | 0 | 98.2884 | 117.911 | on_peak | 748.759 |  |  | 13.61 | 0 | 86.39 | 617.9766 | 0
3641 | 842.74 | 395.749 | 29.3 | 78.8986 | 78.8986 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 763.8414 | 0 | 0.088511 | 5.5242 | 0 | 0 | 98.2884 | 78.8986 | on_peak | 763.8414 |  |  | 9.36 | 0 | 90.64 | 435.85 | 0
3642 | 841.54 | 178.64 | 28.8 | 35.6797 | 35.6797 | 0 | 0 | 0 | 0 | 62.63 | 62.63 | 0 | 7.4394 | 743.2303 | 0 | 0.088511 | 6.0304 | 0 | 0 | 98.2884 | 35.6797 | on_peak | 743.2303 |  |  | 4.24 | 7.44 | 88.32 | 215.1634 | 0
3643 | 811.84 | 55.9568 | 28.5 | 11.1885 | 11.1885 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 800.6515 | 0 | 0.088511 | 6.3502 | 0 | 0 | 98.2884 | 11.1885 | on_peak | 800.6515 |  |  | 1.38 | 0 | 98.62 | 71.0496 | 0
3644 | 817.63 | 0 | 27.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 817.63 | 0 | 0.088511 | 6.444 | 0 | 0 | 98.2884 | 0 | on_peak | 817.63 |  |  | 0 | 0 | 100 | 0 | 0
3645 | 814.93 | 0 | 27.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 814.93 | 0 | 0.088511 | 6.4394 | 0 | 0 | 98.2884 | 0 | on_peak | 814.93 |  |  | 0 | 0 | 100 | 0 | 0
3646 | 791.35 | 0 | 27.3 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 19.0375 | 803.7489 | 0 | 0.05921 | 6.5898 | 0 | 0 | 98.2884 | 0 | off_peak | 791.35 | 0 | 100 | 0 | 0 | 100 | 0 | 0
3647 | 815.86 | 0 | 27.2 | 0 | 0 | 0 | 0 | 8.7263 | 8.7263 | 0 | 0 | 0 | 27.2003 | 824.5863 | 0 | 0.05921 | 6.6245 | 0 | 0 | 98.2884 | 0 | off_peak | 815.86 | 0 | 100 | 0 | 0 | 100 | 0 | 0
3648 | 829.36 | 0 | 27.2 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 38.7984 | 841.7589 | 0 | 0.05921 | 6.8266 | 0 | 0 | 98.2884 | 0 | off_peak | 829.36 | 0 | 100 | 0 | 0 | 100 | 0 | 0
3649 | 606.39 | 0 | 27.2 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 50.3966 | 618.7889 | 0 | 0.05921 | 6.7833 | 0 | 0 | 98.2884 | 0 | off_peak | 606.39 | 0 | 100 | 0 | 0 | 100 | 0 | 0
3650 | 570.24 | 0 | 27.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50.3966 | 570.24 | 0 | 0.05921 | 6.6731 | 0 | 0 | 98.2884 | 0 | off_peak | 570.24 |  |  | 0 | 0 | 100 | 0 | 0
3651 | 523.98 | 0 | 27.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50.3966 | 523.98 | 0 | 0.05921 | 6.2277 | 0 | 0 | 98.2884 | 0 | off_peak | 523.98 |  |  | 0 | 0 | 100 | 0 | 0
3652 | 564.47 | 0 | 27.1 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 61.9947 | 576.8689 | 0 | 0.05921 | 5.6593 | 0 | 0 | 98.2884 | 0 | off_peak | 564.47 | 0 | 100 | 0 | 0 | 100 | 0 | 0
3653 | 576.71 | 0 | 27.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 61.9947 | 576.71 | 0 | 0.05921 | 4.8254 | 0 | 0 | 98.2884 | 0 | off_peak | 576.71 |  |  | 0 | 0 | 100 | 0 | 0
3654 | 684.87 | 4.75 | 27.2 | 0.95426 | 0.95426 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 61.9947 | 683.9157 | 0 | 0.05921 | 4.3744 | 0 | 0 | 98.2884 | 0.95426 | off_peak | 683.9157 |  |  | 0.14 | 0 | 99.86 | 4.1743 | 0
3655 | 738.92 | 132.118 | 27.5 | 26.5131 | 26.5131 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 61.9947 | 712.4069 | 0 | 0.05921 | 3.8846 | 0 | 0 | 98.2884 | 26.5131 | off_peak | 712.4069 |  |  | 3.59 | 0 | 96.41 | 102.9918 | 0
3656 | 768.19 | 330.447 | 27.8 | 66.241 | 66.241 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 73.5928 | 714.3479 | 0 | 0.05921 | 3.5717 | 0 | 0 | 98.2884 | 66.241 | off_peak | 701.949 | 0 | 100 | 8.62 | 0 | 91.38 | 236.591 | 0
3657 | 763.27 | 530.938 | 28 | 106.3538 | 106.3538 | 0 | 0 | 0.80079 | 0.80079 | 0 | 0 | 0 | 74.3419 | 657.717 | 0 | 0.05921 | 3.4245 | 0 | 0 | 98.2884 | 106.3538 | off_peak | 656.9162 | 0 | 100 | 13.93 | 0 | 86.07 | 364.2117 | 0
3658 | 758.86 | 709.636 | 28.1 | 142.0976 | 142.0976 | 0 | 0 | 0.05172 | 0.05172 | 0 | 0 | 0 | 74.3903 | 616.8141 | 0 | 0.05921 | 3.4083 | 0 | 0 | 98.2884 | 142.0976 | off_peak | 616.7624 | 0 | 100 | 18.73 | 0 | 81.27 | 484.3127 | 0
3659 | 771.81 | 845.418 | 28.2 | 169.225 | 169.225 | 0 | 0 | 0.0033404 | 0.0033404 | 0 | 0 | 0 | 74.3934 | 602.5884 | 0 | 0.05921 | 3.5708 | 0 | 0 | 98.2884 | 169.225 | off_peak | 602.585 | 0 | 100 | 21.93 | 0 | 78.07 | 604.2728 | 0
3660 | 790.09 | 871.174 | 28.3 | 174.317 | 174.317 | 0 | 0 | 0.00021574 | 0.00021574 | 0 | 0 | 0 | 74.3936 | 615.7733 | 0 | 0.05921 | 3.901 | 0 | 0 | 98.2884 | 174.317 | off_peak | 615.773 | 0 | 100 | 22.06 | 0 | 77.94 | 680.0146 | 0
3661 | 759.42 | 732.304 | 28.2 | 146.5832 | 146.5832 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 612.8368 | 0 | 0.088511 | 4.1807 | 0 | 0 | 98.2884 | 146.5832 | on_peak | 612.8368 |  |  | 19.3 | 0 | 80.7 | 612.8172 | 0
3662 | 869.76 | 604.747 | 28.2 | 121.0505 | 121.0505 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 748.7095 | 0 | 0.088511 | 4.2423 | 0 | 0 | 98.2884 | 121.0505 | on_peak | 748.7095 |  |  | 13.92 | 0 | 86.08 | 513.5342 | 0
3663 | 894.24 | 574.069 | 28.1 | 114.9516 | 114.9516 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 779.2884 | 0 | 0.088511 | 4.4332 | 0 | 0 | 98.2884 | 114.9516 | on_peak | 779.2884 |  |  | 12.85 | 0 | 87.15 | 509.6075 | 0
3664 | 836.87 | 559.383 | 27.9 | 112.0925 | 112.0925 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 724.7775 | 0 | 0.088511 | 4.7747 | 0 | 0 | 98.2884 | 112.0925 | on_peak | 724.7775 |  |  | 13.39 | 0 | 86.61 | 535.2132 | 0
3665 | 843.25 | 196.369 | 27.7 | 39.3782 | 39.3782 | 0 | 0 | 0 | 0 | 62.63 | 62.63 | 0 | 7.4394 | 741.2418 | 0 | 0.088511 | 5.3247 | 0 | 0 | 98.2884 | 39.3782 | on_peak | 741.2418 |  |  | 4.67 | 7.43 | 87.9 | 209.6773 | 0
3666 | 812.37 | 247.416 | 27.5 | 49.6508 | 49.6508 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 762.7192 | 0 | 0.088511 | 5.7235 | 0 | 0 | 98.2884 | 49.6508 | on_peak | 762.7192 |  |  | 6.11 | 0 | 93.89 | 284.1776 | 0
3667 | 765.58 | 65.877 | 27.3 | 13.2296 | 13.2296 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 752.3504 | 0 | 0.088511 | 6.2363 | 0 | 0 | 98.2884 | 13.2296 | on_peak | 752.3504 |  |  | 1.73 | 0 | 98.27 | 82.504 | 0
3668 | 762.53 | 0 | 27.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 762.53 | 0 | 0.088511 | 6.3341 | 0 | 0 | 98.2884 | 0 | on_peak | 762.53 |  |  | 0 | 0 | 100 | 0 | 0
3669 | 761.3 | 0 | 27 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 761.3 | 0 | 0.088511 | 6.2726 | 0 | 0 | 98.2884 | 0 | on_peak | 761.3 |  |  | 0 | 0 | 100 | 0 | 0
3670 | 722.99 | 0 | 27 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 722.99 | 0 | 0.05921 | 6.3971 | 0 | 0 | 98.2884 | 0 | off_peak | 722.99 |  |  | 0 | 0 | 100 | 0 | 0
3671 | 774.1 | 0 | 27 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 774.1 | 0 | 0.05921 | 6.5141 | 0 | 0 | 98.2884 | 0 | off_peak | 774.1 |  |  | 0 | 0 | 100 | 0 | 0
3672 | 738.22 | 0 | 26.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 738.22 | 0 | 0.05921 | 6.5758 | 0 | 0 | 98.2884 | 0 | off_peak | 738.22 |  |  | 0 | 0 | 100 | 0 | 0
3673 | 681.81 | 0 | 26.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 681.81 | 0 | 0.05921 | 6.6519 | 0 | 0 | 98.2884 | 0 | off_peak | 681.81 |  |  | 0 | 0 | 100 | 0 | 0
3674 | 596.94 | 0 | 26.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 596.94 | 0 | 0.05921 | 6.5157 | 0 | 0 | 98.2884 | 0 | off_peak | 596.94 |  |  | 0 | 0 | 100 | 0 | 0
3675 | 593.56 | 0 | 26.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 593.56 | 0 | 0.05921 | 6.0681 | 0 | 0 | 98.2884 | 0 | off_peak | 593.56 |  |  | 0 | 0 | 100 | 0 | 0
3676 | 589.75 | 0 | 26.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 589.75 | 0 | 0.05921 | 5.5979 | 0 | 0 | 98.2884 | 0 | off_peak | 589.75 |  |  | 0 | 0 | 100 | 0 | 0
3677 | 620.43 | 0 | 26.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 620.43 | 0 | 0.05921 | 4.9574 | 0 | 0 | 98.2884 | 0 | off_peak | 620.43 |  |  | 0 | 0 | 100 | 0 | 0
3678 | 678.81 | 3.8 | 26.7 | 0.76479 | 0.76479 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 678.0452 | 0 | 0.05921 | 4.452 | 0 | 0 | 98.2884 | 0.76479 | off_peak | 678.0452 |  |  | 0.11 | 0 | 99.89 | 3.4049 | 0
3679 | 740.29 | 128.944 | 27.2 | 25.9044 | 25.9044 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 714.3856 | 0 | 0.05921 | 3.9882 | 0 | 0 | 98.2884 | 25.9044 | off_peak | 714.3856 |  |  | 3.5 | 0 | 96.5 | 103.3126 | 0
3680 | 741.04 | 290.259 | 27.7 | 58.2061 | 58.2061 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 682.8339 | 0 | 0.05921 | 3.6563 | 0 | 0 | 98.2884 | 58.2061 | off_peak | 682.8339 |  |  | 7.85 | 0 | 92.15 | 212.8212 | 0
3681 | 770.33 | 505.147 | 28.1 | 101.1507 | 101.1507 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 669.1793 | 0 | 0.05921 | 3.4353 | 0 | 0 | 98.2884 | 101.1507 | off_peak | 669.1793 |  |  | 13.13 | 0 | 86.87 | 347.4785 | 0
3682 | 767.22 | 662.217 | 28.6 | 132.361 | 132.361 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 634.859 | 0 | 0.05921 | 3.3677 | 0 | 0 | 98.2884 | 132.361 | off_peak | 634.859 |  |  | 17.25 | 0 | 82.75 | 445.7577 | 0
3683 | 751.62 | 837.725 | 29 | 167.1965 | 167.1965 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 584.4235 | 0 | 0.05921 | 3.3842 | 0 | 0 | 98.2884 | 167.1965 | off_peak | 584.4235 |  |  | 22.24 | 0 | 77.76 | 565.8305 | 0
3684 | 752.94 | 932.503 | 29.3 | 185.9087 | 185.9087 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 567.0313 | 0 | 0.05921 | 3.4736 | 0 | 0 | 98.2884 | 185.9087 | off_peak | 567.0313 |  |  | 24.69 | 0 | 75.31 | 645.7746 | 0
3685 | 758.66 | 956.239 | 29.5 | 190.5015 | 190.5015 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 19.0375 | 580.5575 | 0 | 0.05921 | 3.6897 | 0 | 0 | 98.2884 | 190.5015 | off_peak | 568.1585 | 0 | 100 | 25.11 | 0 | 74.89 | 702.9022 | 0
3686 | 776.32 | 914.631 | 29.7 | 182.079 | 182.079 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19.0375 | 594.241 | 0 | 0.05921 | 4.0972 | 0 | 0 | 98.2884 | 182.079 | off_peak | 594.241 |  |  | 23.45 | 0 | 76.55 | 746.0135 | 0
3687 | 799.02 | 750.379 | 29.7 | 149.3807 | 149.3807 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19.0375 | 649.6393 | 0 | 0.05921 | 4.567 | 0 | 0 | 98.2884 | 149.3807 | off_peak | 649.6393 |  |  | 18.7 | 0 | 81.3 | 682.2238 | 0
3688 | 787.33 | 661.989 | 29.6 | 131.8329 | 131.8329 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19.0375 | 655.4971 | 0 | 0.05921 | 4.8288 | 0 | 0 | 98.2884 | 131.8329 | off_peak | 655.4971 |  |  | 16.74 | 0 | 83.26 | 636.5971 | 0
3689 | 797.69 | 455.802 | 29.4 | 90.8379 | 90.8379 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19.0375 | 706.8521 | 0 | 0.05921 | 5.3938 | 0 | 0 | 98.2884 | 90.8379 | off_peak | 706.8521 |  |  | 11.39 | 0 | 88.61 | 489.9617 | 0
3690 | 713.34 | 214.975 | 28.9 | 42.9212 | 39.6536 | 0 | 3.2677 | 3.2677 | 0 | 0 | 0 | 0 | 22.0941 | 673.6864 | 0 | 0.05921 | 5.7909 | 0 | 0 | 101.345 | 39.6536 | off_peak | 673.6864 | 100 | 0 | 5.56 | 0 | 94.44 | 229.6307 | 0
3691 | 654.39 | 75.7664 | 28.7 | 15.1383 | 15.1383 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22.0941 | 639.2517 | 0 | 0.05921 | 5.8458 | 0 | 0 | 101.345 | 15.1383 | off_peak | 639.2517 |  |  | 2.31 | 0 | 97.69 | 88.4958 | 0
3692 | 635.89 | 0 | 27.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22.0941 | 635.89 | 0 | 0.05921 | 5.6601 | 0 | 0 | 101.345 | 0 | off_peak | 635.89 |  |  | 0 | 0 | 100 | 0 | 0
3693 | 642.28 | 0 | 27.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22.0941 | 642.28 | 0 | 0.05921 | 5.7473 | 0 | 0 | 101.345 | 0 | off_peak | 642.28 |  |  | 0 | 0 | 100 | 0 | 0
3694 | 645.03 | 0 | 27.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22.0941 | 645.03 | 0 | 0.05921 | 6.1578 | 0 | 0 | 101.345 | 0 | off_peak | 645.03 |  |  | 0 | 0 | 100 | 0 | 0
3695 | 619.19 | 0 | 27.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22.0941 | 619.19 | 0 | 0.05921 | 6.3452 | 0 | 0 | 101.345 | 0 | off_peak | 619.19 |  |  | 0 | 0 | 100 | 0 | 0
3696 | 661.74 | 0 | 27.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22.0941 | 661.74 | 0 | 0.05921 | 6.2877 | 0 | 0 | 101.345 | 0 | off_peak | 661.74 |  |  | 0 | 0 | 100 | 0 | 0
3697 | 622.67 | 0 | 27.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22.0941 | 622.67 | 0 | 0.05921 | 6.3394 | 0 | 0 | 101.345 | 0 | off_peak | 622.67 |  |  | 0 | 0 | 100 | 0 | 0
3698 | 639.19 | 0 | 27 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22.0941 | 639.19 | 0 | 0.05921 | 6.2833 | 0 | 0 | 101.345 | 0 | off_peak | 639.19 |  |  | 0 | 0 | 100 | 0 | 0
3699 | 651.93 | 0 | 26.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22.0941 | 651.93 | 0 | 0.05921 | 5.9628 | 0 | 0 | 101.345 | 0 | off_peak | 651.93 |  |  | 0 | 0 | 100 | 0 | 0
3700 | 603.31 | 0 | 26.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22.0941 | 603.31 | 0 | 0.05921 | 5.5164 | 0 | 0 | 101.345 | 0 | off_peak | 603.31 |  |  | 0 | 0 | 100 | 0 | 0
3701 | 667.39 | 0 | 26.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22.0941 | 667.39 | 0 | 0.05921 | 4.9285 | 0 | 0 | 101.345 | 0 | off_peak | 667.39 |  |  | 0 | 0 | 100 | 0 | 0
3702 | 712.15 | 4.75 | 27.3 | 0.95391 | 0.95391 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 33.6923 | 723.595 | 0 | 0.05921 | 4.3997 | 0 | 0 | 101.345 | 0.95391 | off_peak | 711.1961 | 0 | 100 | 0.13 | 0 | 99.87 | 4.1969 | 0
3703 | 702.48 | 139.239 | 27.9 | 27.9015 | 27.9015 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 33.6923 | 674.5785 | 0 | 0.05921 | 3.9301 | 0 | 0 | 101.345 | 27.9015 | off_peak | 674.5785 |  |  | 3.97 | 0 | 96.03 | 109.6558 | 0
3704 | 729.63 | 340.492 | 28.3 | 68.1305 | 68.1305 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 33.6923 | 661.4995 | 0 | 0.05921 | 3.5953 | 0 | 0 | 101.345 | 68.1305 | off_peak | 661.4995 |  |  | 9.34 | 0 | 90.66 | 244.9512 | 0
3705 | 720.26 | 542.844 | 28.8 | 108.4221 | 108.4221 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 45.2904 | 624.2368 | 0 | 0.05921 | 3.3856 | 0 | 0 | 101.345 | 108.4221 | off_peak | 611.8379 | 0 | 100 | 15.05 | 0 | 84.95 | 367.0735 | 0
3706 | 721.96 | 717.657 | 29.2 | 143.1282 | 143.1282 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 45.2904 | 578.8318 | 0 | 0.05921 | 3.2821 | 0 | 0 | 101.345 | 143.1282 | off_peak | 578.8318 |  |  | 19.82 | 0 | 80.18 | 469.7612 | 0
3707 | 701.75 | 849.976 | 29.6 | 169.2698 | 169.2698 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 45.2904 | 532.4802 | 0 | 0.05921 | 3.249 | 0 | 0 | 101.345 | 169.2698 | off_peak | 532.4802 |  |  | 24.12 | 0 | 75.88 | 549.9611 | 0
3708 | 740.22 | 929.918 | 30 | 184.9188 | 184.9188 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 45.2904 | 555.3012 | 0 | 0.05921 | 3.2962 | 0 | 0 | 101.345 | 184.9188 | off_peak | 555.3012 |  |  | 24.98 | 0 | 75.02 | 609.5297 | 0
3709 | 727.52 | 946.009 | 30.2 | 187.9807 | 187.9807 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 45.2904 | 539.5393 | 0 | 0.05921 | 3.521 | 0 | 0 | 101.345 | 187.9807 | off_peak | 539.5393 |  |  | 25.84 | 0 | 74.16 | 661.8727 | 0
3710 | 706.28 | 899.145 | 30.3 | 178.6028 | 178.6028 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 45.2904 | 527.6772 | 0 | 0.05921 | 3.7448 | 0 | 0 | 101.345 | 178.6028 | off_peak | 527.6772 |  |  | 25.29 | 0 | 74.71 | 668.8231 | 0
3711 | 742.81 | 794.445 | 30.2 | 157.8635 | 157.8635 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 45.2904 | 584.9465 | 0 | 0.05921 | 4.02 | 0 | 0 | 101.345 | 157.8635 | off_peak | 584.9465 |  |  | 21.25 | 0 | 78.75 | 634.608 | 0
3712 | 756.3 | 634.591 | 30 | 126.1916 | 126.1916 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 45.2904 | 630.1084 | 0 | 0.05921 | 4.5183 | 0 | 0 | 101.345 | 126.1916 | off_peak | 630.1084 |  |  | 16.69 | 0 | 83.31 | 570.1671 | 0
3713 | 710.34 | 457.137 | 29.6 | 91.0373 | 91.0373 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 56.8886 | 631.7017 | 0 | 0.05921 | 5.0123 | 0 | 0 | 101.345 | 91.0373 | off_peak | 619.3027 | 0 | 100 | 12.82 | 0 | 87.18 | 456.3056 | 0
3714 | 626.69 | 166.652 | 29.1 | 33.2489 | 33.2489 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 68.4867 | 605.84 | 0 | 0.05921 | 5.5805 | 0 | 0 | 101.345 | 33.2489 | off_peak | 593.4411 | 0 | 100 | 5.31 | 0 | 94.69 | 185.5442 | 0
3715 | 610.48 | 29.5746 | 28.8 | 5.9069 | 0 | 0 | 5.9069 | 5.9069 | 0 | 0 | 0 | 0 | 74.0121 | 610.48 | 0 | 0.05921 | 5.9005 | 0 | 0 | 106.8704 | 0 | off_peak | 610.48 | 100 | 0 | 0 | 0 | 100 | 0 | 0
3716 | 601.09 | 0 | 28.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.0121 | 601.09 | 0 | 0.05921 | 6.2652 | 0 | 0 | 106.8704 | 0 | off_peak | 601.09 |  |  | 0 | 0 | 100 | 0 | 0
3717 | 591.02 | 0 | 27.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.0121 | 591.02 | 0 | 0.05921 | 6.4555 | 0 | 0 | 106.8704 | 0 | off_peak | 591.02 |  |  | 0 | 0 | 100 | 0 | 0
3718 | 601.53 | 0 | 27.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.0121 | 601.53 | 0 | 0.05921 | 6.6487 | 0 | 0 | 106.8704 | 0 | off_peak | 601.53 |  |  | 0 | 0 | 100 | 0 | 0
3719 | 605.83 | 0 | 27.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.0121 | 605.83 | 0 | 0.05921 | 6.9504 | 0 | 0 | 106.8704 | 0 | off_peak | 605.83 |  |  | 0 | 0 | 100 | 0 | 0
3720 | 587.22 | 0 | 27.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.0121 | 587.22 | 0 | 0.05921 | 7.1137 | 0 | 0 | 106.8704 | 0 | off_peak | 587.22 |  |  | 0 | 0 | 100 | 0 | 0
3721 | 587.18 | 0 | 27.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.0121 | 587.18 | 0 | 0.05921 | 7.0651 | 0 | 0 | 106.8704 | 0 | off_peak | 587.18 |  |  | 0 | 0 | 100 | 0 | 0
3722 | 554.75 | 0 | 27.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.0121 | 554.75 | 0 | 0.05921 | 6.8783 | 0 | 0 | 106.8704 | 0 | off_peak | 554.75 |  |  | 0 | 0 | 100 | 0 | 0
3723 | 587.74 | 0 | 27.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.0121 | 587.74 | 0 | 0.05921 | 6.5245 | 0 | 0 | 106.8704 | 0 | off_peak | 587.74 |  |  | 0 | 0 | 100 | 0 | 0
3724 | 608.22 | 0 | 27.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.0121 | 608.22 | 0 | 0.05921 | 5.9377 | 0 | 0 | 106.8704 | 0 | off_peak | 608.22 |  |  | 0 | 0 | 100 | 0 | 0
3725 | 576.8 | 0 | 27.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.0121 | 576.8 | 0 | 0.05921 | 5.1982 | 0 | 0 | 106.8704 | 0 | off_peak | 576.8 |  |  | 0 | 0 | 100 | 0 | 0
3726 | 683.55 | 4.75 | 27.5 | 0.95322 | 0.95322 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.0121 | 682.5968 | 0 | 0.05921 | 4.5275 | 0 | 0 | 106.8704 | 0.95322 | off_peak | 682.5968 |  |  | 0.14 | 0 | 99.86 | 4.3157 | 0
3727 | 751.5 | 135.098 | 28.1 | 27.052 | 27.052 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.0121 | 724.448 | 0 | 0.05921 | 3.9542 | 0 | 0 | 106.8704 | 27.052 | off_peak | 724.448 |  |  | 3.6 | 0 | 96.4 | 106.9697 | 0
3728 | 812.21 | 334.549 | 28.5 | 66.8926 | 66.5111 | 0 | 0.3815 | 0.3815 | 0 | 0 | 0 | 0 | 74.369 | 745.6989 | 0 | 0.05921 | 3.6528 | 0 | 0 | 107.2273 | 66.5111 | off_peak | 745.6989 | 100 | 0 | 8.19 | 0 | 91.81 | 242.9533 | 0
3729 | 822.3 | 535.83 | 28.9 | 106.9822 | 106.9822 | 0 | 0 | 0.02464 | 0.02464 | 0 | 0 | 0 | 74.3921 | 715.3425 | 0 | 0.05921 | 3.4577 | 0 | 0 | 107.2273 | 106.9822 | off_peak | 715.3178 | 0 | 100 | 13.01 | 0 | 86.99 | 369.9116 | 0
3730 | 852.01 | 710.075 | 29.3 | 141.5643 | 141.5643 | 0 | 0 | 0.0015914 | 0.0015914 | 0 | 0 | 0 | 74.3935 | 710.4473 | 0 | 0.05921 | 3.434 | 0 | 0 | 107.2273 | 141.5643 | off_peak | 710.4457 | 0 | 100 | 16.62 | 0 | 83.38 | 486.1369 | 0
3731 | 835.58 | 794.436 | 29.6 | 158.2092 | 158.2092 | 0 | 0 | 0.00010278 | 0.00010278 | 0 | 0 | 0 | 74.3936 | 677.3709 | 0 | 0.05921 | 3.6365 | 0 | 0 | 107.2273 | 158.2092 | off_peak | 677.3708 | 0 | 100 | 18.93 | 0 | 81.07 | 575.3349 | 0
3732 | 872.57 | 893.855 | 29.8 | 177.8779 | 177.8779 | 0 | 0 | 6.6381e-06 | 6.6381e-06 | 0 | 0 | 0 | 74.3936 | 694.6921 | 0 | 0.05921 | 3.9241 | 0 | 0 | 107.2273 | 177.8779 | off_peak | 694.6921 | 0 | 100 | 20.39 | 0 | 79.61 | 698.0033 | 0
3733 | 853.13 | 936.685 | 29.9 | 186.3328 | 186.3328 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 666.7972 | 0 | 0.088511 | 4.2573 | 0 | 0 | 107.2273 | 186.3328 | on_peak | 666.7972 |  |  | 21.84 | 0 | 78.16 | 793.2699 | 0
3734 | 858.82 | 843.677 | 29.9 | 167.8309 | 167.8309 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 690.9891 | 0 | 0.088511 | 4.4542 | 0 | 0 | 107.2273 | 167.8309 | on_peak | 690.9891 |  |  | 19.54 | 0 | 80.46 | 747.5508 | 0
3735 | 873.21 | 726.125 | 29.8 | 144.4995 | 144.4995 | 0 | 0 | 0 | 0 | 62.63 | 62.63 | 0 | 7.4394 | 666.0806 | 0 | 0.088511 | 4.6856 | 0 | 0 | 107.2273 | 144.4995 | on_peak | 666.0806 |  |  | 16.55 | 7.17 | 76.28 | 677.0653 | 0
3736 | 840.26 | 594.607 | 29.6 | 118.414 | 118.414 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 721.846 | 0 | 0.088511 | 4.9244 | 0 | 0 | 107.2273 | 118.414 | on_peak | 721.846 |  |  | 14.09 | 0 | 85.91 | 583.1165 | 0
3737 | 846.14 | 384.781 | 29.3 | 76.712 | 76.712 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 769.428 | 0 | 0.088511 | 5.3049 | 0 | 0 | 107.2273 | 76.712 | on_peak | 769.428 |  |  | 9.07 | 0 | 90.93 | 406.9474 | 0
3738 | 859.75 | 171.222 | 28.9 | 34.1857 | 34.1857 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 825.5643 | 0 | 0.088511 | 5.6396 | 0 | 0 | 107.2273 | 34.1857 | on_peak | 825.5643 |  |  | 3.98 | 0 | 96.02 | 192.7924 | 0
3739 | 834.93 | 62.8049 | 28.6 | 12.5532 | 12.5532 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 822.3768 | 0 | 0.088511 | 5.9801 | 0 | 0 | 107.2273 | 12.5532 | on_peak | 822.3768 |  |  | 1.5 | 0 | 98.5 | 75.0691 | 0
3740 | 829.08 | 0 | 28.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 829.08 | 0 | 0.088511 | 6.1722 | 0 | 0 | 107.2273 | 0 | on_peak | 829.08 |  |  | 0 | 0 | 100 | 0 | 0
3741 | 825.6 | 0 | 28 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 825.6 | 0 | 0.088511 | 6.3758 | 0 | 0 | 107.2273 | 0 | on_peak | 825.6 |  |  | 0 | 0 | 100 | 0 | 0
3742 | 810.71 | 0 | 28 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 19.0375 | 823.1089 | 0 | 0.05921 | 6.6085 | 0 | 0 | 107.2273 | 0 | off_peak | 810.71 | 0 | 100 | 0 | 0 | 100 | 0 | 0
3743 | 815.92 | 0 | 28 | 0 | 0 | 0 | 0 | 8.7263 | 8.7263 | 0 | 0 | 0 | 27.2003 | 824.6463 | 0 | 0.05921 | 6.9191 | 0 | 0 | 107.2273 | 0 | off_peak | 815.92 | 0 | 100 | 0 | 0 | 100 | 0 | 0
3744 | 804.24 | 0 | 27.9 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 38.7984 | 816.6389 | 0 | 0.05921 | 7.0295 | 0 | 0 | 107.2273 | 0 | off_peak | 804.24 | 0 | 100 | 0 | 0 | 100 | 0 | 0
3745 | 713.6 | 0 | 27.8 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 50.3966 | 725.9989 | 0 | 0.05921 | 7.0754 | 0 | 0 | 107.2273 | 0 | off_peak | 713.6 | 0 | 100 | 0 | 0 | 100 | 0 | 0
3746 | 652.2 | 0 | 27.7 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 61.9947 | 664.5989 | 0 | 0.05921 | 6.9057 | 0 | 0 | 107.2273 | 0 | off_peak | 652.2 | 0 | 100 | 0 | 0 | 100 | 0 | 0
3747 | 636.2 | 0 | 27.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 61.9947 | 636.2 | 0 | 0.05921 | 6.6111 | 0 | 0 | 107.2273 | 0 | off_peak | 636.2 |  |  | 0 | 0 | 100 | 0 | 0
3748 | 662.65 | 0 | 27.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 61.9947 | 662.65 | 0 | 0.05921 | 6.0047 | 0 | 0 | 107.2273 | 0 | off_peak | 662.65 |  |  | 0 | 0 | 100 | 0 | 0
3749 | 642.2 | 0 | 27.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 61.9947 | 642.2 | 0 | 0.05921 | 5.1865 | 0 | 0 | 107.2273 | 0 | off_peak | 642.2 |  |  | 0 | 0 | 100 | 0 | 0
3750 | 710.77 | 3.8 | 27.7 | 0.76202 | 0.76202 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 61.9947 | 710.008 | 0 | 0.05921 | 4.545 | 0 | 0 | 107.2273 | 0.76202 | off_peak | 710.008 |  |  | 0.11 | 0 | 99.89 | 3.4634 | 0
3751 | 761.44 | 90.4476 | 28.2 | 18.1046 | 18.1046 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 61.9947 | 743.3354 | 0 | 0.05921 | 4.0516 | 0 | 0 | 107.2273 | 18.1046 | off_peak | 743.3354 |  |  | 2.38 | 0 | 97.62 | 73.3522 | 0
3752 | 803.33 | 286.978 | 28.6 | 57.3599 | 57.3599 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 73.5928 | 758.369 | 0 | 0.05921 | 3.7128 | 0 | 0 | 107.2273 | 57.3599 | off_peak | 745.9701 | 0 | 100 | 7.14 | 0 | 92.86 | 212.9657 | 0
3753 | 833.97 | 546.291 | 29 | 109.0309 | 109.0309 | 0 | 0 | 0.80079 | 0.80079 | 0 | 0 | 0 | 74.3419 | 725.7399 | 0 | 0.05921 | 3.4946 | 0 | 0 | 107.2273 | 109.0309 | off_peak | 724.9391 | 0 | 100 | 13.07 | 0 | 86.93 | 381.0143 | 0
3754 | 878.75 | 724.876 | 29.4 | 144.4623 | 144.4106 | 0 | 0.05172 | 0.05172 | 0 | 0 | 0 | 0 | 74.3903 | 734.3394 | 0 | 0.05921 | 3.4448 | 0 | 0 | 107.2756 | 144.4106 | off_peak | 734.3394 | 100 | 0 | 16.43 | 0 | 83.57 | 497.4609 | 0
3755 | 814.1 | 860.692 | 29.6 | 171.4039 | 171.4039 | 0 | 0 | 0.0033404 | 0.0033404 | 0 | 0 | 0 | 74.3934 | 642.6995 | 0 | 0.05921 | 3.6445 | 0 | 0 | 107.2756 | 171.4039 | off_peak | 642.6961 | 0 | 100 | 21.05 | 0 | 78.95 | 624.6866 | 0
3756 | 887.58 | 940.546 | 29.8 | 187.1694 | 187.1694 | 0 | 0 | 0.00021574 | 0.00021574 | 0 | 0 | 0 | 74.3936 | 700.4108 | 0 | 0.05921 | 3.9932 | 0 | 0 | 107.2756 | 187.1694 | off_peak | 700.4106 | 0 | 100 | 21.09 | 0 | 78.91 | 747.4058 | 0
3757 | 817.31 | 943.416 | 29.9 | 187.6718 | 187.6718 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 629.6382 | 0 | 0.088511 | 4.2668 | 0 | 0 | 107.2756 | 187.6718 | on_peak | 629.6382 |  |  | 22.96 | 0 | 77.04 | 800.7589 | 0
3758 | 851.55 | 730.406 | 29.9 | 145.2981 | 145.2981 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 706.2519 | 0 | 0.088511 | 4.2644 | 0 | 0 | 107.2756 | 145.2981 | on_peak | 706.2519 |  |  | 17.06 | 0 | 82.94 | 619.6096 | 0
3759 | 919.61 | 684.462 | 29.7 | 136.2584 | 136.2584 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 783.3516 | 0 | 0.088511 | 4.2396 | 0 | 0 | 107.2756 | 136.2584 | on_peak | 783.3516 |  |  | 14.82 | 0 | 85.18 | 577.6752 | 0
3760 | 847.45 | 350.556 | 29.3 | 69.8887 | 69.8887 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 777.5613 | 0 | 0.088511 | 4.3903 | 0 | 0 | 107.2756 | 69.8887 | on_peak | 777.5613 |  |  | 8.25 | 0 | 91.75 | 306.8302 | 0
3761 | 864.52 | 269.85 | 29 | 53.8577 | 53.8577 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 810.6623 | 0 | 0.088511 | 4.6793 | 0 | 0 | 107.2756 | 53.8577 | on_peak | 810.6623 |  |  | 6.23 | 0 | 93.77 | 252.0189 | 0
3762 | 857.32 | 163.792 | 28.5 | 32.75 | 32.75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 824.57 | 0 | 0.088511 | 5.1031 | 0 | 0 | 107.2756 | 32.75 | on_peak | 824.57 |  |  | 3.82 | 0 | 96.18 | 167.127 | 0
3763 | 844.09 | 50.5548 | 28.3 | 10.1157 | 10.1157 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 833.9743 | 0 | 0.088511 | 5.5922 | 0 | 0 | 107.2756 | 10.1157 | on_peak | 833.9743 |  |  | 1.2 | 0 | 98.8 | 56.5692 | 0
3764 | 864.88 | 0 | 27.9 | 0 | 0 | 0 | 0 | 0 | 0 | 62.63 | 62.63 | 0 | 7.4394 | 802.25 | 0 | 0.088511 | 5.9675 | 0 | 0 | 107.2756 | 0 | on_peak | 802.25 |  |  | 0 | 7.24 | 92.76 | 0 | 0
3765 | 826.43 | 0 | 27.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 826.43 | 0 | 0.088511 | 6.419 | 0 | 0 | 107.2756 | 0 | on_peak | 826.43 |  |  | 0 | 0 | 100 | 0 | 0
3766 | 794.06 | 0 | 27.7 | 0 | 0 | 0 | 0 | 8.7263 | 8.7263 | 0 | 0 | 0 | 15.6021 | 802.7863 | 0 | 0.05921 | 6.6947 | 0 | 0 | 107.2756 | 0 | off_peak | 794.06 | 0 | 100 | 0 | 0 | 100 | 0 | 0
3767 | 824.83 | 0 | 27.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15.6021 | 824.83 | 0 | 0.05921 | 6.8752 | 0 | 0 | 107.2756 | 0 | off_peak | 824.83 |  |  | 0 | 0 | 100 | 0 | 0
3768 | 821.64 | 0 | 27.6 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 27.2003 | 834.0389 | 0 | 0.05921 | 6.9603 | 0 | 0 | 107.2756 | 0 | off_peak | 821.64 | 0 | 100 | 0 | 0 | 100 | 0 | 0
3769 | 708.19 | 0 | 27.5 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 38.7984 | 720.5889 | 0 | 0.05921 | 6.9543 | 0 | 0 | 107.2756 | 0 | off_peak | 708.19 | 0 | 100 | 0 | 0 | 100 | 0 | 0
3770 | 622.72 | 0 | 27.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 38.7984 | 622.72 | 0 | 0.05921 | 6.8575 | 0 | 0 | 107.2756 | 0 | off_peak | 622.72 |  |  | 0 | 0 | 100 | 0 | 0
3771 | 639.61 | 0 | 27.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 38.7984 | 639.61 | 0 | 0.05921 | 6.4688 | 0 | 0 | 107.2756 | 0 | off_peak | 639.61 |  |  | 0 | 0 | 100 | 0 | 0
3772 | 630.68 | 0 | 27.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 38.7984 | 630.68 | 0 | 0.05921 | 5.8728 | 0 | 0 | 107.2756 | 0 | off_peak | 630.68 |  |  | 0 | 0 | 100 | 0 | 0
3773 | 608.46 | 0 | 27.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 38.7984 | 608.46 | 0 | 0.05921 | 5.1957 | 0 | 0 | 107.2756 | 0 | off_peak | 608.46 |  |  | 0 | 0 | 100 | 0 | 0
3774 | 747.01 | 3.8 | 27.5 | 0.76257 | 0.76257 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 50.3966 | 758.6464 | 0 | 0.05921 | 4.5127 | 0 | 0 | 107.2756 | 0.76257 | off_peak | 746.2474 | 0 | 100 | 0.1 | 0 | 99.9 | 3.4412 | 0
3775 | 738.83 | 119.347 | 27.9 | 23.9155 | 23.9155 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 61.9947 | 727.3135 | 0 | 0.05921 | 4.075 | 0 | 0 | 107.2756 | 23.9155 | off_peak | 714.9145 | 0 | 100 | 3.24 | 0 | 96.76 | 97.4554 | 0
3776 | 785.5 | 282.208 | 28.4 | 56.4476 | 56.4476 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 73.5928 | 741.4513 | 0 | 0.05921 | 3.7926 | 0 | 0 | 107.2756 | 56.4476 | off_peak | 729.0524 | 0 | 100 | 7.19 | 0 | 92.81 | 214.0859 | 0
3777 | 852.47 | 305.201 | 28.8 | 60.9577 | 60.9577 | 0 | 0 | 0.80079 | 0.80079 | 0 | 0 | 0 | 74.3419 | 792.3131 | 0 | 0.05921 | 3.625 | 0 | 0 | 107.2756 | 60.9577 | off_peak | 791.5123 | 0 | 100 | 7.15 | 0 | 92.85 | 220.9746 | 0
3778 | 844.25 | 633.765 | 29.1 | 126.4432 | 126.3914 | 0 | 0.05172 | 0.05172 | 0 | 0 | 0 | 0 | 74.3903 | 717.8586 | 0 | 0.05921 | 3.5654 | 0 | 0 | 107.324 | 126.3914 | off_peak | 717.8586 | 100 | 0 | 14.97 | 0 | 85.03 | 450.632 | 0
3779 | 816.99 | 686.649 | 29.4 | 136.8439 | 136.8439 | 0 | 0 | 0.0033404 | 0.0033404 | 0 | 0 | 0 | 74.3934 | 680.1494 | 0 | 0.05921 | 3.6813 | 0 | 0 | 107.324 | 136.8439 | off_peak | 680.1461 | 0 | 100 | 16.75 | 0 | 83.25 | 503.7599 | 0
3780 | 929.01 | 848.881 | 29.6 | 169.0518 | 169.0518 | 0 | 0 | 0.00021574 | 0.00021574 | 0 | 0 | 0 | 74.3936 | 759.9585 | 0 | 0.05921 | 3.9625 | 0 | 0 | 107.324 | 169.0518 | off_peak | 759.9582 | 0 | 100 | 18.2 | 0 | 81.8 | 669.8718 | 0
3781 | 824.53 | 542.054 | 29.6 | 107.9482 | 107.9482 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 716.5818 | 0 | 0.088511 | 4.2904 | 0 | 0 | 107.324 | 107.9482 | on_peak | 716.5818 |  |  | 13.09 | 0 | 86.91 | 463.1399 | 0
3782 | 859.7 | 128.25 | 29.5 | 25.5499 | 25.5499 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 834.1501 | 0 | 0.088511 | 4.5615 | 0 | 0 | 107.324 | 25.5499 | on_peak | 834.1501 |  |  | 2.97 | 0 | 97.03 | 116.5456 | 0
3783 | 862.46 | 264.088 | 29.3 | 52.65 | 52.65 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 809.81 | 0 | 0.088511 | 4.8536 | 0 | 0 | 107.324 | 52.65 | on_peak | 809.81 |  |  | 6.1 | 0 | 93.9 | 255.5424 | 0
3784 | 846.61 | 84.2935 | 29 | 16.8236 | 16.8236 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 829.7864 | 0 | 0.088511 | 5.3129 | 0 | 0 | 107.324 | 16.8236 | on_peak | 829.7864 |  |  | 1.99 | 0 | 98.01 | 89.3822 | 0
3785 | 829.8 | 282.334 | 28.7 | 56.4111 | 56.4111 | 0 | 0 | 0 | 0 | 62.63 | 62.63 | 0 | 7.4394 | 710.7589 | 0 | 0.088511 | 5.729 | 62.63 | 0 | 40.3697 | 119.0411 | on_peak | 710.7589 |  |  | 6.8 | 7.55 | 85.65 | 681.987 | 0
3786 | 831.27 | 89.2028 | 28.2 | 17.8555 | 17.8555 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 813.4145 | 0 | 0.088511 | 6.124 | 0 | 0 | 40.3697 | 17.8555 | on_peak | 813.4145 |  |  | 2.15 | 0 | 97.85 | 109.3472 | 0
3787 | 845.7 | 48.8358 | 28 | 9.7824 | 9.7824 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 835.9176 | 0 | 0.088511 | 6.3509 | 0 | 0 | 40.3697 | 9.7824 | on_peak | 835.9176 |  |  | 1.16 | 0 | 98.84 | 62.1271 | 0
3788 | 806.82 | 0 | 27.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 806.82 | 0 | 0.088511 | 6.5835 | 0 | 0 | 40.3697 | 0 | on_peak | 806.82 |  |  | 0 | 0 | 100 | 0 | 0
3789 | 784.59 | 0 | 27.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 784.59 | 0 | 0.088511 | 6.7807 | 0 | 0 | 40.3697 | 0 | on_peak | 784.59 |  |  | 0 | 0 | 100 | 0 | 0
3790 | 792.89 | 0 | 27.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 792.89 | 0 | 0.05921 | 6.7303 | 0 | 0 | 40.3697 | 0 | off_peak | 792.89 |  |  | 0 | 0 | 100 | 0 | 0
3791 | 820.5 | 0 | 27 | 0 | 0 | 0 | 0 | 8.7263 | 8.7263 | 0 | 0 | 0 | 15.6021 | 829.2263 | 0 | 0.05921 | 6.8012 | 0 | 0 | 40.3697 | 0 | off_peak | 820.5 | 0 | 100 | 0 | 0 | 100 | 0 | 0
3792 | 818.37 | 0 | 26.9 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 27.2003 | 830.7689 | 0 | 0.05921 | 6.9306 | 0 | 0 | 40.3697 | 0 | off_peak | 818.37 | 0 | 100 | 0 | 0 | 100 | 0 | 0
3793 | 745.63 | 0 | 26.9 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 38.7984 | 758.0289 | 0 | 0.05921 | 6.9029 | 0 | 0 | 40.3697 | 0 | off_peak | 745.63 | 0 | 100 | 0 | 0 | 100 | 0 | 0
3794 | 628.43 | 0 | 26.8 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 50.3966 | 640.8289 | 0 | 0.05921 | 6.8348 | 0 | 0 | 40.3697 | 0 | off_peak | 628.43 | 0 | 100 | 0 | 0 | 100 | 0 | 0
3795 | 573.99 | 0 | 26.7 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 61.9947 | 586.3889 | 0 | 0.05921 | 6.531 | 0 | 0 | 40.3697 | 0 | off_peak | 573.99 | 0 | 100 | 0 | 0 | 100 | 0 | 0
3796 | 578.75 | 0 | 26.7 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 73.5928 | 591.1489 | 0 | 0.05921 | 5.9126 | 0 | 0 | 40.3697 | 0 | off_peak | 578.75 | 0 | 100 | 0 | 0 | 100 | 0 | 0
3797 | 595.86 | 0 | 26.6 | 0 | 0 | 0 | 0 | 0.80079 | 0.80079 | 0 | 0 | 0 | 74.3419 | 596.6608 | 0 | 0.05921 | 5.1924 | 0 | 0 | 40.3697 | 0 | off_peak | 595.86 | 0 | 100 | 0 | 0 | 100 | 0 | 0
3798 | 642.65 | 2.85 | 26.9 | 0.57318 | 0.57318 | 0 | 0 | 0.05172 | 0.05172 | 0 | 0 | 0 | 74.3903 | 642.1285 | 0 | 0.05921 | 4.5948 | 0 | 0 | 40.3697 | 0.57318 | off_peak | 642.0768 | 0 | 100 | 0.09 | 0 | 99.91 | 2.6336 | 0
3799 | 726.84 | 63.3146 | 27.4 | 12.7104 | 12.7104 | 0 | 0 | 0.0033404 | 0.0033404 | 0 | 0 | 0 | 74.3934 | 714.1329 | 0 | 0.05921 | 4.1512 | 0 | 0 | 40.3697 | 12.7104 | off_peak | 714.1296 | 0 | 100 | 1.75 | 0 | 98.25 | 52.7633 | 0
3800 | 770.32 | 213.772 | 27.9 | 42.8369 | 42.8369 | 0 | 0 | 0.00021574 | 0.00021574 | 0 | 0 | 0 | 74.3936 | 727.4833 | 0 | 0.05921 | 3.8431 | 0 | 0 | 40.3697 | 42.8369 | off_peak | 727.4831 | 0 | 100 | 5.56 | 0 | 94.44 | 164.6264 | 0
3801 | 835.38 | 528.923 | 28.2 | 105.873 | 105.873 | 0 | 0 | 1.3934e-05 | 1.3934e-05 | 0 | 0 | 0 | 74.3936 | 729.507 | 0 | 0.05921 | 3.6607 | 0 | 0 | 40.3697 | 105.873 | off_peak | 729.507 | 0 | 100 | 12.67 | 0 | 87.33 | 387.5698 | 0
3802 | 811.78 | 664.536 | 28.6 | 132.8245 | 132.8245 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 678.9555 | 0 | 0.05921 | 3.6014 | 0 | 0 | 40.3697 | 132.8245 | off_peak | 678.9555 |  |  | 16.36 | 0 | 83.64 | 478.3481 | 0
3803 | 856.53 | 704.407 | 28.9 | 140.6397 | 140.6397 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 715.8903 | 0 | 0.05921 | 3.7495 | 0 | 0 | 40.3697 | 140.6397 | off_peak | 715.8903 |  |  | 16.42 | 0 | 83.58 | 527.3327 | 0
3804 | 896.42 | 718.015 | 29.2 | 143.1996 | 143.1996 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 753.2204 | 0 | 0.05921 | 4.0416 | 0 | 0 | 40.3697 | 143.1996 | off_peak | 753.2204 |  |  | 15.97 | 0 | 84.03 | 578.7609 | 0
3805 | 863.51 | 489.088 | 29.3 | 97.5072 | 97.5072 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 766.0028 | 0 | 0.088511 | 4.4128 | 0 | 0 | 40.3697 | 97.5072 | on_peak | 766.0028 |  |  | 11.29 | 0 | 88.71 | 430.2756 | 0
3806 | 930.85 | 378.536 | 29.2 | 75.4945 | 75.4945 | 0 | 0 | 0 | 0 | 62.63 | 62.63 | 0 | 7.4394 | 792.7255 | 0 | 0.088511 | 4.6233 | 0 | 0 | 40.3697 | 75.4945 | on_peak | 792.7255 |  |  | 8.11 | 6.73 | 85.16 | 349.0332 | 0
3807 | 866.71 | 63.65 | 29.1 | 12.6989 | 12.6989 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 854.0111 | 0 | 0.088511 | 5 | 0 | 0 | 40.3697 | 12.6989 | on_peak | 854.0111 |  |  | 1.47 | 0 | 98.53 | 63.4939 | 0
3808 | 875.47 | 41.8 | 28.8 | 8.3487 | 8.3487 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 867.1213 | 0 | 0.088511 | 5.4507 | 0 | 0 | 40.3697 | 8.3487 | on_peak | 867.1213 |  |  | 0.95 | 0 | 99.05 | 45.5059 | 0
3809 | 874.19 | 269.555 | 28.5 | 53.8971 | 53.8971 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 820.2929 | 0 | 0.088511 | 6.0441 | 0 | 0 | 40.3697 | 53.8971 | on_peak | 820.2929 |  |  | 6.17 | 0 | 93.83 | 325.7619 | 0
3810 | 781.48 | 161.093 | 28.1 | 32.2573 | 32.2573 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 749.2227 | 0 | 0.088511 | 6.4821 | 0 | 0 | 40.3697 | 32.2573 | on_peak | 749.2227 |  |  | 4.13 | 0 | 95.87 | 209.096 | 0
3811 | 812.73 | 56.9589 | 27.9 | 11.4138 | 11.4138 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 801.3162 | 0 | 0.088511 | 6.6424 | 0 | 0 | 40.3697 | 11.4138 | on_peak | 801.3162 |  |  | 1.4 | 0 | 98.6 | 75.8145 | 0
3812 | 774.03 | 0 | 27.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 774.03 | 0 | 0.088511 | 6.4126 | 0 | 0 | 40.3697 | 0 | on_peak | 774.03 |  |  | 0 | 0 | 100 | 0 | 0
3813 | 754.71 | 0 | 27.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 754.71 | 0 | 0.088511 | 6.7394 | 0 | 0 | 40.3697 | 0 | on_peak | 754.71 |  |  | 0 | 0 | 100 | 0 | 0
3814 | 774.93 | 0 | 27 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 19.0375 | 787.3289 | 0 | 0.05921 | 6.9316 | 0 | 0 | 40.3697 | 0 | off_peak | 774.93 | 0 | 100 | 0 | 0 | 100 | 0 | 0
3815 | 763.11 | 0 | 26.9 | 0 | 0 | 0 | 0 | 8.7263 | 8.7263 | 0 | 0 | 0 | 27.2003 | 771.8363 | 0 | 0.05921 | 7.0256 | 0 | 0 | 40.3697 | 0 | off_peak | 763.11 | 0 | 100 | 0 | 0 | 100 | 0 | 0
3816 | 739.29 | 0 | 26.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27.2003 | 739.29 | 0 | 0.05921 | 7.1653 | 0 | 0 | 40.3697 | 0 | off_peak | 739.29 |  |  | 0 | 0 | 100 | 0 | 0
3817 | 636.04 | 0 | 26.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27.2003 | 636.04 | 0 | 0.05921 | 7.2351 | 0 | 0 | 40.3697 | 0 | off_peak | 636.04 |  |  | 0 | 0 | 100 | 0 | 0
3818 | 579.17 | 0 | 26.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27.2003 | 579.17 | 0 | 0.05921 | 7.1784 | 0 | 0 | 40.3697 | 0 | off_peak | 579.17 |  |  | 0 | 0 | 100 | 0 | 0
3819 | 559.71 | 0 | 26.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27.2003 | 559.71 | 0 | 0.05921 | 6.9242 | 0 | 0 | 40.3697 | 0 | off_peak | 559.71 |  |  | 0 | 0 | 100 | 0 | 0
3820 | 574.64 | 0 | 26.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27.2003 | 574.64 | 0 | 0.05921 | 6.3066 | 0 | 0 | 40.3697 | 0 | off_peak | 574.64 |  |  | 0 | 0 | 100 | 0 | 0
3821 | 585.54 | 0 | 26.6 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 38.7984 | 597.9389 | 0 | 0.05921 | 5.4629 | 0 | 0 | 40.3697 | 0 | off_peak | 585.54 | 0 | 100 | 0 | 0 | 100 | 0 | 0
3822 | 676.26 | 3.8 | 26.8 | 0.76451 | 0.76451 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 50.3966 | 687.8944 | 0 | 0.05921 | 4.6696 | 0 | 0 | 40.3697 | 0.76451 | off_peak | 675.4955 | 0 | 100 | 0.11 | 0 | 99.89 | 3.57 | 0
3823 | 702.16 | 106.609 | 27.2 | 21.4173 | 9.0184 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 0 | 61.9947 | 693.1416 | 0 | 0.05921 | 4.4726 | 0 | 0 | 51.9679 | 9.0184 | off_peak | 693.1416 | 100 | 0 | 1.28 | 0 | 98.72 | 40.3359 | 0
3824 | 815.53 | 311.692 | 27.6 | 62.5268 | 62.5268 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 73.5928 | 765.4021 | 0 | 0.05921 | 4.1751 | 0 | 0 | 51.9679 | 62.5268 | off_peak | 753.0032 | 0 | 100 | 7.67 | 0 | 92.33 | 261.058 | 0
3825 | 821.26 | 507.072 | 27.9 | 101.6101 | 101.6101 | 0 | 0 | 0.80079 | 0.80079 | 0 | 0 | 0 | 74.3419 | 720.4507 | 0 | 0.05921 | 3.9722 | 0 | 0 | 51.9679 | 101.6101 | off_peak | 719.6499 | 0 | 100 | 12.37 | 0 | 87.63 | 403.6162 | 0
3826 | 840.73 | 434.793 | 28.2 | 87.0313 | 87.0313 | 0 | 0 | 0.05172 | 0.05172 | 0 | 0 | 0 | 74.3903 | 753.7504 | 0 | 0.05921 | 3.8902 | 0 | 0 | 51.9679 | 87.0313 | off_peak | 753.6987 | 0 | 100 | 10.35 | 0 | 89.65 | 338.5696 | 0
3827 | 840.3 | 170.818 | 28.5 | 34.1548 | 34.1548 | 0 | 0 | 0.0033404 | 0.0033404 | 0 | 0 | 0 | 74.3934 | 806.1485 | 0 | 0.05921 | 3.9248 | 0 | 0 | 51.9679 | 34.1548 | off_peak | 806.1452 | 0 | 100 | 4.06 | 0 | 95.94 | 134.0499 | 0
3828 | 865.52 | 497.617 | 28.6 | 99.4615 | 99.4615 | 0 | 0 | 0.00021574 | 0.00021574 | 0 | 0 | 0 | 74.3936 | 766.0587 | 0 | 0.05921 | 4.1043 | 0 | 0 | 51.9679 | 99.4615 | off_peak | 766.0585 | 0 | 100 | 11.49 | 0 | 88.51 | 408.2214 | 0
3829 | 861.54 | 393.219 | 28.7 | 78.5662 | 78.5662 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 782.9738 | 0 | 0.088511 | 4.5247 | 0 | 0 | 51.9679 | 78.5662 | on_peak | 782.9738 |  |  | 9.12 | 0 | 90.88 | 355.492 | 0
3830 | 880.67 | 89.3 | 28.6 | 17.8489 | 17.8489 | 0 | 0 | 0 | 0 | 61.33 | 61.33 | 0 | 8.8291 | 801.4911 | 0 | 0.088511 | 4.8666 | 0 | 0 | 51.9679 | 17.8489 | on_peak | 801.4911 |  |  | 2.03 | 6.96 | 91.01 | 86.8629 | 0
3831 | 871.83 | 41.8 | 28.6 | 8.3548 | 8.3548 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.8291 | 863.4752 | 0 | 0.088511 | 5.2246 | 0 | 0 | 51.9679 | 8.3548 | on_peak | 863.4752 |  |  | 0.96 | 0 | 99.04 | 43.6506 | 0
3832 | 829.55 | 57.95 | 28.5 | 11.587 | 11.587 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.8291 | 817.963 | 0 | 0.088511 | 5.6193 | 0 | 0 | 51.9679 | 11.587 | on_peak | 817.963 |  |  | 1.4 | 0 | 98.6 | 65.1107 | 0
3833 | 874.08 | 42.75 | 28.3 | 8.554 | 8.554 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.8291 | 865.526 | 0 | 0.088511 | 5.8459 | 0 | 0 | 51.9679 | 8.554 | on_peak | 865.526 |  |  | 0.98 | 0 | 99.02 | 50.0059 | 0
3834 | 847.56 | 120.229 | 28 | 24.0834 | 24.0834 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.8291 | 823.4766 | 0 | 0.088511 | 6.4275 | 0 | 0 | 51.9679 | 24.0834 | on_peak | 823.4766 |  |  | 2.84 | 0 | 97.16 | 154.7965 | 0
3835 | 803.74 | 35.2811 | 27.9 | 7.0698 | 7.0698 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.8291 | 796.6702 | 0 | 0.088511 | 7.1458 | 0 | 0 | 51.9679 | 7.0698 | on_peak | 796.6702 |  |  | 0.88 | 0 | 99.12 | 50.5194 | 0
3836 | 877.87 | 0 | 27.3 | 0 | 0 | 0 | 0 | 0 | 0 | 1.3 | 1.3 | 0 | 7.4394 | 876.57 | 0 | 0.088511 | 7.2485 | 1.3 | 0 | 50.5782 | 1.3 | on_peak | 876.57 |  |  | 0 | 0.15 | 99.85 | 9.4229 | 0
3837 | 823.85 | 0 | 27.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 823.85 | 0 | 0.088511 | 7.5326 | 0 | 0 | 50.5782 | 0 | on_peak | 823.85 |  |  | 0 | 0 | 100 | 0 | 0
3838 | 833.26 | 0 | 27.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 833.26 | 0 | 0.05921 | 7.6383 | 0 | 0 | 50.5782 | 0 | off_peak | 833.26 |  |  | 0 | 0 | 100 | 0 | 0
3839 | 817.13 | 0 | 27 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 817.13 | 0 | 0.05921 | 7.4781 | 0 | 0 | 50.5782 | 0 | off_peak | 817.13 |  |  | 0 | 0 | 100 | 0 | 0
3840 | 822.17 | 0 | 26.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 822.17 | 0 | 0.05921 | 7.5886 | 0 | 0 | 50.5782 | 0 | off_peak | 822.17 |  |  | 0 | 0 | 100 | 0 | 0
3841 | 707.97 | 0 | 26.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 707.97 | 0 | 0.05921 | 7.4198 | 0 | 0 | 50.5782 | 0 | off_peak | 707.97 |  |  | 0 | 0 | 100 | 0 | 0
3842 | 646.43 | 0 | 26.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 646.43 | 0 | 0.05921 | 7.1682 | 0 | 0 | 50.5782 | 0 | off_peak | 646.43 |  |  | 0 | 0 | 100 | 0 | 0
3843 | 654.56 | 0 | 26.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 654.56 | 0 | 0.05921 | 6.7557 | 0 | 0 | 50.5782 | 0 | off_peak | 654.56 |  |  | 0 | 0 | 100 | 0 | 0
3844 | 655.12 | 0 | 26.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 655.12 | 0 | 0.05921 | 6.1772 | 0 | 0 | 50.5782 | 0 | off_peak | 655.12 |  |  | 0 | 0 | 100 | 0 | 0
3845 | 641.7 | 0 | 26.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 641.7 | 0 | 0.05921 | 5.4655 | 0 | 0 | 50.5782 | 0 | off_peak | 641.7 |  |  | 0 | 0 | 100 | 0 | 0
3846 | 701.25 | 2.85 | 26.9 | 0.57318 | 0.57318 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 700.6768 | 0 | 0.05921 | 4.8093 | 0 | 0 | 50.5782 | 0.57318 | off_peak | 700.6768 |  |  | 0.08 | 0 | 99.92 | 2.7566 | 0
3847 | 760.77 | 92.192 | 27.1 | 18.5277 | 18.5277 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 742.2423 | 0 | 0.05921 | 4.3334 | 0 | 0 | 50.5782 | 18.5277 | off_peak | 742.2423 |  |  | 2.44 | 0 | 97.56 | 80.2886 | 0
3848 | 783.01 | 236.63 | 27.3 | 47.5208 | 47.5208 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 735.4892 | 0 | 0.05921 | 3.9874 | 0 | 0 | 50.5782 | 47.5208 | off_peak | 735.4892 |  |  | 6.07 | 0 | 93.93 | 189.4849 | 0
3849 | 758.58 | 413.084 | 27.5 | 82.8967 | 82.8967 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 675.6833 | 0 | 0.05921 | 3.7203 | 0 | 0 | 50.5782 | 82.8967 | off_peak | 675.6833 |  |  | 10.93 | 0 | 89.07 | 308.3975 | 0
3850 | 813.71 | 497.903 | 27.8 | 99.809 | 99.809 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 19.0375 | 726.2999 | 0 | 0.05921 | 3.5685 | 0 | 0 | 50.5782 | 99.809 | off_peak | 713.901 | 0 | 100 | 12.27 | 0 | 87.73 | 356.1722 | 0
3851 | 802.01 | 496.423 | 28.2 | 99.3676 | 99.3676 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 30.6357 | 715.0413 | 0 | 0.05921 | 3.5233 | 0 | 0 | 50.5782 | 99.3676 | off_peak | 702.6424 | 0 | 100 | 12.39 | 0 | 87.61 | 350.1049 | 0
3852 | 899 | 421.918 | 28.5 | 84.3619 | 84.3619 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30.6357 | 814.6381 | 0 | 0.05921 | 3.5622 | 0 | 0 | 50.5782 | 84.3619 | off_peak | 814.6381 |  |  | 9.38 | 0 | 90.62 | 300.5122 | 0
3853 | 813.35 | 523.198 | 28.6 | 104.5745 | 95.8482 | 0 | 8.7263 | 8.7263 | 0 | 0 | 0 | 0 | 38.7984 | 717.5018 | 0 | 0.05921 | 3.8939 | 0 | 0 | 58.7409 | 95.8482 | off_peak | 717.5018 | 100 | 0 | 11.78 | 0 | 88.22 | 373.2274 | 0
3854 | 753.74 | 328.907 | 28.8 | 65.6925 | 53.2936 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 0 | 50.3966 | 700.4464 | 0 | 0.05921 | 4.2868 | 0 | 0 | 70.3391 | 53.2936 | off_peak | 700.4464 | 100 | 0 | 7.07 | 0 | 92.93 | 228.4578 | 0
3855 | 783.36 | 445.171 | 28.9 | 88.8815 | 88.8815 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50.3966 | 694.4785 | 0 | 0.05921 | 4.6592 | 0 | 0 | 70.3391 | 88.8815 | off_peak | 694.4785 |  |  | 11.35 | 0 | 88.65 | 414.1169 | 0
3856 | 749.3 | 74.1 | 28.8 | 14.8 | 14.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50.3966 | 734.5 | 0 | 0.05921 | 5.1223 | 0 | 0 | 70.3391 | 14.8 | off_peak | 734.5 |  |  | 1.98 | 0 | 98.02 | 75.8095 | 0
3857 | 726.23 | 333.608 | 28.5 | 66.7044 | 66.7044 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50.3966 | 659.5256 | 0 | 0.05921 | 5.6788 | 0 | 0 | 70.3391 | 66.7044 | off_peak | 659.5256 |  |  | 9.19 | 0 | 90.81 | 378.8027 | 0
3858 | 660.74 | 156.273 | 28.1 | 31.2921 | 31.2921 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50.3966 | 629.4479 | 0 | 0.05921 | 6.3191 | 0 | 0 | 70.3391 | 31.2921 | off_peak | 629.4479 |  |  | 4.74 | 0 | 95.26 | 197.7381 | 0
3859 | 629.81 | 57.2162 | 27.9 | 11.4653 | 11.4653 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50.3966 | 618.3447 | 0 | 0.05921 | 6.9396 | 0 | 0 | 70.3391 | 11.4653 | off_peak | 618.3447 |  |  | 1.82 | 0 | 98.18 | 79.5647 | 0
3860 | 608 | 0 | 27.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50.3966 | 608 | 0 | 0.05921 | 7.3633 | 0 | 0 | 70.3391 | 0 | off_peak | 608 |  |  | 0 | 0 | 100 | 0 | 0
3861 | 601.16 | 0 | 27.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50.3966 | 601.16 | 0 | 0.05921 | 7.6508 | 0 | 0 | 70.3391 | 0 | off_peak | 601.16 |  |  | 0 | 0 | 100 | 0 | 0
3862 | 583.55 | 0 | 27.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50.3966 | 583.55 | 0 | 0.05921 | 7.947 | 0 | 0 | 70.3391 | 0 | off_peak | 583.55 |  |  | 0 | 0 | 100 | 0 | 0
3863 | 611.7 | 0 | 27.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50.3966 | 611.7 | 0 | 0.05921 | 8.1744 | 0 | 0 | 70.3391 | 0 | off_peak | 611.7 |  |  | 0 | 0 | 100 | 0 | 0
3864 | 590.22 | 0 | 27 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50.3966 | 590.22 | 0 | 0.05921 | 7.8471 | 0 | 0 | 70.3391 | 0 | off_peak | 590.22 |  |  | 0 | 0 | 100 | 0 | 0
3865 | 578.87 | 0 | 26.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50.3966 | 578.87 | 0 | 0.05921 | 7.4734 | 0 | 0 | 70.3391 | 0 | off_peak | 578.87 |  |  | 0 | 0 | 100 | 0 | 0
3866 | 617.33 | 0 | 26.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50.3966 | 617.33 | 0 | 0.05921 | 7.13 | 0 | 0 | 70.3391 | 0 | off_peak | 617.33 |  |  | 0 | 0 | 100 | 0 | 0
3867 | 598.9 | 0 | 26.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50.3966 | 598.9 | 0 | 0.05921 | 6.787 | 0 | 0 | 70.3391 | 0 | off_peak | 598.9 |  |  | 0 | 0 | 100 | 0 | 0
3868 | 604.24 | 0 | 26.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50.3966 | 604.24 | 0 | 0.05921 | 6.2831 | 0 | 0 | 70.3391 | 0 | off_peak | 604.24 |  |  | 0 | 0 | 100 | 0 | 0
3869 | 602.72 | 0 | 26.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50.3966 | 602.72 | 0 | 0.05921 | 5.6151 | 0 | 0 | 70.3391 | 0 | off_peak | 602.72 |  |  | 0 | 0 | 100 | 0 | 0
3870 | 694.65 | 2.85 | 26.8 | 0.57339 | 0.57339 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 61.9947 | 706.4756 | 0 | 0.05921 | 4.9896 | 0 | 0 | 70.3391 | 0.57339 | off_peak | 694.0766 | 0 | 100 | 0.08 | 0 | 99.92 | 2.861 | 0
3871 | 724.67 | 114.982 | 27.1 | 23.1078 | 23.1078 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 61.9947 | 701.5622 | 0 | 0.05921 | 4.5503 | 0 | 0 | 70.3391 | 23.1078 | off_peak | 701.5622 |  |  | 3.19 | 0 | 96.81 | 105.1479 | 0
3872 | 741.58 | 304.754 | 27.6 | 61.1351 | 61.1351 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 61.9947 | 680.4449 | 0 | 0.05921 | 4.1775 | 0 | 0 | 70.3391 | 61.1351 | off_peak | 680.4449 |  |  | 8.24 | 0 | 91.76 | 255.3908 | 0
3873 | 742.43 | 445.975 | 28.2 | 89.2696 | 89.2696 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 61.9947 | 653.1604 | 0 | 0.05921 | 3.9085 | 0 | 0 | 70.3391 | 89.2696 | off_peak | 653.1604 |  |  | 12.02 | 0 | 87.98 | 348.9131 | 0
3874 | 708.53 | 512.895 | 28.6 | 102.5152 | 102.5152 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 61.9947 | 606.0148 | 0 | 0.05921 | 3.7391 | 0 | 0 | 70.3391 | 102.5152 | off_peak | 606.0148 |  |  | 14.47 | 0 | 85.53 | 383.313 | 0
3875 | 759.5 | 395.567 | 29 | 78.9488 | 78.9488 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 61.9947 | 680.5512 | 0 | 0.05921 | 3.6537 | 0 | 0 | 70.3391 | 78.9488 | off_peak | 680.5512 |  |  | 10.39 | 0 | 89.61 | 288.4522 | 0
3876 | 748.07 | 346.301 | 29.2 | 69.0656 | 69.0656 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 61.9947 | 679.0044 | 0 | 0.05921 | 3.6788 | 0 | 0 | 70.3391 | 69.0656 | off_peak | 679.0044 |  |  | 9.23 | 0 | 90.77 | 254.0802 | 0
3877 | 742.66 | 296.391 | 29.3 | 59.0901 | 59.0901 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 61.9947 | 683.5699 | 0 | 0.05921 | 3.9308 | 0 | 0 | 70.3391 | 59.0901 | off_peak | 683.5699 |  |  | 7.96 | 0 | 92.04 | 232.2732 | 0
3878 | 753.39 | 237.354 | 29.3 | 47.3202 | 47.3202 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 61.9947 | 706.0698 | 0 | 0.05921 | 4.3652 | 0 | 0 | 70.3391 | 47.3202 | off_peak | 706.0698 |  |  | 6.28 | 0 | 93.72 | 206.564 | 0
3879 | 734.21 | 383.163 | 29.2 | 76.4173 | 76.4173 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 61.9947 | 657.7927 | 0 | 0.05921 | 4.8631 | 0 | 0 | 70.3391 | 76.4173 | off_peak | 657.7927 |  |  | 10.41 | 0 | 89.59 | 371.6241 | 0
3880 | 736.84 | 633.072 | 29 | 126.351 | 126.351 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 61.9947 | 610.489 | 0 | 0.05921 | 5.2198 | 0 | 0 | 70.3391 | 126.351 | off_peak | 610.489 |  |  | 17.15 | 0 | 82.85 | 659.5273 | 0
3881 | 650.7 | 327.37 | 28.7 | 65.4094 | 65.4094 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 61.9947 | 585.2906 | 0 | 0.05921 | 5.6928 | 0 | 0 | 70.3391 | 65.4094 | off_peak | 585.2906 |  |  | 10.05 | 0 | 89.95 | 372.3597 | 0
3882 | 649.26 | 191.117 | 28.3 | 38.2414 | 38.2414 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 61.9947 | 611.0186 | 0 | 0.05921 | 6.245 | 0 | 0 | 70.3391 | 38.2414 | off_peak | 611.0186 |  |  | 5.89 | 0 | 94.11 | 238.8185 | 0
3883 | 601.7 | 53.4669 | 28 | 10.7101 | 10.7101 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 61.9947 | 590.9899 | 0 | 0.05921 | 6.4454 | 0 | 0 | 70.3391 | 10.7101 | off_peak | 590.9899 |  |  | 1.78 | 0 | 98.22 | 69.0311 | 0
3884 | 595.17 | 0 | 27.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 61.9947 | 595.17 | 0 | 0.05921 | 6.7071 | 0 | 0 | 70.3391 | 0 | off_peak | 595.17 |  |  | 0 | 0 | 100 | 0 | 0
3885 | 572.08 | 0 | 27.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 61.9947 | 572.08 | 0 | 0.05921 | 7.0967 | 0 | 0 | 70.3391 | 0 | off_peak | 572.08 |  |  | 0 | 0 | 100 | 0 | 0
3886 | 588.28 | 0 | 27.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 61.9947 | 588.28 | 0 | 0.05921 | 7.5149 | 0 | 0 | 70.3391 | 0 | off_peak | 588.28 |  |  | 0 | 0 | 100 | 0 | 0
3887 | 594.26 | 0 | 27.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 61.9947 | 594.26 | 0 | 0.05921 | 7.8978 | 0 | 0 | 70.3391 | 0 | off_peak | 594.26 |  |  | 0 | 0 | 100 | 0 | 0
3888 | 566.78 | 0 | 27.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 61.9947 | 566.78 | 0 | 0.05921 | 7.9637 | 0 | 0 | 70.3391 | 0 | off_peak | 566.78 |  |  | 0 | 0 | 100 | 0 | 0
3889 | 567.31 | 0 | 27.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 61.9947 | 567.31 | 0 | 0.05921 | 7.8724 | 0 | 0 | 70.3391 | 0 | off_peak | 567.31 |  |  | 0 | 0 | 100 | 0 | 0
3890 | 562.89 | 0 | 27 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 61.9947 | 562.89 | 0 | 0.05921 | 7.708 | 0 | 0 | 70.3391 | 0 | off_peak | 562.89 |  |  | 0 | 0 | 100 | 0 | 0
3891 | 573.15 | 0 | 27 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 61.9947 | 573.15 | 0 | 0.05921 | 7.3166 | 0 | 0 | 70.3391 | 0 | off_peak | 573.15 |  |  | 0 | 0 | 100 | 0 | 0
3892 | 568.92 | 0 | 26.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 61.9947 | 568.92 | 0 | 0.05921 | 6.6999 | 0 | 0 | 70.3391 | 0 | off_peak | 568.92 |  |  | 0 | 0 | 100 | 0 | 0
3893 | 605.6 | 0 | 27 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 61.9947 | 605.6 | 0 | 0.05921 | 5.8508 | 0 | 0 | 70.3391 | 0 | off_peak | 605.6 |  |  | 0 | 0 | 100 | 0 | 0
3894 | 696 | 2.85 | 27.2 | 0.57255 | 0.57255 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 73.5928 | 707.8264 | 0 | 0.05921 | 5.19 | 0 | 0 | 70.3391 | 0.57255 | off_peak | 695.4274 | 0 | 100 | 0.08 | 0 | 99.92 | 2.9716 | 0
3895 | 729.01 | 86.3502 | 27.7 | 17.316 | 17.316 | 0 | 0 | 0.80079 | 0.80079 | 0 | 0 | 0 | 74.3419 | 712.4948 | 0 | 0.05921 | 4.7302 | 0 | 0 | 70.3391 | 17.316 | off_peak | 711.694 | 0 | 100 | 2.38 | 0 | 97.62 | 81.9086 | 0
3896 | 781.44 | 245.097 | 28.1 | 49.0782 | 49.0782 | 0 | 0 | 0.05172 | 0.05172 | 0 | 0 | 0 | 74.3903 | 732.4135 | 0 | 0.05921 | 4.3795 | 0 | 0 | 70.3391 | 49.0782 | off_peak | 732.3618 | 0 | 100 | 6.28 | 0 | 93.72 | 214.9381 | 0
3897 | 825.67 | 296.075 | 28.4 | 59.2213 | 59.2213 | 0 | 0 | 0.0033404 | 0.0033404 | 0 | 0 | 0 | 74.3934 | 766.452 | 0 | 0.05921 | 4.1575 | 0 | 0 | 70.3391 | 59.2213 | off_peak | 766.4487 | 0 | 100 | 7.17 | 0 | 92.83 | 246.2112 | 0
3898 | 857.47 | 640.906 | 28.6 | 128.1015 | 128.1013 | 0 | 0.00021574 | 0.00021574 | 0 | 0 | 0 | 0 | 74.3936 | 729.3687 | 0 | 0.05921 | 4.0811 | 0 | 0 | 70.3393 | 128.1013 | off_peak | 729.3687 | 100 | 0 | 14.94 | 0 | 85.06 | 522.7949 | 0
3899 | 843.35 | 830.891 | 28.7 | 166.0143 | 166.0143 | 0 | 0 | 1.3934e-05 | 1.3934e-05 | 0 | 0 | 0 | 74.3936 | 677.3357 | 0 | 0.05921 | 4.2345 | 0 | 0 | 70.3393 | 166.0143 | off_peak | 677.3357 | 0 | 100 | 19.69 | 0 | 80.31 | 702.991 | 0
3900 | 895.93 | 613.911 | 28.8 | 122.6163 | 122.6163 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 773.3137 | 0 | 0.05921 | 4.47 | 0 | 0 | 70.3393 | 122.6163 | off_peak | 773.3137 |  |  | 13.69 | 0 | 86.31 | 548.1005 | 0
3901 | 870.34 | 197.597 | 28.7 | 39.4804 | 39.4804 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 830.8596 | 0 | 0.088511 | 4.8038 | 0 | 0 | 70.3393 | 39.4804 | on_peak | 830.8596 |  |  | 4.54 | 0 | 95.46 | 189.6576 | 0
3902 | 891.24 | 71.25 | 28.6 | 14.2411 | 14.2411 | 0 | 0 | 0 | 0 | 0.42884 | 0.42884 | 0 | 73.9352 | 876.57 | 0 | 0.088511 | 5.1763 | 0 | 0 | 70.3393 | 14.2411 | on_peak | 876.57 |  |  | 1.6 | 0.05 | 98.35 | 73.7167 | 0
3903 | 918.89 | 89.3 | 28.4 | 17.8619 | 17.8619 | 0 | 0 | 0 | 0 | 62.2012 | 62.2012 | 0 | 7.4394 | 838.8269 | 0 | 0.088511 | 5.6636 | 0 | 0 | 70.3393 | 17.8619 | on_peak | 838.8269 |  |  | 1.94 | 6.77 | 91.29 | 101.162 | 0
3904 | 890.2 | 520.256 | 28.2 | 104.1382 | 104.1382 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 786.0618 | 0 | 0.088511 | 6.1095 | 0 | 0 | 70.3393 | 104.1382 | on_peak | 786.0618 |  |  | 11.7 | 0 | 88.3 | 636.2285 | 0
3905 | 834.27 | 432.443 | 27.9 | 86.6555 | 86.6555 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 747.6145 | 0 | 0.088511 | 6.4985 | 0 | 0 | 70.3393 | 86.6555 | on_peak | 747.6145 |  |  | 10.39 | 0 | 89.61 | 563.1341 | 0
3906 | 902.18 | 219.163 | 27.6 | 43.9651 | 43.9651 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 858.2149 | 0 | 0.088511 | 6.6478 | 0 | 0 | 70.3393 | 43.9651 | on_peak | 858.2149 |  |  | 4.87 | 0 | 95.13 | 292.269 | 0
3907 | 827.92 | 60.2373 | 27.4 | 12.0927 | 12.0927 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 815.8273 | 0 | 0.088511 | 6.8297 | 0 | 0 | 70.3393 | 12.0927 | on_peak | 815.8273 |  |  | 1.46 | 0 | 98.54 | 82.5894 | 0
3908 | 851.17 | 0 | 27 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 851.17 | 0 | 0.088511 | 7.1757 | 0 | 0 | 70.3393 | 0 | on_peak | 851.17 |  |  | 0 | 0 | 100 | 0 | 0
3909 | 833.23 | 0 | 27 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 833.23 | 0 | 0.088511 | 7.6279 | 0 | 0 | 70.3393 | 0 | on_peak | 833.23 |  |  | 0 | 0 | 100 | 0 | 0
3910 | 774.08 | 0 | 26.9 | 0 | 0 | 0 | 0 | 8.7263 | 8.7263 | 0 | 0 | 0 | 15.6021 | 782.8063 | 0 | 0.05921 | 7.5546 | 0 | 0 | 70.3393 | 0 | off_peak | 774.08 | 0 | 100 | 0 | 0 | 100 | 0 | 0
3911 | 803.08 | 0 | 26.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15.6021 | 803.08 | 0 | 0.05921 | 7.6505 | 0 | 0 | 70.3393 | 0 | off_peak | 803.08 |  |  | 0 | 0 | 100 | 0 | 0
3912 | 779.09 | 0 | 26.9 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 27.2003 | 791.4889 | 0 | 0.05921 | 7.9571 | 0 | 0 | 70.3393 | 0 | off_peak | 779.09 | 0 | 100 | 0 | 0 | 100 | 0 | 0
3913 | 708.01 | 0 | 26.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27.2003 | 708.01 | 0 | 0.05921 | 7.9952 | 0 | 0 | 70.3393 | 0 | off_peak | 708.01 |  |  | 0 | 0 | 100 | 0 | 0
3914 | 645.36 | 0 | 26.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27.2003 | 645.36 | 0 | 0.05921 | 7.8783 | 0 | 0 | 70.3393 | 0 | off_peak | 645.36 |  |  | 0 | 0 | 100 | 0 | 0
3915 | 598.45 | 0 | 26.8 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 38.7984 | 610.8489 | 0 | 0.05921 | 7.3882 | 0 | 0 | 70.3393 | 0 | off_peak | 598.45 | 0 | 100 | 0 | 0 | 100 | 0 | 0
3916 | 634.73 | 0 | 26.7 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 50.3966 | 647.1289 | 0 | 0.05921 | 6.6922 | 0 | 0 | 70.3393 | 0 | off_peak | 634.73 | 0 | 100 | 0 | 0 | 100 | 0 | 0
3917 | 660.8 | 0 | 26.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50.3966 | 660.8 | 0 | 0.05921 | 5.8487 | 0 | 0 | 70.3393 | 0 | off_peak | 660.8 |  |  | 0 | 0 | 100 | 0 | 0
3918 | 721.26 | 2.85 | 26.8 | 0.57339 | 0.57339 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 61.9947 | 733.0856 | 0 | 0.05921 | 5.2647 | 0 | 0 | 70.3393 | 0.57339 | off_peak | 720.6866 | 0 | 100 | 0.08 | 0 | 99.92 | 3.0187 | 0
3919 | 736.35 | 77.8596 | 27.2 | 15.6417 | 15.6417 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 61.9947 | 720.7083 | 0 | 0.05921 | 4.7445 | 0 | 0 | 70.3393 | 15.6417 | off_peak | 720.7083 |  |  | 2.12 | 0 | 97.88 | 74.212 | 0
3920 | 820.2 | 58.3459 | 27.5 | 11.7087 | 11.7087 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 73.5928 | 820.8902 | 0 | 0.05921 | 4.3929 | 0 | 0 | 70.3393 | 11.7087 | off_peak | 808.4913 | 0 | 100 | 1.43 | 0 | 98.57 | 51.4348 | 0
3921 | 827.06 | 196.248 | 27.7 | 39.3539 | 39.3539 | 0 | 0 | 0.80079 | 0.80079 | 0 | 0 | 0 | 74.3419 | 788.5068 | 0 | 0.05921 | 4.1774 | 0 | 0 | 70.3393 | 39.3539 | off_peak | 787.7061 | 0 | 100 | 4.76 | 0 | 95.24 | 164.3966 | 0
3922 | 834.99 | 367.078 | 28 | 73.5305 | 73.5305 | 0 | 0 | 0.05172 | 0.05172 | 0 | 0 | 0 | 74.3903 | 761.5112 | 0 | 0.05921 | 4.1127 | 0 | 0 | 70.3393 | 73.5305 | off_peak | 761.4595 | 0 | 100 | 8.81 | 0 | 91.19 | 302.4124 | 0
3923 | 853.86 | 578.621 | 28.3 | 115.7788 | 115.7788 | 0 | 0 | 0.0033404 | 0.0033404 | 0 | 0 | 0 | 74.3934 | 738.0846 | 0 | 0.05921 | 4.2111 | 0 | 0 | 70.3393 | 115.7788 | off_peak | 738.0812 | 0 | 100 | 13.56 | 0 | 86.44 | 487.558 | 0
3924 | 888.28 | 703.52 | 28.6 | 140.6165 | 140.6165 | 0 | 0 | 0.00021574 | 0.00021574 | 0 | 0 | 0 | 74.3936 | 747.6637 | 0 | 0.05921 | 4.4437 | 0 | 0 | 70.3393 | 140.6165 | off_peak | 747.6635 | 0 | 100 | 15.83 | 0 | 84.17 | 624.8565 | 0
3925 | 851.09 | 632.256 | 28.7 | 126.3265 | 126.3265 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 724.7635 | 0 | 0.088511 | 4.6999 | 0 | 0 | 70.3393 | 126.3265 | on_peak | 724.7635 |  |  | 14.84 | 0 | 85.16 | 593.7164 | 0
3926 | 904.81 | 529.362 | 28.8 | 105.7294 | 105.7294 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 799.0806 | 0 | 0.088511 | 5.0682 | 0 | 0 | 70.3393 | 105.7294 | on_peak | 799.0806 |  |  | 11.69 | 0 | 88.31 | 535.8614 | 0
3927 | 887.11 | 306.056 | 28.7 | 61.1508 | 61.1508 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 825.9592 | 0 | 0.088511 | 5.5106 | 0 | 0 | 70.3393 | 61.1508 | on_peak | 825.9592 |  |  | 6.89 | 0 | 93.11 | 336.9804 | 0
3928 | 908.91 | 464.379 | 28.6 | 92.818 | 92.818 | 0 | 0 | 0 | 0 | 62.63 | 62.63 | 0 | 7.4394 | 753.462 | 0 | 0.088511 | 5.9862 | 0 | 0 | 70.3393 | 92.818 | on_peak | 753.462 |  |  | 10.21 | 6.89 | 82.9 | 555.6292 | 0
3929 | 877.63 | 417.657 | 28.4 | 83.5403 | 83.5403 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 794.0897 | 0 | 0.088511 | 6.598 | 0 | 0 | 70.3393 | 83.5403 | on_peak | 794.0897 |  |  | 9.52 | 0 | 90.48 | 551.2019 | 0
3930 | 907.37 | 209.738 | 28.1 | 41.998 | 41.998 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 865.372 | 0 | 0.088511 | 7.1252 | 0 | 0 | 70.3393 | 41.998 | on_peak | 865.372 |  |  | 4.63 | 0 | 95.37 | 299.2424 | 0
3931 | 864.63 | 57.2702 | 27.9 | 11.4761 | 11.4761 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 853.1539 | 0 | 0.088511 | 7.5565 | 0 | 0 | 70.3393 | 11.4761 | on_peak | 853.1539 |  |  | 1.33 | 0 | 98.67 | 86.7192 | 0
3932 | 861.5 | 0 | 27.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 861.5 | 0 | 0.088511 | 7.8746 | 0 | 0 | 70.3393 | 0 | on_peak | 861.5 |  |  | 0 | 0 | 100 | 0 | 0
3933 | 835.83 | 0 | 27.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 835.83 | 0 | 0.088511 | 7.9782 | 0 | 0 | 70.3393 | 0 | on_peak | 835.83 |  |  | 0 | 0 | 100 | 0 | 0
3934 | 789.6 | 0 | 27.1 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 19.0375 | 801.9989 | 0 | 0.05921 | 8.1413 | 0 | 0 | 70.3393 | 0 | off_peak | 789.6 | 0 | 100 | 0 | 0 | 100 | 0 | 0
3935 | 842.21 | 0 | 27 | 0 | 0 | 0 | 0 | 8.7263 | 8.7263 | 0 | 0 | 0 | 27.2003 | 850.9363 | 0 | 0.05921 | 8.2944 | 0 | 0 | 70.3393 | 0 | off_peak | 842.21 | 0 | 100 | 0 | 0 | 100 | 0 | 0
3936 | 790.49 | 0 | 26.9 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 38.7984 | 802.8889 | 0 | 0.05921 | 8.1781 | 0 | 0 | 70.3393 | 0 | off_peak | 790.49 | 0 | 100 | 0 | 0 | 100 | 0 | 0
3937 | 732.61 | 0 | 26.8 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 50.3966 | 745.0089 | 0 | 0.05921 | 7.8889 | 0 | 0 | 70.3393 | 0 | off_peak | 732.61 | 0 | 100 | 0 | 0 | 100 | 0 | 0
3938 | 667.72 | 0 | 26.7 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 61.9947 | 680.1189 | 0 | 0.05921 | 7.5531 | 0 | 0 | 70.3393 | 0 | off_peak | 667.72 | 0 | 100 | 0 | 0 | 100 | 0 | 0
3939 | 656.67 | 0 | 26.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 61.9947 | 656.67 | 0 | 0.05921 | 7.2036 | 0 | 0 | 70.3393 | 0 | off_peak | 656.67 |  |  | 0 | 0 | 100 | 0 | 0
3940 | 665.66 | 0 | 26.6 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 73.5928 | 678.0589 | 0 | 0.05921 | 6.5875 | 0 | 0 | 70.3393 | 0 | off_peak | 665.66 | 0 | 100 | 0 | 0 | 100 | 0 | 0
3941 | 668.89 | 0 | 26.6 | 0 | 0 | 0 | 0 | 0.80079 | 0.80079 | 0 | 0 | 0 | 74.3419 | 669.6908 | 0 | 0.05921 | 5.8012 | 0 | 0 | 70.3393 | 0 | off_peak | 668.89 | 0 | 100 | 0 | 0 | 100 | 0 | 0
3942 | 742.28 | 2.85 | 26.9 | 0.57318 | 0.57318 | 0 | 0 | 0.05172 | 0.05172 | 0 | 0 | 0 | 74.3903 | 741.7585 | 0 | 0.05921 | 5.1602 | 0 | 0 | 70.3393 | 0.57318 | off_peak | 741.7068 | 0 | 100 | 0.08 | 0 | 99.92 | 2.9577 | 0
3943 | 763.37 | 93.668 | 27.4 | 18.8039 | 18.8039 | 0 | 0 | 0.0033404 | 0.0033404 | 0 | 0 | 0 | 74.3934 | 744.5695 | 0 | 0.05921 | 4.6764 | 0 | 0 | 70.3393 | 18.8039 | off_peak | 744.5661 | 0 | 100 | 2.46 | 0 | 97.54 | 87.9344 | 0
3944 | 791.77 | 269.289 | 27.8 | 53.9813 | 53.9813 | 0 | 0 | 0.00021574 | 0.00021574 | 0 | 0 | 0 | 74.3936 | 737.7889 | 0 | 0.05921 | 4.3599 | 0 | 0 | 70.3393 | 53.9813 | off_peak | 737.7887 | 0 | 100 | 6.82 | 0 | 93.18 | 235.3555 | 0
3945 | 825.64 | 410.356 | 28.2 | 82.1398 | 82.1398 | 0 | 0 | 1.3934e-05 | 1.3934e-05 | 0 | 0 | 0 | 74.3936 | 743.5002 | 0 | 0.05921 | 4.1738 | 0 | 0 | 70.3393 | 82.1398 | off_peak | 743.5002 | 0 | 100 | 9.95 | 0 | 90.05 | 342.8327 | 0
3946 | 851.6 | 567.008 | 28.5 | 113.3724 | 113.3724 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 738.2276 | 0 | 0.05921 | 4.1124 | 0 | 0 | 70.3393 | 113.3724 | off_peak | 738.2276 |  |  | 13.31 | 0 | 86.69 | 466.2351 | 0
3947 | 861.28 | 629.349 | 28.7 | 125.7456 | 125.7456 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 735.5344 | 0 | 0.05921 | 4.2363 | 0 | 0 | 70.3393 | 125.7456 | off_peak | 735.5344 |  |  | 14.6 | 0 | 85.4 | 532.702 | 0
3948 | 928.85 | 395.567 | 28.9 | 78.9777 | 78.9777 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 849.8723 | 0 | 0.05921 | 4.4545 | 0 | 0 | 70.3393 | 78.9777 | off_peak | 849.8723 |  |  | 8.5 | 0 | 91.5 | 351.8062 | 0
3949 | 878.09 | 55.1 | 28.9 | 11.0011 | 11.0011 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 867.0889 | 0 | 0.088511 | 4.8749 | 0 | 0 | 70.3393 | 11.0011 | on_peak | 867.0889 |  |  | 1.25 | 0 | 98.75 | 53.6287 | 0
3950 | 866.09 | 153.864 | 28.9 | 30.72 | 30.72 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 835.37 | 0 | 0.088511 | 5.2915 | 0 | 0 | 70.3393 | 30.72 | on_peak | 835.37 |  |  | 3.55 | 0 | 96.45 | 162.5539 | 0
3951 | 884.21 | 94.05 | 28.8 | 18.7846 | 18.7846 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 865.4254 | 0 | 0.088511 | 5.8415 | 0 | 0 | 70.3393 | 18.7846 | on_peak | 865.4254 |  |  | 2.12 | 0 | 97.88 | 109.7295 | 0
3952 | 831.04 | 114 | 28.6 | 22.7858 | 22.7858 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 808.2542 | 0 | 0.088511 | 6.358 | 0 | 0 | 70.3393 | 22.7858 | on_peak | 808.2542 |  |  | 2.74 | 0 | 97.26 | 144.8716 | 0
3953 | 862.38 | 78.4315 | 28.3 | 15.6937 | 15.6937 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 846.6863 | 0 | 0.088511 | 6.761 | 0 | 0 | 70.3393 | 15.6937 | on_peak | 846.6863 |  |  | 1.82 | 0 | 98.18 | 106.1047 | 0
3954 | 862.53 | 109.054 | 27.9 | 21.8529 | 21.8529 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 840.6771 | 0 | 0.088511 | 7.1846 | 0 | 0 | 70.3393 | 21.8529 | on_peak | 840.6771 |  |  | 2.53 | 0 | 97.47 | 157.0039 | 0
3955 | 862 | 54.4234 | 27.8 | 10.9096 | 10.9096 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 851.0904 | 0 | 0.088511 | 7.6773 | 0 | 0 | 70.3393 | 10.9096 | on_peak | 851.0904 |  |  | 1.27 | 0 | 98.73 | 83.7563 | 0
3956 | 838.2 | 0 | 27.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 838.2 | 0 | 0.088511 | 8.0404 | 0 | 0 | 70.3393 | 0 | on_peak | 838.2 |  |  | 0 | 0 | 100 | 0 | 0
3957 | 827.03 | 0 | 27 | 0 | 0 | 0 | 0 | 0 | 0 | 62.63 | 62.63 | 0 | 7.4394 | 764.4 | 0 | 0.088511 | 8.4328 | 0 | 0 | 70.3393 | 0 | on_peak | 764.4 |  |  | 0 | 7.57 | 92.43 | 0 | 0
3958 | 797.3 | 0 | 26.9 | 0 | 0 | 0 | 0 | 8.7263 | 8.7263 | 0 | 0 | 0 | 15.6021 | 806.0263 | 0 | 0.05921 | 8.6588 | 0 | 0 | 70.3393 | 0 | off_peak | 797.3 | 0 | 100 | 0 | 0 | 100 | 0 | 0
3959 | 829.82 | 0 | 26.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15.6021 | 829.82 | 0 | 0.05921 | 8.7343 | 0 | 0 | 70.3393 | 0 | off_peak | 829.82 |  |  | 0 | 0 | 100 | 0 | 0
3960 | 772.1 | 0 | 26.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15.6021 | 772.1 | 0 | 0.05921 | 8.6216 | 0 | 0 | 70.3393 | 0 | off_peak | 772.1 |  |  | 0 | 0 | 100 | 0 | 0
3961 | 716.96 | 0 | 26.5 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 27.2003 | 729.3589 | 0 | 0.05921 | 8.58 | 0 | 0 | 70.3393 | 0 | off_peak | 716.96 | 0 | 100 | 0 | 0 | 100 | 0 | 0
3962 | 622.6 | 0 | 26.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27.2003 | 622.6 | 0 | 0.05921 | 8.3438 | 0 | 0 | 70.3393 | 0 | off_peak | 622.6 |  |  | 0 | 0 | 100 | 0 | 0
3963 | 584.87 | 0 | 26.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27.2003 | 584.87 | 0 | 0.05921 | 7.9313 | 0 | 0 | 70.3393 | 0 | off_peak | 584.87 |  |  | 0 | 0 | 100 | 0 | 0
3964 | 600.47 | 0 | 26.3 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 38.7984 | 612.8689 | 0 | 0.05921 | 7.1611 | 0 | 0 | 70.3393 | 0 | off_peak | 600.47 | 0 | 100 | 0 | 0 | 100 | 0 | 0
3965 | 596.8 | 0 | 26.3 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 50.3966 | 609.1989 | 0 | 0.05921 | 6.3741 | 0 | 0 | 70.3393 | 0 | off_peak | 596.8 | 0 | 100 | 0 | 0 | 100 | 0 | 0
3966 | 691.21 | 2.85 | 26.6 | 0.5738 | 0.5738 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 61.9947 | 703.0351 | 0 | 0.05921 | 5.7299 | 0 | 0 | 70.3393 | 0.5738 | off_peak | 690.6362 | 0 | 100 | 0.08 | 0 | 99.92 | 3.2878 | 0
3967 | 755.4 | 111.578 | 27 | 22.4319 | 10.0329 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 0 | 73.5928 | 745.3671 | 0 | 0.05921 | 5.2199 | 0 | 0 | 81.9374 | 10.0329 | off_peak | 745.3671 | 100 | 0 | 1.33 | 0 | 98.67 | 52.3713 | 0
3968 | 820.67 | 322.498 | 27.5 | 64.7181 | 64.7181 | 0 | 0 | 0.80079 | 0.80079 | 0 | 0 | 0 | 74.3419 | 756.7527 | 0 | 0.05921 | 4.8794 | 0 | 0 | 81.9374 | 64.7181 | off_peak | 755.9519 | 0 | 100 | 7.89 | 0 | 92.11 | 315.7882 | 0
3969 | 872.49 | 487.646 | 27.9 | 97.7174 | 97.7174 | 0 | 0 | 0.05172 | 0.05172 | 0 | 0 | 0 | 74.3903 | 774.8243 | 0 | 0.05921 | 4.6265 | 0 | 0 | 81.9374 | 97.7174 | off_peak | 774.7726 | 0 | 100 | 11.2 | 0 | 88.8 | 452.0923 | 0
3970 | 823.71 | 585.214 | 28.3 | 117.098 | 117.098 | 0 | 0 | 0.0033404 | 0.0033404 | 0 | 0 | 0 | 74.3934 | 706.6154 | 0 | 0.05921 | 4.5303 | 0 | 0 | 81.9374 | 117.098 | off_peak | 706.612 | 0 | 100 | 14.22 | 0 | 85.78 | 530.4943 | 0
3971 | 855.71 | 619.72 | 28.8 | 123.7766 | 123.7766 | 0 | 0 | 0.00021574 | 0.00021574 | 0 | 0 | 0 | 74.3936 | 731.9337 | 0 | 0.05921 | 4.5473 | 0 | 0 | 81.9374 | 123.7766 | off_peak | 731.9334 | 0 | 100 | 14.46 | 0 | 85.54 | 562.8456 | 0
3972 | 902.59 | 455.941 | 29.2 | 90.9321 | 90.9321 | 0 | 0 | 1.3934e-05 | 1.3934e-05 | 0 | 0 | 0 | 74.3936 | 811.658 | 0 | 0.05921 | 4.7219 | 0 | 0 | 81.9374 | 90.9321 | off_peak | 811.6579 | 0 | 100 | 10.07 | 0 | 89.93 | 429.373 | 0
3973 | 821.69 | 610.631 | 29.5 | 121.6496 | 121.6496 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 700.0404 | 0 | 0.088511 | 4.9242 | 0 | 0 | 81.9374 | 121.6496 | on_peak | 700.0404 |  |  | 14.8 | 0 | 85.2 | 599.0252 | 0
3974 | 872.32 | 810.772 | 29.7 | 161.4034 | 161.4034 | 0 | 0 | 0 | 0 | 62.63 | 62.63 | 0 | 7.4394 | 648.2866 | 0 | 0.088511 | 5.2516 | 0 | 0 | 81.9374 | 161.4034 | on_peak | 648.2866 |  |  | 18.5 | 7.18 | 74.32 | 847.6251 | 0
3975 | 877.34 | 516.618 | 29.8 | 102.8074 | 102.8074 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 774.5326 | 0 | 0.088511 | 5.6745 | 0 | 0 | 81.9374 | 102.8074 | on_peak | 774.5326 |  |  | 11.72 | 0 | 88.28 | 583.377 | 0
3976 | 844.25 | 242.537 | 29.7 | 48.2827 | 48.2827 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 795.9673 | 0 | 0.088511 | 6.1547 | 0 | 0 | 81.9374 | 48.2827 | on_peak | 795.9673 |  |  | 5.72 | 0 | 94.28 | 297.1639 | 0
3977 | 866.36 | 126.808 | 29.4 | 25.2719 | 25.2719 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 841.0881 | 0 | 0.088511 | 6.7237 | 0 | 0 | 81.9374 | 25.2719 | on_peak | 841.0881 |  |  | 2.92 | 0 | 97.08 | 169.9214 | 0
3978 | 860.32 | 15.2 | 28.9 | 3.0348 | 3.0348 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 857.2852 | 0 | 0.088511 | 7.1871 | 0 | 0 | 81.9374 | 3.0348 | on_peak | 857.2852 |  |  | 0.35 | 0 | 99.65 | 21.8114 | 0
3979 | 811.44 | 30.4 | 28.7 | 6.074 | 6.074 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 805.366 | 0 | 0.088511 | 7.7672 | 0 | 0 | 81.9374 | 6.074 | on_peak | 805.366 |  |  | 0.75 | 0 | 99.25 | 47.1783 | 0
3980 | 831.69 | 0 | 27.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 831.69 | 0 | 0.088511 | 8.196 | 0 | 0 | 81.9374 | 0 | on_peak | 831.69 |  |  | 0 | 0 | 100 | 0 | 0
3981 | 832.65 | 0 | 27.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 832.65 | 0 | 0.088511 | 8.5597 | 0 | 0 | 81.9374 | 0 | on_peak | 832.65 |  |  | 0 | 0 | 100 | 0 | 0
3982 | 814.72 | 0 | 27.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 814.72 | 0 | 0.05921 | 8.7794 | 0 | 0 | 81.9374 | 0 | off_peak | 814.72 |  |  | 0 | 0 | 100 | 0 | 0
3983 | 837.09 | 0 | 27.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 837.09 | 0 | 0.05921 | 8.8646 | 0 | 0 | 81.9374 | 0 | off_peak | 837.09 |  |  | 0 | 0 | 100 | 0 | 0
3984 | 825.56 | 0 | 27.1 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 19.0375 | 837.9589 | 0 | 0.05921 | 8.9026 | 0 | 0 | 81.9374 | 0 | off_peak | 825.56 | 0 | 100 | 0 | 0 | 100 | 0 | 0
3985 | 748.13 | 0 | 27 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19.0375 | 748.13 | 0 | 0.05921 | 8.6417 | 0 | 0 | 81.9374 | 0 | off_peak | 748.13 |  |  | 0 | 0 | 100 | 0 | 0
3986 | 667.74 | 0 | 26.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19.0375 | 667.74 | 0 | 0.05921 | 8.283 | 0 | 0 | 81.9374 | 0 | off_peak | 667.74 |  |  | 0 | 0 | 100 | 0 | 0
3987 | 634.21 | 0 | 26.9 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 30.6357 | 646.6089 | 0 | 0.05921 | 7.8721 | 0 | 0 | 81.9374 | 0 | off_peak | 634.21 | 0 | 100 | 0 | 0 | 100 | 0 | 0
3988 | 603.23 | 0 | 26.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30.6357 | 603.23 | 0 | 0.05921 | 7.262 | 0 | 0 | 81.9374 | 0 | off_peak | 603.23 |  |  | 0 | 0 | 100 | 0 | 0
3989 | 625.93 | 0 | 26.9 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 42.2338 | 638.3289 | 0 | 0.05921 | 6.4391 | 0 | 0 | 81.9374 | 0 | off_peak | 625.93 | 0 | 100 | 0 | 0 | 100 | 0 | 0
3990 | 707.02 | 3.8 | 27.3 | 0.76313 | 0.76313 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 53.832 | 718.6558 | 0 | 0.05921 | 5.7452 | 0 | 0 | 81.9374 | 0.76313 | off_peak | 706.2569 | 0 | 100 | 0.11 | 0 | 99.89 | 4.3843 | 0
3991 | 754.26 | 109.338 | 27.9 | 21.9098 | 21.9098 | 0 | 0 | 8.7263 | 8.7263 | 0 | 0 | 0 | 61.9947 | 741.0766 | 0 | 0.05921 | 5.1735 | 0 | 0 | 81.9374 | 21.9098 | off_peak | 732.3502 | 0 | 100 | 2.9 | 0 | 97.1 | 113.3501 | 0
3992 | 807.63 | 321.496 | 28.4 | 64.3061 | 64.3061 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 73.5928 | 755.7229 | 0 | 0.05921 | 4.7958 | 0 | 0 | 81.9374 | 64.3061 | off_peak | 743.3239 | 0 | 100 | 7.96 | 0 | 92.04 | 308.3993 | 0
3993 | 838.26 | 503.836 | 28.8 | 100.6311 | 100.6311 | 0 | 0 | 0.80079 | 0.80079 | 0 | 0 | 0 | 74.3419 | 738.4297 | 0 | 0.05921 | 4.5129 | 0 | 0 | 81.9374 | 100.6311 | off_peak | 737.6289 | 0 | 100 | 12 | 0 | 88 | 454.1335 | 0
3994 | 871.19 | 691.949 | 29 | 138.1019 | 138.1019 | 0 | 0 | 0.05172 | 0.05172 | 0 | 0 | 0 | 74.3903 | 733.1398 | 0 | 0.05921 | 4.3944 | 0 | 0 | 81.9374 | 138.1019 | off_peak | 733.0881 | 0 | 100 | 15.85 | 0 | 84.15 | 606.8685 | 0
3995 | 858.37 | 645.57 | 29.2 | 128.7513 | 128.7513 | 0 | 0 | 0.0033404 | 0.0033404 | 0 | 0 | 0 | 74.3934 | 729.622 | 0 | 0.05921 | 4.4641 | 0 | 0 | 81.9374 | 128.7513 | off_peak | 729.6187 | 0 | 100 | 15 | 0 | 85 | 574.7592 | 0
3996 | 930.74 | 569.647 | 29.3 | 113.5678 | 113.5678 | 0 | 0 | 0.00021574 | 0.00021574 | 0 | 0 | 0 | 74.3936 | 817.1724 | 0 | 0.05921 | 4.6512 | 0 | 0 | 81.9374 | 113.5678 | off_peak | 817.1722 | 0 | 100 | 12.2 | 0 | 87.8 | 528.2249 | 0
3997 | 838.14 | 169.1 | 29.3 | 33.7127 | 33.7127 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 804.4273 | 0 | 0.088511 | 4.9636 | 0 | 0 | 81.9374 | 33.7127 | on_peak | 804.4273 |  |  | 4.02 | 0 | 95.98 | 167.3352 | 0
3998 | 853.63 | 560.922 | 29.2 | 111.8693 | 111.8693 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 741.7607 | 0 | 0.088511 | 5.3875 | 0 | 0 | 81.9374 | 111.8693 | on_peak | 741.7607 |  |  | 13.11 | 0 | 86.89 | 602.6999 | 0
3999 | 878.68 | 784.548 | 29.2 | 156.4688 | 156.4688 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 722.2112 | 0 | 0.088511 | 5.7801 | 0 | 0 | 81.9374 | 156.4688 | on_peak | 722.2112 |  |  | 17.81 | 0 | 82.19 | 904.4061 | 0
4000 | 871.51 | 638.79 | 29 | 127.4923 | 127.4923 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 744.0177 | 0 | 0.088511 | 6.3657 | 0 | 0 | 81.9374 | 127.4923 | on_peak | 744.0177 |  |  | 14.63 | 0 | 85.37 | 811.5813 | 0
4001 | 846.98 | 408.809 | 28.8 | 81.6513 | 81.6513 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 765.3287 | 0 | 0.088511 | 6.9056 | 0 | 0 | 81.9374 | 81.6513 | on_peak | 765.3287 |  |  | 9.64 | 0 | 90.36 | 563.8478 | 0
4002 | 882.93 | 256.16 | 28.5 | 51.2188 | 51.2188 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 831.7112 | 0 | 0.088511 | 7.238 | 0 | 0 | 81.9374 | 51.2188 | on_peak | 831.7112 |  |  | 5.8 | 0 | 94.2 | 370.7193 | 0
4003 | 833.31 | 65.8683 | 28.3 | 13.1799 | 13.1799 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 820.1301 | 0 | 0.088511 | 7.4991 | 0 | 0 | 81.9374 | 13.1799 | on_peak | 820.1301 |  |  | 1.58 | 0 | 98.42 | 98.8367 | 0
4004 | 891.7 | 0 | 27.7 | 0 | 0 | 0 | 0 | 0 | 0 | 62.63 | 62.63 | 0 | 7.4394 | 829.07 | 0 | 0.088511 | 7.7614 | 0 | 0 | 81.9374 | 0 | on_peak | 829.07 |  |  | 0 | 7.02 | 92.98 | 0 | 0
4005 | 858.59 | 0 | 27.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 858.59 | 0 | 0.088511 | 7.8077 | 0 | 0 | 81.9374 | 0 | on_peak | 858.59 |  |  | 0 | 0 | 100 | 0 | 0
4006 | 865.19 | 0 | 27.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 865.19 | 0 | 0.05921 | 7.8095 | 0 | 0 | 81.9374 | 0 | off_peak | 865.19 |  |  | 0 | 0 | 100 | 0 | 0
4007 | 871.31 | 0 | 27.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 871.31 | 0 | 0.05921 | 8.148 | 0 | 0 | 81.9374 | 0 | off_peak | 871.31 |  |  | 0 | 0 | 100 | 0 | 0
4008 | 856.1 | 0 | 27.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 856.1 | 0 | 0.05921 | 8.207 | 0 | 0 | 81.9374 | 0 | off_peak | 856.1 |  |  | 0 | 0 | 100 | 0 | 0
4009 | 804.36 | 0 | 27.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 804.36 | 0 | 0.05921 | 8.0591 | 0 | 0 | 81.9374 | 0 | off_peak | 804.36 |  |  | 0 | 0 | 100 | 0 | 0
4010 | 701.03 | 0 | 27.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 701.03 | 0 | 0.05921 | 7.7395 | 0 | 0 | 81.9374 | 0 | off_peak | 701.03 |  |  | 0 | 0 | 100 | 0 | 0
4011 | 677.68 | 0 | 27.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 677.68 | 0 | 0.05921 | 7.2794 | 0 | 0 | 81.9374 | 0 | off_peak | 677.68 |  |  | 0 | 0 | 100 | 0 | 0
4012 | 677.49 | 0 | 27.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 677.49 | 0 | 0.05921 | 6.7524 | 0 | 0 | 81.9374 | 0 | off_peak | 677.49 |  |  | 0 | 0 | 100 | 0 | 0
4013 | 684.8 | 0 | 27.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 684.8 | 0 | 0.05921 | 6.1154 | 0 | 0 | 81.9374 | 0 | off_peak | 684.8 |  |  | 0 | 0 | 100 | 0 | 0
4014 | 784.13 | 2.85 | 27.3 | 0.57235 | 0.57235 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 783.5577 | 0 | 0.05921 | 5.5239 | 0 | 0 | 81.9374 | 0.57235 | off_peak | 783.5577 |  |  | 0.07 | 0 | 99.93 | 3.1616 | 0
4015 | 759.69 | 94.8954 | 27.4 | 19.0503 | 19.0503 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 740.6397 | 0 | 0.05921 | 5.1151 | 0 | 0 | 81.9374 | 19.0503 | off_peak | 740.6397 |  |  | 2.51 | 0 | 97.49 | 97.4442 | 0
4016 | 846.16 | 241.434 | 27.5 | 48.4504 | 48.4504 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 19.0375 | 810.1086 | 0 | 0.05921 | 4.7925 | 0 | 0 | 81.9374 | 48.4504 | off_peak | 797.7096 | 0 | 100 | 5.73 | 0 | 94.27 | 232.1998 | 0
4017 | 801.8 | 373.654 | 27.5 | 74.984 | 74.984 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19.0375 | 726.816 | 0 | 0.05921 | 4.5398 | 0 | 0 | 81.9374 | 74.984 | off_peak | 726.816 |  |  | 9.35 | 0 | 90.65 | 340.4137 | 0
4018 | 807.17 | 594.211 | 27.6 | 119.2015 | 119.2015 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 30.6357 | 700.3675 | 0 | 0.05921 | 4.3984 | 0 | 0 | 81.9374 | 119.2015 | off_peak | 687.9685 | 0 | 100 | 14.77 | 0 | 85.23 | 524.2986 | 0
4019 | 800.05 | 467.294 | 27.8 | 93.6732 | 93.6732 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30.6357 | 706.3768 | 0 | 0.05921 | 4.3651 | 0 | 0 | 81.9374 | 93.6732 | off_peak | 706.3768 |  |  | 11.71 | 0 | 88.29 | 408.8973 | 0
4020 | 832.11 | 483.802 | 28.3 | 96.806 | 96.806 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 42.2338 | 747.7029 | 0 | 0.05921 | 4.4786 | 0 | 0 | 81.9374 | 96.806 | off_peak | 735.304 | 0 | 100 | 11.63 | 0 | 88.37 | 433.5529 | 0
4021 | 770.34 | 689.279 | 28.8 | 137.6696 | 137.6696 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 42.2338 | 632.6704 | 0 | 0.05921 | 4.7096 | 0 | 0 | 81.9374 | 137.6696 | off_peak | 632.6704 |  |  | 17.87 | 0 | 82.13 | 648.3691 | 0
4022 | 798.18 | 748.962 | 29.2 | 149.3716 | 140.6453 | 0 | 8.7263 | 8.7263 | 0 | 0 | 0 | 0 | 50.3966 | 657.5347 | 0 | 0.05921 | 5.1402 | 0 | 0 | 90.1002 | 140.6453 | off_peak | 657.5347 | 100 | 0 | 17.62 | 0 | 82.38 | 722.9477 | 0
4023 | 788.04 | 682.233 | 29.3 | 136.0136 | 136.0136 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50.3966 | 652.0264 | 0 | 0.05921 | 5.6522 | 0 | 0 | 90.1002 | 136.0136 | off_peak | 652.0264 |  |  | 17.26 | 0 | 82.74 | 768.7699 | 0
4024 | 730.91 | 473.693 | 29.2 | 94.4725 | 94.4725 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50.3966 | 636.4375 | 0 | 0.05921 | 6.2255 | 0 | 0 | 90.1002 | 94.4725 | off_peak | 636.4375 |  |  | 12.93 | 0 | 87.07 | 588.142 | 0
4025 | 730.27 | 43.7 | 28.9 | 8.725 | 8.725 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50.3966 | 721.545 | 0 | 0.05921 | 6.6606 | 0 | 0 | 90.1002 | 8.725 | off_peak | 721.545 |  |  | 1.19 | 0 | 98.81 | 58.1139 | 0
4026 | 677.69 | 40.3968 | 28.5 | 8.0773 | 8.0773 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50.3966 | 669.6127 | 0 | 0.05921 | 7.01 | 0 | 0 | 90.1002 | 8.0773 | off_peak | 669.6127 |  |  | 1.19 | 0 | 98.81 | 56.6215 | 0
4027 | 608.56 | 43.9791 | 28.2 | 8.8032 | 8.8032 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50.3966 | 599.7568 | 0 | 0.05921 | 6.7122 | 0 | 0 | 90.1002 | 8.8032 | off_peak | 599.7568 |  |  | 1.45 | 0 | 98.55 | 59.0886 | 0
4028 | 597.68 | 0 | 27.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50.3966 | 597.68 | 0 | 0.05921 | 6.4889 | 0 | 0 | 90.1002 | 0 | off_peak | 597.68 |  |  | 0 | 0 | 100 | 0 | 0
4029 | 582.84 | 0 | 27.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50.3966 | 582.84 | 0 | 0.05921 | 6.7026 | 0 | 0 | 90.1002 | 0 | off_peak | 582.84 |  |  | 0 | 0 | 100 | 0 | 0
4030 | 607.49 | 0 | 27.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50.3966 | 607.49 | 0 | 0.05921 | 7.1401 | 0 | 0 | 90.1002 | 0 | off_peak | 607.49 |  |  | 0 | 0 | 100 | 0 | 0
4031 | 569.34 | 0 | 27.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50.3966 | 569.34 | 0 | 0.05921 | 7.2938 | 0 | 0 | 90.1002 | 0 | off_peak | 569.34 |  |  | 0 | 0 | 100 | 0 | 0
4032 | 568.25 | 0 | 27.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50.3966 | 568.25 | 0 | 0.05921 | 7.2902 | 0 | 0 | 90.1002 | 0 | off_peak | 568.25 |  |  | 0 | 0 | 100 | 0 | 0
4033 | 600.68 | 0 | 27.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50.3966 | 600.68 | 0 | 0.05921 | 7.1994 | 0 | 0 | 90.1002 | 0 | off_peak | 600.68 |  |  | 0 | 0 | 100 | 0 | 0
4034 | 597.35 | 0 | 27.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50.3966 | 597.35 | 0 | 0.05921 | 6.828 | 0 | 0 | 90.1002 | 0 | off_peak | 597.35 |  |  | 0 | 0 | 100 | 0 | 0
4035 | 572.73 | 0 | 27.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50.3966 | 572.73 | 0 | 0.05921 | 6.5085 | 0 | 0 | 90.1002 | 0 | off_peak | 572.73 |  |  | 0 | 0 | 100 | 0 | 0
4036 | 606.88 | 0 | 27.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50.3966 | 606.88 | 0 | 0.05921 | 6.1064 | 0 | 0 | 90.1002 | 0 | off_peak | 606.88 |  |  | 0 | 0 | 100 | 0 | 0
4037 | 585.05 | 0 | 27.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50.3966 | 585.05 | 0 | 0.05921 | 5.4545 | 0 | 0 | 90.1002 | 0 | off_peak | 585.05 |  |  | 0 | 0 | 100 | 0 | 0
4038 | 664.23 | 2.85 | 27.3 | 0.57235 | 0.57235 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50.3966 | 663.6577 | 0 | 0.05921 | 4.9312 | 0 | 0 | 90.1002 | 0.57235 | off_peak | 663.6577 |  |  | 0.09 | 0 | 99.91 | 2.8224 | 0
4039 | 677.61 | 122.176 | 27.5 | 24.518 | 24.518 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 61.9947 | 665.491 | 0 | 0.05921 | 4.5218 | 0 | 0 | 90.1002 | 24.518 | off_peak | 653.092 | 0 | 100 | 3.62 | 0 | 96.38 | 110.8654 | 0
4040 | 713.02 | 237.653 | 27.6 | 47.6743 | 47.6743 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 61.9947 | 665.3457 | 0 | 0.05921 | 4.2023 | 0 | 0 | 90.1002 | 47.6743 | off_peak | 665.3457 |  |  | 6.69 | 0 | 93.31 | 200.3437 | 0
4041 | 728.59 | 504.626 | 27.7 | 101.1935 | 101.1935 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 61.9947 | 627.3965 | 0 | 0.05921 | 3.9646 | 0 | 0 | 90.1002 | 101.1935 | off_peak | 627.3965 |  |  | 13.89 | 0 | 86.11 | 401.1921 | 0
4042 | 692.99 | 529.09 | 27.7 | 106.0993 | 106.0993 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 61.9947 | 586.8907 | 0 | 0.05921 | 3.7992 | 0 | 0 | 90.1002 | 106.0993 | off_peak | 586.8907 |  |  | 15.31 | 0 | 84.69 | 403.0876 | 0
4043 | 696.48 | 676.462 | 27.6 | 135.7014 | 135.7014 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 61.9947 | 560.7786 | 0 | 0.05921 | 3.7539 | 0 | 0 | 90.1002 | 135.7014 | off_peak | 560.7786 |  |  | 19.48 | 0 | 80.52 | 509.4112 | 0
4044 | 733.7 | 732.358 | 27.5 | 146.9678 | 146.9678 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 61.9947 | 586.7322 | 0 | 0.05921 | 3.7451 | 0 | 0 | 90.1002 | 146.9678 | off_peak | 586.7322 |  |  | 20.03 | 0 | 79.97 | 550.4116 | 0
4045 | 728.76 | 581.119 | 27.4 | 116.6599 | 116.6599 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 61.9947 | 612.1001 | 0 | 0.05921 | 3.7925 | 0 | 0 | 90.1002 | 116.6599 | off_peak | 612.1001 |  |  | 16.01 | 0 | 83.99 | 442.4313 | 0
4046 | 700.43 | 733.239 | 27.3 | 147.2515 | 147.2515 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 61.9947 | 553.1785 | 0 | 0.05921 | 3.8991 | 0 | 0 | 90.1002 | 147.2515 | off_peak | 553.1785 |  |  | 21.02 | 0 | 78.98 | 574.1479 | 0
4047 | 664.38 | 683.054 | 27.2 | 137.223 | 137.223 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 73.5928 | 539.556 | 0 | 0.05921 | 4.2392 | 0 | 0 | 90.1002 | 137.223 | off_peak | 527.157 | 0 | 100 | 20.65 | 0 | 79.35 | 581.7118 | 0
4048 | 645.55 | 650.113 | 27 | 130.7 | 130.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 73.5928 | 514.85 | 0 | 0.05921 | 4.6509 | 0 | 0 | 90.1002 | 130.7 | off_peak | 514.85 |  |  | 20.25 | 0 | 79.75 | 607.8666 | 0
4049 | 668.71 | 467.832 | 26.7 | 94.1562 | 94.1562 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 73.5928 | 574.5538 | 0 | 0.05921 | 5.1875 | 0 | 0 | 90.1002 | 94.1562 | off_peak | 574.5538 |  |  | 14.08 | 0 | 85.92 | 488.4314 | 0
4050 | 562.36 | 267.619 | 26.4 | 53.9197 | 53.9197 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 73.5928 | 508.4403 | 0 | 0.05921 | 5.7726 | 0 | 0 | 90.1002 | 53.9197 | off_peak | 508.4403 |  |  | 9.59 | 0 | 90.41 | 311.2586 | 0
4051 | 575.38 | 83.421 | 26.3 | 16.8137 | 16.0129 | 0 | 0.80079 | 0.80079 | 0 | 0 | 0 | 0 | 74.3419 | 559.3671 | 0 | 0.05921 | 6.2417 | 0 | 0 | 90.8492 | 16.0129 | off_peak | 559.3671 | 100 | 0 | 2.78 | 0 | 97.22 | 99.948 | 0
4052 | 542.61 | 0 | 25.9 | 0 | 0 | 0 | 0 | 0.05172 | 0.05172 | 0 | 0 | 0 | 74.3903 | 542.6617 | 0 | 0.05921 | 6.4989 | 0 | 0 | 90.8492 | 0 | off_peak | 542.61 | 0 | 100 | 0 | 0 | 100 | 0 | 0
4053 | 542.62 | 0 | 25.7 | 0 | 0 | 0 | 0 | 0.0033404 | 0.0033404 | 0 | 0 | 0 | 74.3934 | 542.6233 | 0 | 0.05921 | 6.2014 | 0 | 0 | 90.8492 | 0 | off_peak | 542.62 | 0 | 100 | 0 | 0 | 100 | 0 | 0
4054 | 548.43 | 0 | 25.8 | 0 | 0 | 0 | 0 | 0.00021574 | 0.00021574 | 0 | 0 | 0 | 74.3936 | 548.4302 | 0 | 0.05921 | 6.3387 | 0 | 0 | 90.8492 | 0 | off_peak | 548.43 | 0 | 100 | 0 | 0 | 100 | 0 | 0
4055 | 549.91 | 0 | 25.9 | 0 | 0 | 0 | 0 | 1.4896e-05 | 1.4896e-05 | 0 | 0 | 0 | 74.3936 | 549.91 | 0 | 0.05921 | 6.7736 | 0 | 0 | 90.8492 | 0 | off_peak | 549.91 | 0 | 100 | 0 | 0 | 100 | 0 | 0
4056 | 540.47 | 0 | 26.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 540.47 | 0 | 0.05921 | 6.9076 | 0 | 0 | 90.8492 | 0 | off_peak | 540.47 |  |  | 0 | 0 | 100 | 0 | 0
4057 | 557.1 | 0 | 26.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 557.1 | 0 | 0.05921 | 6.8284 | 0 | 0 | 90.8492 | 0 | off_peak | 557.1 |  |  | 0 | 0 | 100 | 0 | 0
4058 | 560.95 | 0 | 26.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 560.95 | 0 | 0.05921 | 6.8301 | 0 | 0 | 90.8492 | 0 | off_peak | 560.95 |  |  | 0 | 0 | 100 | 0 | 0
4059 | 527.26 | 0 | 26.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 527.26 | 0 | 0.05921 | 6.5201 | 0 | 0 | 90.8492 | 0 | off_peak | 527.26 |  |  | 0 | 0 | 100 | 0 | 0
4060 | 535.66 | 0 | 26.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 535.66 | 0 | 0.05921 | 6.1687 | 0 | 0 | 90.8492 | 0 | off_peak | 535.66 |  |  | 0 | 0 | 100 | 0 | 0
4061 | 572.34 | 0 | 26.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 572.34 | 0 | 0.05921 | 5.4392 | 0 | 0 | 90.8492 | 0 | off_peak | 572.34 |  |  | 0 | 0 | 100 | 0 | 0
4062 | 645.99 | 4.75 | 26.8 | 0.95564 | 0.95564 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 645.0344 | 0 | 0.05921 | 4.9184 | 0 | 0 | 90.8492 | 0.95564 | off_peak | 645.0344 |  |  | 0.15 | 0 | 99.85 | 4.7003 | 0
4063 | 740.92 | 130.071 | 27 | 26.1497 | 26.1497 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 714.7703 | 0 | 0.05921 | 4.4649 | 0 | 0 | 90.8492 | 26.1497 | off_peak | 714.7703 |  |  | 3.53 | 0 | 96.47 | 116.7566 | 0
4064 | 776.91 | 327.924 | 27.2 | 65.8787 | 65.8787 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 711.0313 | 0 | 0.05921 | 4.1771 | 0 | 0 | 90.8492 | 65.8787 | off_peak | 711.0313 |  |  | 8.48 | 0 | 91.52 | 275.1815 | 0
4065 | 869.38 | 496.745 | 27.3 | 99.758 | 99.758 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 769.622 | 0 | 0.05921 | 4.0289 | 0 | 0 | 90.8492 | 99.758 | off_peak | 769.622 |  |  | 11.47 | 0 | 88.53 | 401.9162 | 0
4066 | 885.03 | 531.809 | 27.5 | 106.7221 | 106.7221 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 778.3079 | 0 | 0.05921 | 4.011 | 0 | 0 | 90.8492 | 106.7221 | off_peak | 778.3079 |  |  | 12.06 | 0 | 87.94 | 428.064 | 0
4067 | 841.33 | 684.076 | 27.6 | 137.2288 | 137.2288 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 704.1012 | 0 | 0.05921 | 4.1413 | 0 | 0 | 90.8492 | 137.2288 | off_peak | 704.1012 |  |  | 16.31 | 0 | 83.69 | 568.3123 | 0
4068 | 853.86 | 663.087 | 27.9 | 132.8733 | 132.8733 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 720.9867 | 0 | 0.05921 | 4.3193 | 0 | 0 | 90.8492 | 132.8733 | off_peak | 720.9867 |  |  | 15.56 | 0 | 84.44 | 573.9252 | 0
4069 | 925.89 | 502.443 | 28.1 | 100.6092 | 100.6092 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 825.2808 | 0 | 0.088511 | 4.6102 | 0 | 0 | 90.8492 | 100.6092 | on_peak | 825.2808 |  |  | 10.87 | 0 | 89.13 | 463.8321 | 0
4070 | 915.74 | 835.978 | 28.3 | 167.2744 | 167.2744 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 748.4656 | 0 | 0.088511 | 5.0466 | 0 | 0 | 90.8492 | 167.2744 | on_peak | 748.4656 |  |  | 18.27 | 0 | 81.73 | 844.1687 | 0
4071 | 922.91 | 688.598 | 28.4 | 137.7343 | 137.7343 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 785.1757 | 0 | 0.088511 | 5.5376 | 0 | 0 | 90.8492 | 137.7343 | on_peak | 785.1757 |  |  | 14.92 | 0 | 85.08 | 762.7238 | 0
4072 | 889.22 | 663.967 | 28.4 | 132.8076 | 132.8076 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 756.4124 | 0 | 0.088511 | 6.1158 | 0 | 0 | 90.8492 | 132.8076 | on_peak | 756.4124 |  |  | 14.94 | 0 | 85.06 | 812.2291 | 0
4073 | 848.34 | 445.047 | 28.4 | 89.0189 | 89.0189 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 759.3211 | 0 | 0.088511 | 6.6109 | 0 | 0 | 90.8492 | 89.0189 | on_peak | 759.3211 |  |  | 10.49 | 0 | 89.51 | 588.4934 | 0
4074 | 855.94 | 278.893 | 28.3 | 55.8049 | 55.8049 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 800.1351 | 0 | 0.088511 | 7.1543 | 0 | 0 | 90.8492 | 55.8049 | on_peak | 800.1351 |  |  | 6.52 | 0 | 93.48 | 399.2437 | 0
4075 | 836.07 | 89.1898 | 28.2 | 17.8529 | 17.8529 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 818.2171 | 0 | 0.088511 | 7.611 | 0 | 0 | 90.8492 | 17.8529 | on_peak | 818.2171 |  |  | 2.14 | 0 | 97.86 | 135.879 | 0
4076 | 792.01 | 0 | 27.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 792.01 | 0 | 0.088511 | 7.7179 | 0 | 0 | 90.8492 | 0 | on_peak | 792.01 |  |  | 0 | 0 | 100 | 0 | 0
4077 | 838.83 | 0 | 27.7 | 0 | 0 | 0 | 0 | 0 | 0 | 62.63 | 62.63 | 0 | 7.4394 | 776.2 | 0 | 0.088511 | 7.5283 | 0 | 0 | 90.8492 | 0 | on_peak | 776.2 |  |  | 0 | 7.47 | 92.53 | 0 | 0
4078 | 764.62 | 0 | 27.6 | 0 | 0 | 0 | 0 | 8.7263 | 8.7263 | 0 | 0 | 0 | 15.6021 | 773.3463 | 0 | 0.05921 | 7.4473 | 0 | 0 | 90.8492 | 0 | off_peak | 764.62 | 0 | 100 | 0 | 0 | 100 | 0 | 0
4079 | 846 | 0 | 27.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15.6021 | 846 | 0 | 0.05921 | 7.3512 | 0 | 0 | 90.8492 | 0 | off_peak | 846 |  |  | 0 | 0 | 100 | 0 | 0
4080 | 809.66 | 0 | 27 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15.6021 | 809.66 | 0 | 0.05921 | 7.4048 | 0 | 0 | 90.8492 | 0 | off_peak | 809.66 |  |  | 0 | 0 | 100 | 0 | 0
4081 | 813.29 | 0 | 26.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15.6021 | 813.29 | 0 | 0.05921 | 7.2494 | 0 | 0 | 90.8492 | 0 | off_peak | 813.29 |  |  | 0 | 0 | 100 | 0 | 0
4082 | 675.8 | 0 | 26.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15.6021 | 675.8 | 0 | 0.05921 | 6.9722 | 0 | 0 | 90.8492 | 0 | off_peak | 675.8 |  |  | 0 | 0 | 100 | 0 | 0
4083 | 665.35 | 0 | 26.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15.6021 | 665.35 | 0 | 0.05921 | 6.5072 | 0 | 0 | 90.8492 | 0 | off_peak | 665.35 |  |  | 0 | 0 | 100 | 0 | 0
4084 | 625.1 | 0 | 26 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 27.2003 | 637.4989 | 0 | 0.05921 | 5.8936 | 0 | 0 | 90.8492 | 0 | off_peak | 625.1 | 0 | 100 | 0 | 0 | 100 | 0 | 0
4085 | 696.51 | 0 | 26 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 38.7984 | 708.9089 | 0 | 0.05921 | 5.2115 | 0 | 0 | 90.8492 | 0 | off_peak | 696.51 | 0 | 100 | 0 | 0 | 100 | 0 | 0
4086 | 737.95 | 0 | 26.3 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 50.3966 | 750.3489 | 0 | 0.05921 | 4.6231 | 0 | 0 | 90.8492 | 0 | off_peak | 737.95 | 0 | 100 | 0 | 0 | 100 | 0 | 0
4087 | 788.31 | 96.3583 | 26.9 | 19.3791 | 6.9801 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 0 | 61.9947 | 781.3299 | 0 | 0.05921 | 4.1964 | 0 | 0 | 102.4474 | 6.9801 | off_peak | 781.3299 | 100 | 0 | 0.89 | 0 | 99.11 | 29.2917 | 0
4088 | 890.88 | 287.078 | 27.4 | 57.631 | 45.2321 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 0 | 73.5928 | 845.6479 | 0 | 0.05921 | 3.8617 | 0 | 0 | 114.0455 | 45.2321 | off_peak | 845.6479 | 100 | 0 | 5.08 | 0 | 94.92 | 174.6721 | 0
4089 | 924.07 | 531.182 | 27.9 | 106.4414 | 106.4414 | 0 | 0 | 0.80079 | 0.80079 | 0 | 0 | 0 | 74.3419 | 818.4294 | 0 | 0.05921 | 3.6459 | 0 | 0 | 114.0455 | 106.4414 | off_peak | 817.6286 | 0 | 100 | 11.52 | 0 | 88.48 | 388.07 | 0
4090 | 963.12 | 673.658 | 28.3 | 134.7951 | 134.7951 | 0 | 0 | 0.05172 | 0.05172 | 0 | 0 | 0 | 74.3903 | 828.3766 | 0 | 0.05921 | 3.6087 | 0 | 0 | 114.0455 | 134.7951 | off_peak | 828.3249 | 0 | 100 | 14 | 0 | 86 | 486.4306 | 0
4091 | 884.19 | 831.719 | 28.7 | 166.1797 | 166.1797 | 0 | 0 | 0.0033404 | 0.0033404 | 0 | 0 | 0 | 74.3934 | 718.0136 | 0 | 0.05921 | 3.7241 | 0 | 0 | 114.0455 | 166.1797 | off_peak | 718.0103 | 0 | 100 | 18.79 | 0 | 81.21 | 618.8758 | 0
4092 | 943.28 | 796.296 | 29 | 158.9279 | 158.9279 | 0 | 0 | 0.00021574 | 0.00021574 | 0 | 0 | 0 | 74.3936 | 784.3523 | 0 | 0.05921 | 4.0118 | 0 | 0 | 114.0455 | 158.9279 | off_peak | 784.3521 | 0 | 100 | 16.85 | 0 | 83.15 | 637.5948 | 0
4093 | 936.38 | 807.778 | 29.2 | 161.1018 | 161.1018 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 775.2782 | 0 | 0.088511 | 4.3549 | 0 | 0 | 114.0455 | 161.1018 | on_peak | 775.2782 |  |  | 17.2 | 0 | 82.8 | 701.5851 | 0
4094 | 973.87 | 834.637 | 29.2 | 166.4585 | 166.4585 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 807.4115 | 0 | 0.088511 | 4.6076 | 0 | 0 | 114.0455 | 166.4585 | on_peak | 807.4115 |  |  | 17.09 | 0 | 82.91 | 766.9757 | 0
4095 | 948.93 | 759.168 | 29.2 | 151.4071 | 151.4071 | 0 | 0 | 0 | 0 | 62.63 | 62.63 | 0 | 7.4394 | 734.8929 | 0 | 0.088511 | 5.0335 | 0 | 0 | 114.0455 | 151.4071 | on_peak | 734.8929 |  |  | 15.96 | 6.6 | 77.44 | 762.1008 | 0
4096 | 888.12 | 622.706 | 29.1 | 124.2368 | 124.2368 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 763.8832 | 0 | 0.088511 | 5.3687 | 0 | 0 | 114.0455 | 124.2368 | on_peak | 763.8832 |  |  | 13.99 | 0 | 86.01 | 666.9897 | 0
4097 | 875.13 | 370.913 | 28.9 | 74.0553 | 74.0553 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 801.0747 | 0 | 0.088511 | 5.8385 | 0 | 0 | 114.0455 | 74.0553 | on_peak | 801.0747 |  |  | 8.46 | 0 | 91.54 | 432.3723 | 0
4098 | 834.4 | 267.307 | 28.5 | 53.4476 | 53.4476 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 780.9524 | 0 | 0.088511 | 6.2724 | 0 | 0 | 114.0455 | 53.4476 | on_peak | 780.9524 |  |  | 6.41 | 0 | 93.59 | 335.2436 | 0
4099 | 839.03 | 86.4738 | 28.3 | 17.3029 | 17.3029 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 821.7271 | 0 | 0.088511 | 6.5888 | 0 | 0 | 114.0455 | 17.3029 | on_peak | 821.7271 |  |  | 2.06 | 0 | 97.94 | 114.0049 | 0
4100 | 858.12 | 0 | 27.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 858.12 | 0 | 0.088511 | 7.0618 | 0 | 0 | 114.0455 | 0 | on_peak | 858.12 |  |  | 0 | 0 | 100 | 0 | 0
4101 | 793.81 | 0 | 27.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 793.81 | 0 | 0.088511 | 7.4157 | 0 | 0 | 114.0455 | 0 | on_peak | 793.81 |  |  | 0 | 0 | 100 | 0 | 0
4102 | 795.51 | 0 | 27.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 795.51 | 0 | 0.05921 | 7.3984 | 0 | 0 | 114.0455 | 0 | off_peak | 795.51 |  |  | 0 | 0 | 100 | 0 | 0
4103 | 735.41 | 0 | 27.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 735.41 | 0 | 0.05921 | 7.0532 | 0 | 0 | 114.0455 | 0 | off_peak | 735.41 |  |  | 0 | 0 | 100 | 0 | 0
4104 | 685.27 | 0 | 27.3 | 0 | 0 | 0 | 0 | 8.7263 | 8.7263 | 0 | 0 | 0 | 15.6021 | 693.9963 | 0 | 0.05921 | 7.022 | 0 | 0 | 114.0455 | 0 | off_peak | 685.27 | 0 | 100 | 0 | 0 | 100 | 0 | 0
4105 | 638.79 | 0 | 27.2 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 27.2003 | 651.1889 | 0 | 0.05921 | 6.9096 | 0 | 0 | 114.0455 | 0 | off_peak | 638.79 | 0 | 100 | 0 | 0 | 100 | 0 | 0
4106 | 505.29 | 0 | 27.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27.2003 | 505.29 | 0 | 0.05921 | 6.6956 | 0 | 0 | 114.0455 | 0 | off_peak | 505.29 |  |  | 0 | 0 | 100 | 0 | 0
4107 | 504.51 | 0 | 27 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 38.7984 | 516.9089 | 0 | 0.05921 | 6.2018 | 0 | 0 | 114.0455 | 0 | off_peak | 504.51 | 0 | 100 | 0 | 0 | 100 | 0 | 0
4108 | 473.1 | 0 | 26.9 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 50.3966 | 485.4989 | 0 | 0.05921 | 5.5798 | 0 | 0 | 114.0455 | 0 | off_peak | 473.1 | 0 | 100 | 0 | 0 | 100 | 0 | 0
4109 | 506.64 | 0 | 26.9 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 61.9947 | 519.0389 | 0 | 0.05921 | 4.8538 | 0 | 0 | 114.0455 | 0 | off_peak | 506.64 | 0 | 100 | 0 | 0 | 100 | 0 | 0
4110 | 628.86 | 0 | 27.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 61.9947 | 628.86 | 0 | 0.05921 | 4.2946 | 0 | 0 | 114.0455 | 0 | off_peak | 628.86 |  |  | 0 | 0 | 100 | 0 | 0
4111 | 752.98 | 122.514 | 27.5 | 24.5858 | 12.1869 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 0 | 73.5928 | 740.7931 | 0 | 0.05921 | 3.8792 | 0 | 0 | 125.6437 | 12.1869 | off_peak | 740.7931 | 100 | 0 | 1.62 | 0 | 98.38 | 47.2751 | 0
4112 | 760.23 | 313.494 | 27.8 | 62.8426 | 62.8426 | 0 | 0 | 0.80079 | 0.80079 | 0 | 0 | 0 | 74.3419 | 698.1882 | 0 | 0.05921 | 3.5518 | 0 | 0 | 125.6437 | 62.8426 | off_peak | 697.3874 | 0 | 100 | 8.27 | 0 | 91.73 | 223.2015 | 0
4113 | 800.66 | 510.201 | 28.1 | 102.1627 | 102.1627 | 0 | 0 | 0.05172 | 0.05172 | 0 | 0 | 0 | 74.3903 | 698.549 | 0 | 0.05921 | 3.362 | 0 | 0 | 125.6437 | 102.1627 | off_peak | 698.4973 | 0 | 100 | 12.76 | 0 | 87.24 | 343.4712 | 0
4114 | 838.36 | 685.176 | 28.3 | 137.0998 | 137.0998 | 0 | 0 | 0.0033404 | 0.0033404 | 0 | 0 | 0 | 74.3934 | 701.2635 | 0 | 0.05921 | 3.323 | 0 | 0 | 125.6437 | 137.0998 | off_peak | 701.2602 | 0 | 100 | 16.35 | 0 | 83.65 | 455.5834 | 0
4115 | 760.71 | 815.151 | 28.5 | 162.9882 | 162.9882 | 0 | 0 | 0.00021574 | 0.00021574 | 0 | 0 | 0 | 74.3936 | 597.722 | 0 | 0.05921 | 3.492 | 0 | 0 | 125.6437 | 162.9882 | off_peak | 597.7218 | 0 | 100 | 21.43 | 0 | 78.57 | 569.1484 | 0
4116 | 847.92 | 881.527 | 28.7 | 176.1315 | 176.1315 | 0 | 0 | 1.3934e-05 | 1.3934e-05 | 0 | 0 | 0 | 74.3936 | 671.7885 | 0 | 0.05921 | 3.7036 | 0 | 0 | 125.6437 | 176.1315 | off_peak | 671.7885 | 0 | 100 | 20.77 | 0 | 79.23 | 652.314 | 0
4117 | 773.19 | 881.696 | 29 | 175.9724 | 175.9724 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 597.2176 | 0 | 0.088511 | 3.9704 | 0 | 0 | 125.6437 | 175.9724 | on_peak | 597.2176 |  |  | 22.76 | 0 | 77.24 | 698.6803 | 0
4118 | 820.51 | 717.134 | 29.1 | 143.0762 | 143.0762 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 677.4338 | 0 | 0.088511 | 4.2413 | 0 | 0 | 125.6437 | 143.0762 | on_peak | 677.4338 |  |  | 17.44 | 0 | 82.56 | 606.8353 | 0
4119 | 849.8 | 700.421 | 29.2 | 139.6907 | 139.6907 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 710.1093 | 0 | 0.088511 | 4.612 | 0 | 0 | 125.6437 | 139.6907 | on_peak | 710.1093 |  |  | 16.44 | 0 | 83.56 | 644.2594 | 0
4120 | 737.58 | 543.09 | 29.2 | 108.3129 | 108.3129 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 629.2671 | 0 | 0.088511 | 4.9625 | 0 | 0 | 125.6437 | 108.3129 | on_peak | 629.2671 |  |  | 14.68 | 0 | 85.32 | 537.4995 | 0
4121 | 771.67 | 411.527 | 29 | 82.1342 | 82.1342 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 689.5358 | 0 | 0.088511 | 5.3271 | 0 | 0 | 125.6437 | 82.1342 | on_peak | 689.5358 |  |  | 10.64 | 0 | 89.36 | 437.5335 | 0
4122 | 869.4 | 182.32 | 28.7 | 36.428 | 36.428 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 832.972 | 0 | 0.088511 | 5.8592 | 0 | 0 | 125.6437 | 36.428 | on_peak | 832.972 |  |  | 4.19 | 0 | 95.81 | 213.4383 | 0
4123 | 843.95 | 44.985 | 28.6 | 8.9914 | 8.9914 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 834.9586 | 0 | 0.088511 | 6.552 | 0 | 0 | 125.6437 | 8.9914 | on_peak | 834.9586 |  |  | 1.07 | 0 | 98.93 | 58.9119 | 0
4124 | 891.27 | 0 | 28.2 | 0 | 0 | 0 | 0 | 0 | 0 | 62.63 | 62.63 | 0 | 7.4394 | 828.64 | 0 | 0.088511 | 6.9532 | 62.63 | 0 | 58.6894 | 62.63 | on_peak | 828.64 |  |  | 0 | 7.03 | 92.97 | 435.4816 | 0
4125 | 831.55 | 0 | 28 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 831.55 | 0 | 0.088511 | 7.1403 | 0 | 0 | 58.6894 | 0 | on_peak | 831.55 |  |  | 0 | 0 | 100 | 0 | 0
4126 | 790.79 | 0 | 27.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 790.79 | 0 | 0.05921 | 7.1853 | 0 | 0 | 58.6894 | 0 | off_peak | 790.79 |  |  | 0 | 0 | 100 | 0 | 0
4127 | 855.91 | 0 | 27.6 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 19.0375 | 868.3089 | 0 | 0.05921 | 7.3646 | 0 | 0 | 58.6894 | 0 | off_peak | 855.91 | 0 | 100 | 0 | 0 | 100 | 0 | 0
4128 | 794.11 | 0 | 27.3 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 30.6357 | 806.5089 | 0 | 0.05921 | 7.3881 | 0 | 0 | 58.6894 | 0 | off_peak | 794.11 | 0 | 100 | 0 | 0 | 100 | 0 | 0
4129 | 702.75 | 0 | 27.1 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 42.2338 | 715.1489 | 0 | 0.05921 | 7.0622 | 0 | 0 | 58.6894 | 0 | off_peak | 702.75 | 0 | 100 | 0 | 0 | 100 | 0 | 0
4130 | 636 | 0 | 27.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 42.2338 | 636 | 0 | 0.05921 | 6.7789 | 0 | 0 | 58.6894 | 0 | off_peak | 636 |  |  | 0 | 0 | 100 | 0 | 0
4131 | 625.99 | 0 | 27 | 0 | 0 | 0 | 0 | 8.7263 | 8.7263 | 0 | 0 | 0 | 50.3966 | 634.7163 | 0 | 0.05921 | 6.3594 | 0 | 0 | 58.6894 | 0 | off_peak | 625.99 | 0 | 100 | 0 | 0 | 100 | 0 | 0
4132 | 619.77 | 0 | 27 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 61.9947 | 632.1689 | 0 | 0.05921 | 5.8153 | 0 | 0 | 58.6894 | 0 | off_peak | 619.77 | 0 | 100 | 0 | 0 | 100 | 0 | 0
4133 | 635.1 | 0 | 27 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 61.9947 | 635.1 | 0 | 0.05921 | 5.1954 | 0 | 0 | 58.6894 | 0 | off_peak | 635.1 |  |  | 0 | 0 | 100 | 0 | 0
4134 | 718.42 | 0 | 27.3 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 73.5928 | 730.8189 | 0 | 0.05921 | 4.5712 | 0 | 0 | 58.6894 | 0 | off_peak | 718.42 | 0 | 100 | 0 | 0 | 100 | 0 | 0
4135 | 776.86 | 122.668 | 27.9 | 24.5809 | 23.7801 | 0 | 0.80079 | 0.80079 | 0 | 0 | 0 | 0 | 74.3419 | 753.0799 | 0 | 0.05921 | 4.1016 | 0 | 0 | 59.4385 | 23.7801 | off_peak | 753.0799 | 100 | 0 | 3.06 | 0 | 96.94 | 97.5356 | 0
4136 | 833.95 | 311.888 | 28.3 | 62.407 | 62.407 | 0 | 0 | 0.05172 | 0.05172 | 0 | 0 | 0 | 74.3903 | 771.5947 | 0 | 0.05921 | 3.7859 | 0 | 0 | 59.4385 | 62.407 | off_peak | 771.543 | 0 | 100 | 7.48 | 0 | 92.52 | 236.2693 | 0
4137 | 877.6 | 352.853 | 28.6 | 70.5267 | 70.5267 | 0 | 0 | 0.0033404 | 0.0033404 | 0 | 0 | 0 | 74.3934 | 807.0766 | 0 | 0.05921 | 3.607 | 0 | 0 | 59.4385 | 70.5267 | off_peak | 807.0733 | 0 | 100 | 8.04 | 0 | 91.96 | 254.3879 | 0
4138 | 851.02 | 628.528 | 28.8 | 125.5358 | 125.5358 | 0 | 0 | 0.00021574 | 0.00021574 | 0 | 0 | 0 | 74.3936 | 725.4844 | 0 | 0.05921 | 3.5521 | 0 | 0 | 59.4385 | 125.5358 | off_peak | 725.4842 | 0 | 100 | 14.75 | 0 | 85.25 | 445.9204 | 0
4139 | 820.7 | 768.751 | 28.9 | 153.4864 | 153.4864 | 0 | 0 | 1.3934e-05 | 1.3934e-05 | 0 | 0 | 0 | 74.3936 | 667.2136 | 0 | 0.05921 | 3.6919 | 0 | 0 | 59.4385 | 153.4864 | off_peak | 667.2136 | 0 | 100 | 18.7 | 0 | 81.3 | 566.6491 | 0
4140 | 907.4 | 770.935 | 29.1 | 153.8101 | 153.8101 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 753.5899 | 0 | 0.05921 | 3.9714 | 0 | 0 | 59.4385 | 153.8101 | off_peak | 753.5899 |  |  | 16.95 | 0 | 83.05 | 610.8468 | 0
4141 | 842.7 | 934.765 | 29.2 | 186.4278 | 186.4278 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 656.2722 | 0 | 0.088511 | 4.315 | 0 | 0 | 59.4385 | 186.4278 | on_peak | 656.2722 |  |  | 22.12 | 0 | 77.88 | 804.4431 | 0
4142 | 876.5 | 889.959 | 29.2 | 177.4918 | 177.4918 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 699.0082 | 0 | 0.088511 | 4.5968 | 0 | 0 | 59.4385 | 177.4918 | on_peak | 699.0082 |  |  | 20.25 | 0 | 79.75 | 815.8924 | 0
4143 | 915.12 | 764.044 | 29.3 | 152.3239 | 152.3239 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 762.7961 | 0 | 0.088511 | 5.0404 | 0 | 0 | 59.4385 | 152.3239 | on_peak | 762.7961 |  |  | 16.65 | 0 | 83.35 | 767.7734 | 0
4144 | 844.78 | 540.806 | 29.1 | 107.8968 | 107.8968 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 736.8832 | 0 | 0.088511 | 5.5311 | 0 | 0 | 59.4385 | 107.8968 | on_peak | 736.8832 |  |  | 12.77 | 0 | 87.23 | 596.7839 | 0
4145 | 821.13 | 342.031 | 28.8 | 68.3138 | 68.3138 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 752.8162 | 0 | 0.088511 | 6.0193 | 0 | 0 | 59.4385 | 68.3138 | on_peak | 752.8162 |  |  | 8.32 | 0 | 91.68 | 411.2037 | 0
4146 | 851.5 | 40.6809 | 28.3 | 8.14 | 8.14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 843.36 | 0 | 0.088511 | 6.3901 | 0 | 0 | 59.4385 | 8.14 | on_peak | 843.36 |  |  | 0.96 | 0 | 99.04 | 52.0157 | 0
4147 | 857.51 | 20.9 | 28.1 | 4.185 | 4.185 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 853.325 | 0 | 0.088511 | 6.8761 | 0 | 0 | 59.4385 | 4.185 | on_peak | 853.325 |  |  | 0.49 | 0 | 99.51 | 28.7766 | 0
4148 | 862.44 | 0 | 27.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 862.44 | 0 | 0.088511 | 7.1666 | 0 | 0 | 59.4385 | 0 | on_peak | 862.44 |  |  | 0 | 0 | 100 | 0 | 0
4149 | 851.67 | 0 | 26.9 | 0 | 0 | 0 | 0 | 0 | 0 | 62.63 | 62.63 | 0 | 7.4394 | 789.04 | 0 | 0.088511 | 7.4251 | 0 | 0 | 59.4385 | 0 | on_peak | 789.04 |  |  | 0 | 7.35 | 92.65 | 0 | 0
4150 | 773.88 | 0 | 26.7 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 19.0375 | 786.2789 | 0 | 0.05921 | 7.6188 | 0 | 0 | 59.4385 | 0 | off_peak | 773.88 | 0 | 100 | 0 | 0 | 100 | 0 | 0
4151 | 860.78 | 0 | 26.7 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 30.6357 | 873.1789 | 0 | 0.05921 | 7.4994 | 0 | 0 | 59.4385 | 0 | off_peak | 860.78 | 0 | 100 | 0 | 0 | 100 | 0 | 0
4152 | 835.83 | 0 | 26.7 | 0 | 0 | 0 | 0 | 8.7263 | 8.7263 | 0 | 0 | 0 | 38.7984 | 844.5563 | 0 | 0.05921 | 7.472 | 0 | 0 | 59.4385 | 0 | off_peak | 835.83 | 0 | 100 | 0 | 0 | 100 | 0 | 0
4153 | 765.45 | 0 | 26.8 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 50.3966 | 777.8489 | 0 | 0.05921 | 7.4045 | 0 | 0 | 59.4385 | 0 | off_peak | 765.45 | 0 | 100 | 0 | 0 | 100 | 0 | 0
4154 | 638.99 | 0 | 26.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50.3966 | 638.99 | 0 | 0.05921 | 7.3886 | 0 | 0 | 59.4385 | 0 | off_peak | 638.99 |  |  | 0 | 0 | 100 | 0 | 0
4155 | 620.05 | 0 | 26.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50.3966 | 620.05 | 0 | 0.05921 | 7.0565 | 0 | 0 | 59.4385 | 0 | off_peak | 620.05 |  |  | 0 | 0 | 100 | 0 | 0
4156 | 612 | 0 | 27 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50.3966 | 612 | 0 | 0.05921 | 6.5659 | 0 | 0 | 59.4385 | 0 | off_peak | 612 |  |  | 0 | 0 | 100 | 0 | 0
4157 | 640.94 | 0 | 27.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50.3966 | 640.94 | 0 | 0.05921 | 5.8337 | 0 | 0 | 59.4385 | 0 | off_peak | 640.94 |  |  | 0 | 0 | 100 | 0 | 0
4158 | 690.76 | 0 | 27.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50.3966 | 690.76 | 0 | 0.05921 | 5.2312 | 0 | 0 | 59.4385 | 0 | off_peak | 690.76 |  |  | 0 | 0 | 100 | 0 | 0
4159 | 739.27 | 119.408 | 27.8 | 23.9364 | 11.5374 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 0 | 61.9947 | 727.7326 | 0 | 0.05921 | 4.7492 | 0 | 0 | 71.0366 | 11.5374 | off_peak | 727.7326 | 100 | 0 | 1.56 | 0 | 98.44 | 54.7937 | 0
4160 | 795.73 | 310.986 | 28.2 | 62.2492 | 62.2492 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 73.5928 | 745.8797 | 0 | 0.05921 | 4.441 | 0 | 0 | 71.0366 | 62.2492 | off_peak | 733.4808 | 0 | 100 | 7.82 | 0 | 92.18 | 276.4495 | 0
4161 | 817.24 | 499.348 | 28.5 | 99.8439 | 99.8439 | 0 | 0 | 0.80079 | 0.80079 | 0 | 0 | 0 | 74.3419 | 718.1969 | 0 | 0.05921 | 4.2799 | 0 | 0 | 71.0366 | 99.8439 | off_peak | 717.3961 | 0 | 100 | 12.22 | 0 | 87.78 | 427.32 | 0
4162 | 868.81 | 452.823 | 28.7 | 90.4753 | 90.4753 | 0 | 0 | 0.05172 | 0.05172 | 0 | 0 | 0 | 74.3903 | 778.3865 | 0 | 0.05921 | 4.2701 | 0 | 0 | 71.0366 | 90.4753 | off_peak | 778.3347 | 0 | 100 | 10.41 | 0 | 89.59 | 386.3382 | 0
4163 | 852.39 | 290.795 | 29 | 58.038 | 58.038 | 0 | 0 | 0.0033404 | 0.0033404 | 0 | 0 | 0 | 74.3934 | 794.3553 | 0 | 0.05921 | 4.4164 | 0 | 0 | 71.0366 | 58.038 | off_peak | 794.352 | 0 | 100 | 6.81 | 0 | 93.19 | 256.3174 | 0
4164 | 904.83 | 395.994 | 29.2 | 78.9763 | 78.9763 | 0 | 0 | 0.00021574 | 0.00021574 | 0 | 0 | 0 | 74.3936 | 825.8539 | 0 | 0.05921 | 4.5957 | 0 | 0 | 71.0366 | 78.9763 | off_peak | 825.8537 | 0 | 100 | 8.73 | 0 | 91.27 | 362.9497 | 0
4165 | 870.69 | 580.254 | 29.3 | 115.6825 | 115.6825 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 755.0075 | 0 | 0.088511 | 4.7964 | 0 | 0 | 71.0366 | 115.6825 | on_peak | 755.0075 |  |  | 13.29 | 0 | 86.71 | 554.8552 | 0
4166 | 825.95 | 843.709 | 29.4 | 168.1448 | 168.1448 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 657.8052 | 0 | 0.088511 | 5.102 | 0 | 0 | 71.0366 | 168.1448 | on_peak | 657.8052 |  |  | 20.36 | 0 | 79.64 | 857.8782 | 0
4167 | 847.66 | 750.171 | 29.5 | 149.4487 | 149.4487 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 698.2113 | 0 | 0.088511 | 5.5828 | 0 | 0 | 71.0366 | 149.4487 | on_peak | 698.2113 |  |  | 17.63 | 0 | 82.37 | 834.3377 | 0
4168 | 785.6 | 396.838 | 29.4 | 79.0868 | 79.0868 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 706.5132 | 0 | 0.088511 | 6.0128 | 0 | 0 | 71.0366 | 79.0868 | on_peak | 706.5132 |  |  | 10.07 | 0 | 89.93 | 475.5324 | 0
4169 | 830.9 | 76.915 | 29.1 | 15.3454 | 15.3454 | 0 | 0 | 0 | 0 | 62.63 | 62.63 | 0 | 7.4394 | 752.9246 | 0 | 0.088511 | 6.33 | 0 | 0 | 71.0366 | 15.3454 | on_peak | 752.9246 |  |  | 1.85 | 7.54 | 90.62 | 97.1361 | 0
4170 | 824.82 | 222.347 | 28.7 | 44.4255 | 44.4255 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 780.3945 | 0 | 0.088511 | 6.7499 | 0 | 0 | 71.0366 | 44.4255 | on_peak | 780.3945 |  |  | 5.39 | 0 | 94.61 | 299.8674 | 0
4171 | 765.44 | 60.8908 | 28.5 | 12.175 | 12.175 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 753.265 | 0 | 0.088511 | 7.0011 | 0 | 0 | 71.0366 | 12.175 | on_peak | 753.265 |  |  | 1.59 | 0 | 98.41 | 85.2391 | 0
4172 | 803.38 | 0 | 27.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 803.38 | 0 | 0.088511 | 7.3356 | 0 | 0 | 71.0366 | 0 | on_peak | 803.38 |  |  | 0 | 0 | 100 | 0 | 0
4173 | 803.45 | 0 | 27.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 803.45 | 0 | 0.088511 | 7.4092 | 0 | 0 | 71.0366 | 0 | on_peak | 803.45 |  |  | 0 | 0 | 100 | 0 | 0
4174 | 778.71 | 0 | 27.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 778.71 | 0 | 0.05921 | 7.6176 | 0 | 0 | 71.0366 | 0 | off_peak | 778.71 |  |  | 0 | 0 | 100 | 0 | 0
4175 | 761.35 | 0 | 27.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 761.35 | 0 | 0.05921 | 7.9207 | 0 | 0 | 71.0366 | 0 | off_peak | 761.35 |  |  | 0 | 0 | 100 | 0 | 0
4176 | 798.84 | 0 | 27.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 798.84 | 0 | 0.05921 | 7.9746 | 0 | 0 | 71.0366 | 0 | off_peak | 798.84 |  |  | 0 | 0 | 100 | 0 | 0
4177 | 689.12 | 0 | 27.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 689.12 | 0 | 0.05921 | 7.7717 | 0 | 0 | 71.0366 | 0 | off_peak | 689.12 |  |  | 0 | 0 | 100 | 0 | 0
4178 | 604.72 | 0 | 27.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 604.72 | 0 | 0.05921 | 7.5479 | 0 | 0 | 71.0366 | 0 | off_peak | 604.72 |  |  | 0 | 0 | 100 | 0 | 0
4179 | 625.21 | 0 | 27.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 625.21 | 0 | 0.05921 | 7.1332 | 0 | 0 | 71.0366 | 0 | off_peak | 625.21 |  |  | 0 | 0 | 100 | 0 | 0
4180 | 582.66 | 0 | 27.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 582.66 | 0 | 0.05921 | 6.5265 | 0 | 0 | 71.0366 | 0 | off_peak | 582.66 |  |  | 0 | 0 | 100 | 0 | 0
4181 | 608.7 | 0 | 27.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 608.7 | 0 | 0.05921 | 6.0092 | 0 | 0 | 71.0366 | 0 | off_peak | 608.7 |  |  | 0 | 0 | 100 | 0 | 0
4182 | 667.6 | 0 | 27.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 667.6 | 0 | 0.05921 | 5.382 | 0 | 0 | 71.0366 | 0 | off_peak | 667.6 |  |  | 0 | 0 | 100 | 0 | 0
4183 | 711.75 | 126.166 | 28.2 | 25.2543 | 25.2543 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 19.0375 | 698.8946 | 0 | 0.05921 | 4.9281 | 0 | 0 | 71.0366 | 25.2543 | off_peak | 686.4957 | 0 | 100 | 3.55 | 0 | 96.45 | 124.4562 | 0
4184 | 745.1 | 321.185 | 28.5 | 64.2205 | 64.2205 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19.0375 | 680.8795 | 0 | 0.05921 | 4.5546 | 0 | 0 | 71.0366 | 64.2205 | off_peak | 680.8795 |  |  | 8.62 | 0 | 91.38 | 292.5002 | 0
4185 | 819.68 | 518.602 | 28.7 | 103.6181 | 103.6181 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19.0375 | 716.0619 | 0 | 0.05921 | 4.2774 | 0 | 0 | 71.0366 | 103.6181 | off_peak | 716.0619 |  |  | 12.64 | 0 | 87.36 | 443.2161 | 0
4186 | 757.76 | 290.348 | 28.9 | 57.97 | 57.97 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19.0375 | 699.79 | 0 | 0.05921 | 4.1258 | 0 | 0 | 71.0366 | 57.97 | off_peak | 699.79 |  |  | 7.65 | 0 | 92.35 | 239.1754 | 0
4187 | 795.26 | 218.103 | 29.1 | 43.514 | 43.514 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19.0375 | 751.746 | 0 | 0.05921 | 4.0814 | 0 | 0 | 71.0366 | 43.514 | off_peak | 751.746 |  |  | 5.47 | 0 | 94.53 | 177.5993 | 0
4188 | 806.63 | 473.096 | 29.2 | 94.3534 | 94.3534 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19.0375 | 712.2766 | 0 | 0.05921 | 4.1565 | 0 | 0 | 71.0366 | 94.3534 | off_peak | 712.2766 |  |  | 11.7 | 0 | 88.3 | 392.177 | 0
4189 | 779.63 | 931.94 | 29.2 | 185.8644 | 185.8644 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19.0375 | 593.7656 | 0 | 0.05921 | 4.3053 | 0 | 0 | 71.0366 | 185.8644 | off_peak | 593.7656 |  |  | 23.84 | 0 | 76.16 | 800.2108 | 0
4190 | 738.63 | 892.582 | 29.2 | 178.0149 | 178.0149 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19.0375 | 560.6151 | 0 | 0.05921 | 4.5314 | 0 | 0 | 71.0366 | 178.0149 | off_peak | 560.6151 |  |  | 24.1 | 0 | 75.9 | 806.6539 | 0
4191 | 751.45 | 799.321 | 29.1 | 159.4734 | 159.4734 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19.0375 | 591.9766 | 0 | 0.05921 | 4.9499 | 0 | 0 | 71.0366 | 159.4734 | off_peak | 591.9766 |  |  | 21.22 | 0 | 78.78 | 789.3716 | 0
4192 | 717.75 | 584.978 | 29 | 116.7522 | 116.7522 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19.0375 | 600.9978 | 0 | 0.05921 | 5.5818 | 0 | 0 | 71.0366 | 116.7522 | off_peak | 600.9978 |  |  | 16.27 | 0 | 83.73 | 651.6889 | 0
4193 | 736.82 | 395.964 | 28.8 | 79.0858 | 79.0858 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19.0375 | 657.7342 | 0 | 0.05921 | 6.2608 | 0 | 0 | 71.0366 | 79.0858 | off_peak | 657.7342 |  |  | 10.73 | 0 | 89.27 | 495.1382 | 0
4194 | 680.16 | 114.077 | 28.4 | 22.8178 | 14.0915 | 0 | 8.7263 | 8.7263 | 0 | 0 | 0 | 0 | 27.2003 | 666.0685 | 0 | 0.05921 | 6.9174 | 0 | 0 | 79.1994 | 14.0915 | off_peak | 666.0685 | 100 | 0 | 2.07 | 0 | 97.93 | 97.4765 | 0
4195 | 580.51 | 86.0882 | 28.2 | 17.232 | 4.8331 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 0 | 38.7984 | 575.6769 | 0 | 0.05921 | 7.2173 | 0 | 0 | 90.7975 | 4.8331 | off_peak | 575.6769 | 100 | 0 | 0.83 | 0 | 99.17 | 34.8818 | 0
4196 | 587.93 | 0 | 27.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 38.7984 | 587.93 | 0 | 0.05921 | 7.4023 | 0 | 0 | 90.7975 | 0 | off_peak | 587.93 |  |  | 0 | 0 | 100 | 0 | 0
4197 | 584.59 | 0 | 27.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 38.7984 | 584.59 | 0 | 0.05921 | 7.4342 | 0 | 0 | 90.7975 | 0 | off_peak | 584.59 |  |  | 0 | 0 | 100 | 0 | 0
4198 | 558.97 | 0 | 27.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 38.7984 | 558.97 | 0 | 0.05921 | 7.2221 | 0 | 0 | 90.7975 | 0 | off_peak | 558.97 |  |  | 0 | 0 | 100 | 0 | 0
4199 | 589.97 | 0 | 27.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 38.7984 | 589.97 | 0 | 0.05921 | 7.1448 | 0 | 0 | 90.7975 | 0 | off_peak | 589.97 |  |  | 0 | 0 | 100 | 0 | 0
4200 | 569.59 | 0 | 27.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 38.7984 | 569.59 | 0 | 0.05921 | 6.9037 | 0 | 0 | 90.7975 | 0 | off_peak | 569.59 |  |  | 0 | 0 | 100 | 0 | 0
4201 | 572.03 | 0 | 27.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 38.7984 | 572.03 | 0 | 0.05921 | 6.5406 | 0 | 0 | 90.7975 | 0 | off_peak | 572.03 |  |  | 0 | 0 | 100 | 0 | 0
4202 | 571.86 | 0 | 27.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 38.7984 | 571.86 | 0 | 0.05921 | 6.3846 | 0 | 0 | 90.7975 | 0 | off_peak | 571.86 |  |  | 0 | 0 | 100 | 0 | 0
4203 | 580.32 | 0 | 27.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 38.7984 | 580.32 | 0 | 0.05921 | 6.0567 | 0 | 0 | 90.7975 | 0 | off_peak | 580.32 |  |  | 0 | 0 | 100 | 0 | 0
4204 | 571.12 | 0 | 27.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 38.7984 | 571.12 | 0 | 0.05921 | 5.6165 | 0 | 0 | 90.7975 | 0 | off_peak | 571.12 |  |  | 0 | 0 | 100 | 0 | 0
4205 | 597.54 | 0 | 27.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 38.7984 | 597.54 | 0 | 0.05921 | 5.1123 | 0 | 0 | 90.7975 | 0 | off_peak | 597.54 |  |  | 0 | 0 | 100 | 0 | 0
4206 | 669.05 | 0 | 27.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 38.7984 | 669.05 | 0 | 0.05921 | 4.5984 | 0 | 0 | 90.7975 | 0 | off_peak | 669.05 |  |  | 0 | 0 | 100 | 0 | 0
4207 | 663.13 | 98.4254 | 28.2 | 19.7015 | 7.3026 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 0 | 50.3966 | 655.8274 | 0 | 0.05921 | 4.2159 | 0 | 0 | 102.3957 | 7.3026 | off_peak | 655.8274 | 100 | 0 | 1.1 | 0 | 98.9 | 30.7871 | 0
4208 | 714.43 | 291.274 | 28.5 | 58.2398 | 58.2398 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50.3966 | 656.1902 | 0 | 0.05921 | 3.8856 | 0 | 0 | 102.3957 | 58.2398 | off_peak | 656.1902 |  |  | 8.15 | 0 | 91.85 | 226.2992 | 0
4209 | 704.33 | 483.023 | 28.7 | 96.5093 | 96.5093 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50.3966 | 607.8207 | 0 | 0.05921 | 3.6608 | 0 | 0 | 102.3957 | 96.5093 | off_peak | 607.8207 |  |  | 13.7 | 0 | 86.3 | 353.2979 | 0
4210 | 736.73 | 411.463 | 28.9 | 82.1514 | 82.1514 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50.3966 | 654.5786 | 0 | 0.05921 | 3.5752 | 0 | 0 | 102.3957 | 82.1514 | off_peak | 654.5786 |  |  | 11.15 | 0 | 88.85 | 293.7054 | 0
4211 | 691.26 | 737.214 | 29.1 | 147.0824 | 147.0824 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50.3966 | 544.1776 | 0 | 0.05921 | 3.5035 | 0 | 0 | 102.3957 | 147.0824 | off_peak | 544.1776 |  |  | 21.28 | 0 | 78.72 | 515.2966 | 0
4212 | 739.96 | 892.716 | 29.3 | 177.9766 | 177.9766 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50.3966 | 561.9834 | 0 | 0.05921 | 3.5639 | 0 | 0 | 102.3957 | 177.9766 | off_peak | 561.9834 |  |  | 24.05 | 0 | 75.95 | 634.2956 | 0
4213 | 731.56 | 779.453 | 29.3 | 155.3959 | 155.3959 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50.3966 | 576.1641 | 0 | 0.05921 | 3.6616 | 0 | 0 | 102.3957 | 155.3959 | off_peak | 576.1641 |  |  | 21.24 | 0 | 78.76 | 568.99 | 0
4214 | 718.81 | 767.439 | 29.3 | 153.0007 | 153.0007 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50.3966 | 565.8093 | 0 | 0.05921 | 4.0003 | 0 | 0 | 102.3957 | 153.0007 | off_peak | 565.8093 |  |  | 21.29 | 0 | 78.71 | 612.0482 | 0
4215 | 707.69 | 574.127 | 29.2 | 114.5029 | 114.5029 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50.3966 | 593.1871 | 0 | 0.05921 | 4.5193 | 0 | 0 | 102.3957 | 114.5029 | off_peak | 593.1871 |  |  | 16.18 | 0 | 83.82 | 517.4771 | 0
4216 | 698.32 | 522.521 | 29.1 | 104.2487 | 104.2487 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50.3966 | 594.0713 | 0 | 0.05921 | 5.1399 | 0 | 0 | 102.3957 | 104.2487 | off_peak | 594.0713 |  |  | 14.93 | 0 | 85.07 | 535.8331 | 0
4217 | 667.71 | 474.613 | 28.8 | 94.7944 | 94.7944 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50.3966 | 572.9156 | 0 | 0.05921 | 5.7018 | 0 | 0 | 102.3957 | 94.7944 | off_peak | 572.9156 |  |  | 14.2 | 0 | 85.8 | 540.5005 | 0
4218 | 625.51 | 276.011 | 28.4 | 55.2081 | 55.2081 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50.3966 | 570.3019 | 0 | 0.05921 | 6.2341 | 0 | 0 | 102.3957 | 55.2081 | off_peak | 570.3019 |  |  | 8.83 | 0 | 91.17 | 344.1707 | 0
4219 | 585.42 | 89.1887 | 28.2 | 17.8527 | 5.4537 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 0 | 61.9947 | 579.9663 | 0 | 0.05921 | 6.4134 | 0 | 0 | 113.9938 | 5.4537 | off_peak | 579.9663 | 100 | 0 | 0.93 | 0 | 99.07 | 34.9769 | 0
4220 | 579.92 | 0 | 27.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 61.9947 | 579.92 | 0 | 0.05921 | 6.5634 | 0 | 0 | 113.9938 | 0 | off_peak | 579.92 |  |  | 0 | 0 | 100 | 0 | 0
4221 | 558.85 | 0 | 27.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 61.9947 | 558.85 | 0 | 0.05921 | 6.7186 | 0 | 0 | 113.9938 | 0 | off_peak | 558.85 |  |  | 0 | 0 | 100 | 0 | 0
4222 | 578.95 | 0 | 27.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 61.9947 | 578.95 | 0 | 0.05921 | 6.994 | 0 | 0 | 113.9938 | 0 | off_peak | 578.95 |  |  | 0 | 0 | 100 | 0 | 0
4223 | 563.93 | 0 | 27.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 61.9947 | 563.93 | 0 | 0.05921 | 6.9607 | 0 | 0 | 113.9938 | 0 | off_peak | 563.93 |  |  | 0 | 0 | 100 | 0 | 0
4224 | 555.68 | 0 | 27.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 61.9947 | 555.68 | 0 | 0.05921 | 6.8106 | 0 | 0 | 113.9938 | 0 | off_peak | 555.68 |  |  | 0 | 0 | 100 | 0 | 0
4225 | 585.74 | 0 | 27.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 61.9947 | 585.74 | 0 | 0.05921 | 6.7305 | 0 | 0 | 113.9938 | 0 | off_peak | 585.74 |  |  | 0 | 0 | 100 | 0 | 0
4226 | 562.5 | 0 | 27.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 61.9947 | 562.5 | 0 | 0.05921 | 6.7316 | 0 | 0 | 113.9938 | 0 | off_peak | 562.5 |  |  | 0 | 0 | 100 | 0 | 0
4227 | 575.63 | 0 | 27.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 61.9947 | 575.63 | 0 | 0.05921 | 6.5057 | 0 | 0 | 113.9938 | 0 | off_peak | 575.63 |  |  | 0 | 0 | 100 | 0 | 0
4228 | 562.86 | 0 | 27.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 61.9947 | 562.86 | 0 | 0.05921 | 5.8979 | 0 | 0 | 113.9938 | 0 | off_peak | 562.86 |  |  | 0 | 0 | 100 | 0 | 0
4229 | 576.93 | 0 | 27.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 61.9947 | 576.93 | 0 | 0.05921 | 5.2547 | 0 | 0 | 113.9938 | 0 | off_peak | 576.93 |  |  | 0 | 0 | 100 | 0 | 0
4230 | 694.74 | 0 | 27.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 61.9947 | 694.74 | 0 | 0.05921 | 4.5986 | 0 | 0 | 113.9938 | 0 | off_peak | 694.74 |  |  | 0 | 0 | 100 | 0 | 0
4231 | 727.39 | 126.852 | 27.9 | 25.4194 | 13.0204 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 0 | 73.5928 | 714.3696 | 0 | 0.05921 | 4.1642 | 0 | 0 | 125.592 | 13.0204 | off_peak | 714.3696 | 100 | 0 | 1.79 | 0 | 98.21 | 54.2192 | 0
4232 | 790.99 | 302.31 | 28.3 | 60.4905 | 60.4905 | 0 | 0 | 0.80079 | 0.80079 | 0 | 0 | 0 | 74.3419 | 731.3003 | 0 | 0.05921 | 3.8983 | 0 | 0 | 125.592 | 60.4905 | off_peak | 730.4995 | 0 | 100 | 7.65 | 0 | 92.35 | 235.8109 | 0
4233 | 828.34 | 439.83 | 28.6 | 87.9113 | 87.9113 | 0 | 0 | 0.05172 | 0.05172 | 0 | 0 | 0 | 74.3903 | 740.4804 | 0 | 0.05921 | 3.7214 | 0 | 0 | 125.592 | 87.9113 | off_peak | 740.4287 | 0 | 100 | 10.61 | 0 | 89.39 | 327.154 | 0
4234 | 852.22 | 695.979 | 28.8 | 139.0077 | 139.0077 | 0 | 0 | 0.0033404 | 0.0033404 | 0 | 0 | 0 | 74.3934 | 713.2156 | 0 | 0.05921 | 3.6902 | 0 | 0 | 125.592 | 139.0077 | off_peak | 713.2123 | 0 | 100 | 16.31 | 0 | 83.69 | 512.972 | 0
4235 | 842.74 | 834.541 | 28.9 | 166.6219 | 166.6219 | 0 | 0 | 0.00021574 | 0.00021574 | 0 | 0 | 0 | 74.3936 | 676.1183 | 0 | 0.05921 | 3.8135 | 0 | 0 | 125.592 | 166.6219 | off_peak | 676.1181 | 0 | 100 | 19.77 | 0 | 80.23 | 635.4166 | 0
4236 | 940.74 | 919.068 | 29 | 183.4313 | 183.4313 | 0 | 1.3934e-05 | 1.3934e-05 | 0 | 0 | 0 | 0 | 74.3936 | 757.3087 | 0 | 0.05921 | 4.0806 | 0 | 0 | 125.592 | 183.4313 | off_peak | 757.3087 | 100 | 0 | 19.5 | 0 | 80.5 | 748.5074 | 0
4237 | 834.16 | 943.286 | 29.1 | 188.196 | 188.196 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 645.964 | 0 | 0.088511 | 4.4303 | 0 | 0 | 125.592 | 188.196 | on_peak | 645.964 |  |  | 22.56 | 0 | 77.44 | 833.7683 | 0
4238 | 857.04 | 907.229 | 29 | 181.0684 | 181.0684 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 675.9716 | 0 | 0.088511 | 4.8475 | 0 | 0 | 125.592 | 181.0684 | on_peak | 675.9716 |  |  | 21.13 | 0 | 78.87 | 877.7336 | 0
4239 | 922.37 | 811.122 | 29 | 161.887 | 161.887 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 760.483 | 0 | 0.088511 | 5.1645 | 0 | 0 | 125.592 | 161.887 | on_peak | 760.483 |  |  | 17.55 | 0 | 82.45 | 836.0697 | 0
4240 | 848.17 | 664.778 | 28.8 | 132.776 | 132.776 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 715.394 | 0 | 0.088511 | 5.5767 | 0 | 0 | 125.592 | 132.776 | on_peak | 715.394 |  |  | 15.65 | 0 | 84.35 | 740.4472 | 0
4241 | 880.13 | 473.401 | 28.6 | 94.6213 | 94.6213 | 0 | 0 | 0 | 0 | 61.79 | 61.79 | 0 | 8.3373 | 723.7187 | 0 | 0.088511 | 6.1067 | 0 | 0 | 125.592 | 94.6213 | on_peak | 723.7187 |  |  | 10.75 | 7.02 | 82.23 | 577.8194 | 0
4242 | 882.32 | 235.579 | 28.2 | 47.1552 | 47.1552 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.3373 | 835.1648 | 0 | 0.088511 | 6.6131 | 0 | 0 | 125.592 | 47.1552 | on_peak | 835.1648 |  |  | 5.34 | 0 | 94.66 | 311.8408 | 0
4243 | 865.33 | 78.689 | 28 | 15.7624 | 15.7624 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.3373 | 849.5676 | 0 | 0.088511 | 6.752 | 0 | 0 | 125.592 | 15.7624 | on_peak | 849.5676 |  |  | 1.82 | 0 | 98.18 | 106.4277 | 0
4244 | 877.41 | 0 | 27.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0.83998 | 0.83998 | 0 | 7.4394 | 876.57 | 0 | 0.088511 | 6.8206 | 0 | 0 | 125.592 | 0 | on_peak | 876.57 |  |  | 0 | 0.1 | 99.9 | 0 | 0
4245 | 866.29 | 0 | 27.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 866.29 | 0 | 0.088511 | 7.1035 | 0 | 0 | 125.592 | 0 | on_peak | 866.29 |  |  | 0 | 0 | 100 | 0 | 0
4246 | 824.46 | 0 | 27.5 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 19.0375 | 836.8589 | 0 | 0.05921 | 7.5255 | 0 | 0 | 125.592 | 0 | off_peak | 824.46 | 0 | 100 | 0 | 0 | 100 | 0 | 0
4247 | 841.8 | 0 | 27.4 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 30.6357 | 854.1989 | 0 | 0.05921 | 7.8651 | 0 | 0 | 125.592 | 0 | off_peak | 841.8 | 0 | 100 | 0 | 0 | 100 | 0 | 0
4248 | 871.8 | 0 | 27.4 | 0 | 0 | 0 | 0 | 8.7263 | 8.7263 | 0 | 0 | 0 | 38.7984 | 880.5263 | 0 | 0.05921 | 8.1219 | 0 | 0 | 125.592 | 0 | off_peak | 871.8 | 0 | 100 | 0 | 0 | 100 | 0 | 0
4249 | 750.21 | 0 | 27.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 38.7984 | 750.21 | 0 | 0.05921 | 8.224 | 0 | 0 | 125.592 | 0 | off_peak | 750.21 |  |  | 0 | 0 | 100 | 0 | 0
4250 | 685.95 | 0 | 27.3 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 50.3966 | 698.3489 | 0 | 0.05921 | 8.2069 | 0 | 0 | 125.592 | 0 | off_peak | 685.95 | 0 | 100 | 0 | 0 | 100 | 0 | 0
4251 | 639.64 | 0 | 27.3 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 61.9947 | 652.0389 | 0 | 0.05921 | 7.7058 | 0 | 0 | 125.592 | 0 | off_peak | 639.64 | 0 | 100 | 0 | 0 | 100 | 0 | 0
4252 | 624.34 | 0 | 27.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 61.9947 | 624.34 | 0 | 0.05921 | 6.9073 | 0 | 0 | 125.592 | 0 | off_peak | 624.34 |  |  | 0 | 0 | 100 | 0 | 0
4253 | 654.17 | 0 | 27.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 61.9947 | 654.17 | 0 | 0.05921 | 6.0533 | 0 | 0 | 125.592 | 0 | off_peak | 654.17 |  |  | 0 | 0 | 100 | 0 | 0
4254 | 740.45 | 0 | 27.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 61.9947 | 740.45 | 0 | 0.05921 | 5.3668 | 0 | 0 | 125.592 | 0 | off_peak | 740.45 |  |  | 0 | 0 | 100 | 0 | 0
4255 | 754.72 | 125.615 | 27.9 | 25.1715 | 25.1715 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 73.5928 | 741.9475 | 0 | 0.05921 | 4.8463 | 0 | 0 | 125.592 | 25.1715 | off_peak | 729.5485 | 0 | 100 | 3.34 | 0 | 96.66 | 121.9897 | 0
4256 | 835.75 | 321.307 | 28.2 | 64.3151 | 64.3151 | 0 | 0 | 0.80079 | 0.80079 | 0 | 0 | 0 | 74.3419 | 772.2357 | 0 | 0.05921 | 4.5117 | 0 | 0 | 125.592 | 64.3151 | off_peak | 771.4349 | 0 | 100 | 7.7 | 0 | 92.3 | 290.1701 | 0
4257 | 862.03 | 519.377 | 28.4 | 103.8865 | 103.8865 | 0 | 0 | 0.05172 | 0.05172 | 0 | 0 | 0 | 74.3903 | 758.1952 | 0 | 0.05921 | 4.2804 | 0 | 0 | 125.592 | 103.8865 | off_peak | 758.1435 | 0 | 100 | 12.05 | 0 | 87.95 | 444.6784 | 0
4258 | 870.22 | 692.259 | 28.7 | 138.3152 | 138.3152 | 0 | 0 | 0.0033404 | 0.0033404 | 0 | 0 | 0 | 74.3934 | 731.9081 | 0 | 0.05921 | 4.18 | 0 | 0 | 125.592 | 138.3152 | off_peak | 731.9048 | 0 | 100 | 15.89 | 0 | 84.11 | 578.1633 | 0
4259 | 840.54 | 531.137 | 28.9 | 106.0452 | 106.0452 | 0 | 0 | 0.00021574 | 0.00021574 | 0 | 0 | 0 | 74.3936 | 734.495 | 0 | 0.05921 | 4.2617 | 0 | 0 | 125.592 | 106.0452 | off_peak | 734.4948 | 0 | 100 | 12.62 | 0 | 87.38 | 451.9375 | 0
4260 | 905.35 | 456.63 | 29.1 | 91.1028 | 91.1028 | 0 | 0 | 1.3934e-05 | 1.3934e-05 | 0 | 0 | 0 | 74.3936 | 814.2473 | 0 | 0.05921 | 4.4669 | 0 | 0 | 125.592 | 91.1028 | off_peak | 814.2472 | 0 | 100 | 10.06 | 0 | 89.94 | 406.9493 | 0
4261 | 826.47 | 236.544 | 29.2 | 47.1759 | 47.1759 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 779.2941 | 0 | 0.088511 | 4.7085 | 0 | 0 | 125.592 | 47.1759 | on_peak | 779.2941 |  |  | 5.71 | 0 | 94.29 | 222.1278 | 0
4262 | 899.58 | 609.965 | 29.2 | 121.6503 | 121.6503 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 777.9297 | 0 | 0.088511 | 5.1046 | 0 | 0 | 125.592 | 121.6503 | on_peak | 777.9297 |  |  | 13.52 | 0 | 86.48 | 620.9724 | 0
4263 | 897.27 | 782.772 | 29.3 | 156.0576 | 156.0576 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 741.2124 | 0 | 0.088511 | 5.3727 | 0 | 0 | 125.592 | 156.0576 | on_peak | 741.2124 |  |  | 17.39 | 0 | 82.61 | 838.4545 | 0
4264 | 860.64 | 644.908 | 29.2 | 128.6193 | 128.6193 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 732.0207 | 0 | 0.088511 | 5.8571 | 0 | 0 | 125.592 | 128.6193 | on_peak | 732.0207 |  |  | 14.94 | 0 | 85.06 | 753.3322 | 0
4265 | 840.57 | 463.876 | 29 | 92.5822 | 92.5822 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 747.9878 | 0 | 0.088511 | 6.3333 | 0 | 0 | 125.592 | 92.5822 | on_peak | 747.9878 |  |  | 11.01 | 0 | 88.99 | 586.3494 | 0
4266 | 899.78 | 233.406 | 28.7 | 46.6351 | 46.6351 | 0 | 0 | 0 | 0 | 60.09 | 60.09 | 0 | 10.1547 | 793.0548 | 0 | 0.088511 | 6.8394 | 0 | 0 | 125.592 | 46.6351 | on_peak | 793.0548 |  |  | 5.18 | 6.68 | 88.14 | 318.9572 | 0
4267 | 836.88 | 63.0649 | 28.5 | 12.6097 | 12.6097 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1547 | 824.2703 | 0 | 0.088511 | 7.3565 | 0 | 0 | 125.592 | 12.6097 | on_peak | 824.2703 |  |  | 1.51 | 0 | 98.49 | 92.7638 | 0
4268 | 868.25 | 0 | 28 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1547 | 868.25 | 0 | 0.088511 | 7.7964 | 0 | 0 | 125.592 | 0 | on_peak | 868.25 |  |  | 0 | 0 | 100 | 0 | 0
4269 | 879.11 | 0 | 27.9 | 0 | 0 | 0 | 0 | 0 | 0 | 2.54 | 2.54 | 0 | 7.4394 | 876.57 | 0 | 0.088511 | 8.1366 | 0 | 0 | 125.592 | 0 | on_peak | 876.57 |  |  | 0 | 0.29 | 99.71 | 0 | 0
4270 | 808.12 | 0 | 27.8 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 19.0375 | 820.5189 | 0 | 0.05921 | 8.4793 | 0 | 0 | 125.592 | 0 | off_peak | 808.12 | 0 | 100 | 0 | 0 | 100 | 0 | 0
4271 | 818.71 | 0 | 27.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19.0375 | 818.71 | 0 | 0.05921 | 8.842 | 0 | 0 | 125.592 | 0 | off_peak | 818.71 |  |  | 0 | 0 | 100 | 0 | 0
4272 | 819.1 | 0 | 27.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19.0375 | 819.1 | 0 | 0.05921 | 9.0607 | 0 | 0 | 125.592 | 0 | off_peak | 819.1 |  |  | 0 | 0 | 100 | 0 | 0
4273 | 745.01 | 0 | 27.4 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 30.6357 | 757.4089 | 0 | 0.05921 | 8.9763 | 0 | 0 | 125.592 | 0 | off_peak | 745.01 | 0 | 100 | 0 | 0 | 100 | 0 | 0
4274 | 682.96 | 0 | 27.4 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 42.2338 | 695.3589 | 0 | 0.05921 | 8.677 | 0 | 0 | 125.592 | 0 | off_peak | 682.96 | 0 | 100 | 0 | 0 | 100 | 0 | 0
4275 | 665.99 | 0 | 27.3 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 53.832 | 678.3889 | 0 | 0.05921 | 8.2253 | 0 | 0 | 125.592 | 0 | off_peak | 665.99 | 0 | 100 | 0 | 0 | 100 | 0 | 0
4276 | 607.24 | 0 | 27.3 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 65.4301 | 619.6389 | 0 | 0.05921 | 7.5106 | 0 | 0 | 125.592 | 0 | off_peak | 607.24 | 0 | 100 | 0 | 0 | 100 | 0 | 0
4277 | 623.48 | 0 | 27.2 | 0 | 0 | 0 | 0 | 8.9635 | 8.9635 | 0 | 0 | 0 | 73.8147 | 632.4435 | 0 | 0.05921 | 6.6497 | 0 | 0 | 125.592 | 0 | off_peak | 623.48 | 0 | 100 | 0 | 0 | 100 | 0 | 0
4278 | 731.21 | 0 | 27.4 | 0 | 0 | 0 | 0 | 0.57892 | 0.57892 | 0 | 0 | 0 | 74.3563 | 731.7889 | 0 | 0.05921 | 6.0049 | 0 | 0 | 125.592 | 0 | off_peak | 731.21 | 0 | 100 | 0 | 0 | 100 | 0 | 0
4279 | 755.5 | 111.917 | 27.9 | 22.4266 | 22.3892 | 0 | 0.03739 | 0.03739 | 0 | 0 | 0 | 0 | 74.3912 | 733.1108 | 0 | 0.05921 | 5.4977 | 0 | 0 | 125.6269 | 22.3892 | off_peak | 733.1108 | 100 | 0 | 2.96 | 0 | 97.04 | 123.0889 | 0
4280 | 773.8 | 309.886 | 28.4 | 61.9838 | 61.9814 | 0 | 0.0024148 | 0.0024148 | 0 | 0 | 0 | 0 | 74.3935 | 711.8186 | 0 | 0.05921 | 5.1484 | 0 | 0 | 125.6292 | 61.9814 | off_peak | 711.8186 | 100 | 0 | 8.01 | 0 | 91.99 | 319.1065 | 0
4281 | 816.28 | 503.024 | 28.7 | 100.5056 | 100.5056 | 0 | 0 | 0.00015596 | 0.00015596 | 0 | 0 | 0 | 74.3936 | 715.7746 | 0 | 0.05921 | 4.8439 | 0 | 0 | 125.6292 | 100.5056 | off_peak | 715.7744 | 0 | 100 | 12.31 | 0 | 87.69 | 486.8425 | 0
4282 | 861.72 | 669.398 | 29 | 133.6011 | 133.6011 | 0 | 0 | 1.0073e-05 | 1.0073e-05 | 0 | 0 | 0 | 74.3936 | 728.1189 | 0 | 0.05921 | 4.7314 | 0 | 0 | 125.6292 | 133.6011 | off_peak | 728.1189 | 0 | 100 | 15.5 | 0 | 84.5 | 632.1201 | 0
4283 | 862.9 | 695.118 | 29.2 | 138.6331 | 138.6331 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 724.2669 | 0 | 0.05921 | 4.8242 | 0 | 0 | 125.6292 | 138.6331 | off_peak | 724.2669 |  |  | 16.07 | 0 | 83.93 | 668.7876 | 0
4284 | 920.18 | 854.174 | 29.4 | 170.2304 | 170.2304 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 749.9496 | 0 | 0.05921 | 4.879 | 0 | 0 | 125.6292 | 170.2304 | off_peak | 749.9496 |  |  | 18.5 | 0 | 81.5 | 830.5582 | 0
4285 | 827.34 | 926.236 | 29.5 | 184.5243 | 184.5243 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 642.8157 | 0 | 0.088511 | 5.1197 | 0 | 0 | 125.6292 | 184.5243 | on_peak | 642.8157 |  |  | 22.3 | 0 | 77.7 | 944.7041 | 0
4286 | 879.55 | 432.183 | 29.5 | 86.0993 | 86.0993 | 0 | 0 | 0 | 0 | 62.63 | 62.63 | 0 | 7.4394 | 730.8207 | 0 | 0.088511 | 5.4172 | 0 | 0 | 125.6292 | 86.0993 | on_peak | 730.8207 |  |  | 9.79 | 7.12 | 83.09 | 466.4186 | 0
4287 | 873.19 | 542.817 | 29.4 | 108.1793 | 108.1793 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 765.0107 | 0 | 0.088511 | 5.7972 | 0 | 0 | 125.6292 | 108.1793 | on_peak | 765.0107 |  |  | 12.39 | 0 | 87.61 | 627.1372 | 0
4288 | 881.13 | 489.539 | 29.3 | 97.5971 | 97.5971 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 783.5329 | 0 | 0.088511 | 6.3011 | 0 | 0 | 125.6292 | 97.5971 | on_peak | 783.5329 |  |  | 11.08 | 0 | 88.92 | 614.9702 | 0
4289 | 830.14 | 280.801 | 29 | 56.0434 | 56.0434 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 774.0966 | 0 | 0.088511 | 6.8219 | 0 | 0 | 125.6292 | 56.0434 | on_peak | 774.0966 |  |  | 6.75 | 0 | 93.25 | 382.3221 | 0
4290 | 876.47 | 126.794 | 28.7 | 25.3338 | 25.3338 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 851.1362 | 0 | 0.088511 | 7.3894 | 0 | 0 | 125.6292 | 25.3338 | on_peak | 851.1362 |  |  | 2.89 | 0 | 97.11 | 187.2024 | 0
4291 | 802.61 | 29.45 | 28.5 | 5.8885 | 5.8885 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 796.7215 | 0 | 0.088511 | 7.8531 | 0 | 0 | 125.6292 | 5.8885 | on_peak | 796.7215 |  |  | 0.73 | 0 | 99.27 | 46.2428 | 0
4292 | 845.9 | 0 | 28 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 845.9 | 0 | 0.088511 | 8.1578 | 0 | 0 | 125.6292 | 0 | on_peak | 845.9 |  |  | 0 | 0 | 100 | 0 | 0
4293 | 872.98 | 0 | 27.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 872.98 | 0 | 0.088511 | 8.4323 | 0 | 0 | 125.6292 | 0 | on_peak | 872.98 |  |  | 0 | 0 | 100 | 0 | 0
4294 | 838.2 | 0 | 27.7 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 19.0375 | 850.5989 | 0 | 0.05921 | 8.6023 | 0 | 0 | 125.6292 | 0 | off_peak | 838.2 | 0 | 100 | 0 | 0 | 100 | 0 | 0
4295 | 889.93 | 0 | 27.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19.0375 | 889.93 | 0 | 0.05921 | 8.7147 | 0 | 0 | 125.6292 | 0 | off_peak | 889.93 |  |  | 0 | 0 | 100 | 0 | 0
4296 | 819.44 | 0 | 27.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19.0375 | 819.44 | 0 | 0.05921 | 8.8101 | 0 | 0 | 125.6292 | 0 | off_peak | 819.44 |  |  | 0 | 0 | 100 | 0 | 0
4297 | 769.51 | 0 | 27.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19.0375 | 769.51 | 0 | 0.05921 | 8.7498 | 0 | 0 | 125.6292 | 0 | off_peak | 769.51 |  |  | 0 | 0 | 100 | 0 | 0
4298 | 694.35 | 0 | 27.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19.0375 | 694.35 | 0 | 0.05921 | 8.5514 | 0 | 0 | 125.6292 | 0 | off_peak | 694.35 |  |  | 0 | 0 | 100 | 0 | 0
4299 | 633.26 | 0 | 27.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19.0375 | 633.26 | 0 | 0.05921 | 8.0414 | 0 | 0 | 125.6292 | 0 | off_peak | 633.26 |  |  | 0 | 0 | 100 | 0 | 0
4300 | 642.23 | 0 | 27.5 | 0 | 0 | 0 | 0 | 8.7263 | 8.7263 | 0 | 0 | 0 | 27.2003 | 650.9563 | 0 | 0.05921 | 7.1941 | 0 | 0 | 125.6292 | 0 | off_peak | 642.23 | 0 | 100 | 0 | 0 | 100 | 0 | 0
4301 | 660.47 | 0 | 27.5 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 38.7984 | 672.8689 | 0 | 0.05921 | 6.388 | 0 | 0 | 125.6292 | 0 | off_peak | 660.47 | 0 | 100 | 0 | 0 | 100 | 0 | 0
4302 | 706.37 | 0 | 27.7 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 50.3966 | 718.7689 | 0 | 0.05921 | 5.6523 | 0 | 0 | 125.6292 | 0 | off_peak | 706.37 | 0 | 100 | 0 | 0 | 100 | 0 | 0
4303 | 740.64 | 117.994 | 28.1 | 23.6271 | 11.2282 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 0 | 61.9947 | 729.4118 | 0 | 0.05921 | 5.1415 | 0 | 0 | 137.2274 | 11.2282 | off_peak | 729.4118 | 100 | 0 | 1.52 | 0 | 98.48 | 57.7298 | 0
4304 | 760.3 | 309.228 | 28.4 | 61.8522 | 61.8522 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 73.5928 | 710.8467 | 0 | 0.05921 | 4.7923 | 0 | 0 | 137.2274 | 61.8522 | off_peak | 698.4478 | 0 | 100 | 8.14 | 0 | 91.86 | 296.4146 | 0
4305 | 809.3 | 507.514 | 28.7 | 101.4027 | 101.4027 | 0 | 0 | 0.80079 | 0.80079 | 0 | 0 | 0 | 74.3419 | 708.6981 | 0 | 0.05921 | 4.5418 | 0 | 0 | 137.2274 | 101.4027 | off_peak | 707.8973 | 0 | 100 | 12.53 | 0 | 87.47 | 460.5484 | 0
4306 | 845.77 | 681.142 | 28.9 | 135.9947 | 135.9947 | 0 | 0 | 0.05172 | 0.05172 | 0 | 0 | 0 | 74.3903 | 709.827 | 0 | 0.05921 | 4.4301 | 0 | 0 | 137.2274 | 135.9947 | off_peak | 709.7753 | 0 | 100 | 16.08 | 0 | 83.92 | 602.4737 | 0
4307 | 858.12 | 669.974 | 29.2 | 133.6184 | 133.6184 | 0 | 0 | 0.0033404 | 0.0033404 | 0 | 0 | 0 | 74.3934 | 724.5049 | 0 | 0.05921 | 4.5107 | 0 | 0 | 137.2274 | 133.6184 | off_peak | 724.5016 | 0 | 100 | 15.57 | 0 | 84.43 | 602.7084 | 0
4308 | 945.59 | 747.689 | 29.3 | 149.0632 | 149.0632 | 0 | 0 | 0.00021574 | 0.00021574 | 0 | 0 | 0 | 74.3936 | 796.527 | 0 | 0.05921 | 4.6769 | 0 | 0 | 137.2274 | 149.0632 | off_peak | 796.5268 | 0 | 100 | 15.76 | 0 | 84.24 | 697.1592 | 0
4309 | 850.71 | 736.669 | 29.5 | 146.7588 | 146.7588 | 0 | 0 | 1.4896e-05 | 1.4896e-05 | 0 | 0 | 0 | 74.3936 | 703.9512 | 0 | 0.088511 | 4.7509 | 0 | 0 | 137.2274 | 146.7588 | on_peak | 703.9512 | 0 | 100 | 17.25 | 0 | 82.75 | 697.2412 | 0
4310 | 905.14 | 555.807 | 29.5 | 110.7276 | 110.7276 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 794.4124 | 0 | 0.088511 | 5.0787 | 0 | 0 | 137.2274 | 110.7276 | on_peak | 794.4124 |  |  | 12.23 | 0 | 87.77 | 562.356 | 0
4311 | 948.32 | 349.814 | 29.6 | 69.6643 | 69.6643 | 0 | 0 | 0 | 0 | 2.0857 | 2.0857 | 0 | 72.1639 | 876.57 | 0 | 0.088511 | 5.4294 | 0 | 0 | 137.2274 | 69.6643 | on_peak | 876.57 |  |  | 7.35 | 0.22 | 92.43 | 378.2328 | 0
4312 | 918.76 | 520.165 | 29.5 | 103.627 | 101.3973 | 0 | 2.2297 | 2.2297 | 0 | 0 | 0 | 0 | 74.2496 | 817.3627 | 0 | 0.088511 | 5.9872 | 0 | 0 | 139.3131 | 101.3973 | on_peak | 817.3627 | 100 | 0 | 11.04 | 0 | 88.96 | 607.09 | 0
4313 | 908.45 | 440.751 | 29.3 | 87.8705 | 87.7264 | 0 | 0.14401 | 0.14401 | 0 | 0 | 0 | 0 | 74.3843 | 820.7236 | 0 | 0.088511 | 6.5599 | 0 | 0 | 139.4478 | 87.7264 | on_peak | 820.7236 | 100 | 0 | 9.66 | 0 | 90.34 | 575.4794 | 0
4314 | 912.3 | 273.181 | 29 | 54.5226 | 54.5133 | 0 | 0.0093008 | 0.0093008 | 0 | 0 | 0 | 0 | 74.393 | 857.7867 | 0 | 0.088511 | 6.947 | 0 | 0 | 139.4565 | 54.5133 | on_peak | 857.7867 | 100 | 0 | 5.98 | 0 | 94.02 | 378.706 | 0
4315 | 883.31 | 72.8508 | 28.8 | 14.5505 | 14.5505 | 0 | 0 | 0.0006007 | 0.0006007 | 0 | 0 | 0 | 74.3936 | 868.7601 | 0 | 0.088511 | 7.6054 | 0 | 0 | 139.4565 | 14.5505 | on_peak | 868.7595 | 0 | 100 | 1.65 | 0 | 98.35 | 110.6627 | 0
4316 | 903.02 | 0 | 28.2 | 0 | 0 | 0 | 0 | 0 | 0 | 26.45 | 26.45 | 0 | 46.1174 | 876.57 | 0 | 0.088511 | 7.7649 | 26.45 | 0 | 111.1803 | 26.45 | on_peak | 876.57 |  |  | 0 | 2.93 | 97.07 | 205.3821 | 0
4317 | 912.75 | 0 | 28 | 0 | 0 | 0 | 0 | 0 | 0 | 36.18 | 36.18 | 0 | 7.4394 | 876.57 | 0 | 0.088511 | 7.5488 | 0 | 0 | 111.1803 | 0 | on_peak | 876.57 |  |  | 0 | 3.96 | 96.04 | 0 | 0
4318 | 898.63 | 0 | 27.9 | 0 | 0 | 0 | 0 | 1.28 | 1.28 | 0 | 0 | 0 | 8.6367 | 899.91 | 0 | 0.05921 | 7.5593 | 0 | 0 | 111.1803 | 0 | off_peak | 898.63 | 0 | 100 | 0 | 0 | 100 | 0 | 0
4319 | 901.03 | 0 | 27.7 | 0 | 0 | 0 | 0 | 0 | 0 | 1.12 | 1.12 | 0 | 7.4394 | 899.91 | 0 | 0.05921 | 7.7988 | 0 | 0 | 111.1803 | 0 | off_peak | 899.91 |  |  | 0 | 0.12 | 99.88 | 0 | 0
4320 | 855.91 | 0 | 27.6 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 19.0375 | 868.3089 | 0 | 0.05921 | 8.0187 | 0 | 0 | 111.1803 | 0 | off_peak | 855.91 | 0 | 100 | 0 | 0 | 100 | 0 | 0
4321 | 808.07 | 0 | 27.6 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 30.6357 | 820.4689 | 0 | 0.05921 | 8.0122 | 0 | 0 | 111.1803 | 0 | off_peak | 808.07 | 0 | 100 | 0 | 0 | 100 | 0 | 0
4322 | 700.18 | 0 | 27.5 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 42.2338 | 712.5789 | 0 | 0.05921 | 7.7607 | 0 | 0 | 111.1803 | 0 | off_peak | 700.18 | 0 | 100 | 0 | 0 | 100 | 0 | 0
4323 | 689.71 | 0 | 27.5 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 53.832 | 702.1089 | 0 | 0.05921 | 7.344 | 0 | 0 | 111.1803 | 0 | off_peak | 689.71 | 0 | 100 | 0 | 0 | 100 | 0 | 0
4324 | 691.77 | 0 | 27.5 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 65.4301 | 704.1689 | 0 | 0.05921 | 6.848 | 0 | 0 | 111.1803 | 0 | off_peak | 691.77 | 0 | 100 | 0 | 0 | 100 | 0 | 0
4325 | 652.42 | 0 | 27.6 | 0 | 0 | 0 | 0 | 8.9635 | 8.9635 | 0 | 0 | 0 | 73.8147 | 661.3835 | 0 | 0.05921 | 6.1972 | 0 | 0 | 111.1803 | 0 | off_peak | 652.42 | 0 | 100 | 0 | 0 | 100 | 0 | 0
4326 | 796.84 | 0 | 27.7 | 0 | 0 | 0 | 0 | 0.57892 | 0.57892 | 0 | 0 | 0 | 74.3563 | 797.4189 | 0 | 0.05921 | 5.5312 | 0 | 0 | 111.1803 | 0 | off_peak | 796.84 | 0 | 100 | 0 | 0 | 100 | 0 | 0
4327 | 841.46 | 105.825 | 28 | 21.1981 | 21.1607 | 0 | 0.03739 | 0.03739 | 0 | 0 | 0 | 0 | 74.3912 | 820.2993 | 0 | 0.05921 | 4.9401 | 0 | 0 | 111.2152 | 21.1607 | off_peak | 820.2993 | 100 | 0 | 2.51 | 0 | 97.49 | 104.5353 | 0
4328 | 861.1 | 27.9337 | 28.4 | 5.5873 | 5.5849 | 0 | 0.0024148 | 0.0024148 | 0 | 0 | 0 | 0 | 74.3935 | 855.5151 | 0 | 0.05921 | 4.5396 | 0 | 0 | 111.2175 | 5.5849 | off_peak | 855.5151 | 100 | 0 | 0.65 | 0 | 99.35 | 25.3532 | 0
4329 | 910.25 | 18.05 | 28.6 | 3.6078 | 3.6078 | 0 | 0 | 0 | 0 | 6.7322 | 6.7322 | 0 | 67.1964 | 899.91 | 0 | 0.05921 | 4.298 | 0 | 0 | 111.2175 | 3.6078 | off_peak | 899.91 |  |  | 0.4 | 0.74 | 98.86 | 15.5063 | 0
4330 | 941.69 | 537.796 | 28.8 | 107.4139 | 107.4139 | 0 | 0 | 7.1972 | 7.1972 | 0 | 0 | 0 | 73.9288 | 841.4733 | 0 | 0.05921 | 4.1918 | 0 | 0 | 111.2175 | 107.4139 | off_peak | 834.2761 | 0 | 100 | 11.41 | 0 | 88.59 | 450.2606 | 0
4331 | 905.85 | 447.146 | 29.1 | 89.2106 | 89.2106 | 0 | 0 | 0.46484 | 0.46484 | 0 | 0 | 0 | 74.3636 | 817.1042 | 0 | 0.05921 | 4.2528 | 0 | 0 | 111.2175 | 89.2106 | off_peak | 816.6394 | 0 | 100 | 9.85 | 0 | 90.15 | 379.3919 | 0
4332 | 974.85 | 251.585 | 29.3 | 50.1573 | 50.1573 | 0 | 0 | 0 | 0 | 24.7827 | 24.7827 | 0 | 47.8698 | 899.91 | 0 | 0.05921 | 4.4395 | 24.7827 | 0 | 84.7237 | 74.94 | off_peak | 899.91 |  |  | 5.15 | 2.54 | 92.31 | 332.698 | 0
4333 | 914.45 | 542.299 | 29.4 | 108.0761 | 108.0761 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 47.8698 | 806.3739 | 0 | 0.088511 | 4.6461 | 0 | 0 | 84.7237 | 108.0761 | on_peak | 806.3739 |  |  | 11.82 | 0 | 88.18 | 502.1275 | 0
4334 | 929.73 | 562.378 | 29.4 | 112.0777 | 112.0777 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 47.8698 | 817.6523 | 0 | 0.088511 | 5.019 | 0 | 0 | 84.7237 | 112.0777 | on_peak | 817.6523 |  |  | 12.05 | 0 | 87.95 | 562.5176 | 0
4335 | 947.18 | 514.986 | 29.4 | 102.6328 | 102.6328 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 47.8698 | 844.5472 | 0 | 0.088511 | 5.4925 | 0 | 0 | 84.7237 | 102.6328 | on_peak | 844.5472 |  |  | 10.84 | 0 | 89.16 | 563.715 | 0
4336 | 893.49 | 448.287 | 29.3 | 89.3729 | 89.3729 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 47.8698 | 804.1171 | 0 | 0.088511 | 5.9493 | 0 | 0 | 84.7237 | 89.3729 | on_peak | 804.1171 |  |  | 10 | 0 | 90 | 531.7095 | 0
4337 | 903.1 | 478.94 | 29.2 | 95.5189 | 95.5189 | 0 | 0 | 0 | 0 | 26.6593 | 26.6593 | 0 | 19.3699 | 780.9218 | 0 | 0.088511 | 6.3663 | 0 | 0 | 84.7237 | 95.5189 | on_peak | 780.9218 |  |  | 10.58 | 2.95 | 86.47 | 608.1031 | 0
4338 | 887.66 | 283.102 | 28.9 | 56.5233 | 56.5233 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19.3699 | 831.1367 | 0 | 0.088511 | 6.6553 | 0 | 0 | 84.7237 | 56.5233 | on_peak | 831.1367 |  |  | 6.37 | 0 | 93.63 | 376.1794 | 0
4339 | 886.01 | 70.0284 | 28.7 | 13.9919 | 13.9919 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19.3699 | 872.0181 | 0 | 0.088511 | 6.8055 | 0 | 0 | 84.7237 | 13.9919 | on_peak | 872.0181 |  |  | 1.58 | 0 | 98.42 | 95.2223 | 0
4340 | 887.73 | 0 | 27.6 | 0 | 0 | 0 | 0 | 0 | 0 | 11.16 | 11.16 | 0 | 7.4394 | 876.57 | 0 | 0.088511 | 6.8945 | 0 | 0 | 84.7237 | 0 | on_peak | 876.57 |  |  | 0 | 1.26 | 98.74 | 0 | 0
4341 | 857.14 | 0 | 27.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 857.14 | 0 | 0.088511 | 7.1954 | 0 | 0 | 84.7237 | 0 | on_peak | 857.14 |  |  | 0 | 0 | 100 | 0 | 0
4342 | 835.6 | 0 | 27.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 835.6 | 0 | 0.05921 | 7.5435 | 0 | 0 | 84.7237 | 0 | off_peak | 835.6 |  |  | 0 | 0 | 100 | 0 | 0
4343 | 852.37 | 0 | 27.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 852.37 | 0 | 0.05921 | 7.7541 | 0 | 0 | 84.7237 | 0 | off_peak | 852.37 |  |  | 0 | 0 | 100 | 0 | 0
4344 | 851.91 | 0 | 27.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 851.91 | 0 | 0.05921 | 7.894 | 0 | 0 | 84.7237 | 0 | off_peak | 851.91 |  |  | 0 | 0 | 100 | 0 | 0
4345 | 743.62 | 0 | 27.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 743.62 | 0 | 0.05921 | 7.9798 | 0 | 0 | 84.7237 | 0 | off_peak | 743.62 |  |  | 0 | 0 | 100 | 0 | 0
4346 | 708.41 | 0 | 27.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 708.41 | 0 | 0.05921 | 7.7705 | 0 | 0 | 84.7237 | 0 | off_peak | 708.41 |  |  | 0 | 0 | 100 | 0 | 0
4347 | 651.52 | 0 | 27 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 651.52 | 0 | 0.05921 | 7.3122 | 0 | 0 | 84.7237 | 0 | off_peak | 651.52 |  |  | 0 | 0 | 100 | 0 | 0
4348 | 683.67 | 0 | 27 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 683.67 | 0 | 0.05921 | 6.7962 | 0 | 0 | 84.7237 | 0 | off_peak | 683.67 |  |  | 0 | 0 | 100 | 0 | 0
4349 | 691.87 | 0 | 27 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 691.87 | 0 | 0.05921 | 6.171 | 0 | 0 | 84.7237 | 0 | off_peak | 691.87 |  |  | 0 | 0 | 100 | 0 | 0
4350 | 746.31 | 0 | 27.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 746.31 | 0 | 0.05921 | 5.6381 | 0 | 0 | 84.7237 | 0 | off_peak | 746.31 |  |  | 0 | 0 | 100 | 0 | 0
4351 | 800.65 | 86.7005 | 27.6 | 17.3925 | 4.9936 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 0 | 19.0375 | 795.6564 | 0 | 0.05921 | 5.1201 | 0 | 0 | 96.3218 | 4.9936 | off_peak | 795.6564 | 100 | 0 | 0.62 | 0 | 99.38 | 25.5675 | 0
4352 | 822.7 | 244.12 | 28 | 48.9004 | 48.9004 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19.0375 | 773.7996 | 0 | 0.05921 | 4.7271 | 0 | 0 | 96.3218 | 48.9004 | off_peak | 773.7996 |  |  | 5.94 | 0 | 94.06 | 231.1573 | 0
4353 | 858.84 | 514.472 | 28.3 | 102.9429 | 102.9429 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19.0375 | 755.8971 | 0 | 0.05921 | 4.437 | 0 | 0 | 96.3218 | 102.9429 | off_peak | 755.8971 |  |  | 11.99 | 0 | 88.01 | 456.7583 | 0
4354 | 826.64 | 692.662 | 28.5 | 138.4967 | 138.4967 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 30.6357 | 700.5422 | 0 | 0.05921 | 4.2707 | 0 | 0 | 96.3218 | 138.4967 | off_peak | 688.1433 | 0 | 100 | 16.75 | 0 | 83.25 | 591.4813 | 0
4355 | 816.58 | 786.418 | 28.8 | 157.0711 | 157.0711 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30.6357 | 659.5089 | 0 | 0.05921 | 4.2362 | 0 | 0 | 96.3218 | 157.0711 | off_peak | 659.5089 |  |  | 19.24 | 0 | 80.76 | 665.3883 | 0
4356 | 858.86 | 873.086 | 29 | 174.254 | 174.254 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30.6357 | 684.606 | 0 | 0.05921 | 4.2407 | 0 | 0 | 96.3218 | 174.254 | off_peak | 684.606 |  |  | 20.29 | 0 | 79.71 | 738.9508 | 0
4357 | 803.29 | 945.072 | 29.2 | 188.4835 | 188.4835 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30.6357 | 614.8065 | 0 | 0.05921 | 4.3977 | 0 | 0 | 96.3218 | 188.4835 | off_peak | 614.8065 |  |  | 23.46 | 0 | 76.54 | 828.8969 | 0
4358 | 797.82 | 910.765 | 29.3 | 181.5749 | 181.5749 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30.6357 | 616.2451 | 0 | 0.05921 | 4.8615 | 0 | 0 | 96.3218 | 181.5749 | off_peak | 616.2451 |  |  | 22.76 | 0 | 77.24 | 882.7186 | 0
4359 | 779.69 | 815.628 | 29.3 | 162.6079 | 162.6079 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 42.2338 | 629.481 | 0 | 0.05921 | 5.3287 | 0 | 0 | 96.3218 | 162.6079 | off_peak | 617.0821 | 0 | 100 | 20.86 | 0 | 79.14 | 866.4882 | 0
4360 | 820.62 | 671.374 | 29.2 | 133.8976 | 133.8976 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 53.832 | 699.1213 | 0 | 0.05921 | 5.8104 | 0 | 0 | 96.3218 | 133.8976 | off_peak | 686.7224 | 0 | 100 | 16.32 | 0 | 83.68 | 778.0021 | 0
4361 | 802.32 | 487.968 | 29 | 97.3906 | 97.3906 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 53.832 | 704.9294 | 0 | 0.05921 | 6.3024 | 0 | 0 | 96.3218 | 97.3906 | off_peak | 704.9294 |  |  | 12.14 | 0 | 87.86 | 613.7972 | 0
4362 | 786.89 | 285.764 | 28.6 | 57.1173 | 57.1173 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 53.832 | 729.7727 | 0 | 0.05921 | 6.7152 | 0 | 0 | 96.3218 | 57.1173 | off_peak | 729.7727 |  |  | 7.26 | 0 | 92.74 | 383.5519 | 0
4363 | 679.62 | 93.4044 | 28.4 | 18.6829 | 9.9565 | 0 | 8.7263 | 8.7263 | 0 | 0 | 0 | 0 | 61.9947 | 669.6635 | 0 | 0.05921 | 6.972 | 0 | 0 | 104.4846 | 9.9565 | off_peak | 669.6635 | 100 | 0 | 1.47 | 0 | 98.53 | 69.4165 | 0
4364 | 696.89 | 0 | 27.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 61.9947 | 696.89 | 0 | 0.05921 | 7.173 | 0 | 0 | 104.4846 | 0 | off_peak | 696.89 |  |  | 0 | 0 | 100 | 0 | 0
4365 | 689.52 | 0 | 27.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 61.9947 | 689.52 | 0 | 0.05921 | 7.4858 | 0 | 0 | 104.4846 | 0 | off_peak | 689.52 |  |  | 0 | 0 | 100 | 0 | 0
4366 | 693.36 | 0 | 27.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 61.9947 | 693.36 | 0 | 0.05921 | 7.756 | 0 | 0 | 104.4846 | 0 | off_peak | 693.36 |  |  | 0 | 0 | 100 | 0 | 0
4367 | 682.92 | 0 | 27.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 61.9947 | 682.92 | 0 | 0.05921 | 7.9149 | 0 | 0 | 104.4846 | 0 | off_peak | 682.92 |  |  | 0 | 0 | 100 | 0 | 0
4368 | 656 | 0 | 27.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 61.9947 | 656 | 0 | 0.05921 | 7.9831 | 0 | 0 | 104.4846 | 0 | off_peak | 656 |  |  | 0 | 0 | 100 | 0 | 0
4369 | 706.09 | 0 | 27.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 61.9947 | 706.09 | 0 | 0.05921 | 8.007 | 0 | 0 | 104.4846 | 0 | off_peak | 706.09 |  |  | 0 | 0 | 100 | 0 | 0
4370 | 664.52 | 0 | 27.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 61.9947 | 664.52 | 0 | 0.05921 | 7.8044 | 0 | 0 | 104.4846 | 0 | off_peak | 664.52 |  |  | 0 | 0 | 100 | 0 | 0
4371 | 672.79 | 0 | 27 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 61.9947 | 672.79 | 0 | 0.05921 | 7.2976 | 0 | 0 | 104.4846 | 0 | off_peak | 672.79 |  |  | 0 | 0 | 100 | 0 | 0
4372 | 702.91 | 0 | 27 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 61.9947 | 702.91 | 0 | 0.05921 | 6.7205 | 0 | 0 | 104.4846 | 0 | off_peak | 702.91 |  |  | 0 | 0 | 100 | 0 | 0
4373 | 708.77 | 0 | 27 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 61.9947 | 708.77 | 0 | 0.05921 | 6.1674 | 0 | 0 | 104.4846 | 0 | off_peak | 708.77 |  |  | 0 | 0 | 100 | 0 | 0
4374 | 741.57 | 0 | 27.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 61.9947 | 741.57 | 0 | 0.05921 | 5.5509 | 0 | 0 | 104.4846 | 0 | off_peak | 741.57 |  |  | 0 | 0 | 100 | 0 | 0
4375 | 756.16 | 93.0262 | 27.6 | 18.6615 | 18.6615 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 61.9947 | 737.4985 | 0 | 0.05921 | 5.0615 | 0 | 0 | 104.4846 | 18.6615 | off_peak | 737.4985 |  |  | 2.47 | 0 | 97.53 | 94.455 | 0
4376 | 798.95 | 143.675 | 27.9 | 28.7904 | 28.7904 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 61.9947 | 770.1596 | 0 | 0.05921 | 4.6975 | 0 | 0 | 104.4846 | 28.7904 | off_peak | 770.1596 |  |  | 3.6 | 0 | 96.4 | 135.2437 | 0
4377 | 802.2 | 513.126 | 28 | 102.7858 | 102.7858 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 61.9947 | 699.4142 | 0 | 0.05921 | 4.435 | 0 | 0 | 104.4846 | 102.7858 | off_peak | 699.4142 |  |  | 12.81 | 0 | 87.19 | 455.8521 | 0
4378 | 819.79 | 648.081 | 28.2 | 129.7246 | 129.7246 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 61.9947 | 690.0654 | 0 | 0.05921 | 4.2468 | 0 | 0 | 104.4846 | 129.7246 | off_peak | 690.0654 |  |  | 15.82 | 0 | 84.18 | 550.9122 | 0
4379 | 836.92 | 422.996 | 28.4 | 84.6083 | 84.6083 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 61.9947 | 752.3117 | 0 | 0.05921 | 4.1604 | 0 | 0 | 104.4846 | 84.6083 | off_peak | 752.3117 |  |  | 10.11 | 0 | 89.89 | 352.0053 | 0
4380 | 814.26 | 839.142 | 28.6 | 167.724 | 167.724 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 61.9947 | 646.536 | 0 | 0.05921 | 4.1449 | 0 | 0 | 104.4846 | 167.724 | off_peak | 646.536 |  |  | 20.6 | 0 | 79.4 | 695.1915 | 0
4381 | 834.32 | 943.139 | 28.7 | 188.4417 | 188.4417 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 61.9947 | 645.8783 | 0 | 0.05921 | 4.2393 | 0 | 0 | 104.4846 | 188.4417 | off_peak | 645.8783 |  |  | 22.59 | 0 | 77.41 | 798.8562 | 0
4382 | 799.08 | 823.107 | 28.7 | 164.459 | 164.459 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 61.9947 | 634.621 | 0 | 0.05921 | 4.6399 | 0 | 0 | 104.4846 | 164.459 | off_peak | 634.621 |  |  | 20.58 | 0 | 79.42 | 763.0664 | 0
4383 | 798.31 | 812.051 | 28.7 | 162.25 | 162.25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 61.9947 | 636.06 | 0 | 0.05921 | 5.1784 | 0 | 0 | 104.4846 | 162.25 | off_peak | 636.06 |  |  | 20.32 | 0 | 79.68 | 840.1999 | 0
4384 | 786.82 | 667.187 | 28.7 | 133.3058 | 133.3058 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 61.9947 | 653.5142 | 0 | 0.05921 | 5.7346 | 0 | 0 | 104.4846 | 133.3058 | off_peak | 653.5142 |  |  | 16.94 | 0 | 83.06 | 764.4518 | 0
4385 | 757.03 | 476.033 | 28.5 | 95.1821 | 95.1821 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 61.9947 | 661.8479 | 0 | 0.05921 | 6.3444 | 0 | 0 | 104.4846 | 95.1821 | off_peak | 661.8479 |  |  | 12.57 | 0 | 87.43 | 603.877 | 0
4386 | 747.46 | 265.568 | 28.2 | 53.158 | 53.158 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 61.9947 | 694.302 | 0 | 0.05921 | 6.9806 | 0 | 0 | 104.4846 | 53.158 | off_peak | 694.302 |  |  | 7.11 | 0 | 92.89 | 371.076 | 0
4387 | 680.55 | 89.5663 | 28 | 17.9413 | 5.5424 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 0 | 73.5928 | 675.0076 | 0 | 0.05921 | 7.4921 | 0 | 0 | 116.0827 | 5.5424 | off_peak | 675.0076 | 100 | 0 | 0.81 | 0 | 99.19 | 41.5238 | 0
4388 | 664.54 | 0 | 27.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 73.5928 | 664.54 | 0 | 0.05921 | 7.8088 | 0 | 0 | 116.0827 | 0 | off_peak | 664.54 |  |  | 0 | 0 | 100 | 0 | 0
4389 | 662.87 | 0 | 27.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 73.5928 | 662.87 | 0 | 0.05921 | 7.925 | 0 | 0 | 116.0827 | 0 | off_peak | 662.87 |  |  | 0 | 0 | 100 | 0 | 0
4390 | 652.76 | 0 | 27.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 73.5928 | 652.76 | 0 | 0.05921 | 8.2159 | 0 | 0 | 116.0827 | 0 | off_peak | 652.76 |  |  | 0 | 0 | 100 | 0 | 0
4391 | 664.28 | 0 | 27.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 73.5928 | 664.28 | 0 | 0.05921 | 8.2881 | 0 | 0 | 116.0827 | 0 | off_peak | 664.28 |  |  | 0 | 0 | 100 | 0 | 0
4392 | 672.53 | 0 | 27 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 73.5928 | 672.53 | 0 | 0.05921 | 8.2934 | 0 | 0 | 116.0827 | 0 | off_peak | 672.53 |  |  | 0 | 0 | 100 | 0 | 0
4393 | 638.74 | 0 | 26.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 73.5928 | 638.74 | 0 | 0.05921 | 8.1646 | 0 | 0 | 116.0827 | 0 | off_peak | 638.74 |  |  | 0 | 0 | 100 | 0 | 0
4394 | 655.29 | 0 | 26.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 73.5928 | 655.29 | 0 | 0.05921 | 7.7503 | 0 | 0 | 116.0827 | 0 | off_peak | 655.29 |  |  | 0 | 0 | 100 | 0 | 0
4395 | 666 | 0 | 26.8 | 0 | 0 | 0 | 0 | 0.80079 | 0.80079 | 0 | 0 | 0 | 74.3419 | 666.8008 | 0 | 0.05921 | 7.3272 | 0 | 0 | 116.0827 | 0 | off_peak | 666 | 0 | 100 | 0 | 0 | 100 | 0 | 0
4396 | 649.29 | 0 | 26.7 | 0 | 0 | 0 | 0 | 0.05172 | 0.05172 | 0 | 0 | 0 | 74.3903 | 649.3417 | 0 | 0.05921 | 6.7722 | 0 | 0 | 116.0827 | 0 | off_peak | 649.29 | 0 | 100 | 0 | 0 | 100 | 0 | 0
4397 | 668.43 | 0 | 26.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3903 | 668.43 | 0 | 0.05921 | 6.1403 | 0 | 0 | 116.0827 | 0 | off_peak | 668.43 |  |  | 0 | 0 | 100 | 0 | 0
4398 | 797.81 | 0 | 27 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3903 | 797.81 | 0 | 0.05921 | 5.5721 | 0 | 0 | 116.0827 | 0 | off_peak | 797.81 |  |  | 0 | 0 | 100 | 0 | 0
4399 | 775.9 | 118.305 | 27.5 | 23.7412 | 23.7378 | 0 | 0.0033404 | 0.0033404 | 0 | 0 | 0 | 0 | 74.3934 | 752.1622 | 0 | 0.05921 | 5.0449 | 0 | 0 | 116.0859 | 23.7378 | off_peak | 752.1622 | 100 | 0 | 3.06 | 0 | 96.94 | 119.7558 | 0
4400 | 837.95 | 316.085 | 27.9 | 63.339 | 63.339 | 0 | 0 | 0.00021574 | 0.00021574 | 0 | 0 | 0 | 74.3936 | 774.6112 | 0 | 0.05921 | 4.7205 | 0 | 0 | 116.0859 | 63.339 | off_peak | 774.611 | 0 | 100 | 7.56 | 0 | 92.44 | 298.9913 | 0
4401 | 900.6 | 458.135 | 28.3 | 91.6702 | 91.6702 | 0 | 0 | 1.4896e-05 | 1.4896e-05 | 0 | 0 | 0 | 74.3936 | 808.9298 | 0 | 0.05921 | 4.5163 | 0 | 0 | 116.0859 | 91.6702 | off_peak | 808.9298 | 0 | 100 | 10.18 | 0 | 89.82 | 414.0105 | 0
4402 | 900.67 | 698.718 | 28.7 | 139.6057 | 139.6057 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 761.0643 | 0 | 0.05921 | 4.4207 | 0 | 0 | 116.0859 | 139.6057 | off_peak | 761.0643 |  |  | 15.5 | 0 | 84.5 | 617.1527 | 0
4403 | 799.69 | 838.458 | 29.1 | 167.2817 | 167.2817 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 632.4083 | 0 | 0.05921 | 4.5195 | 0 | 0 | 116.0859 | 167.2817 | off_peak | 632.4083 |  |  | 20.92 | 0 | 79.08 | 756.0231 | 0
4404 | 868.75 | 924.241 | 29.3 | 184.2616 | 184.2616 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 684.4884 | 0 | 0.05921 | 4.6764 | 0 | 0 | 116.0859 | 184.2616 | off_peak | 684.4884 |  |  | 21.21 | 0 | 78.79 | 861.6772 | 0
4405 | 844.78 | 948.774 | 29.5 | 189.0143 | 189.0143 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 655.7657 | 0 | 0.088511 | 4.8678 | 0 | 0 | 116.0859 | 189.0143 | on_peak | 655.7657 |  |  | 22.37 | 0 | 77.63 | 920.0892 | 0
4406 | 856.31 | 893.517 | 29.6 | 177.9409 | 177.9409 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 678.3691 | 0 | 0.088511 | 5.3286 | 0 | 0 | 116.0859 | 177.9409 | on_peak | 678.3691 |  |  | 20.78 | 0 | 79.22 | 948.1775 | 0
4407 | 898.97 | 797.416 | 29.5 | 158.8608 | 158.8608 | 0 | 0 | 0 | 0 | 62.63 | 62.63 | 0 | 7.4394 | 677.4792 | 0 | 0.088511 | 5.781 | 0 | 0 | 116.0859 | 158.8608 | on_peak | 677.4792 |  |  | 17.67 | 6.97 | 75.36 | 918.3742 | 0
4408 | 872.61 | 652.805 | 29.3 | 130.1467 | 130.1467 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 742.4633 | 0 | 0.088511 | 6.373 | 0 | 0 | 116.0859 | 130.1467 | on_peak | 742.4633 |  |  | 14.91 | 0 | 85.09 | 829.4273 | 0
4409 | 840.78 | 471.055 | 29 | 94.015 | 94.015 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 746.765 | 0 | 0.088511 | 7.012 | 0 | 0 | 116.0859 | 94.015 | on_peak | 746.765 |  |  | 11.18 | 0 | 88.82 | 659.2344 | 0
4410 | 782.81 | 272.047 | 28.6 | 54.3756 | 54.3756 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 728.4344 | 0 | 0.088511 | 7.6409 | 0 | 0 | 116.0859 | 54.3756 | on_peak | 728.4344 |  |  | 6.95 | 0 | 93.05 | 415.4789 | 0
4411 | 788.76 | 86.2231 | 28.4 | 17.2465 | 17.2465 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 771.5135 | 0 | 0.088511 | 8.0509 | 0 | 0 | 116.0859 | 17.2465 | on_peak | 771.5135 |  |  | 2.19 | 0 | 97.81 | 138.8504 | 0
4412 | 777.62 | 0 | 27.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 777.62 | 0 | 0.088511 | 8.3378 | 0 | 0 | 116.0859 | 0 | on_peak | 777.62 |  |  | 0 | 0 | 100 | 0 | 0
4413 | 789.41 | 0 | 27.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 789.41 | 0 | 0.088511 | 8.4545 | 0 | 0 | 116.0859 | 0 | on_peak | 789.41 |  |  | 0 | 0 | 100 | 0 | 0
4414 | 782.71 | 0 | 27.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 782.71 | 0 | 0.05921 | 8.6239 | 0 | 0 | 116.0859 | 0 | off_peak | 782.71 |  |  | 0 | 0 | 100 | 0 | 0
4415 | 709.22 | 0 | 27.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 709.22 | 0 | 0.05921 | 8.5957 | 0 | 0 | 116.0859 | 0 | off_peak | 709.22 |  |  | 0 | 0 | 100 | 0 | 0
4416 | 731.86 | 0 | 27.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 731.86 | 0 | 0.05921 | 8.6494 | 0 | 0 | 116.0859 | 0 | off_peak | 731.86 |  |  | 0 | 0 | 100 | 0 | 0
4417 | 693.89 | 0 | 27.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 693.89 | 0 | 0.05921 | 8.423 | 0 | 0 | 116.0859 | 0 | off_peak | 693.89 |  |  | 0 | 0 | 100 | 0 | 0
4418 | 597.81 | 0 | 27.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 597.81 | 0 | 0.05921 | 8.205 | 0 | 0 | 116.0859 | 0 | off_peak | 597.81 |  |  | 0 | 0 | 100 | 0 | 0
4419 | 608.58 | 0 | 27.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 608.58 | 0 | 0.05921 | 7.7275 | 0 | 0 | 116.0859 | 0 | off_peak | 608.58 |  |  | 0 | 0 | 100 | 0 | 0
4420 | 610.75 | 0 | 27.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 610.75 | 0 | 0.05921 | 7.2014 | 0 | 0 | 116.0859 | 0 | off_peak | 610.75 |  |  | 0 | 0 | 100 | 0 | 0
4421 | 594.65 | 0 | 27.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 594.65 | 0 | 0.05921 | 6.6062 | 0 | 0 | 116.0859 | 0 | off_peak | 594.65 |  |  | 0 | 0 | 100 | 0 | 0
4422 | 586.81 | 0 | 27.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 586.81 | 0 | 0.05921 | 5.9552 | 0 | 0 | 116.0859 | 0 | off_peak | 586.81 |  |  | 0 | 0 | 100 | 0 | 0
4423 | 580.9 | 78.4762 | 27.5 | 15.7484 | 15.7484 | 0 | 0 | 8.7263 | 8.7263 | 0 | 0 | 0 | 15.6021 | 573.8779 | 0 | 0.05921 | 5.4309 | 0 | 0 | 116.0859 | 15.7484 | off_peak | 565.1516 | 0 | 100 | 2.71 | 0 | 97.29 | 85.5283 | 0
4424 | 603.54 | 310.015 | 27.8 | 62.1452 | 62.1452 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15.6021 | 541.3948 | 0 | 0.05921 | 5.0295 | 0 | 0 | 116.0859 | 62.1452 | off_peak | 541.3948 |  |  | 10.3 | 0 | 89.7 | 312.5605 | 0
4425 | 578.41 | 424.225 | 27.9 | 85.0087 | 85.0087 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15.6021 | 493.4013 | 0 | 0.05921 | 4.7458 | 0 | 0 | 116.0859 | 85.0087 | off_peak | 493.4013 |  |  | 14.7 | 0 | 85.3 | 403.4345 | 0
4426 | 562.95 | 573.872 | 28.1 | 114.9122 | 114.9122 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15.6021 | 448.0378 | 0 | 0.05921 | 4.5582 | 0 | 0 | 116.0859 | 114.9122 | off_peak | 448.0378 |  |  | 20.41 | 0 | 79.59 | 523.7906 | 0
4427 | 610.3 | 741.581 | 28.3 | 148.3861 | 148.3861 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15.6021 | 461.9139 | 0 | 0.05921 | 4.4234 | 0 | 0 | 116.0859 | 148.3861 | off_peak | 461.9139 |  |  | 24.31 | 0 | 75.69 | 656.3783 | 0
4428 | 612.87 | 597.253 | 28.6 | 119.3763 | 119.3763 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15.6021 | 493.4937 | 0 | 0.05921 | 4.4249 | 0 | 0 | 116.0859 | 119.3763 | off_peak | 493.4937 |  |  | 19.48 | 0 | 80.52 | 528.2262 | 0
4429 | 572.12 | 181.449 | 28.7 | 36.254 | 36.254 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 27.2003 | 548.2649 | 0 | 0.05921 | 4.488 | 0 | 0 | 116.0859 | 36.254 | on_peak | 535.866 | 0 | 100 | 6.34 | 0 | 93.66 | 162.7085 | 0
4430 | 609.57 | 633.833 | 28.8 | 126.5953 | 126.5953 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 38.7984 | 495.3736 | 0 | 0.05921 | 4.9248 | 0 | 0 | 116.0859 | 126.5953 | on_peak | 482.9747 | 0 | 100 | 20.77 | 0 | 79.23 | 623.4567 | 0
4431 | 592.65 | 565.109 | 28.8 | 112.8691 | 112.8691 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 38.7984 | 479.7809 | 0 | 0.05921 | 5.6053 | 0 | 0 | 116.0859 | 112.8691 | on_peak | 479.7809 |  |  | 19.04 | 0 | 80.96 | 632.6618 | 0
4432 | 602.96 | 662.632 | 28.8 | 132.3474 | 132.3474 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 38.7984 | 470.6126 | 0 | 0.05921 | 6.2702 | 0 | 0 | 116.0859 | 132.3474 | on_peak | 470.6126 |  |  | 21.95 | 0 | 78.05 | 829.8488 | 0
4433 | 593.69 | 482.922 | 28.8 | 96.4539 | 96.4539 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 38.7984 | 497.2361 | 0 | 0.05921 | 6.9096 | 0 | 0 | 116.0859 | 96.4539 | on_peak | 497.2361 |  |  | 16.25 | 0 | 83.75 | 666.4534 | 0
4434 | 596.71 | 282.289 | 28.6 | 56.4227 | 56.4227 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 38.7984 | 540.2873 | 0 | 0.05921 | 7.553 | 0 | 0 | 116.0859 | 56.4227 | on_peak | 540.2873 |  |  | 9.46 | 0 | 90.54 | 426.1619 | 0
4435 | 601.46 | 92.2655 | 28.5 | 18.4483 | 6.0494 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 0 | 50.3966 | 595.4106 | 0 | 0.05921 | 8.0736 | 0 | 0 | 127.684 | 6.0494 | on_peak | 595.4106 | 100 | 0 | 1.01 | 0 | 98.99 | 48.8402 | 0
4436 | 605.08 | 0 | 28 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50.3966 | 605.08 | 0 | 0.05921 | 8.3152 | 0 | 0 | 127.684 | 0 | on_peak | 605.08 |  |  | 0 | 0 | 100 | 0 | 0
4437 | 575.67 | 0 | 27.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50.3966 | 575.67 | 0 | 0.05921 | 8.4668 | 0 | 0 | 127.684 | 0 | on_peak | 575.67 |  |  | 0 | 0 | 100 | 0 | 0
4438 | 591.06 | 0 | 27.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50.3966 | 591.06 | 0 | 0.05921 | 8.6516 | 0 | 0 | 127.684 | 0 | off_peak | 591.06 |  |  | 0 | 0 | 100 | 0 | 0
4439 | 587.51 | 0 | 27.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50.3966 | 587.51 | 0 | 0.05921 | 8.5426 | 0 | 0 | 127.684 | 0 | off_peak | 587.51 |  |  | 0 | 0 | 100 | 0 | 0
4440 | 575.96 | 0 | 27.7 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 61.9947 | 588.3589 | 0 | 0.05921 | 8.4097 | 0 | 0 | 127.684 | 0 | off_peak | 575.96 | 0 | 100 | 0 | 0 | 100 | 0 | 0
4441 | 580.02 | 0 | 27.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 61.9947 | 580.02 | 0 | 0.05921 | 8.1826 | 0 | 0 | 127.684 | 0 | off_peak | 580.02 |  |  | 0 | 0 | 100 | 0 | 0
4442 | 601.28 | 0 | 27.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 61.9947 | 601.28 | 0 | 0.05921 | 7.9403 | 0 | 0 | 127.684 | 0 | off_peak | 601.28 |  |  | 0 | 0 | 100 | 0 | 0
4443 | 584.12 | 0 | 27.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 61.9947 | 584.12 | 0 | 0.05921 | 7.5173 | 0 | 0 | 127.684 | 0 | off_peak | 584.12 |  |  | 0 | 0 | 100 | 0 | 0
4444 | 583.34 | 0 | 27.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 61.9947 | 583.34 | 0 | 0.05921 | 7.3197 | 0 | 0 | 127.684 | 0 | off_peak | 583.34 |  |  | 0 | 0 | 100 | 0 | 0
4445 | 604.29 | 0 | 27.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 61.9947 | 604.29 | 0 | 0.05921 | 6.8643 | 0 | 0 | 127.684 | 0 | off_peak | 604.29 |  |  | 0 | 0 | 100 | 0 | 0
4446 | 690.7 | 0 | 27.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 61.9947 | 690.7 | 0 | 0.05921 | 6.1795 | 0 | 0 | 127.684 | 0 | off_peak | 690.7 |  |  | 0 | 0 | 100 | 0 | 0
4447 | 759.17 | 114.301 | 27.9 | 22.9043 | 10.5054 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 0 | 73.5928 | 748.6646 | 0 | 0.05921 | 5.561 | 0 | 0 | 139.2821 | 10.5054 | off_peak | 748.6646 | 100 | 0 | 1.38 | 0 | 98.62 | 58.4204 | 0
4448 | 807.74 | 309.728 | 28.2 | 61.9974 | 61.9974 | 0 | 0 | 0.80079 | 0.80079 | 0 | 0 | 0 | 74.3419 | 746.5434 | 0 | 0.05921 | 5.1596 | 0 | 0 | 139.2821 | 61.9974 | off_peak | 745.7426 | 0 | 100 | 7.68 | 0 | 92.32 | 319.8839 | 0
4449 | 814.24 | 512.276 | 28.3 | 102.5035 | 102.4518 | 0 | 0.05172 | 0.05172 | 0 | 0 | 0 | 0 | 74.3903 | 711.7882 | 0 | 0.05921 | 4.8902 | 0 | 0 | 139.3305 | 102.4518 | off_peak | 711.7882 | 100 | 0 | 12.58 | 0 | 87.42 | 501.0076 | 0
4450 | 822.4 | 586.67 | 28.4 | 117.3466 | 117.3466 | 0 | 0 | 0.0033404 | 0.0033404 | 0 | 0 | 0 | 74.3934 | 705.0568 | 0 | 0.05921 | 4.7861 | 0 | 0 | 139.3305 | 117.3466 | off_peak | 705.0534 | 0 | 100 | 14.27 | 0 | 85.73 | 561.6324 | 0
4451 | 843.32 | 834.469 | 28.5 | 166.8508 | 166.8508 | 0 | 0 | 0.00021574 | 0.00021574 | 0 | 0 | 0 | 74.3936 | 676.4694 | 0 | 0.05921 | 4.8579 | 0 | 0 | 139.3305 | 166.8508 | off_peak | 676.4692 | 0 | 100 | 19.78 | 0 | 80.22 | 810.5483 | 0
4452 | 957.93 | 865.632 | 28.6 | 173.0187 | 173.0187 | 0 | 0 | 1.3934e-05 | 1.3934e-05 | 0 | 0 | 0 | 74.3936 | 784.9113 | 0 | 0.05921 | 5.0442 | 0 | 0 | 139.3305 | 173.0187 | off_peak | 784.9113 | 0 | 100 | 18.06 | 0 | 81.94 | 872.7378 | 0
4453 | 902.98 | 952.454 | 28.7 | 190.3029 | 190.3029 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 712.6771 | 0 | 0.088511 | 5.1883 | 0 | 0 | 139.3305 | 190.3029 | on_peak | 712.6771 |  |  | 21.07 | 0 | 78.93 | 987.3514 | 0
4454 | 893.05 | 891.792 | 28.8 | 178.1174 | 178.1174 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 714.9326 | 0 | 0.088511 | 5.5874 | 0 | 0 | 139.3305 | 178.1174 | on_peak | 714.9326 |  |  | 19.94 | 0 | 80.06 | 995.2096 | 0
4455 | 879.43 | 795.215 | 28.8 | 158.8281 | 158.8281 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 720.6019 | 0 | 0.088511 | 6.1254 | 0 | 0 | 139.3305 | 158.8281 | on_peak | 720.6019 |  |  | 18.06 | 0 | 81.94 | 972.8934 | 0
4456 | 859.06 | 651.355 | 28.8 | 130.095 | 130.095 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 728.965 | 0 | 0.088511 | 6.7429 | 0 | 0 | 139.3305 | 130.095 | on_peak | 728.965 |  |  | 15.14 | 0 | 84.86 | 877.2151 | 0
4457 | 853.63 | 470.055 | 28.7 | 93.9183 | 93.9183 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 759.7117 | 0 | 0.088511 | 7.2954 | 0 | 0 | 139.3305 | 93.9183 | on_peak | 759.7117 |  |  | 11 | 0 | 89 | 685.1701 | 0
4458 | 896.37 | 271.244 | 28.5 | 54.2348 | 54.2348 | 0 | 0 | 0 | 0 | 62.63 | 62.63 | 0 | 7.4394 | 779.5052 | 0 | 0.088511 | 7.8959 | 0 | 0 | 139.3305 | 54.2348 | on_peak | 779.5052 |  |  | 6.05 | 6.99 | 86.96 | 428.2355 | 0
4459 | 847.67 | 85.5188 | 28.3 | 17.1118 | 17.1118 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 830.5582 | 0 | 0.088511 | 8.4152 | 0 | 0 | 139.3305 | 17.1118 | on_peak | 830.5582 |  |  | 2.02 | 0 | 97.98 | 143.9993 | 0
4460 | 880.86 | 0 | 28 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 880.86 | 0 | 0.088511 | 8.505 | 0 | 0 | 139.3305 | 0 | on_peak | 880.86 |  |  | 0 | 0 | 100 | 0 | 0
4461 | 869.4 | 0 | 28 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 869.4 | 0 | 0.088511 | 8.6427 | 0 | 0 | 139.3305 | 0 | on_peak | 869.4 |  |  | 0 | 0 | 100 | 0 | 0
4462 | 807.51 | 0 | 28 | 0 | 0 | 0 | 0 | 8.7263 | 8.7263 | 0 | 0 | 0 | 15.6021 | 816.2363 | 0 | 0.05921 | 8.7651 | 0 | 0 | 139.3305 | 0 | off_peak | 807.51 | 0 | 100 | 0 | 0 | 100 | 0 | 0
4463 | 849.64 | 0 | 27.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15.6021 | 849.64 | 0 | 0.05921 | 8.7917 | 0 | 0 | 139.3305 | 0 | off_peak | 849.64 |  |  | 0 | 0 | 100 | 0 | 0
4464 | 816.81 | 0 | 27.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15.6021 | 816.81 | 0 | 0.05921 | 8.5836 | 0 | 0 | 139.3305 | 0 | off_peak | 816.81 |  |  | 0 | 0 | 100 | 0 | 0
4465 | 741.34 | 0 | 27.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15.6021 | 741.34 | 0 | 0.05921 | 8.2442 | 0 | 0 | 139.3305 | 0 | off_peak | 741.34 |  |  | 0 | 0 | 100 | 0 | 0
4466 | 651.91 | 0 | 27.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15.6021 | 651.91 | 0 | 0.05921 | 8.0297 | 0 | 0 | 139.3305 | 0 | off_peak | 651.91 |  |  | 0 | 0 | 100 | 0 | 0
4467 | 641.96 | 0 | 27.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15.6021 | 641.96 | 0 | 0.05921 | 7.8185 | 0 | 0 | 139.3305 | 0 | off_peak | 641.96 |  |  | 0 | 0 | 100 | 0 | 0
4468 | 634.71 | 0 | 27.6 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 27.2003 | 647.1089 | 0 | 0.05921 | 7.2825 | 0 | 0 | 139.3305 | 0 | off_peak | 634.71 | 0 | 100 | 0 | 0 | 100 | 0 | 0
4469 | 662.05 | 0 | 27.6 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 38.7984 | 674.4489 | 0 | 0.05921 | 6.7006 | 0 | 0 | 139.3305 | 0 | off_peak | 662.05 | 0 | 100 | 0 | 0 | 100 | 0 | 0
4470 | 690.94 | 0 | 27.7 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 50.3966 | 703.3389 | 0 | 0.05921 | 6.0173 | 0 | 0 | 139.3305 | 0 | off_peak | 690.94 | 0 | 100 | 0 | 0 | 100 | 0 | 0
4471 | 728.06 | 116.195 | 28.1 | 23.2669 | 23.2669 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 61.9947 | 717.192 | 0 | 0.05921 | 5.4794 | 0 | 0 | 139.3305 | 23.2669 | off_peak | 704.7931 | 0 | 100 | 3.2 | 0 | 96.8 | 127.4878 | 0
4472 | 797.97 | 313.584 | 28.5 | 62.7007 | 62.7007 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 73.5928 | 747.6683 | 0 | 0.05921 | 5.1587 | 0 | 0 | 139.3305 | 62.7007 | off_peak | 735.2693 | 0 | 100 | 7.86 | 0 | 92.14 | 323.454 | 0
4473 | 882.13 | 516.312 | 28.8 | 103.1229 | 103.1229 | 0 | 0 | 0.80079 | 0.80079 | 0 | 0 | 0 | 74.3419 | 779.8079 | 0 | 0.05921 | 4.9217 | 0 | 0 | 139.3305 | 103.1229 | off_peak | 779.0071 | 0 | 100 | 11.69 | 0 | 88.31 | 507.5407 | 0
4474 | 832.29 | 511.034 | 29.2 | 101.9197 | 101.9197 | 0 | 0 | 0.05172 | 0.05172 | 0 | 0 | 0 | 74.3903 | 730.422 | 0 | 0.05921 | 4.8264 | 0 | 0 | 139.3305 | 101.9197 | off_peak | 730.3703 | 0 | 100 | 12.25 | 0 | 87.75 | 491.9061 | 0
4475 | 854.78 | 760.265 | 29.4 | 151.515 | 151.515 | 0 | 0 | 0.0033404 | 0.0033404 | 0 | 0 | 0 | 74.3934 | 703.2683 | 0 | 0.05921 | 4.9093 | 0 | 0 | 139.3305 | 151.515 | off_peak | 703.265 | 0 | 100 | 17.73 | 0 | 82.27 | 743.8352 | 0
4476 | 945.43 | 917.459 | 29.6 | 182.7088 | 182.7088 | 0 | 0 | 0.00021574 | 0.00021574 | 0 | 0 | 0 | 74.3936 | 762.7214 | 0 | 0.05921 | 5.084 | 0 | 0 | 139.3305 | 182.7088 | off_peak | 762.7212 | 0 | 100 | 19.33 | 0 | 80.67 | 928.883 | 0
4477 | 888.57 | 405.639 | 29.7 | 80.7521 | 80.7521 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 807.8179 | 0 | 0.088511 | 5.2801 | 0 | 0 | 139.3305 | 80.7521 | on_peak | 807.8179 |  |  | 9.09 | 0 | 90.91 | 426.3816 | 0
4478 | 897.61 | 909.68 | 29.7 | 181.0934 | 181.0934 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 716.5166 | 0 | 0.088511 | 5.6417 | 0 | 0 | 139.3305 | 181.0934 | on_peak | 716.5166 |  |  | 20.18 | 0 | 79.82 | 1021.681 | 0
4479 | 1003.94 | 816.227 | 29.7 | 162.4893 | 162.4893 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 841.4507 | 0 | 0.088511 | 6.101 | 0 | 0 | 139.3305 | 162.4893 | on_peak | 841.4507 |  |  | 16.19 | 0 | 83.81 | 991.344 | 0
4480 | 864.55 | 670.849 | 29.5 | 133.6462 | 133.6462 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 730.9038 | 0 | 0.088511 | 6.6345 | 0 | 0 | 139.3305 | 133.6462 | on_peak | 730.9038 |  |  | 15.46 | 0 | 84.54 | 886.6757 | 0
4481 | 850.88 | 487.016 | 29.3 | 97.0941 | 97.0941 | 0 | 0 | 0 | 0 | 62.63 | 62.63 | 0 | 7.4394 | 691.1559 | 0 | 0.088511 | 7.2035 | 62.63 | 0 | 72.3763 | 159.7241 | on_peak | 691.1559 |  |  | 11.41 | 7.36 | 81.23 | 1150.5706 | 0
4482 | 897.87 | 283.623 | 28.9 | 56.6273 | 56.6273 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 841.2427 | 0 | 0.088511 | 7.6843 | 0 | 0 | 72.3763 | 56.6273 | on_peak | 841.2427 |  |  | 6.31 | 0 | 93.69 | 435.1414 | 0
4483 | 885.95 | 91.5283 | 28.7 | 18.2876 | 18.2876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 867.6624 | 0 | 0.088511 | 8.2054 | 0 | 0 | 72.3763 | 18.2876 | on_peak | 867.6624 |  |  | 2.06 | 0 | 97.94 | 150.0565 | 0
4484 | 914.35 | 0 | 28.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 914.35 | 0 | 0.088511 | 8.5337 | 0 | 0 | 72.3763 | 0 | on_peak | 914.35 |  |  | 0 | 0 | 100 | 0 | 0
4485 | 902.85 | 0 | 28.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 902.85 | 0 | 0.088511 | 8.6584 | 0 | 0 | 72.3763 | 0 | on_peak | 902.85 |  |  | 0 | 0 | 100 | 0 | 0
4486 | 856.69 | 0 | 28 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 19.0375 | 869.0889 | 0 | 0.05921 | 8.6109 | 0 | 0 | 72.3763 | 0 | off_peak | 856.69 | 0 | 100 | 0 | 0 | 100 | 0 | 0
4487 | 860.03 | 0 | 27.9 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 30.6357 | 872.4289 | 0 | 0.05921 | 8.5615 | 0 | 0 | 72.3763 | 0 | off_peak | 860.03 | 0 | 100 | 0 | 0 | 100 | 0 | 0
4488 | 862.64 | 0 | 27.8 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 42.2338 | 875.0389 | 0 | 0.05921 | 8.488 | 0 | 0 | 72.3763 | 0 | off_peak | 862.64 | 0 | 100 | 0 | 0 | 100 | 0 | 0
4489 | 738.81 | 0 | 27.7 | 0 | 0 | 0 | 0 | 8.7263 | 8.7263 | 0 | 0 | 0 | 50.3966 | 747.5363 | 0 | 0.05921 | 8.1299 | 0 | 0 | 72.3763 | 0 | off_peak | 738.81 | 0 | 100 | 0 | 0 | 100 | 0 | 0
4490 | 655.82 | 0 | 27.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50.3966 | 655.82 | 0 | 0.05921 | 7.9416 | 0 | 0 | 72.3763 | 0 | off_peak | 655.82 |  |  | 0 | 0 | 100 | 0 | 0
4491 | 636.04 | 0 | 27.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50.3966 | 636.04 | 0 | 0.05921 | 7.6337 | 0 | 0 | 72.3763 | 0 | off_peak | 636.04 |  |  | 0 | 0 | 100 | 0 | 0
4492 | 658.67 | 0 | 27.5 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 61.9947 | 671.0689 | 0 | 0.05921 | 7.0337 | 0 | 0 | 72.3763 | 0 | off_peak | 658.67 | 0 | 100 | 0 | 0 | 100 | 0 | 0
4493 | 657.67 | 0 | 27.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 61.9947 | 657.67 | 0 | 0.05921 | 6.3229 | 0 | 0 | 72.3763 | 0 | off_peak | 657.67 |  |  | 0 | 0 | 100 | 0 | 0
4494 | 731.61 | 0 | 27.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 61.9947 | 731.61 | 0 | 0.05921 | 5.768 | 0 | 0 | 72.3763 | 0 | off_peak | 731.61 |  |  | 0 | 0 | 100 | 0 | 0
4495 | 732.99 | 81.3588 | 28.1 | 16.2913 | 16.2913 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 73.5928 | 729.0976 | 0 | 0.05921 | 5.3309 | 0 | 0 | 72.3763 | 16.2913 | off_peak | 716.6987 | 0 | 100 | 2.22 | 0 | 97.78 | 86.8479 | 0
4496 | 847.69 | 310.879 | 28.4 | 62.1825 | 62.1825 | 0 | 0 | 0.80079 | 0.80079 | 0 | 0 | 0 | 74.3419 | 786.3083 | 0 | 0.05921 | 4.9892 | 0 | 0 | 72.3763 | 62.1825 | off_peak | 785.5075 | 0 | 100 | 7.34 | 0 | 92.66 | 310.2382 | 0
4497 | 911.62 | 488.674 | 28.8 | 97.6028 | 97.6028 | 0 | 0 | 0.05172 | 0.05172 | 0 | 0 | 0 | 74.3903 | 814.069 | 0 | 0.05921 | 4.7698 | 0 | 0 | 72.3763 | 97.6028 | off_peak | 814.0172 | 0 | 100 | 10.71 | 0 | 89.29 | 465.5468 | 0
4498 | 872.98 | 638.293 | 29.1 | 127.3465 | 127.3465 | 0 | 0 | 0.0033404 | 0.0033404 | 0 | 0 | 0 | 74.3934 | 745.6368 | 0 | 0.05921 | 4.6795 | 0 | 0 | 72.3763 | 127.3465 | off_peak | 745.6335 | 0 | 100 | 14.59 | 0 | 85.41 | 595.914 | 0
4499 | 824.9 | 660.444 | 29.4 | 131.6215 | 131.6215 | 0 | 0 | 0.00021574 | 0.00021574 | 0 | 0 | 0 | 74.3936 | 693.2787 | 0 | 0.05921 | 4.7761 | 0 | 0 | 72.3763 | 131.6215 | off_peak | 693.2785 | 0 | 100 | 15.96 | 0 | 84.04 | 628.642 | 0
4500 | 909.53 | 819.498 | 29.6 | 163.2002 | 163.2002 | 0 | 0 | 1.3934e-05 | 1.3934e-05 | 0 | 0 | 0 | 74.3936 | 746.3298 | 0 | 0.05921 | 4.9317 | 0 | 0 | 72.3763 | 163.2002 | off_peak | 746.3298 | 0 | 100 | 17.94 | 0 | 82.06 | 804.8543 | 0
4501 | 850.38 | 884.121 | 29.7 | 176.0052 | 176.0052 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 674.3748 | 0 | 0.088511 | 5.1425 | 0 | 0 | 72.3763 | 176.0052 | on_peak | 674.3748 |  |  | 20.7 | 0 | 79.3 | 905.1099 | 0
4502 | 867.56 | 848.928 | 29.7 | 168.9992 | 168.9992 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 698.5608 | 0 | 0.088511 | 5.5499 | 0 | 0 | 72.3763 | 168.9992 | on_peak | 698.5608 |  |  | 19.48 | 0 | 80.52 | 937.9325 | 0
4503 | 949.46 | 614.887 | 29.6 | 122.4527 | 122.4527 | 0 | 0 | 0 | 0 | 62.63 | 62.63 | 0 | 7.4394 | 764.3774 | 0 | 0.088511 | 6.0706 | 0 | 0 | 72.3763 | 122.4527 | on_peak | 764.3774 |  |  | 12.9 | 6.6 | 80.51 | 743.3583 | 0
4504 | 899.44 | 523.476 | 29.5 | 104.2866 | 104.2866 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 795.1534 | 0 | 0.088511 | 6.5642 | 0 | 0 | 72.3763 | 104.2866 | on_peak | 795.1534 |  |  | 11.59 | 0 | 88.41 | 684.561 | 0
4505 | 937.62 | 477.025 | 29.3 | 95.1022 | 95.1022 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 842.5178 | 0 | 0.088511 | 7.1496 | 0 | 0 | 72.3763 | 95.1022 | on_peak | 842.5178 |  |  | 10.14 | 0 | 89.86 | 679.9451 | 0
4506 | 940.05 | 277.548 | 28.9 | 55.4144 | 55.4144 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 884.6356 | 0 | 0.088511 | 7.6689 | 0 | 0 | 72.3763 | 55.4144 | on_peak | 884.6356 |  |  | 5.89 | 0 | 94.11 | 424.9661 | 0
4507 | 867.96 | 88.1406 | 28.8 | 17.6043 | 17.6043 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 850.3557 | 0 | 0.088511 | 8.0883 | 0 | 0 | 72.3763 | 17.6043 | on_peak | 850.3557 |  |  | 2.03 | 0 | 97.97 | 142.3881 | 0
4508 | 933.95 | 0 | 28.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 933.95 | 0 | 0.088511 | 8.1893 | 0 | 0 | 72.3763 | 0 | on_peak | 933.95 |  |  | 0 | 0 | 100 | 0 | 0
4509 | 847.65 | 0 | 28.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 847.65 | 0 | 0.088511 | 8.1169 | 0 | 0 | 72.3763 | 0 | on_peak | 847.65 |  |  | 0 | 0 | 100 | 0 | 0
4510 | 798.73 | 0 | 28.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 798.73 | 0 | 0.05921 | 8.0822 | 0 | 0 | 72.3763 | 0 | off_peak | 798.73 |  |  | 0 | 0 | 100 | 0 | 0
4511 | 864.51 | 0 | 28.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 864.51 | 0 | 0.05921 | 8.0449 | 0 | 0 | 72.3763 | 0 | off_peak | 864.51 |  |  | 0 | 0 | 100 | 0 | 0
4512 | 797.93 | 0 | 28 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 797.93 | 0 | 0.05921 | 7.7529 | 0 | 0 | 72.3763 | 0 | off_peak | 797.93 |  |  | 0 | 0 | 100 | 0 | 0
4513 | 744.28 | 0 | 27.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 744.28 | 0 | 0.05921 | 7.6032 | 0 | 0 | 72.3763 | 0 | off_peak | 744.28 |  |  | 0 | 0 | 100 | 0 | 0
4514 | 695.78 | 0 | 27.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 695.78 | 0 | 0.05921 | 7.3515 | 0 | 0 | 72.3763 | 0 | off_peak | 695.78 |  |  | 0 | 0 | 100 | 0 | 0
4515 | 678.36 | 0 | 27.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 678.36 | 0 | 0.05921 | 7.0028 | 0 | 0 | 72.3763 | 0 | off_peak | 678.36 |  |  | 0 | 0 | 100 | 0 | 0
4516 | 708.71 | 0 | 27.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 708.71 | 0 | 0.05921 | 6.5087 | 0 | 0 | 72.3763 | 0 | off_peak | 708.71 |  |  | 0 | 0 | 100 | 0 | 0
4517 | 701.46 | 0 | 27.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 701.46 | 0 | 0.05921 | 5.9753 | 0 | 0 | 72.3763 | 0 | off_peak | 701.46 |  |  | 0 | 0 | 100 | 0 | 0
4518 | 698.64 | 0 | 27.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 698.64 | 0 | 0.05921 | 5.3413 | 0 | 0 | 72.3763 | 0 | off_peak | 698.64 |  |  | 0 | 0 | 100 | 0 | 0
4519 | 681.42 | 113.614 | 28.3 | 22.7335 | 22.7335 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 658.6865 | 0 | 0.05921 | 4.895 | 0 | 0 | 72.3763 | 22.7335 | off_peak | 658.6865 |  |  | 3.34 | 0 | 96.66 | 111.2817 | 0
4520 | 785.39 | 310.151 | 28.7 | 61.969 | 61.969 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 723.421 | 0 | 0.05921 | 4.6099 | 0 | 0 | 72.3763 | 61.969 | off_peak | 723.421 |  |  | 7.89 | 0 | 92.11 | 285.6734 | 0
4521 | 808.09 | 472.753 | 28.9 | 94.3884 | 94.3884 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 713.7016 | 0 | 0.05921 | 4.3772 | 0 | 0 | 72.3763 | 94.3884 | off_peak | 713.7016 |  |  | 11.68 | 0 | 88.32 | 413.1599 | 0
4522 | 811.68 | 380.704 | 29.2 | 75.9269 | 75.9269 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 735.7531 | 0 | 0.05921 | 4.2442 | 0 | 0 | 72.3763 | 75.9269 | off_peak | 735.7531 |  |  | 9.35 | 0 | 90.65 | 322.2526 | 0
4523 | 774.19 | 98.8 | 29.5 | 19.6829 | 19.6829 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 754.5071 | 0 | 0.05921 | 4.2353 | 0 | 0 | 72.3763 | 19.6829 | off_peak | 754.5071 |  |  | 2.54 | 0 | 97.46 | 83.3623 | 0
4524 | 780.7 | 776.934 | 29.7 | 154.6671 | 154.6671 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 626.0329 | 0 | 0.05921 | 4.2881 | 0 | 0 | 72.3763 | 154.6671 | off_peak | 626.0329 |  |  | 19.81 | 0 | 80.19 | 663.2218 | 0
4525 | 747.57 | 938.955 | 29.8 | 186.8528 | 186.8528 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 560.7172 | 0 | 0.05921 | 4.4389 | 0 | 0 | 72.3763 | 186.8528 | off_peak | 560.7172 |  |  | 24.99 | 0 | 75.01 | 829.4134 | 0
4526 | 762.85 | 857.84 | 29.9 | 170.6483 | 170.6483 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 592.2017 | 0 | 0.05921 | 4.8825 | 0 | 0 | 72.3763 | 170.6483 | off_peak | 592.2017 |  |  | 22.37 | 0 | 77.63 | 833.1853 | 0
4527 | 788.78 | 808.064 | 29.8 | 160.8054 | 160.8054 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 627.9746 | 0 | 0.05921 | 5.5026 | 0 | 0 | 72.3763 | 160.8054 | off_peak | 627.9746 |  |  | 20.39 | 0 | 79.61 | 884.8536 | 0
4528 | 771.08 | 512.561 | 29.7 | 102.0374 | 102.0374 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 669.0426 | 0 | 0.05921 | 6.0226 | 0 | 0 | 72.3763 | 102.0374 | off_peak | 669.0426 |  |  | 13.23 | 0 | 86.77 | 614.535 | 0
4529 | 788.41 | 481.494 | 29.5 | 95.923 | 95.923 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 692.487 | 0 | 0.05921 | 6.5774 | 0 | 0 | 72.3763 | 95.923 | off_peak | 692.487 |  |  | 12.17 | 0 | 87.83 | 630.9265 | 0
4530 | 678.74 | 279.156 | 29.1 | 55.6947 | 55.6947 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 623.0453 | 0 | 0.05921 | 7.1543 | 0 | 0 | 72.3763 | 55.6947 | off_peak | 623.0453 |  |  | 8.21 | 0 | 91.79 | 398.4556 | 0
4531 | 671.77 | 54.2967 | 28.9 | 10.8407 | 2.1144 | 0 | 8.7263 | 8.7263 | 0 | 0 | 0 | 0 | 15.6021 | 669.6556 | 0 | 0.05921 | 7.4812 | 0 | 0 | 80.539 | 2.1144 | off_peak | 669.6556 | 100 | 0 | 0.31 | 0 | 99.69 | 15.8181 | 0
4532 | 619.92 | 0 | 28.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15.6021 | 619.92 | 0 | 0.05921 | 7.5286 | 0 | 0 | 80.539 | 0 | off_peak | 619.92 |  |  | 0 | 0 | 100 | 0 | 0
4533 | 653.43 | 0 | 28.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15.6021 | 653.43 | 0 | 0.05921 | 7.5266 | 0 | 0 | 80.539 | 0 | off_peak | 653.43 |  |  | 0 | 0 | 100 | 0 | 0
4534 | 621.4 | 0 | 27.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15.6021 | 621.4 | 0 | 0.05921 | 7.5652 | 0 | 0 | 80.539 | 0 | off_peak | 621.4 |  |  | 0 | 0 | 100 | 0 | 0
4535 | 588.54 | 0 | 27.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15.6021 | 588.54 | 0 | 0.05921 | 7.6859 | 0 | 0 | 80.539 | 0 | off_peak | 588.54 |  |  | 0 | 0 | 100 | 0 | 0
4536 | 651.57 | 0 | 27.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15.6021 | 651.57 | 0 | 0.05921 | 7.448 | 0 | 0 | 80.539 | 0 | off_peak | 651.57 |  |  | 0 | 0 | 100 | 0 | 0
4537 | 618.85 | 0 | 27.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15.6021 | 618.85 | 0 | 0.05921 | 7.2676 | 0 | 0 | 80.539 | 0 | off_peak | 618.85 |  |  | 0 | 0 | 100 | 0 | 0
4538 | 611.94 | 0 | 27.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15.6021 | 611.94 | 0 | 0.05921 | 7.0669 | 0 | 0 | 80.539 | 0 | off_peak | 611.94 |  |  | 0 | 0 | 100 | 0 | 0
4539 | 634.08 | 0 | 27.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15.6021 | 634.08 | 0 | 0.05921 | 6.7447 | 0 | 0 | 80.539 | 0 | off_peak | 634.08 |  |  | 0 | 0 | 100 | 0 | 0
4540 | 635.25 | 0 | 27.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15.6021 | 635.25 | 0 | 0.05921 | 6.2823 | 0 | 0 | 80.539 | 0 | off_peak | 635.25 |  |  | 0 | 0 | 100 | 0 | 0
4541 | 637.34 | 0 | 27 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15.6021 | 637.34 | 0 | 0.05921 | 5.7368 | 0 | 0 | 80.539 | 0 | off_peak | 637.34 |  |  | 0 | 0 | 100 | 0 | 0
4542 | 710.81 | 0 | 27.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15.6021 | 710.81 | 0 | 0.05921 | 5.3217 | 0 | 0 | 80.539 | 0 | off_peak | 710.81 |  |  | 0 | 0 | 100 | 0 | 0
4543 | 730.98 | 113.809 | 27.9 | 22.8057 | 22.8057 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15.6021 | 708.1743 | 0 | 0.05921 | 4.9211 | 0 | 0 | 80.539 | 22.8057 | off_peak | 708.1743 |  |  | 3.12 | 0 | 96.88 | 112.2303 | 0
4544 | 791.92 | 311.34 | 28.3 | 62.2974 | 62.2974 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15.6021 | 729.6226 | 0 | 0.05921 | 4.6478 | 0 | 0 | 80.539 | 62.2974 | off_peak | 729.6226 |  |  | 7.87 | 0 | 92.13 | 289.5426 | 0
4545 | 757.23 | 512.825 | 28.7 | 102.4638 | 102.4638 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15.6021 | 654.7662 | 0 | 0.05921 | 4.4333 | 0 | 0 | 80.539 | 102.4638 | off_peak | 654.7662 |  |  | 13.53 | 0 | 86.47 | 454.254 | 0
4546 | 791.68 | 644.168 | 29 | 128.5656 | 128.5656 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15.6021 | 663.1144 | 0 | 0.05921 | 4.3063 | 0 | 0 | 80.539 | 128.5656 | off_peak | 663.1144 |  |  | 16.24 | 0 | 83.76 | 553.6367 | 0
4547 | 766.01 | 833.35 | 29.3 | 166.1411 | 166.1411 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15.6021 | 599.8689 | 0 | 0.05921 | 4.2682 | 0 | 0 | 80.539 | 166.1411 | off_peak | 599.8689 |  |  | 21.69 | 0 | 78.31 | 709.1287 | 0
4548 | 804.71 | 922.856 | 29.5 | 183.8509 | 183.8509 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15.6021 | 620.8591 | 0 | 0.05921 | 4.2901 | 0 | 0 | 80.539 | 183.8509 | off_peak | 620.8591 |  |  | 22.85 | 0 | 77.15 | 788.7389 | 0
4549 | 791.25 | 845.092 | 29.6 | 168.2972 | 168.2972 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15.6021 | 622.9528 | 0 | 0.05921 | 4.3062 | 0 | 0 | 80.539 | 168.2972 | off_peak | 622.9528 |  |  | 21.27 | 0 | 78.73 | 724.7137 | 0
4550 | 796.37 | 857.042 | 29.7 | 170.6145 | 170.6145 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15.6021 | 625.7555 | 0 | 0.05921 | 4.6289 | 0 | 0 | 80.539 | 170.6145 | off_peak | 625.7555 |  |  | 21.42 | 0 | 78.58 | 789.755 | 0
4551 | 767.8 | 818.241 | 29.7 | 162.8903 | 162.8903 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15.6021 | 604.9097 | 0 | 0.05921 | 5.0779 | 0 | 0 | 80.539 | 162.8903 | off_peak | 604.9097 |  |  | 21.22 | 0 | 78.78 | 827.1479 | 0
4552 | 756.38 | 673.748 | 29.5 | 134.2237 | 134.2237 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15.6021 | 622.1563 | 0 | 0.05921 | 5.7694 | 0 | 0 | 80.539 | 134.2237 | off_peak | 622.1563 |  |  | 17.75 | 0 | 82.25 | 774.3909 | 0
4553 | 758.18 | 489.991 | 29.3 | 97.6872 | 97.6872 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 27.2003 | 672.8917 | 0 | 0.05921 | 6.4411 | 0 | 0 | 80.539 | 97.6872 | off_peak | 660.4928 | 0 | 100 | 12.88 | 0 | 87.12 | 629.2128 | 0
4554 | 700.67 | 286.247 | 28.9 | 57.1512 | 57.1512 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 38.7984 | 655.9178 | 0 | 0.05921 | 6.9858 | 0 | 0 | 80.539 | 57.1512 | off_peak | 643.5188 | 0 | 100 | 8.16 | 0 | 91.84 | 399.2448 | 0
4555 | 660.26 | 93.1116 | 28.6 | 18.6107 | 6.2118 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 0 | 50.3966 | 654.0482 | 0 | 0.05921 | 7.5227 | 0 | 0 | 92.1372 | 6.2118 | off_peak | 654.0482 | 100 | 0 | 0.94 | 0 | 99.06 | 46.7296 | 0
4556 | 627.02 | 0 | 28.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50.3966 | 627.02 | 0 | 0.05921 | 7.7676 | 0 | 0 | 92.1372 | 0 | off_peak | 627.02 |  |  | 0 | 0 | 100 | 0 | 0
4557 | 643.21 | 0 | 28.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50.3966 | 643.21 | 0 | 0.05921 | 8.1632 | 0 | 0 | 92.1372 | 0 | off_peak | 643.21 |  |  | 0 | 0 | 100 | 0 | 0
4558 | 653.05 | 0 | 28.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50.3966 | 653.05 | 0 | 0.05921 | 8.4502 | 0 | 0 | 92.1372 | 0 | off_peak | 653.05 |  |  | 0 | 0 | 100 | 0 | 0
4559 | 656.94 | 0 | 28 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50.3966 | 656.94 | 0 | 0.05921 | 8.7033 | 0 | 0 | 92.1372 | 0 | off_peak | 656.94 |  |  | 0 | 0 | 100 | 0 | 0
4560 | 648.06 | 0 | 27.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50.3966 | 648.06 | 0 | 0.05921 | 8.817 | 0 | 0 | 92.1372 | 0 | off_peak | 648.06 |  |  | 0 | 0 | 100 | 0 | 0
4561 | 656.92 | 0 | 27.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50.3966 | 656.92 | 0 | 0.05921 | 8.3178 | 0 | 0 | 92.1372 | 0 | off_peak | 656.92 |  |  | 0 | 0 | 100 | 0 | 0
4562 | 641.95 | 0 | 27.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50.3966 | 641.95 | 0 | 0.05921 | 8.1229 | 0 | 0 | 92.1372 | 0 | off_peak | 641.95 |  |  | 0 | 0 | 100 | 0 | 0
4563 | 617.19 | 0 | 27.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50.3966 | 617.19 | 0 | 0.05921 | 7.7424 | 0 | 0 | 92.1372 | 0 | off_peak | 617.19 |  |  | 0 | 0 | 100 | 0 | 0
4564 | 637.86 | 0 | 27.7 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 61.9947 | 650.2589 | 0 | 0.05921 | 7.1175 | 0 | 0 | 92.1372 | 0 | off_peak | 637.86 | 0 | 100 | 0 | 0 | 100 | 0 | 0
4565 | 671.05 | 0 | 27.7 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 73.5928 | 683.4489 | 0 | 0.05921 | 6.4398 | 0 | 0 | 92.1372 | 0 | off_peak | 671.05 | 0 | 100 | 0 | 0 | 100 | 0 | 0
4566 | 716.83 | 0 | 27.9 | 0 | 0 | 0 | 0 | 0.80079 | 0.80079 | 0 | 0 | 0 | 74.3419 | 717.6308 | 0 | 0.05921 | 0 | 0 | 0 | 92.1372 | 0 | off_peak | 716.83 | 0 | 100 | 0 | 0 | 100 | 0 | 0
4567 | 782.79 | 41.9693 | 28.4 | 8.3948 | 8.3948 | 0 | 0 | 0.05172 | 0.05172 | 0 | 0 | 0 | 74.3903 | 774.447 | 0 | 0.05921 | 0 | 0 | 0 | 92.1372 | 8.3948 | off_peak | 774.3952 | 0 | 100 | 1.07 | 0 | 98.93 | 0 | 0
4568 | 853.48 | 144.668 | 28.8 | 28.8945 | 28.8945 | 0 | 0 | 0.0033404 | 0.0033404 | 0 | 0 | 0 | 74.3934 | 824.5888 | 0 | 0.05921 | 0 | 0 | 0 | 92.1372 | 28.8945 | off_peak | 824.5855 | 0 | 100 | 3.39 | 0 | 96.61 | 0 | 0
4569 | 894.04 | 237.099 | 29.1 | 47.3039 | 47.3039 | 0 | 0 | 0.00021574 | 0.00021574 | 0 | 0 | 0 | 74.3936 | 846.7363 | 0 | 0.05921 | 0 | 0 | 0 | 92.1372 | 47.3039 | off_peak | 846.7361 | 0 | 100 | 5.29 | 0 | 94.71 | 0 | 0
4570 | 901.31 | 224.746 | 29.3 | 44.8066 | 44.8065 | 0 | 1.3934e-05 | 1.3934e-05 | 0 | 0 | 0 | 0 | 74.3936 | 856.5035 | 0 | 0.05921 | 0 | 0 | 0 | 92.1372 | 44.8065 | off_peak | 856.5035 | 100 | 0 | 4.97 | 0 | 95.03 | 0 | 0
4571 | 903.57 | 505.139 | 29.5 | 100.6335 | 100.6335 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 802.9365 | 0 | 0.05921 | 0 | 0 | 0 | 92.1372 | 100.6335 | off_peak | 802.9365 |  |  | 11.14 | 0 | 88.86 | 0 | 0
4572 | 932.91 | 716.086 | 29.6 | 142.6061 | 142.6061 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 790.3039 | 0 | 0.05921 | 0 | 0 | 0 | 92.1372 | 142.6061 | off_peak | 790.3039 |  |  | 15.29 | 0 | 84.71 | 0 | 0
4573 | 850.71 | 739.159 | 29.7 | 147.1471 | 147.1471 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 703.5629 | 0 | 0.088511 | 0 | 0 | 0 | 92.1372 | 147.1471 | on_peak | 703.5629 |  |  | 17.3 | 0 | 82.7 | 0 | 0
4574 | 833.24 | 554.083 | 29.8 | 110.263 | 110.263 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 722.977 | 0 | 0.088511 | 0 | 0 | 0 | 92.1372 | 110.263 | on_peak | 722.977 |  |  | 13.23 | 0 | 86.77 | 0 | 0
4575 | 938.74 | 520.203 | 29.8 | 103.5208 | 103.5208 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 835.2192 | 0 | 0.088511 | 0 | 0 | 0 | 92.1372 | 103.5208 | on_peak | 835.2192 |  |  | 11.03 | 0 | 88.97 | 0 | 0
4576 | 929.28 | 490.048 | 29.8 | 97.5199 | 97.5199 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 831.7601 | 0 | 0.088511 | 0 | 0 | 0 | 92.1372 | 97.5199 | on_peak | 831.7601 |  |  | 10.49 | 0 | 89.51 | 0 | 0
4577 | 921.04 | 369.012 | 29.5 | 73.5144 | 73.5144 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 847.5256 | 0 | 0.088511 | 0 | 0 | 0 | 92.1372 | 73.5144 | on_peak | 847.5256 |  |  | 7.98 | 0 | 92.02 | 0 | 0
4578 | 946.87 | 264.994 | 29.2 | 52.8499 | 52.8499 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 894.0201 | 0 | 0.088511 | 0 | 0 | 0 | 92.1372 | 52.8499 | on_peak | 894.0201 |  |  | 5.58 | 0 | 94.42 | 0 | 0
4579 | 928.29 | 59.41 | 29 | 11.8573 | 11.8573 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 916.4327 | 0 | 0.088511 | 0 | 0 | 0 | 92.1372 | 11.8573 | on_peak | 916.4327 |  |  | 1.28 | 0 | 98.72 | 0 | 0
4580 | 912.41 | 0 | 28.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 912.41 | 0 | 0.088511 | 0 | 0 | 0 | 92.1372 | 0 | on_peak | 912.41 |  |  | 0 | 0 | 100 | 0 | 0
4581 | 912.53 | 0 | 28.4 | 0 | 0 | 0 | 0 | 0 | 0 | 62.63 | 62.63 | 0 | 7.4394 | 849.9 | 0 | 0.088511 | 0 | 62.63 | 0 | 25.1829 | 62.63 | on_peak | 849.9 |  |  | 0 | 6.86 | 93.14 | 0 | 0
4582 | 901.67 | 0 | 28.4 | 0 | 0 | 0 | 0 | 8.7263 | 8.7263 | 0 | 0 | 0 | 15.6021 | 910.3963 | 0 | 0.05921 | 0 | 0 | 0 | 25.1829 | 0 | off_peak | 901.67 | 0 | 100 | 0 | 0 | 100 | 0 | 0
4583 | 930.5 | 0 | 28.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15.6021 | 930.5 | 0 | 0.05921 | 0 | 0 | 0 | 25.1829 | 0 | off_peak | 930.5 |  |  | 0 | 0 | 100 | 0 | 0
4584 | 881.38 | 0 | 28.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15.6021 | 881.38 | 0 | 0.05921 | 0 | 0 | 0 | 25.1829 | 0 | off_peak | 881.38 |  |  | 0 | 0 | 100 | 0 | 0
4585 | 763.26 | 0 | 28.1 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 27.2003 | 775.6589 | 0 | 0.05921 | 0 | 0 | 0 | 25.1829 | 0 | off_peak | 763.26 | 0 | 100 | 0 | 0 | 100 | 0 | 0
4586 | 663.94 | 0 | 28.1 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 38.7984 | 676.3389 | 0 | 0.05921 | 0 | 0 | 0 | 25.1829 | 0 | off_peak | 663.94 | 0 | 100 | 0 | 0 | 100 | 0 | 0
4587 | 694.82 | 0 | 28 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 38.7984 | 694.82 | 0 | 0.05921 | 0 | 0 | 0 | 25.1829 | 0 | off_peak | 694.82 |  |  | 0 | 0 | 100 | 0 | 0
4588 | 653.74 | 0 | 28 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 50.3966 | 666.1389 | 0 | 0.05921 | 0 | 0 | 0 | 25.1829 | 0 | off_peak | 653.74 | 0 | 100 | 0 | 0 | 100 | 0 | 0
4589 | 679.7 | 0 | 27.9 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 61.9947 | 692.0989 | 0 | 0.05921 | 0 | 0 | 0 | 25.1829 | 0 | off_peak | 679.7 | 0 | 100 | 0 | 0 | 100 | 0 | 0
4590 | 718.65 | 0 | 28.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 61.9947 | 718.65 | 0 | 0.05921 | 5.8977 | 0 | 0 | 25.1829 | 0 | off_peak | 718.65 |  |  | 0 | 0 | 100 | 0 | 0
4591 | 757.78 | 73.6604 | 28.5 | 14.7283 | 2.3293 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 0 | 73.5928 | 755.4507 | 0 | 0.05921 | 5.3971 | 0 | 0 | 36.781 | 2.3293 | off_peak | 755.4507 | 100 | 0 | 0.31 | 0 | 99.69 | 12.5716 | 0
4592 | 872.08 | 297.821 | 28.9 | 59.462 | 59.462 | 0 | 0 | 0.80079 | 0.80079 | 0 | 0 | 0 | 74.3419 | 813.4188 | 0 | 0.05921 | 5.0614 | 0 | 0 | 36.781 | 59.462 | off_peak | 812.618 | 0 | 100 | 6.82 | 0 | 93.18 | 300.9618 | 0
4593 | 874.27 | 508.04 | 29.1 | 101.3596 | 101.3596 | 0 | 0 | 0.05172 | 0.05172 | 0 | 0 | 0 | 74.3903 | 772.9621 | 0 | 0.05921 | 4.8264 | 0 | 0 | 36.781 | 101.3596 | off_peak | 772.9104 | 0 | 100 | 11.59 | 0 | 88.41 | 489.1987 | 0
4594 | 891.39 | 686.422 | 29.3 | 136.8487 | 136.8487 | 0 | 0 | 0.0033404 | 0.0033404 | 0 | 0 | 0 | 74.3934 | 754.5446 | 0 | 0.05921 | 4.7288 | 0 | 0 | 36.781 | 136.8487 | off_peak | 754.5413 | 0 | 100 | 15.35 | 0 | 84.65 | 647.1363 | 0
4595 | 869.2 | 710.626 | 29.5 | 141.5706 | 141.5706 | 0 | 0 | 0.00021574 | 0.00021574 | 0 | 0 | 0 | 74.3936 | 727.6297 | 0 | 0.05921 | 4.8026 | 0 | 0 | 36.781 | 141.5706 | off_peak | 727.6294 | 0 | 100 | 16.29 | 0 | 83.71 | 679.9095 | 0
4596 | 936.43 | 736.903 | 29.7 | 146.698 | 146.698 | 0 | 0 | 1.3934e-05 | 1.3934e-05 | 0 | 0 | 0 | 74.3936 | 789.732 | 0 | 0.05921 | 4.9971 | 0 | 0 | 36.781 | 146.698 | off_peak | 789.732 | 0 | 100 | 15.67 | 0 | 84.33 | 733.06 | 0
4597 | 956.47 | 560.258 | 29.8 | 111.4918 | 111.4918 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 844.9782 | 0 | 0.088511 | 4.9912 | 0 | 0 | 36.781 | 111.4918 | on_peak | 844.9782 |  |  | 11.66 | 0 | 88.34 | 556.4768 | 0
4598 | 917.38 | 720.648 | 29.8 | 143.4095 | 143.4095 | 0 | 0 | 0 | 0 | 24.1382 | 24.1382 | 0 | 48.5888 | 749.8323 | 0 | 0.088511 | 5.2995 | 0 | 0 | 36.781 | 143.4095 | on_peak | 749.8323 |  |  | 15.63 | 2.63 | 81.74 | 760.0014 | 0
4599 | 962.94 | 813.741 | 29.7 | 161.9944 | 161.9944 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 48.5888 | 800.9456 | 0 | 0.088511 | 5.7233 | 0 | 0 | 36.781 | 161.9944 | on_peak | 800.9456 |  |  | 16.82 | 0 | 83.18 | 927.1435 | 0
4600 | 906.44 | 628.957 | 29.6 | 125.2546 | 125.2546 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 48.5888 | 781.1854 | 0 | 0.088511 | 6.2554 | 0 | 0 | 36.781 | 125.2546 | on_peak | 781.1854 |  |  | 13.82 | 0 | 86.18 | 783.5174 | 0
4601 | 908.57 | 432.31 | 29.4 | 86.1561 | 86.1561 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 48.5888 | 822.4139 | 0 | 0.088511 | 6.8532 | 0 | 0 | 36.781 | 86.1561 | on_peak | 822.4139 |  |  | 9.48 | 0 | 90.52 | 590.4485 | 0
4602 | 938.82 | 282.683 | 29.2 | 56.3778 | 56.3778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 48.5888 | 882.4422 | 0 | 0.088511 | 7.3242 | 0 | 0 | 36.781 | 56.3778 | on_peak | 882.4422 |  |  | 6.01 | 0 | 93.99 | 412.9196 | 0
4603 | 950 | 90.3481 | 29 | 18.032 | 18.032 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 48.5888 | 931.968 | 0 | 0.088511 | 7.7847 | 0 | 0 | 36.781 | 18.032 | on_peak | 931.968 |  |  | 1.9 | 0 | 98.1 | 140.3737 | 0
4604 | 942.36 | 0 | 28.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 48.5888 | 942.36 | 0 | 0.088511 | 8.0759 | 0 | 0 | 36.781 | 0 | on_peak | 942.36 |  |  | 0 | 0 | 100 | 0 | 0
4605 | 982.04 | 0 | 28.4 | 0 | 0 | 0 | 0 | 0 | 0 | 38.4918 | 38.4918 | 0 | 7.4394 | 943.5482 | 0 | 0.088511 | 8.3582 | 0 | 0 | 36.781 | 0 | on_peak | 943.5482 |  |  | 0 | 3.92 | 96.08 | 0 | 0
4606 | 900.59 | 0 | 28.3 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 19.0375 | 912.9889 | 0 | 0.05921 | 8.6808 | 0 | 0 | 36.781 | 0 | off_peak | 900.59 | 0 | 100 | 0 | 0 | 100 | 0 | 0
4607 | 950.76 | 0 | 28.2 | 0 | 0 | 0 | 0 | 0 | 0 | 7.2118 | 7.2118 | 0 | 11.3278 | 943.5482 | 0 | 0.05921 | 8.9501 | 0 | 0 | 36.781 | 0 | off_peak | 943.5482 |  |  | 0 | 0.76 | 99.24 | 0 | 0
4608 | 887.21 | 0 | 28 | 0 | 0 | 0 | 0 | 4.5694 | 4.5694 | 0 | 0 | 0 | 15.6021 | 891.7794 | 0 | 0.05921 | 8.8951 | 0 | 0 | 36.781 | 0 | off_peak | 887.21 | 0 | 100 | 0 | 0 | 100 | 0 | 0
4609 | 848.29 | 0 | 27.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15.6021 | 848.29 | 0 | 0.05921 | 8.8099 | 0 | 0 | 36.781 | 0 | off_peak | 848.29 |  |  | 0 | 0 | 100 | 0 | 0
4610 | 760.76 | 0 | 27.8 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 27.2003 | 773.1589 | 0 | 0.05921 | 8.6842 | 0 | 0 | 36.781 | 0 | off_peak | 760.76 | 0 | 100 | 0 | 0 | 100 | 0 | 0
4611 | 733.75 | 0 | 27.7 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 38.7984 | 746.1489 | 0 | 0.05921 | 8.1933 | 0 | 0 | 36.781 | 0 | off_peak | 733.75 | 0 | 100 | 0 | 0 | 100 | 0 | 0
4612 | 738.4 | 0 | 27.7 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 50.3966 | 750.7989 | 0 | 0.05921 | 7.5512 | 0 | 0 | 36.781 | 0 | off_peak | 738.4 | 0 | 100 | 0 | 0 | 100 | 0 | 0
4613 | 736.22 | 0 | 27.7 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 61.9947 | 748.6189 | 0 | 0.05921 | 6.9863 | 0 | 0 | 36.781 | 0 | off_peak | 736.22 | 0 | 100 | 0 | 0 | 100 | 0 | 0
4614 | 789.96 | 0 | 27.9 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 73.5928 | 802.3589 | 0 | 0.05921 | 6.3574 | 0 | 0 | 36.781 | 0 | off_peak | 789.96 | 0 | 100 | 0 | 0 | 100 | 0 | 0
4615 | 805.65 | 107.186 | 28.3 | 21.4473 | 20.6465 | 0 | 0.80079 | 0.80079 | 0 | 0 | 0 | 0 | 74.3419 | 785.0035 | 0 | 0.05921 | 5.8199 | 0 | 0 | 37.5301 | 20.6465 | off_peak | 785.0035 | 100 | 0 | 2.56 | 0 | 97.44 | 120.1603 | 0
4616 | 846.67 | 301.265 | 28.7 | 60.1936 | 60.1936 | 0 | 0 | 0.05172 | 0.05172 | 0 | 0 | 0 | 74.3903 | 786.5282 | 0 | 0.05921 | 5.4814 | 0 | 0 | 37.5301 | 60.1936 | off_peak | 786.4764 | 0 | 100 | 7.11 | 0 | 92.89 | 329.9438 | 0
4617 | 904.93 | 245.52 | 28.9 | 49.0198 | 49.0164 | 0 | 0.0033404 | 0.0033404 | 0 | 0 | 0 | 0 | 74.3934 | 855.9136 | 0 | 0.05921 | 5.2093 | 0 | 0 | 37.5332 | 49.0164 | off_peak | 855.9136 | 100 | 0 | 5.42 | 0 | 94.58 | 255.3426 | 0
4618 | 925.73 | 365.829 | 29.1 | 72.9869 | 72.9869 | 0 | 0 | 0.00021574 | 0.00021574 | 0 | 0 | 0 | 74.3936 | 852.7433 | 0 | 0.05921 | 5.0882 | 0 | 0 | 37.5332 | 72.9869 | off_peak | 852.7431 | 0 | 100 | 7.88 | 0 | 92.12 | 371.3707 | 0
4619 | 892.23 | 818.358 | 29.3 | 163.1522 | 163.1522 | 0 | 0 | 1.3934e-05 | 1.3934e-05 | 0 | 0 | 0 | 74.3936 | 729.0778 | 0 | 0.05921 | 5.1434 | 0 | 0 | 37.5332 | 163.1522 | off_peak | 729.0778 | 0 | 100 | 18.29 | 0 | 81.71 | 839.1555 | 0
4620 | 977.64 | 901.766 | 29.5 | 179.6494 | 179.6494 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 797.9906 | 0 | 0.05921 | 5.2804 | 0 | 0 | 37.5332 | 179.6494 | off_peak | 797.9906 |  |  | 18.38 | 0 | 81.62 | 948.619 | 0
4621 | 922.3 | 927.181 | 29.7 | 184.5774 | 184.5774 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 737.7226 | 0 | 0.088511 | 5.2868 | 0 | 0 | 37.5332 | 184.5774 | on_peak | 737.7226 |  |  | 20.01 | 0 | 79.99 | 975.8159 | 0
4622 | 964.86 | 715.901 | 29.8 | 142.4649 | 142.4649 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 822.3951 | 0 | 0.088511 | 5.6349 | 0 | 0 | 37.5332 | 142.4649 | on_peak | 822.3951 |  |  | 14.77 | 0 | 85.23 | 802.7703 | 0
4623 | 1005.13 | 182.286 | 29.8 | 36.2751 | 36.2751 | 0 | 0 | 0 | 0 | 25.3067 | 25.3067 | 0 | 47.3396 | 943.5482 | 0 | 0.088511 | 5.9633 | 0 | 0 | 37.5332 | 36.2751 | on_peak | 943.5482 |  |  | 3.61 | 2.52 | 93.87 | 216.3181 | 0
4624 | 939.12 | 212.539 | 29.7 | 42.3109 | 42.3109 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 58.9378 | 909.208 | 0 | 0.088511 | 6.5118 | 0 | 0 | 37.5332 | 42.3109 | on_peak | 896.8091 | 0 | 100 | 4.51 | 0 | 95.49 | 275.5202 | 0
4625 | 966.81 | 75.05 | 29.5 | 14.9514 | 14.9514 | 0 | 0 | 0 | 0 | 8.3104 | 8.3104 | 0 | 50.0536 | 943.5482 | 0 | 0.088511 | 7.1505 | 0 | 0 | 37.5332 | 14.9514 | on_peak | 943.5482 |  |  | 1.55 | 0.86 | 97.59 | 106.9098 | 0
4626 | 977.58 | 52.25 | 29.2 | 10.4206 | 10.4206 | 0 | 0 | 0 | 0 | 23.6111 | 23.6111 | 0 | 24.8123 | 943.5482 | 0 | 0.088511 | 7.709 | 0 | 0 | 37.5332 | 10.4206 | on_peak | 943.5482 |  |  | 1.07 | 2.42 | 96.52 | 80.3331 | 0
4627 | 944.53 | 4.75 | 29 | 0.94802 | 0.94802 | 0 | 0 | 0 | 0 | 0.033758 | 0.033758 | 0 | 24.7762 | 943.5482 | 0 | 0.088511 | 8.1329 | 0 | 0 | 37.5332 | 0.94802 | on_peak | 943.5482 |  |  | 0.1 | 0 | 99.9 | 7.7102 | 0
4628 | 933.52 | 0 | 28.4 | 0 | 0 | 0 | 0 | 10.0282 | 10.0282 | 0 | 0 | 0 | 34.1567 | 943.5482 | 0 | 0.088511 | 8.3115 | 0 | 0 | 37.5332 | 0 | on_peak | 933.52 | 0 | 100 | 0 | 0 | 100 | 0 | 0
4629 | 968.54 | 0 | 28.3 | 0 | 0 | 0 | 0 | 0 | 0 | 24.9918 | 24.9918 | 0 | 7.4394 | 943.5482 | 0 | 0.088511 | 8.5176 | 0 | 0 | 37.5332 | 0 | on_peak | 943.5482 |  |  | 0 | 2.58 | 97.42 | 0 | 0
4630 | 934.12 | 0 | 28.2 | 0 | 0 | 0 | 0 | 9.4282 | 9.4282 | 0 | 0 | 0 | 16.2587 | 943.5482 | 0 | 0.05921 | 8.7488 | 0 | 0 | 37.5332 | 0 | off_peak | 934.12 | 0 | 100 | 0 | 0 | 100 | 0 | 0
4631 | 947.33 | 0 | 28.1 | 0 | 0 | 0 | 0 | 0 | 0 | 3.7818 | 3.7818 | 0 | 12.2158 | 943.5482 | 0 | 0.05921 | 8.9212 | 0 | 0 | 37.5332 | 0 | off_peak | 943.5482 |  |  | 0 | 0.4 | 99.6 | 0 | 0
4632 | 907.13 | 0 | 28 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 23.8139 | 919.5289 | 0 | 0.05921 | 8.9742 | 0 | 0 | 37.5332 | 0 | off_peak | 907.13 | 0 | 100 | 0 | 0 | 100 | 0 | 0
4633 | 844.18 | 0 | 27.8 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 35.4121 | 856.5789 | 0 | 0.05921 | 8.7432 | 0 | 0 | 37.5332 | 0 | off_peak | 844.18 | 0 | 100 | 0 | 0 | 100 | 0 | 0
4634 | 765.86 | 0 | 27.7 | 0 | 0 | 0 | 0 | 3.6202 | 3.6202 | 0 | 0 | 0 | 38.7984 | 769.4802 | 0 | 0.05921 | 8.553 | 0 | 0 | 37.5332 | 0 | off_peak | 765.86 | 0 | 100 | 0 | 0 | 100 | 0 | 0
4635 | 701.79 | 0 | 27.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 38.7984 | 701.79 | 0 | 0.05921 | 8.1131 | 0 | 0 | 37.5332 | 0 | off_peak | 701.79 |  |  | 0 | 0 | 100 | 0 | 0
4636 | 751.28 | 0 | 27.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 38.7984 | 751.28 | 0 | 0.05921 | 7.517 | 0 | 0 | 37.5332 | 0 | off_peak | 751.28 |  |  | 0 | 0 | 100 | 0 | 0
4637 | 746.02 | 0 | 27.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 38.7984 | 746.02 | 0 | 0.05921 | 6.992 | 0 | 0 | 37.5332 | 0 | off_peak | 746.02 |  |  | 0 | 0 | 100 | 0 | 0
4638 | 785.82 | 0 | 27.7 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 50.3966 | 798.2189 | 0 | 0.05921 | 6.3622 | 0 | 0 | 37.5332 | 0 | off_peak | 785.82 | 0 | 100 | 0 | 0 | 100 | 0 | 0
4639 | 798.03 | 49.7306 | 28.1 | 9.9581 | 0 | 0 | 9.9581 | 12.3989 | 2.4409 | 0 | 0 | 0 | 61.9947 | 800.4709 | 0 | 0.05921 | 5.8575 | 0 | 0 | 46.8482 | 0 | off_peak | 798.03 | 80.31 | 19.69 | 0 | 0 | 100 | 0 | 0
4640 | 849.14 | 130.996 | 28.4 | 26.202 | 13.8031 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 0 | 73.5928 | 835.3369 | 0 | 0.05921 | 5.4588 | 0 | 0 | 58.4463 | 13.8031 | off_peak | 835.3369 | 100 | 0 | 1.63 | 0 | 98.37 | 75.3476 | 0
4641 | 844.44 | 443.482 | 28.7 | 88.6089 | 87.8081 | 0 | 0.80079 | 0.80079 | 0 | 0 | 0 | 0 | 74.3419 | 756.6319 | 0 | 0.05921 | 5.2088 | 0 | 0 | 59.1954 | 87.8081 | off_peak | 756.6319 | 100 | 0 | 10.4 | 0 | 89.6 | 457.3742 | 0
4642 | 899.59 | 637.76 | 28.9 | 127.3332 | 127.3332 | 0 | 0 | 0.05172 | 0.05172 | 0 | 0 | 0 | 74.3903 | 772.3085 | 0 | 0.05921 | 5.1073 | 0 | 0 | 59.1954 | 127.3332 | off_peak | 772.2568 | 0 | 100 | 14.15 | 0 | 85.85 | 650.3226 | 0
4643 | 865.42 | 504.478 | 29.2 | 100.6122 | 100.6122 | 0 | 0 | 0.0033404 | 0.0033404 | 0 | 0 | 0 | 74.3934 | 764.8112 | 0 | 0.05921 | 5.1817 | 0 | 0 | 59.1954 | 100.6122 | off_peak | 764.8078 | 0 | 100 | 11.63 | 0 | 88.37 | 521.3397 | 0
4644 | 979.42 | 791.287 | 29.3 | 157.7552 | 157.7552 | 0 | 0 | 0.00021574 | 0.00021574 | 0 | 0 | 0 | 74.3936 | 821.665 | 0 | 0.05921 | 5.3746 | 0 | 0 | 59.1954 | 157.7552 | off_peak | 821.6648 | 0 | 100 | 16.11 | 0 | 83.89 | 847.8665 | 0
4645 | 919.36 | 804.355 | 29.4 | 160.3018 | 160.3018 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 759.0582 | 0 | 0.088511 | 5.3778 | 0 | 0 | 59.1954 | 160.3018 | on_peak | 759.0582 |  |  | 17.44 | 0 | 82.56 | 862.0772 | 0
4646 | 982.3 | 680.329 | 29.4 | 135.5844 | 135.5844 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 846.7156 | 0 | 0.088511 | 5.8058 | 0 | 0 | 59.1954 | 135.5844 | on_peak | 846.7156 |  |  | 13.8 | 0 | 86.2 | 787.1805 | 0
4647 | 951.21 | 518.505 | 29.4 | 103.3341 | 103.3341 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 847.8759 | 0 | 0.088511 | 6.1789 | 0 | 0 | 59.1954 | 103.3341 | on_peak | 847.8759 |  |  | 10.86 | 0 | 89.14 | 638.4955 | 0
4648 | 885.07 | 604.458 | 29.2 | 120.552 | 120.552 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 764.518 | 0 | 0.088511 | 6.611 | 0 | 0 | 59.1954 | 120.552 | on_peak | 764.518 |  |  | 13.62 | 0 | 86.38 | 796.9721 | 0
4649 | 853.22 | 397.11 | 29 | 79.2568 | 79.2568 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 773.9632 | 0 | 0.088511 | 7.1751 | 0 | 0 | 59.1954 | 79.2568 | on_peak | 773.9632 |  |  | 9.29 | 0 | 90.71 | 568.6721 | 0
4650 | 873.09 | 175.17 | 28.7 | 34.9994 | 34.9994 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 838.0906 | 0 | 0.088511 | 7.6784 | 0 | 0 | 59.1954 | 34.9994 | on_peak | 838.0906 |  |  | 4.01 | 0 | 95.99 | 268.7391 | 0
4651 | 881.46 | 85.0047 | 28.6 | 16.9904 | 16.9904 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 864.4696 | 0 | 0.088511 | 7.9657 | 0 | 0 | 59.1954 | 16.9904 | on_peak | 864.4696 |  |  | 1.93 | 0 | 98.07 | 135.3409 | 0
4652 | 876.92 | 0 | 28.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 876.92 | 0 | 0.088511 | 8.2494 | 0 | 0 | 59.1954 | 0 | on_peak | 876.92 |  |  | 0 | 0 | 100 | 0 | 0
4653 | 883.48 | 0 | 28.1 | 0 | 0 | 0 | 0 | 0 | 0 | 62.63 | 62.63 | 0 | 7.4394 | 820.85 | 0 | 0.088511 | 8.4108 | 0 | 0 | 59.1954 | 0 | on_peak | 820.85 |  |  | 0 | 7.09 | 92.91 | 0 | 0
4654 | 801.29 | 0 | 28.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 801.29 | 0 | 0.05921 | 8.5511 | 0 | 0 | 59.1954 | 0 | off_peak | 801.29 |  |  | 0 | 0 | 100 | 0 | 0
4655 | 850.35 | 0 | 28 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 850.35 | 0 | 0.05921 | 8.6314 | 0 | 0 | 59.1954 | 0 | off_peak | 850.35 |  |  | 0 | 0 | 100 | 0 | 0
4656 | 845.53 | 0 | 28 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 19.0375 | 857.9289 | 0 | 0.05921 | 8.7403 | 0 | 0 | 59.1954 | 0 | off_peak | 845.53 | 0 | 100 | 0 | 0 | 100 | 0 | 0
4657 | 756.94 | 0 | 27.9 | 0 | 0 | 0 | 0 | 8.7263 | 8.7263 | 0 | 0 | 0 | 27.2003 | 765.6663 | 0 | 0.05921 | 8.4192 | 0 | 0 | 59.1954 | 0 | off_peak | 756.94 | 0 | 100 | 0 | 0 | 100 | 0 | 0
4658 | 619.58 | 0 | 27.8 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 38.7984 | 631.9789 | 0 | 0.05921 | 8.0333 | 0 | 0 | 59.1954 | 0 | off_peak | 619.58 | 0 | 100 | 0 | 0 | 100 | 0 | 0
4659 | 642.39 | 0 | 27.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 38.7984 | 642.39 | 0 | 0.05921 | 7.4982 | 0 | 0 | 59.1954 | 0 | off_peak | 642.39 |  |  | 0 | 0 | 100 | 0 | 0
4660 | 600.01 | 0 | 27.6 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 50.3966 | 612.4089 | 0 | 0.05921 | 6.8715 | 0 | 0 | 59.1954 | 0 | off_peak | 600.01 | 0 | 100 | 0 | 0 | 100 | 0 | 0
4661 | 653.95 | 0 | 27.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50.3966 | 653.95 | 0 | 0.05921 | 6.3943 | 0 | 0 | 59.1954 | 0 | off_peak | 653.95 |  |  | 0 | 0 | 100 | 0 | 0
4662 | 742.37 | 0 | 27.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50.3966 | 742.37 | 0 | 0.05921 | 5.7454 | 0 | 0 | 59.1954 | 0 | off_peak | 742.37 |  |  | 0 | 0 | 100 | 0 | 0
4663 | 792.56 | 51.7918 | 28.1 | 10.3708 | 10.3708 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 61.9947 | 794.5881 | 0 | 0.05921 | 5.2516 | 0 | 0 | 59.1954 | 10.3708 | off_peak | 782.1892 | 0 | 100 | 1.31 | 0 | 98.69 | 54.4632 | 0
4664 | 843.84 | 158.4 | 28.5 | 31.6718 | 31.6718 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 73.5928 | 824.5671 | 0 | 0.05921 | 4.902 | 0 | 0 | 59.1954 | 31.6718 | off_peak | 812.1682 | 0 | 100 | 3.75 | 0 | 96.25 | 155.2539 | 0
4665 | 883.84 | 340.49 | 28.8 | 68.006 | 68.006 | 0 | 0 | 0.80079 | 0.80079 | 0 | 0 | 0 | 74.3419 | 816.6348 | 0 | 0.05921 | 4.7065 | 0 | 0 | 59.1954 | 68.006 | off_peak | 815.834 | 0 | 100 | 7.69 | 0 | 92.31 | 320.068 | 0
4666 | 907.4 | 682.839 | 29 | 136.2837 | 136.2837 | 0 | 0 | 0.05172 | 0.05172 | 0 | 0 | 0 | 74.3903 | 771.168 | 0 | 0.05921 | 4.6192 | 0 | 0 | 59.1954 | 136.2837 | off_peak | 771.1163 | 0 | 100 | 15.02 | 0 | 84.98 | 629.5277 | 0
4667 | 907.21 | 752.823 | 29.3 | 150.0868 | 150.0868 | 0 | 0 | 0.0033404 | 0.0033404 | 0 | 0 | 0 | 74.3934 | 757.1266 | 0 | 0.05921 | 4.7025 | 0 | 0 | 59.1954 | 150.0868 | off_peak | 757.1232 | 0 | 100 | 16.54 | 0 | 83.46 | 705.7896 | 0
4668 | 945.71 | 820.947 | 29.5 | 163.5487 | 163.5487 | 0 | 0 | 0.00021574 | 0.00021574 | 0 | 0 | 0 | 74.3936 | 782.1616 | 0 | 0.05921 | 4.889 | 0 | 0 | 59.1954 | 163.5487 | off_peak | 782.1613 | 0 | 100 | 17.29 | 0 | 82.71 | 799.5823 | 0
4669 | 909.2 | 700.489 | 29.7 | 139.4489 | 139.4489 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 769.7511 | 0 | 0.088511 | 4.9411 | 0 | 0 | 59.1954 | 139.4489 | on_peak | 769.7511 |  |  | 15.34 | 0 | 84.66 | 689.0283 | 0
4670 | 942.64 | 909.975 | 29.7 | 181.1521 | 181.1521 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 761.4879 | 0 | 0.088511 | 5.4309 | 0 | 0 | 59.1954 | 181.1521 | on_peak | 761.4879 |  |  | 19.22 | 0 | 80.78 | 983.8188 | 0
4671 | 933.79 | 816.687 | 29.7 | 162.5809 | 162.5809 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 771.2091 | 0 | 0.088511 | 5.9245 | 0 | 0 | 59.1954 | 162.5809 | on_peak | 771.2091 |  |  | 17.41 | 0 | 82.59 | 963.2037 | 0
4672 | 891.2 | 672.197 | 29.6 | 133.8657 | 133.8657 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 757.3343 | 0 | 0.088511 | 6.3282 | 0 | 0 | 59.1954 | 133.8657 | on_peak | 757.3343 |  |  | 15.02 | 0 | 84.98 | 847.1277 | 0
4673 | 893.44 | 488.197 | 29.4 | 97.294 | 97.294 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 796.146 | 0 | 0.088511 | 6.7617 | 0 | 0 | 59.1954 | 97.294 | on_peak | 796.146 |  |  | 10.89 | 0 | 89.11 | 657.8696 | 0
4674 | 898.61 | 284.501 | 29.1 | 56.7611 | 56.7611 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 841.8489 | 0 | 0.088511 | 7.2005 | 0 | 0 | 59.1954 | 56.7611 | on_peak | 841.8489 |  |  | 6.32 | 0 | 93.68 | 408.7056 | 0
4675 | 875.6 | 90.5214 | 29 | 18.0666 | 18.0666 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 857.5334 | 0 | 0.088511 | 7.5433 | 0 | 0 | 59.1954 | 18.0666 | on_peak | 857.5334 |  |  | 2.06 | 0 | 97.94 | 136.2818 | 0
4676 | 862.46 | 0 | 28.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 862.46 | 0 | 0.088511 | 7.7016 | 0 | 0 | 59.1954 | 0 | on_peak | 862.46 |  |  | 0 | 0 | 100 | 0 | 0
4677 | 849.24 | 0 | 28.3 | 0 | 0 | 0 | 0 | 0 | 0 | 62.63 | 62.63 | 0 | 7.4394 | 786.61 | 0 | 0.088511 | 7.7868 | 0 | 0 | 59.1954 | 0 | on_peak | 786.61 |  |  | 0 | 7.37 | 92.63 | 0 | 0
4678 | 862.7 | 0 | 28.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 862.7 | 0 | 0.05921 | 7.9893 | 0 | 0 | 59.1954 | 0 | off_peak | 862.7 |  |  | 0 | 0 | 100 | 0 | 0
4679 | 893.83 | 0 | 28 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 893.83 | 0 | 0.05921 | 8.0147 | 0 | 0 | 59.1954 | 0 | off_peak | 893.83 |  |  | 0 | 0 | 100 | 0 | 0
4680 | 857.8 | 0 | 27.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 857.8 | 0 | 0.05921 | 7.7939 | 0 | 0 | 59.1954 | 0 | off_peak | 857.8 |  |  | 0 | 0 | 100 | 0 | 0
4681 | 765.27 | 0 | 27.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 765.27 | 0 | 0.05921 | 7.4202 | 0 | 0 | 59.1954 | 0 | off_peak | 765.27 |  |  | 0 | 0 | 100 | 0 | 0
4682 | 656.34 | 0 | 27.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 656.34 | 0 | 0.05921 | 7.2216 | 0 | 0 | 59.1954 | 0 | off_peak | 656.34 |  |  | 0 | 0 | 100 | 0 | 0
4683 | 649.63 | 0 | 27.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 649.63 | 0 | 0.05921 | 6.9363 | 0 | 0 | 59.1954 | 0 | off_peak | 649.63 |  |  | 0 | 0 | 100 | 0 | 0
4684 | 670.57 | 0 | 27.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 670.57 | 0 | 0.05921 | 6.4266 | 0 | 0 | 59.1954 | 0 | off_peak | 670.57 |  |  | 0 | 0 | 100 | 0 | 0
4685 | 686.19 | 0 | 27.7 | 0 | 0 | 0 | 0 | 8.7263 | 8.7263 | 0 | 0 | 0 | 15.6021 | 694.9163 | 0 | 0.05921 | 5.9712 | 0 | 0 | 59.1954 | 0 | off_peak | 686.19 | 0 | 100 | 0 | 0 | 100 | 0 | 0
4686 | 698.02 | 0 | 27.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15.6021 | 698.02 | 0 | 0.05921 | 5.3995 | 0 | 0 | 59.1954 | 0 | off_peak | 698.02 |  |  | 0 | 0 | 100 | 0 | 0
4687 | 743.39 | 106.505 | 28.4 | 21.3033 | 8.9043 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 0 | 27.2003 | 734.4857 | 0 | 0.05921 | 4.9696 | 0 | 0 | 70.7935 | 8.9043 | off_peak | 734.4857 | 100 | 0 | 1.2 | 0 | 98.8 | 44.2512 | 0
4688 | 735.94 | 87.4 | 28.7 | 17.4628 | 17.4628 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27.2003 | 718.4772 | 0 | 0.05921 | 4.6181 | 0 | 0 | 70.7935 | 17.4628 | off_peak | 718.4772 |  |  | 2.37 | 0 | 97.63 | 80.6453 | 0
4689 | 762.15 | 247.542 | 29 | 49.4054 | 49.4054 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27.2003 | 712.7446 | 0 | 0.05921 | 4.4001 | 0 | 0 | 70.7935 | 49.4054 | off_peak | 712.7446 |  |  | 6.48 | 0 | 93.52 | 217.3869 | 0
4690 | 725.14 | 690.86 | 29.3 | 137.7335 | 137.7335 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27.2003 | 587.4065 | 0 | 0.05921 | 4.265 | 0 | 0 | 70.7935 | 137.7335 | off_peak | 587.4065 |  |  | 18.99 | 0 | 81.01 | 587.4267 | 0
4691 | 757.33 | 833.502 | 29.6 | 165.9891 | 165.9891 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27.2003 | 591.3409 | 0 | 0.05921 | 4.2482 | 0 | 0 | 70.7935 | 165.9891 | off_peak | 591.3409 |  |  | 21.92 | 0 | 78.08 | 705.1595 | 0
4692 | 734.43 | 922.256 | 29.8 | 183.5297 | 183.5297 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27.2003 | 550.9003 | 0 | 0.05921 | 4.2908 | 0 | 0 | 70.7935 | 183.5297 | off_peak | 550.9003 |  |  | 24.99 | 0 | 75.01 | 787.4862 | 0
4693 | 759.63 | 949.359 | 30 | 188.7848 | 188.7848 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27.2003 | 570.8452 | 0 | 0.05921 | 4.3757 | 0 | 0 | 70.7935 | 188.7848 | off_peak | 570.8452 |  |  | 24.85 | 0 | 75.15 | 826.0748 | 0
4694 | 685.41 | 913.525 | 30.1 | 181.5924 | 181.5924 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 38.7984 | 516.2165 | 0 | 0.05921 | 4.9513 | 0 | 0 | 70.7935 | 181.5924 | off_peak | 503.8176 | 0 | 100 | 26.49 | 0 | 73.51 | 899.1242 | 0
4695 | 762.63 | 818.464 | 30 | 162.7557 | 162.7557 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 38.7984 | 599.8743 | 0 | 0.05921 | 5.5305 | 0 | 0 | 70.7935 | 162.7557 | off_peak | 599.8743 |  |  | 21.34 | 0 | 78.66 | 900.116 | 0
4696 | 701.1 | 671.821 | 29.9 | 133.6439 | 133.6439 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 38.7984 | 567.4561 | 0 | 0.05921 | 5.9735 | 0 | 0 | 70.7935 | 133.6439 | off_peak | 567.4561 |  |  | 19.06 | 0 | 80.94 | 798.319 | 0
4697 | 689.38 | 486.609 | 29.6 | 96.9065 | 96.9065 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 38.7984 | 592.4735 | 0 | 0.05921 | 6.3159 | 0 | 0 | 70.7935 | 96.9065 | off_peak | 592.4735 |  |  | 14.06 | 0 | 85.94 | 612.053 | 0
4698 | 581.24 | 282.565 | 29.2 | 56.3543 | 56.3543 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 38.7984 | 524.8857 | 0 | 0.05921 | 6.5547 | 0 | 0 | 70.7935 | 56.3543 | off_peak | 524.8857 |  |  | 9.7 | 0 | 90.3 | 369.3848 | 0
4699 | 547.65 | 87.8289 | 29 | 17.5292 | 17.5292 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 38.7984 | 530.1208 | 0 | 0.05921 | 6.8163 | 0 | 0 | 70.7935 | 17.5292 | off_peak | 530.1208 |  |  | 3.2 | 0 | 96.8 | 119.4848 | 0
4700 | 542.96 | 0 | 28.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 38.7984 | 542.96 | 0 | 0.05921 | 7.0979 | 0 | 0 | 70.7935 | 0 | off_peak | 542.96 |  |  | 0 | 0 | 100 | 0 | 0
4701 | 526.67 | 0 | 28.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 38.7984 | 526.67 | 0 | 0.05921 | 7.5121 | 0 | 0 | 70.7935 | 0 | off_peak | 526.67 |  |  | 0 | 0 | 100 | 0 | 0
4702 | 537.01 | 0 | 28.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 38.7984 | 537.01 | 0 | 0.05921 | 7.9276 | 0 | 0 | 70.7935 | 0 | off_peak | 537.01 |  |  | 0 | 0 | 100 | 0 | 0
4703 | 537.1 | 0 | 27.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 38.7984 | 537.1 | 0 | 0.05921 | 8.1845 | 0 | 0 | 70.7935 | 0 | off_peak | 537.1 |  |  | 0 | 0 | 100 | 0 | 0
4704 | 530.87 | 0 | 27.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 38.7984 | 530.87 | 0 | 0.05921 | 8.2909 | 0 | 0 | 70.7935 | 0 | off_peak | 530.87 |  |  | 0 | 0 | 100 | 0 | 0
4705 | 528.4 | 0 | 27.6 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 50.3966 | 540.7989 | 0 | 0.05921 | 7.9568 | 0 | 0 | 70.7935 | 0 | off_peak | 528.4 | 0 | 100 | 0 | 0 | 100 | 0 | 0
4706 | 522.85 | 0 | 27.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50.3966 | 522.85 | 0 | 0.05921 | 7.7111 | 0 | 0 | 70.7935 | 0 | off_peak | 522.85 |  |  | 0 | 0 | 100 | 0 | 0
4707 | 544.57 | 0 | 27.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50.3966 | 544.57 | 0 | 0.05921 | 7.3224 | 0 | 0 | 70.7935 | 0 | off_peak | 544.57 |  |  | 0 | 0 | 100 | 0 | 0
4708 | 543.37 | 0 | 27.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50.3966 | 543.37 | 0 | 0.05921 | 6.7582 | 0 | 0 | 70.7935 | 0 | off_peak | 543.37 |  |  | 0 | 0 | 100 | 0 | 0
4709 | 557.74 | 0 | 27.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50.3966 | 557.74 | 0 | 0.05921 | 6.2491 | 0 | 0 | 70.7935 | 0 | off_peak | 557.74 |  |  | 0 | 0 | 100 | 0 | 0
4710 | 617.54 | 0 | 27.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50.3966 | 617.54 | 0 | 0.05921 | 5.8162 | 0 | 0 | 70.7935 | 0 | off_peak | 617.54 |  |  | 0 | 0 | 100 | 0 | 0
4711 | 721.68 | 101.433 | 28 | 20.3183 | 7.9194 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 0 | 61.9947 | 713.7606 | 0 | 0.05921 | 5.3583 | 0 | 0 | 82.3917 | 7.9194 | off_peak | 713.7606 | 100 | 0 | 1.1 | 0 | 98.9 | 42.4347 | 0
4712 | 701.97 | 296.953 | 28.3 | 59.4186 | 59.4186 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 61.9947 | 642.5514 | 0 | 0.05921 | 4.9855 | 0 | 0 | 82.3917 | 59.4186 | off_peak | 642.5514 |  |  | 8.46 | 0 | 91.54 | 296.2287 | 0
4713 | 714.73 | 499.453 | 28.6 | 99.8285 | 99.8285 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 61.9947 | 614.9015 | 0 | 0.05921 | 4.7276 | 0 | 0 | 82.3917 | 99.8285 | off_peak | 614.9015 |  |  | 13.97 | 0 | 86.03 | 471.9511 | 0
4714 | 716.93 | 479.931 | 28.8 | 95.8565 | 95.8565 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 61.9947 | 621.0735 | 0 | 0.05921 | 4.5806 | 0 | 0 | 82.3917 | 95.8565 | off_peak | 621.0735 |  |  | 13.37 | 0 | 86.63 | 439.0819 | 0
4715 | 718.05 | 676.308 | 29.2 | 134.8817 | 134.8817 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 61.9947 | 583.1683 | 0 | 0.05921 | 4.5294 | 0 | 0 | 82.3917 | 134.8817 | off_peak | 583.1683 |  |  | 18.78 | 0 | 81.22 | 610.9341 | 0
4716 | 689.26 | 703.179 | 29.5 | 140.087 | 140.087 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 61.9947 | 549.173 | 0 | 0.05921 | 4.5411 | 0 | 0 | 82.3917 | 140.087 | off_peak | 549.173 |  |  | 20.32 | 0 | 79.68 | 636.1463 | 0
4717 | 722.96 | 869.921 | 29.7 | 173.1784 | 173.1784 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 61.9947 | 549.7816 | 0 | 0.05921 | 4.5393 | 0 | 0 | 82.3917 | 173.1784 | off_peak | 549.7816 |  |  | 23.95 | 0 | 76.05 | 786.1121 | 0
4718 | 720.76 | 810.211 | 29.8 | 161.2326 | 161.2326 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 61.9947 | 559.5274 | 0 | 0.05921 | 5.1215 | 0 | 0 | 82.3917 | 161.2326 | off_peak | 559.5274 |  |  | 22.37 | 0 | 77.63 | 825.7502 | 0
4719 | 726.39 | 708.232 | 29.8 | 140.9387 | 140.9387 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 61.9947 | 585.4513 | 0 | 0.05921 | 5.7452 | 0 | 0 | 82.3917 | 140.9387 | off_peak | 585.4513 |  |  | 19.4 | 0 | 80.6 | 809.7183 | 0
4720 | 737 | 667.107 | 29.7 | 132.8035 | 132.8035 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 61.9947 | 604.1965 | 0 | 0.05921 | 6.2647 | 0 | 0 | 82.3917 | 132.8035 | off_peak | 604.1965 |  |  | 18.02 | 0 | 81.98 | 831.9755 | 0
4721 | 711.64 | 482.537 | 29.5 | 96.1308 | 96.1308 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 61.9947 | 615.5092 | 0 | 0.05921 | 6.6845 | 0 | 0 | 82.3917 | 96.1308 | off_peak | 615.5092 |  |  | 13.51 | 0 | 86.49 | 642.5884 | 0
4722 | 709.84 | 216.266 | 29.1 | 43.1475 | 30.7485 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 0 | 73.5928 | 679.0915 | 0 | 0.05921 | 7.1979 | 0 | 0 | 93.9898 | 30.7485 | off_peak | 679.0915 | 100 | 0 | 4.33 | 0 | 95.67 | 221.3241 | 0
4723 | 598.28 | 57.3295 | 28.9 | 11.4462 | 11.4462 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 73.5928 | 586.8338 | 0 | 0.05921 | 7.7407 | 0 | 0 | 93.9898 | 11.4462 | off_peak | 586.8338 |  |  | 1.91 | 0 | 98.09 | 88.602 | 0
4724 | 587.76 | 0 | 28.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 73.5928 | 587.76 | 0 | 0.05921 | 8.2353 | 0 | 0 | 93.9898 | 0 | off_peak | 587.76 |  |  | 0 | 0 | 100 | 0 | 0
4725 | 593.74 | 0 | 28.1 | 0 | 0 | 0 | 0 | 0.80079 | 0.80079 | 0 | 0 | 0 | 74.3419 | 594.5408 | 0 | 0.05921 | 8.4395 | 0 | 0 | 93.9898 | 0 | off_peak | 593.74 | 0 | 100 | 0 | 0 | 100 | 0 | 0
4726 | 596.68 | 0 | 28 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3419 | 596.68 | 0 | 0.05921 | 8.6767 | 0 | 0 | 93.9898 | 0 | off_peak | 596.68 |  |  | 0 | 0 | 100 | 0 | 0
4727 | 591.66 | 0 | 27.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3419 | 591.66 | 0 | 0.05921 | 8.2017 | 0 | 0 | 93.9898 | 0 | off_peak | 591.66 |  |  | 0 | 0 | 100 | 0 | 0
4728 | 609.22 | 0 | 27.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3419 | 609.22 | 0 | 0.05921 | 7.5129 | 0 | 0 | 93.9898 | 0 | off_peak | 609.22 |  |  | 0 | 0 | 100 | 0 | 0
4729 | 558.99 | 0 | 27.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3419 | 558.99 | 0 | 0.05921 | 7.1349 | 0 | 0 | 93.9898 | 0 | off_peak | 558.99 |  |  | 0 | 0 | 100 | 0 | 0
4730 | 576.54 | 0 | 27.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3419 | 576.54 | 0 | 0.05921 | 6.9685 | 0 | 0 | 93.9898 | 0 | off_peak | 576.54 |  |  | 0 | 0 | 100 | 0 | 0
4731 | 548.41 | 0 | 27.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3419 | 548.41 | 0 | 0.05921 | 6.6362 | 0 | 0 | 93.9898 | 0 | off_peak | 548.41 |  |  | 0 | 0 | 100 | 0 | 0
4732 | 604.7 | 0 | 27.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3419 | 604.7 | 0 | 0.05921 | 6.1448 | 0 | 0 | 93.9898 | 0 | off_peak | 604.7 |  |  | 0 | 0 | 100 | 0 | 0
4733 | 589.47 | 0 | 27.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3419 | 589.47 | 0 | 0.05921 | 5.74 | 0 | 0 | 93.9898 | 0 | off_peak | 589.47 |  |  | 0 | 0 | 100 | 0 | 0
4734 | 667 | 0 | 27.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3419 | 667 | 0 | 0.05921 | 5.2445 | 0 | 0 | 93.9898 | 0 | off_peak | 667 |  |  | 0 | 0 | 100 | 0 | 0
4735 | 748.04 | 104.068 | 27.9 | 20.8538 | 20.802 | 0 | 0.05172 | 0.05172 | 0 | 0 | 0 | 0 | 74.3903 | 727.238 | 0 | 0.05921 | 4.8636 | 0 | 0 | 94.0382 | 20.802 | off_peak | 727.238 | 100 | 0 | 2.78 | 0 | 97.22 | 101.1731 | 0
4736 | 844.14 | 300.93 | 28.2 | 60.2363 | 60.2363 | 0 | 0 | 0.0033404 | 0.0033404 | 0 | 0 | 0 | 74.3934 | 783.907 | 0 | 0.05921 | 4.6173 | 0 | 0 | 94.0382 | 60.2363 | off_peak | 783.9037 | 0 | 100 | 7.14 | 0 | 92.86 | 278.1314 | 0
4737 | 852.32 | 504.402 | 28.4 | 100.8912 | 100.8912 | 0 | 0 | 0.00021574 | 0.00021574 | 0 | 0 | 0 | 74.3936 | 751.429 | 0 | 0.05921 | 4.4624 | 0 | 0 | 94.0382 | 100.8912 | off_peak | 751.4288 | 0 | 100 | 11.84 | 0 | 88.16 | 450.2189 | 0
4738 | 871.34 | 684.959 | 28.6 | 136.9066 | 136.9066 | 0 | 1.3934e-05 | 1.3934e-05 | 0 | 0 | 0 | 0 | 74.3936 | 734.4334 | 0 | 0.05921 | 4.4453 | 0 | 0 | 94.0382 | 136.9066 | off_peak | 734.4334 | 100 | 0 | 15.71 | 0 | 84.29 | 608.5942 | 0
4739 | 854.21 | 825.705 | 28.8 | 164.9179 | 164.9179 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 689.2921 | 0 | 0.05921 | 4.6165 | 0 | 0 | 94.0382 | 164.9179 | off_peak | 689.2921 |  |  | 19.31 | 0 | 80.69 | 761.3427 | 0
4740 | 913.28 | 758.548 | 28.9 | 151.4493 | 151.4493 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 761.8307 | 0 | 0.05921 | 4.8686 | 0 | 0 | 94.0382 | 151.4493 | off_peak | 761.8307 |  |  | 16.58 | 0 | 83.42 | 737.3414 | 0
4741 | 877.93 | 551.591 | 29 | 110.0887 | 110.0887 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 767.8413 | 0 | 0.088511 | 4.9331 | 0 | 0 | 94.0382 | 110.0887 | on_peak | 767.8413 |  |  | 12.54 | 0 | 87.46 | 543.0805 | 0
4742 | 905.59 | 834.259 | 29.1 | 166.4439 | 166.4439 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 739.1461 | 0 | 0.088511 | 5.1852 | 0 | 0 | 94.0382 | 166.4439 | on_peak | 739.1461 |  |  | 18.38 | 0 | 81.62 | 863.0458 | 0
4743 | 899.8 | 735.574 | 29.1 | 146.7552 | 146.7552 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 753.0448 | 0 | 0.088511 | 5.7433 | 0 | 0 | 94.0382 | 146.7552 | on_peak | 753.0448 |  |  | 16.31 | 0 | 83.69 | 842.86 | 0
4744 | 743.88 | 155.313 | 29 | 30.998 | 30.998 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 712.882 | 0 | 0.088511 | 6.4578 | 0 | 0 | 94.0382 | 30.998 | on_peak | 712.882 |  |  | 4.17 | 0 | 95.83 | 200.18 | 0
4745 | 792.64 | 217.327 | 28.8 | 43.4067 | 43.4067 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 749.2333 | 0 | 0.088511 | 7.0313 | 0 | 0 | 94.0382 | 43.4067 | on_peak | 749.2333 |  |  | 5.48 | 0 | 94.52 | 305.2044 | 0
4746 | 818.51 | 120.924 | 28.6 | 24.1698 | 24.1698 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 794.3402 | 0 | 0.088511 | 7.4068 | 0 | 0 | 94.0382 | 24.1698 | on_peak | 794.3402 |  |  | 2.95 | 0 | 97.05 | 179.0203 | 0
4747 | 790.63 | 52.0064 | 28.5 | 10.3986 | 10.3986 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 780.2314 | 0 | 0.088511 | 7.3326 | 0 | 0 | 94.0382 | 10.3986 | on_peak | 780.2314 |  |  | 1.32 | 0 | 98.68 | 76.249 | 0
4748 | 838.51 | 0 | 28.1 | 0 | 0 | 0 | 0 | 0 | 0 | 62.63 | 62.63 | 0 | 7.4394 | 775.88 | 0 | 0.088511 | 7.2037 | 0 | 0 | 94.0382 | 0 | on_peak | 775.88 |  |  | 0 | 7.47 | 92.53 | 0 | 0
4749 | 818.44 | 0 | 28.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 818.44 | 0 | 0.088511 | 7.0398 | 0 | 0 | 94.0382 | 0 | on_peak | 818.44 |  |  | 0 | 0 | 100 | 0 | 0
4750 | 757.91 | 0 | 28 | 0 | 0 | 0 | 0 | 8.7263 | 8.7263 | 0 | 0 | 0 | 15.6021 | 766.6363 | 0 | 0.05921 | 7.1558 | 0 | 0 | 94.0382 | 0 | off_peak | 757.91 | 0 | 100 | 0 | 0 | 100 | 0 | 0
4751 | 786.51 | 0 | 27.9 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 27.2003 | 798.9089 | 0 | 0.05921 | 7.0266 | 0 | 0 | 94.0382 | 0 | off_peak | 786.51 | 0 | 100 | 0 | 0 | 100 | 0 | 0
4752 | 775.53 | 0 | 27.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27.2003 | 775.53 | 0 | 0.05921 | 6.8082 | 0 | 0 | 94.0382 | 0 | off_peak | 775.53 |  |  | 0 | 0 | 100 | 0 | 0
4753 | 647.91 | 0 | 27.8 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 38.7984 | 660.3089 | 0 | 0.05921 | 6.6538 | 0 | 0 | 94.0382 | 0 | off_peak | 647.91 | 0 | 100 | 0 | 0 | 100 | 0 | 0
4754 | 599.55 | 0 | 27.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 38.7984 | 599.55 | 0 | 0.05921 | 6.6226 | 0 | 0 | 94.0382 | 0 | off_peak | 599.55 |  |  | 0 | 0 | 100 | 0 | 0
4755 | 555.53 | 0 | 27.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 38.7984 | 555.53 | 0 | 0.05921 | 6.384 | 0 | 0 | 94.0382 | 0 | off_peak | 555.53 |  |  | 0 | 0 | 100 | 0 | 0
4756 | 570.7 | 0 | 27.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 38.7984 | 570.7 | 0 | 0.05921 | 5.9395 | 0 | 0 | 94.0382 | 0 | off_peak | 570.7 |  |  | 0 | 0 | 100 | 0 | 0
4757 | 561.42 | 0 | 27.6 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 50.3966 | 573.8189 | 0 | 0.05921 | 5.4692 | 0 | 0 | 94.0382 | 0 | off_peak | 561.42 | 0 | 100 | 0 | 0 | 100 | 0 | 0
4758 | 668.52 | 0 | 27.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50.3966 | 668.52 | 0 | 0.05921 | 5.0391 | 0 | 0 | 94.0382 | 0 | off_peak | 668.52 |  |  | 0 | 0 | 100 | 0 | 0
4759 | 671.02 | 100.688 | 28.2 | 20.1544 | 7.7555 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 0 | 61.9947 | 663.2645 | 0 | 0.05921 | 4.6417 | 0 | 0 | 105.6364 | 7.7555 | off_peak | 663.2645 | 100 | 0 | 1.16 | 0 | 98.84 | 35.9984 | 0
4760 | 772.98 | 295.429 | 28.5 | 59.0706 | 59.0706 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 73.5928 | 726.3084 | 0 | 0.05921 | 4.3958 | 0 | 0 | 105.6364 | 59.0706 | off_peak | 713.9094 | 0 | 100 | 7.64 | 0 | 92.36 | 259.6652 | 0
4761 | 818.67 | 497.114 | 28.7 | 99.3247 | 99.3247 | 0 | 0 | 0.80079 | 0.80079 | 0 | 0 | 0 | 74.3419 | 720.1461 | 0 | 0.05921 | 4.2466 | 0 | 0 | 105.6364 | 99.3247 | off_peak | 719.3453 | 0 | 100 | 12.13 | 0 | 87.87 | 421.7909 | 0
4762 | 847.3 | 677.824 | 28.9 | 135.3322 | 135.3322 | 0 | 0 | 0.05172 | 0.05172 | 0 | 0 | 0 | 74.3903 | 712.0195 | 0 | 0.05921 | 4.232 | 0 | 0 | 105.6364 | 135.3322 | off_peak | 711.9678 | 0 | 100 | 15.97 | 0 | 84.03 | 572.7209 | 0
4763 | 818.21 | 417.03 | 29.2 | 83.1717 | 83.1717 | 0 | 0 | 0.0033404 | 0.0033404 | 0 | 0 | 0 | 74.3934 | 735.0416 | 0 | 0.05921 | 4.3976 | 0 | 0 | 105.6364 | 83.1717 | off_peak | 735.0383 | 0 | 100 | 10.17 | 0 | 89.83 | 365.7552 | 0
4764 | 919.78 | 758.556 | 29.5 | 151.1191 | 151.1191 | 0 | 0 | 0.00021574 | 0.00021574 | 0 | 0 | 0 | 74.3936 | 768.6611 | 0 | 0.05921 | 4.6362 | 0 | 0 | 105.6364 | 151.1191 | off_peak | 768.6609 | 0 | 100 | 16.43 | 0 | 83.57 | 700.6217 | 0
4765 | 846.37 | 793.688 | 29.7 | 158.0024 | 158.0024 | 0 | 0 | 0 | 0 | 62.63 | 62.63 | 0 | 7.4394 | 625.7376 | 0 | 0.088511 | 4.8621 | 0 | 0 | 105.6364 | 158.0024 | on_peak | 625.7376 |  |  | 18.67 | 7.4 | 73.93 | 768.2282 | 0
4766 | 867.22 | 114.95 | 29.8 | 22.8751 | 22.8751 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 844.3449 | 0 | 0.088511 | 5.2665 | 0 | 0 | 105.6364 | 22.8751 | on_peak | 844.3449 |  |  | 2.64 | 0 | 97.36 | 120.4709 | 0
4767 | 895.03 | 88.35 | 29.8 | 17.5817 | 17.5817 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 877.4483 | 0 | 0.088511 | 5.6197 | 0 | 0 | 105.6364 | 17.5817 | on_peak | 877.4483 |  |  | 1.96 | 0 | 98.04 | 98.8036 | 0
4768 | 799.47 | 116.606 | 29.7 | 23.2132 | 23.2132 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 776.2568 | 0 | 0.088511 | 6.0715 | 0 | 0 | 105.6364 | 23.2132 | on_peak | 776.2568 |  |  | 2.9 | 0 | 97.1 | 140.9395 | 0
4769 | 833.01 | 70.3 | 29.5 | 14.0051 | 14.0051 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 819.0049 | 0 | 0.088511 | 6.4989 | 0 | 0 | 105.6364 | 14.0051 | on_peak | 819.0049 |  |  | 1.68 | 0 | 98.32 | 91.0176 | 0
4770 | 873.59 | 61.1464 | 29.2 | 12.1949 | 12.1949 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 861.3951 | 0 | 0.088511 | 6.7836 | 0 | 0 | 105.6364 | 12.1949 | on_peak | 861.3951 |  |  | 1.4 | 0 | 98.6 | 82.7257 | 0
4771 | 864.82 | 27.55 | 29 | 5.4985 | 5.4985 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 859.3215 | 0 | 0.088511 | 7.0174 | 0 | 0 | 105.6364 | 5.4985 | on_peak | 859.3215 |  |  | 0.64 | 0 | 99.36 | 38.5856 | 0
4772 | 898.66 | 0 | 28.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 898.66 | 0 | 0.088511 | 7.3215 | 0 | 0 | 105.6364 | 0 | on_peak | 898.66 |  |  | 0 | 0 | 100 | 0 | 0
4773 | 870.29 | 0 | 28.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 870.29 | 0 | 0.088511 | 7.7333 | 0 | 0 | 105.6364 | 0 | on_peak | 870.29 |  |  | 0 | 0 | 100 | 0 | 0
4774 | 798.37 | 0 | 28.2 | 0 | 0 | 0 | 0 | 8.7263 | 8.7263 | 0 | 0 | 0 | 15.6021 | 807.0963 | 0 | 0.05921 | 7.9023 | 0 | 0 | 105.6364 | 0 | off_peak | 798.37 | 0 | 100 | 0 | 0 | 100 | 0 | 0
4775 | 875.33 | 0 | 28.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15.6021 | 875.33 | 0 | 0.05921 | 8.0493 | 0 | 0 | 105.6364 | 0 | off_peak | 875.33 |  |  | 0 | 0 | 100 | 0 | 0
4776 | 798.52 | 0 | 28 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15.6021 | 798.52 | 0 | 0.05921 | 7.8873 | 0 | 0 | 105.6364 | 0 | off_peak | 798.52 |  |  | 0 | 0 | 100 | 0 | 0
4777 | 767.56 | 0 | 27.9 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 27.2003 | 779.9589 | 0 | 0.05921 | 7.7994 | 0 | 0 | 105.6364 | 0 | off_peak | 767.56 | 0 | 100 | 0 | 0 | 100 | 0 | 0
4778 | 665.35 | 0 | 27.9 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 38.7984 | 677.7489 | 0 | 0.05921 | 7.666 | 0 | 0 | 105.6364 | 0 | off_peak | 665.35 | 0 | 100 | 0 | 0 | 100 | 0 | 0
4779 | 703.85 | 0 | 27.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 38.7984 | 703.85 | 0 | 0.05921 | 7.3269 | 0 | 0 | 105.6364 | 0 | off_peak | 703.85 |  |  | 0 | 0 | 100 | 0 | 0
4780 | 662.21 | 0 | 27.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 38.7984 | 662.21 | 0 | 0.05921 | 6.7606 | 0 | 0 | 105.6364 | 0 | off_peak | 662.21 |  |  | 0 | 0 | 100 | 0 | 0
4781 | 639.73 | 0 | 27.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 38.7984 | 639.73 | 0 | 0.05921 | 6.1529 | 0 | 0 | 105.6364 | 0 | off_peak | 639.73 |  |  | 0 | 0 | 100 | 0 | 0
4782 | 717.67 | 0 | 28 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 50.3966 | 730.0689 | 0 | 0.05921 | 5.5586 | 0 | 0 | 105.6364 | 0 | off_peak | 717.67 | 0 | 100 | 0 | 0 | 100 | 0 | 0
4783 | 748.35 | 98.949 | 28.5 | 19.7847 | 7.3858 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 0 | 61.9947 | 740.9642 | 0 | 0.05921 | 5.0828 | 0 | 0 | 117.2345 | 7.3858 | off_peak | 740.9642 | 100 | 0 | 0.99 | 0 | 99.01 | 37.5405 | 0
4784 | 817.94 | 294.005 | 28.8 | 58.7216 | 58.7216 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 73.5928 | 771.6174 | 0 | 0.05921 | 4.7291 | 0 | 0 | 117.2345 | 58.7216 | off_peak | 759.2184 | 0 | 100 | 7.18 | 0 | 92.82 | 277.7019 | 0
4785 | 859.54 | 496.844 | 29 | 99.1621 | 99.1621 | 0 | 0 | 0.80079 | 0.80079 | 0 | 0 | 0 | 74.3419 | 761.1787 | 0 | 0.05921 | 4.532 | 0 | 0 | 117.2345 | 99.1621 | off_peak | 760.3779 | 0 | 100 | 11.54 | 0 | 88.46 | 449.4041 | 0
4786 | 814.96 | 677.253 | 29.2 | 135.0701 | 135.0701 | 0 | 0 | 0.05172 | 0.05172 | 0 | 0 | 0 | 74.3903 | 679.9416 | 0 | 0.05921 | 4.4689 | 0 | 0 | 117.2345 | 135.0701 | off_peak | 679.8899 | 0 | 100 | 16.57 | 0 | 83.43 | 603.6165 | 0
4787 | 829.66 | 817.821 | 29.4 | 162.9855 | 162.9855 | 0 | 0 | 0.0033404 | 0.0033404 | 0 | 0 | 0 | 74.3934 | 666.6778 | 0 | 0.05921 | 4.5898 | 0 | 0 | 117.2345 | 162.9855 | off_peak | 666.6745 | 0 | 100 | 19.64 | 0 | 80.36 | 748.0725 | 0
4788 | 864.25 | 277.256 | 29.6 | 55.2146 | 55.2146 | 0 | 0 | 0.00021574 | 0.00021574 | 0 | 0 | 0 | 74.3936 | 809.0356 | 0 | 0.05921 | 4.8842 | 0 | 0 | 117.2345 | 55.2146 | off_peak | 809.0354 | 0 | 100 | 6.39 | 0 | 93.61 | 269.6773 | 0
4789 | 871.33 | 723.01 | 29.7 | 143.9323 | 143.9323 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 727.3977 | 0 | 0.088511 | 5.1136 | 0 | 0 | 117.2345 | 143.9323 | on_peak | 727.3977 |  |  | 16.52 | 0 | 83.48 | 736.0103 | 0
4790 | 868.04 | 494.868 | 29.7 | 98.5152 | 98.5152 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 769.5248 | 0 | 0.088511 | 5.3816 | 0 | 0 | 117.2345 | 98.5152 | on_peak | 769.5248 |  |  | 11.35 | 0 | 88.65 | 530.1711 | 0
4791 | 878.12 | 439.873 | 29.7 | 87.5671 | 87.5671 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 790.5529 | 0 | 0.088511 | 5.6388 | 0 | 0 | 117.2345 | 87.5671 | on_peak | 790.5529 |  |  | 9.97 | 0 | 90.03 | 493.7776 | 0
4792 | 801.18 | 656.379 | 29.6 | 130.7156 | 130.7156 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 670.4644 | 0 | 0.088511 | 6.1057 | 0 | 0 | 117.2345 | 130.7156 | on_peak | 670.4644 |  |  | 16.32 | 0 | 83.68 | 798.1077 | 0
4793 | 851.95 | 440.305 | 29.4 | 87.7494 | 87.7494 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 764.2006 | 0 | 0.088511 | 6.7511 | 0 | 0 | 117.2345 | 87.7494 | on_peak | 764.2006 |  |  | 10.3 | 0 | 89.7 | 592.4096 | 0
4794 | 882.73 | 208.788 | 29.1 | 41.6555 | 41.6555 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 841.0745 | 0 | 0.088511 | 7.2777 | 0 | 0 | 117.2345 | 41.6555 | on_peak | 841.0745 |  |  | 4.72 | 0 | 95.28 | 303.1563 | 0
4795 | 862.54 | 25.65 | 28.9 | 5.1212 | 5.1212 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 857.4188 | 0 | 0.088511 | 7.9314 | 0 | 0 | 117.2345 | 5.1212 | on_peak | 857.4188 |  |  | 0.59 | 0 | 99.41 | 40.6182 | 0
4796 | 896.82 | 0 | 28.5 | 0 | 0 | 0 | 0 | 0 | 0 | 62.63 | 62.63 | 0 | 7.4394 | 834.19 | 0 | 0.088511 | 8.4003 | 0 | 0 | 117.2345 | 0 | on_peak | 834.19 |  |  | 0 | 6.98 | 93.02 | 0 | 0
4797 | 848.09 | 0 | 28.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 848.09 | 0 | 0.088511 | 8.7714 | 0 | 0 | 117.2345 | 0 | on_peak | 848.09 |  |  | 0 | 0 | 100 | 0 | 0
4798 | 817.89 | 0 | 28.3 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 19.0375 | 830.2889 | 0 | 0.05921 | 8.9792 | 0 | 0 | 117.2345 | 0 | off_peak | 817.89 | 0 | 100 | 0 | 0 | 100 | 0 | 0
4799 | 882.87 | 0 | 28.2 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 30.6357 | 895.2689 | 0 | 0.05921 | 8.6865 | 0 | 0 | 117.2345 | 0 | off_peak | 882.87 | 0 | 100 | 0 | 0 | 100 | 0 | 0
4800 | 829.62 | 0 | 28.2 | 0 | 0 | 0 | 0 | 8.7263 | 8.7263 | 0 | 0 | 0 | 38.7984 | 838.3463 | 0 | 0.05921 | 8.4259 | 0 | 0 | 117.2345 | 0 | off_peak | 829.62 | 0 | 100 | 0 | 0 | 100 | 0 | 0
4801 | 731.22 | 0 | 28.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 38.7984 | 731.22 | 0 | 0.05921 | 8.1272 | 0 | 0 | 117.2345 | 0 | off_peak | 731.22 |  |  | 0 | 0 | 100 | 0 | 0
4802 | 723.92 | 0 | 28 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 38.7984 | 723.92 | 0 | 0.05921 | 8.066 | 0 | 0 | 117.2345 | 0 | off_peak | 723.92 |  |  | 0 | 0 | 100 | 0 | 0
4803 | 653.04 | 0 | 28 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 38.7984 | 653.04 | 0 | 0.05921 | 7.7509 | 0 | 0 | 117.2345 | 0 | off_peak | 653.04 |  |  | 0 | 0 | 100 | 0 | 0
4804 | 643.22 | 0 | 27.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 38.7984 | 643.22 | 0 | 0.05921 | 7.2214 | 0 | 0 | 117.2345 | 0 | off_peak | 643.22 |  |  | 0 | 0 | 100 | 0 | 0
4805 | 691.28 | 0 | 27.9 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 50.3966 | 703.6789 | 0 | 0.05921 | 6.5464 | 0 | 0 | 117.2345 | 0 | off_peak | 691.28 | 0 | 100 | 0 | 0 | 100 | 0 | 0
4806 | 733.92 | 0 | 28 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50.3966 | 733.92 | 0 | 0.05921 | 5.9776 | 0 | 0 | 117.2345 | 0 | off_peak | 733.92 |  |  | 0 | 0 | 100 | 0 | 0
4807 | 720.35 | 96.488 | 28.3 | 19.3067 | 6.9078 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 0 | 61.9947 | 713.4422 | 0 | 0.05921 | 5.5174 | 0 | 0 | 128.8326 | 6.9078 | off_peak | 713.4422 | 100 | 0 | 0.96 | 0 | 99.04 | 38.1128 | 0
4808 | 844.28 | 290.375 | 28.7 | 58.0177 | 58.0177 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 73.5928 | 798.6612 | 0 | 0.05921 | 5.1972 | 0 | 0 | 128.8326 | 58.0177 | off_peak | 786.2623 | 0 | 100 | 6.87 | 0 | 93.13 | 301.527 | 0
4809 | 834.83 | 494.204 | 28.9 | 98.6712 | 98.6712 | 0 | 0 | 0.80079 | 0.80079 | 0 | 0 | 0 | 74.3419 | 736.9596 | 0 | 0.05921 | 5.0068 | 0 | 0 | 128.8326 | 98.6712 | off_peak | 736.1588 | 0 | 100 | 11.82 | 0 | 88.18 | 494.0245 | 0
4810 | 883.49 | 555.149 | 29.3 | 110.6774 | 110.6774 | 0 | 0 | 0.05172 | 0.05172 | 0 | 0 | 0 | 74.3903 | 772.8643 | 0 | 0.05921 | 4.902 | 0 | 0 | 128.8326 | 110.6774 | off_peak | 772.8126 | 0 | 100 | 12.53 | 0 | 87.47 | 542.5424 | 0
4811 | 872.73 | 609.28 | 29.7 | 121.2916 | 121.2916 | 0 | 0 | 0.0033404 | 0.0033404 | 0 | 0 | 0 | 74.3934 | 751.4417 | 0 | 0.05921 | 5.0122 | 0 | 0 | 128.8326 | 121.2916 | off_peak | 751.4384 | 0 | 100 | 13.9 | 0 | 86.1 | 607.9439 | 0
4812 | 896.79 | 899.747 | 30 | 178.9192 | 178.9192 | 0 | 0 | 0.00021574 | 0.00021574 | 0 | 0 | 0 | 74.3936 | 717.871 | 0 | 0.05921 | 5.2233 | 0 | 0 | 128.8326 | 178.9192 | off_peak | 717.8708 | 0 | 100 | 19.95 | 0 | 80.05 | 934.5481 | 0
4813 | 888.02 | 459.613 | 30.3 | 91.2958 | 91.2958 | 0 | 0 | 0 | 0 | 62.63 | 62.63 | 0 | 7.4394 | 734.0942 | 0 | 0.088511 | 5.3356 | 0 | 0 | 128.8326 | 91.2958 | on_peak | 734.0942 |  |  | 10.28 | 7.05 | 82.67 | 487.1176 | 0
4814 | 905.31 | 515.677 | 30.4 | 102.3946 | 102.3946 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 802.9154 | 0 | 0.088511 | 5.5951 | 0 | 0 | 128.8326 | 102.3946 | on_peak | 802.9154 |  |  | 11.31 | 0 | 88.69 | 572.9055 | 0
4815 | 917.08 | 670.067 | 30.5 | 133.0019 | 133.0019 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 784.0781 | 0 | 0.088511 | 5.8591 | 0 | 0 | 128.8326 | 133.0019 | on_peak | 784.0781 |  |  | 14.5 | 0 | 85.5 | 779.2697 | 0
4816 | 894.09 | 542.451 | 30.5 | 107.6714 | 107.6714 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 786.4186 | 0 | 0.088511 | 6.2467 | 0 | 0 | 128.8326 | 107.6714 | on_peak | 786.4186 |  |  | 12.04 | 0 | 87.96 | 672.5952 | 0
4817 | 862.35 | 363.438 | 30.3 | 72.192 | 72.192 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 790.158 | 0 | 0.088511 | 6.7119 | 0 | 0 | 128.8326 | 72.192 | on_peak | 790.158 |  |  | 8.37 | 0 | 91.63 | 484.5484 | 0
4818 | 907.33 | 196.867 | 29.9 | 39.1623 | 39.1623 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 868.1677 | 0 | 0.088511 | 7.3241 | 0 | 0 | 128.8326 | 39.1623 | on_peak | 868.1677 |  |  | 4.32 | 0 | 95.68 | 286.8294 | 0
4819 | 900.4 | 49.8147 | 29.7 | 9.9168 | 9.9168 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 890.4832 | 0 | 0.088511 | 7.8601 | 0 | 0 | 128.8326 | 9.9168 | on_peak | 890.4832 |  |  | 1.1 | 0 | 98.9 | 77.9474 | 0
4820 | 937.3 | 0 | 29 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 937.3 | 0 | 0.088511 | 8.2779 | 0 | 0 | 128.8326 | 0 | on_peak | 937.3 |  |  | 0 | 0 | 100 | 0 | 0
4821 | 888.48 | 0 | 28.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 888.48 | 0 | 0.088511 | 8.3936 | 0 | 0 | 128.8326 | 0 | on_peak | 888.48 |  |  | 0 | 0 | 100 | 0 | 0
4822 | 863.85 | 0 | 28.5 | 0 | 0 | 0 | 0 | 8.7263 | 8.7263 | 0 | 0 | 0 | 15.6021 | 872.5763 | 0 | 0.05921 | 8.7558 | 0 | 0 | 128.8326 | 0 | off_peak | 863.85 | 0 | 100 | 0 | 0 | 100 | 0 | 0
4823 | 896.09 | 0 | 28.4 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 27.2003 | 908.4889 | 0 | 0.05921 | 8.8835 | 0 | 0 | 128.8326 | 0 | off_peak | 896.09 | 0 | 100 | 0 | 0 | 100 | 0 | 0
4824 | 846.99 | 0 | 28.3 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 38.7984 | 859.3889 | 0 | 0.05921 | 8.8037 | 0 | 0 | 128.8326 | 0 | off_peak | 846.99 | 0 | 100 | 0 | 0 | 100 | 0 | 0
4825 | 818.5 | 0 | 28.3 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 50.3966 | 830.8989 | 0 | 0.05921 | 8.6977 | 0 | 0 | 128.8326 | 0 | off_peak | 818.5 | 0 | 100 | 0 | 0 | 100 | 0 | 0
4826 | 742.96 | 0 | 28.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50.3966 | 742.96 | 0 | 0.05921 | 8.4887 | 0 | 0 | 128.8326 | 0 | off_peak | 742.96 |  |  | 0 | 0 | 100 | 0 | 0
4827 | 732.72 | 0 | 28.1 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 61.9947 | 745.1189 | 0 | 0.05921 | 8.316 | 0 | 0 | 128.8326 | 0 | off_peak | 732.72 | 0 | 100 | 0 | 0 | 100 | 0 | 0
4828 | 683.12 | 0 | 28.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 61.9947 | 683.12 | 0 | 0.05921 | 7.7511 | 0 | 0 | 128.8326 | 0 | off_peak | 683.12 |  |  | 0 | 0 | 100 | 0 | 0
4829 | 750.55 | 0 | 28.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 61.9947 | 750.55 | 0 | 0.05921 | 7.0267 | 0 | 0 | 128.8326 | 0 | off_peak | 750.55 |  |  | 0 | 0 | 100 | 0 | 0
4830 | 765.96 | 0 | 28.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 61.9947 | 765.96 | 0 | 0.05921 | 6.4302 | 0 | 0 | 128.8326 | 0 | off_peak | 765.96 |  |  | 0 | 0 | 100 | 0 | 0
4831 | 809.31 | 93.9694 | 28.4 | 18.7959 | 6.397 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 0 | 73.5928 | 802.913 | 0 | 0.05921 | 5.9416 | 0 | 0 | 140.4308 | 6.397 | off_peak | 802.913 | 100 | 0 | 0.79 | 0 | 99.21 | 38.0084 | 0
4832 | 835.66 | 286.849 | 28.8 | 57.2923 | 57.2923 | 0 | 0 | 0.80079 | 0.80079 | 0 | 0 | 0 | 74.3419 | 779.1685 | 0 | 0.05921 | 5.5604 | 0 | 0 | 140.4308 | 57.2923 | off_peak | 778.3677 | 0 | 100 | 6.86 | 0 | 93.14 | 318.5657 | 0
4833 | 905.2 | 489.479 | 29 | 97.6922 | 97.6922 | 0 | 0 | 0.05172 | 0.05172 | 0 | 0 | 0 | 74.3903 | 807.5595 | 0 | 0.05921 | 5.2924 | 0 | 0 | 140.4308 | 97.6922 | off_peak | 807.5078 | 0 | 100 | 10.79 | 0 | 89.21 | 517.0229 | 0
4834 | 887.52 | 523.606 | 29.2 | 104.427 | 104.427 | 0 | 0 | 0.0033404 | 0.0033404 | 0 | 0 | 0 | 74.3934 | 783.0963 | 0 | 0.05921 | 5.1453 | 0 | 0 | 140.4308 | 104.427 | off_peak | 783.093 | 0 | 100 | 11.77 | 0 | 88.23 | 537.304 | 0
4835 | 897.09 | 579.973 | 29.5 | 115.5419 | 115.5419 | 0 | 0 | 0.00021574 | 0.00021574 | 0 | 0 | 0 | 74.3936 | 781.5483 | 0 | 0.05921 | 5.1967 | 0 | 0 | 140.4308 | 115.5419 | off_peak | 781.5481 | 0 | 100 | 12.88 | 0 | 87.12 | 600.4373 | 0
4836 | 937.62 | 41.8 | 29.7 | 8.3213 | 8.3213 | 0 | 0 | 1.3934e-05 | 1.3934e-05 | 0 | 0 | 0 | 74.3936 | 929.2987 | 0 | 0.05921 | 5.3392 | 0 | 0 | 140.4308 | 8.3213 | off_peak | 929.2987 | 0 | 100 | 0.89 | 0 | 99.11 | 44.4286 | 0
4837 | 927.72 | 90.25 | 29.9 | 17.9532 | 17.9532 | 0 | 0 | 0 | 0 | 62.63 | 62.63 | 0 | 7.4394 | 847.1368 | 0 | 0.088511 | 5.5013 | 0 | 0 | 140.4308 | 17.9532 | on_peak | 847.1368 |  |  | 1.94 | 6.75 | 91.31 | 98.7664 | 0
4838 | 936 | 89.3 | 30 | 17.7578 | 17.7578 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 918.2422 | 0 | 0.088511 | 5.8061 | 0 | 0 | 140.4308 | 17.7578 | on_peak | 918.2422 |  |  | 1.9 | 0 | 98.1 | 103.1039 | 0
4839 | 968.64 | 159.484 | 30 | 31.7142 | 31.7142 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 936.9258 | 0 | 0.088511 | 6.2568 | 0 | 0 | 140.4308 | 31.7142 | on_peak | 936.9258 |  |  | 3.27 | 0 | 96.73 | 198.4287 | 0
4840 | 918.11 | 239.34 | 29.9 | 47.6114 | 47.6114 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 870.4986 | 0 | 0.088511 | 6.8003 | 0 | 0 | 140.4308 | 47.6114 | on_peak | 870.4986 |  |  | 5.19 | 0 | 94.81 | 323.7704 | 0
4841 | 906.07 | 194.679 | 29.7 | 38.7555 | 38.7555 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 867.3145 | 0 | 0.088511 | 7.3084 | 0 | 0 | 140.4308 | 38.7555 | on_peak | 867.3145 |  |  | 4.28 | 0 | 95.72 | 283.2419 | 0
4842 | 908.79 | 142.827 | 29.4 | 28.4643 | 28.4643 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 880.3257 | 0 | 0.088511 | 7.8324 | 0 | 0 | 140.4308 | 28.4643 | on_peak | 880.3257 |  |  | 3.13 | 0 | 96.87 | 222.944 | 0
4843 | 911.78 | 58.9094 | 29.2 | 11.7488 | 11.7488 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 900.0312 | 0 | 0.088511 | 8.2351 | 0 | 0 | 140.4308 | 11.7488 | on_peak | 900.0312 |  |  | 1.29 | 0 | 98.71 | 96.7519 | 0
4844 | 881.71 | 0 | 28.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 881.71 | 0 | 0.088511 | 8.3874 | 0 | 0 | 140.4308 | 0 | on_peak | 881.71 |  |  | 0 | 0 | 100 | 0 | 0
4845 | 886.53 | 0 | 28.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 886.53 | 0 | 0.088511 | 8.0503 | 0 | 0 | 140.4308 | 0 | on_peak | 886.53 |  |  | 0 | 0 | 100 | 0 | 0
4846 | 869.16 | 0 | 28.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 869.16 | 0 | 0.05921 | 8.0409 | 0 | 0 | 140.4308 | 0 | off_peak | 869.16 |  |  | 0 | 0 | 100 | 0 | 0
4847 | 871.93 | 0 | 28.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 871.93 | 0 | 0.05921 | 8.0863 | 0 | 0 | 140.4308 | 0 | off_peak | 871.93 |  |  | 0 | 0 | 100 | 0 | 0
4848 | 824.14 | 0 | 28.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 824.14 | 0 | 0.05921 | 8.0937 | 0 | 0 | 140.4308 | 0 | off_peak | 824.14 |  |  | 0 | 0 | 100 | 0 | 0
4849 | 764.38 | 0 | 28.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 764.38 | 0 | 0.05921 | 8.0687 | 0 | 0 | 140.4308 | 0 | off_peak | 764.38 |  |  | 0 | 0 | 100 | 0 | 0
4850 | 712.29 | 0 | 28.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 712.29 | 0 | 0.05921 | 7.9794 | 0 | 0 | 140.4308 | 0 | off_peak | 712.29 |  |  | 0 | 0 | 100 | 0 | 0
4851 | 743.68 | 0 | 28.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 743.68 | 0 | 0.05921 | 7.7623 | 0 | 0 | 140.4308 | 0 | off_peak | 743.68 |  |  | 0 | 0 | 100 | 0 | 0
4852 | 703.96 | 0 | 28.1 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 19.0375 | 716.3589 | 0 | 0.05921 | 7.2446 | 0 | 0 | 140.4308 | 0 | off_peak | 703.96 | 0 | 100 | 0 | 0 | 100 | 0 | 0
4853 | 650.19 | 0 | 28.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19.0375 | 650.19 | 0 | 0.05921 | 6.6533 | 0 | 0 | 140.4308 | 0 | off_peak | 650.19 |  |  | 0 | 0 | 100 | 0 | 0
4854 | 698.6 | 0 | 28.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19.0375 | 698.6 | 0 | 0.05921 | 6.126 | 0 | 0 | 140.4308 | 0 | off_peak | 698.6 |  |  | 0 | 0 | 100 | 0 | 0
4855 | 732.17 | 72.2823 | 28.7 | 14.4422 | 14.4422 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19.0375 | 717.7278 | 0 | 0.05921 | 5.6535 | 0 | 0 | 140.4308 | 14.4422 | off_peak | 717.7278 |  |  | 1.97 | 0 | 98.03 | 81.6496 | 0
4856 | 721.38 | 274.755 | 29 | 54.8367 | 54.8367 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19.0375 | 666.5433 | 0 | 0.05921 | 5.2771 | 0 | 0 | 140.4308 | 54.8367 | off_peak | 666.5433 |  |  | 7.6 | 0 | 92.4 | 289.3799 | 0
4857 | 733.11 | 443.882 | 29.2 | 88.527 | 88.527 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19.0375 | 644.583 | 0 | 0.05921 | 5.0233 | 0 | 0 | 140.4308 | 88.527 | off_peak | 644.583 |  |  | 12.08 | 0 | 87.92 | 444.6935 | 0
4858 | 742.52 | 618.61 | 29.4 | 123.2843 | 123.2843 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19.0375 | 619.2357 | 0 | 0.05921 | 4.884 | 0 | 0 | 140.4308 | 123.2843 | off_peak | 619.2357 |  |  | 16.6 | 0 | 83.4 | 602.1143 | 0
4859 | 742.97 | 525.74 | 29.6 | 104.6993 | 104.6993 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19.0375 | 638.2707 | 0 | 0.05921 | 4.8274 | 0 | 0 | 140.4308 | 104.6993 | off_peak | 638.2707 |  |  | 14.09 | 0 | 85.91 | 505.4269 | 0
4860 | 747.81 | 670.769 | 29.8 | 133.4836 | 133.4836 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19.0375 | 614.3264 | 0 | 0.05921 | 4.844 | 0 | 0 | 140.4308 | 133.4836 | off_peak | 614.3264 |  |  | 17.85 | 0 | 82.15 | 646.5945 | 0
4861 | 750.06 | 522.075 | 30.1 | 103.7792 | 103.7792 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19.0375 | 646.2808 | 0 | 0.05921 | 4.9815 | 0 | 0 | 140.4308 | 103.7792 | off_peak | 646.2808 |  |  | 13.84 | 0 | 86.16 | 516.977 | 0
4862 | 731.91 | 730.318 | 30.2 | 145.1209 | 145.1209 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19.0375 | 586.7891 | 0 | 0.05921 | 5.437 | 0 | 0 | 140.4308 | 145.1209 | off_peak | 586.7891 |  |  | 19.83 | 0 | 80.17 | 789.0248 | 0
4863 | 690.15 | 645.149 | 30.3 | 128.15 | 128.15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19.0375 | 562 | 0 | 0.05921 | 5.9793 | 0 | 0 | 140.4308 | 128.15 | off_peak | 562 |  |  | 18.57 | 0 | 81.43 | 766.2416 | 0
4864 | 750.58 | 487.81 | 30.3 | 96.8968 | 96.8968 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19.0375 | 653.6832 | 0 | 0.05921 | 6.5717 | 0 | 0 | 140.4308 | 96.8968 | off_peak | 653.6832 |  |  | 12.91 | 0 | 87.09 | 636.7769 | 0
4865 | 782.51 | 239.527 | 30 | 47.6311 | 47.6311 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19.0375 | 734.8789 | 0 | 0.05921 | 7.0964 | 0 | 0 | 140.4308 | 47.6311 | off_peak | 734.8789 |  |  | 6.09 | 0 | 93.91 | 338.0109 | 0
4866 | 681.41 | 84.2858 | 29.7 | 16.7791 | 4.3801 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 0 | 30.6357 | 677.0299 | 0 | 0.05921 | 7.7297 | 0 | 0 | 152.0289 | 4.3801 | off_peak | 677.0299 | 100 | 0 | 0.64 | 0 | 99.36 | 33.8574 | 0
4867 | 668.68 | 54.5574 | 29.5 | 10.8689 | 10.8689 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30.6357 | 657.8111 | 0 | 0.05921 | 8.0831 | 0 | 0 | 152.0289 | 10.8689 | off_peak | 657.8111 |  |  | 1.63 | 0 | 98.37 | 87.8541 | 0
4868 | 662.52 | 0 | 29 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30.6357 | 662.52 | 0 | 0.05921 | 8.4095 | 0 | 0 | 152.0289 | 0 | off_peak | 662.52 |  |  | 0 | 0 | 100 | 0 | 0
4869 | 647.21 | 0 | 28.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30.6357 | 647.21 | 0 | 0.05921 | 8.633 | 0 | 0 | 152.0289 | 0 | off_peak | 647.21 |  |  | 0 | 0 | 100 | 0 | 0
4870 | 646.35 | 0 | 28.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30.6357 | 646.35 | 0 | 0.05921 | 8.2525 | 0 | 0 | 152.0289 | 0 | off_peak | 646.35 |  |  | 0 | 0 | 100 | 0 | 0
4871 | 643.86 | 0 | 28.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30.6357 | 643.86 | 0 | 0.05921 | 8.0958 | 0 | 0 | 152.0289 | 0 | off_peak | 643.86 |  |  | 0 | 0 | 100 | 0 | 0
4872 | 648.24 | 0 | 28.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30.6357 | 648.24 | 0 | 0.05921 | 8.0762 | 0 | 0 | 152.0289 | 0 | off_peak | 648.24 |  |  | 0 | 0 | 100 | 0 | 0
4873 | 652.36 | 0 | 28 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30.6357 | 652.36 | 0 | 0.05921 | 7.8314 | 0 | 0 | 152.0289 | 0 | off_peak | 652.36 |  |  | 0 | 0 | 100 | 0 | 0
4874 | 652.85 | 0 | 28 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30.6357 | 652.85 | 0 | 0.05921 | 7.6306 | 0 | 0 | 152.0289 | 0 | off_peak | 652.85 |  |  | 0 | 0 | 100 | 0 | 0
4875 | 624.95 | 0 | 27.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30.6357 | 624.95 | 0 | 0.05921 | 7.4192 | 0 | 0 | 152.0289 | 0 | off_peak | 624.95 |  |  | 0 | 0 | 100 | 0 | 0
4876 | 643.62 | 0 | 28 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30.6357 | 643.62 | 0 | 0.05921 | 6.8905 | 0 | 0 | 152.0289 | 0 | off_peak | 643.62 |  |  | 0 | 0 | 100 | 0 | 0
4877 | 646.32 | 0 | 28 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30.6357 | 646.32 | 0 | 0.05921 | 6.4478 | 0 | 0 | 152.0289 | 0 | off_peak | 646.32 |  |  | 0 | 0 | 100 | 0 | 0
4878 | 752.18 | 0 | 28.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30.6357 | 752.18 | 0 | 0.05921 | 5.8405 | 0 | 0 | 152.0289 | 0 | off_peak | 752.18 |  |  | 0 | 0 | 100 | 0 | 0
4879 | 720.08 | 63.002 | 28.8 | 12.5834 | 3.857 | 0 | 8.7263 | 8.7263 | 0 | 0 | 0 | 0 | 38.7984 | 716.223 | 0 | 0.05921 | 5.422 | 0 | 0 | 160.1917 | 3.857 | off_peak | 716.223 | 100 | 0 | 0.54 | 0 | 99.46 | 20.9129 | 0
4880 | 726.32 | 162.585 | 29.3 | 32.4138 | 32.4138 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 38.7984 | 693.9062 | 0 | 0.05921 | 5.033 | 0 | 0 | 160.1917 | 32.4138 | off_peak | 693.9062 |  |  | 4.46 | 0 | 95.54 | 163.1379 | 0
4881 | 764.03 | 305.469 | 29.6 | 60.8331 | 48.4342 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 0 | 50.3966 | 715.5958 | 0 | 0.05921 | 4.7632 | 0 | 0 | 171.7898 | 48.4342 | off_peak | 715.5958 | 100 | 0 | 6.34 | 0 | 93.66 | 230.7011 | 0
4882 | 777.87 | 462.981 | 29.9 | 92.0998 | 92.0998 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50.3966 | 685.7702 | 0 | 0.05921 | 4.6182 | 0 | 0 | 171.7898 | 92.0998 | off_peak | 685.7702 |  |  | 11.84 | 0 | 88.16 | 425.335 | 0
4883 | 750.02 | 796.129 | 30.1 | 158.2562 | 158.2562 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50.3966 | 591.7638 | 0 | 0.05921 | 4.5355 | 0 | 0 | 171.7898 | 158.2562 | off_peak | 591.7638 |  |  | 21.1 | 0 | 78.9 | 717.7717 | 0
4884 | 747.89 | 866.144 | 30.2 | 172.1108 | 159.7118 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 0 | 61.9947 | 588.1782 | 0 | 0.05921 | 4.5124 | 0 | 0 | 183.388 | 159.7118 | off_peak | 588.1782 | 100 | 0 | 21.35 | 0 | 78.65 | 720.6902 | 0
4885 | 747.76 | 571.327 | 30.3 | 113.4863 | 113.4863 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 61.9947 | 634.2737 | 0 | 0.05921 | 4.5634 | 0 | 0 | 183.388 | 113.4863 | off_peak | 634.2737 |  |  | 15.18 | 0 | 84.82 | 517.8841 | 0
4886 | 758.61 | 831.148 | 30.3 | 165.0962 | 165.0962 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 61.9947 | 593.5138 | 0 | 0.05921 | 5.0747 | 0 | 0 | 183.388 | 165.0962 | off_peak | 593.5138 |  |  | 21.76 | 0 | 78.24 | 837.8078 | 0
4887 | 752.07 | 521.417 | 30.1 | 103.6484 | 103.6484 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 61.9947 | 648.4216 | 0 | 0.05921 | 5.6785 | 0 | 0 | 183.388 | 103.6484 | off_peak | 648.4216 |  |  | 13.78 | 0 | 86.22 | 588.5636 | 0
4888 | 733.89 | 492.676 | 29.9 | 98.007 | 98.007 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 61.9947 | 635.883 | 0 | 0.05921 | 6.3123 | 0 | 0 | 183.388 | 98.007 | off_peak | 635.883 |  |  | 13.35 | 0 | 86.65 | 618.6529 | 0
4889 | 744.75 | 423.586 | 29.7 | 84.3248 | 84.3248 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 61.9947 | 660.4252 | 0 | 0.05921 | 6.8169 | 0 | 0 | 183.388 | 84.3248 | off_peak | 660.4252 |  |  | 11.32 | 0 | 88.68 | 574.8365 | 0
4890 | 686.11 | 172.702 | 29.4 | 34.4182 | 34.4182 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 61.9947 | 651.6918 | 0 | 0.05921 | 7.4207 | 0 | 0 | 183.388 | 34.4182 | off_peak | 651.6918 |  |  | 5.02 | 0 | 94.98 | 255.4076 | 0
4891 | 628.55 | 46.9535 | 29.2 | 9.3643 | 9.3643 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 61.9947 | 619.1857 | 0 | 0.05921 | 7.7704 | 0 | 0 | 183.388 | 9.3643 | off_peak | 619.1857 |  |  | 1.49 | 0 | 98.51 | 72.7643 | 0
4892 | 655.63 | 0 | 28.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 61.9947 | 655.63 | 0 | 0.05921 | 8.002 | 0 | 0 | 183.388 | 0 | off_peak | 655.63 |  |  | 0 | 0 | 100 | 0 | 0
4893 | 631.43 | 0 | 28.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 61.9947 | 631.43 | 0 | 0.05921 | 8.0656 | 0 | 0 | 183.388 | 0 | off_peak | 631.43 |  |  | 0 | 0 | 100 | 0 | 0
4894 | 639.45 | 0 | 28.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 61.9947 | 639.45 | 0 | 0.05921 | 8.3186 | 0 | 0 | 183.388 | 0 | off_peak | 639.45 |  |  | 0 | 0 | 100 | 0 | 0
4895 | 632.43 | 0 | 28.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 61.9947 | 632.43 | 0 | 0.05921 | 8.4738 | 0 | 0 | 183.388 | 0 | off_peak | 632.43 |  |  | 0 | 0 | 100 | 0 | 0
4896 | 637.11 | 0 | 28 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 61.9947 | 637.11 | 0 | 0.05921 | 8.3537 | 0 | 0 | 183.388 | 0 | off_peak | 637.11 |  |  | 0 | 0 | 100 | 0 | 0
4897 | 607.1 | 0 | 27.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 61.9947 | 607.1 | 0 | 0.05921 | 8.1053 | 0 | 0 | 183.388 | 0 | off_peak | 607.1 |  |  | 0 | 0 | 100 | 0 | 0
4898 | 643.59 | 0 | 27.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 61.9947 | 643.59 | 0 | 0.05921 | 7.9288 | 0 | 0 | 183.388 | 0 | off_peak | 643.59 |  |  | 0 | 0 | 100 | 0 | 0
4899 | 610.88 | 0 | 27.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 61.9947 | 610.88 | 0 | 0.05921 | 7.6852 | 0 | 0 | 183.388 | 0 | off_peak | 610.88 |  |  | 0 | 0 | 100 | 0 | 0
4900 | 626.93 | 0 | 27.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 61.9947 | 626.93 | 0 | 0.05921 | 7.1562 | 0 | 0 | 183.388 | 0 | off_peak | 626.93 |  |  | 0 | 0 | 100 | 0 | 0
4901 | 622.78 | 0 | 27.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 61.9947 | 622.78 | 0 | 0.05921 | 6.5178 | 0 | 0 | 183.388 | 0 | off_peak | 622.78 |  |  | 0 | 0 | 100 | 0 | 0
4902 | 704.49 | 0 | 27.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 61.9947 | 704.49 | 0 | 0.05921 | 5.9277 | 0 | 0 | 183.388 | 0 | off_peak | 704.49 |  |  | 0 | 0 | 100 | 0 | 0
4903 | 782.56 | 89.5361 | 27.8 | 17.9483 | 5.5494 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 0 | 73.5928 | 777.0106 | 0 | 0.05921 | 5.4818 | 0 | 0 | 194.9861 | 5.5494 | off_peak | 777.0106 | 100 | 0 | 0.71 | 0 | 99.29 | 30.4203 | 0
4904 | 844.77 | 53.2 | 28 | 10.6567 | 9.8559 | 0 | 0.80079 | 0.80079 | 0 | 0 | 0 | 0 | 74.3419 | 834.9141 | 0 | 0.05921 | 5.1176 | 0 | 0 | 195.7352 | 9.8559 | off_peak | 834.9141 | 100 | 0 | 1.17 | 0 | 98.83 | 50.4388 | 0
4905 | 856.66 | 424.432 | 28.1 | 84.9883 | 84.9883 | 0 | 0 | 0.05172 | 0.05172 | 0 | 0 | 0 | 74.3903 | 771.7234 | 0 | 0.05921 | 4.8964 | 0 | 0 | 195.7352 | 84.9883 | off_peak | 771.6717 | 0 | 100 | 9.92 | 0 | 90.08 | 416.1379 | 0
4906 | 893.65 | 494.324 | 28.2 | 98.9475 | 98.9475 | 0 | 0 | 0.0033404 | 0.0033404 | 0 | 0 | 0 | 74.3934 | 794.7059 | 0 | 0.05921 | 4.8027 | 0 | 0 | 195.7352 | 98.9475 | off_peak | 794.7025 | 0 | 100 | 11.07 | 0 | 88.93 | 475.2178 | 0
4907 | 819.73 | 817.519 | 28.3 | 163.5809 | 163.5809 | 0 | 0 | 0.00021574 | 0.00021574 | 0 | 0 | 0 | 74.3936 | 656.1493 | 0 | 0.05921 | 4.9097 | 0 | 0 | 195.7352 | 163.5809 | off_peak | 656.1491 | 0 | 100 | 19.96 | 0 | 80.04 | 803.1263 | 0
4908 | 913.16 | 907.344 | 28.3 | 181.5544 | 181.5544 | 0 | 0 | 1.3934e-05 | 1.3934e-05 | 0 | 0 | 0 | 74.3936 | 731.6057 | 0 | 0.05921 | 5.0954 | 0 | 0 | 195.7352 | 181.5544 | off_peak | 731.6056 | 0 | 100 | 19.88 | 0 | 80.12 | 925.0936 | 0
4909 | 871.93 | 757.608 | 28.2 | 151.6483 | 151.6483 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 720.2817 | 0 | 0.088511 | 5.2118 | 0 | 0 | 195.7352 | 151.6483 | on_peak | 720.2817 |  |  | 17.39 | 0 | 82.61 | 790.3551 | 0
4910 | 890.71 | 820.911 | 28.2 | 164.3195 | 164.3195 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 726.3905 | 0 | 0.088511 | 5.6605 | 0 | 0 | 195.7352 | 164.3195 | on_peak | 726.3905 |  |  | 18.45 | 0 | 81.55 | 930.1245 | 0
4911 | 957.45 | 569.645 | 28.1 | 114.0658 | 114.0658 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 843.3842 | 0 | 0.088511 | 6.0799 | 0 | 0 | 195.7352 | 114.0658 | on_peak | 843.3842 |  |  | 11.91 | 0 | 88.09 | 693.5037 | 0
4912 | 876.52 | 386.639 | 28 | 77.4488 | 77.4488 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 799.0712 | 0 | 0.088511 | 6.5505 | 0 | 0 | 195.7352 | 77.4488 | on_peak | 799.0712 |  |  | 8.84 | 0 | 91.16 | 507.3322 | 0
4913 | 849.48 | 374.738 | 28 | 75.0649 | 75.0649 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 774.4151 | 0 | 0.088511 | 7.0478 | 0 | 0 | 195.7352 | 75.0649 | on_peak | 774.4151 |  |  | 8.84 | 0 | 91.16 | 529.0441 | 0
4914 | 861.18 | 133.144 | 28 | 26.6705 | 26.6705 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 834.5095 | 0 | 0.088511 | 7.6329 | 0 | 0 | 195.7352 | 26.6705 | on_peak | 834.5095 |  |  | 3.1 | 0 | 96.9 | 203.5739 | 0
4915 | 837.74 | 59.8138 | 27.9 | 11.9858 | 11.9858 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 825.7542 | 0 | 0.088511 | 8.0957 | 0 | 0 | 195.7352 | 11.9858 | on_peak | 825.7542 |  |  | 1.43 | 0 | 98.57 | 97.0335 | 0
4916 | 831.79 | 0 | 28 | 0 | 0 | 0 | 0 | 0 | 0 | 62.63 | 62.63 | 0 | 7.4394 | 769.16 | 0 | 0.088511 | 8.3746 | 0 | 0 | 195.7352 | 0 | on_peak | 769.16 |  |  | 0 | 7.53 | 92.47 | 0 | 0
4917 | 860.77 | 0 | 28.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 860.77 | 0 | 0.088511 | 8.6272 | 0 | 0 | 195.7352 | 0 | on_peak | 860.77 |  |  | 0 | 0 | 100 | 0 | 0
4918 | 798.18 | 0 | 28.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 798.18 | 0 | 0.05921 | 8.8056 | 0 | 0 | 195.7352 | 0 | off_peak | 798.18 |  |  | 0 | 0 | 100 | 0 | 0
4919 | 806.92 | 0 | 28.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 806.92 | 0 | 0.05921 | 8.8977 | 0 | 0 | 195.7352 | 0 | off_peak | 806.92 |  |  | 0 | 0 | 100 | 0 | 0
4920 | 826.02 | 0 | 27.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 826.02 | 0 | 0.05921 | 8.8849 | 0 | 0 | 195.7352 | 0 | off_peak | 826.02 |  |  | 0 | 0 | 100 | 0 | 0
4921 | 739.97 | 0 | 27.7 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 19.0375 | 752.3689 | 0 | 0.05921 | 8.8702 | 0 | 0 | 195.7352 | 0 | off_peak | 739.97 | 0 | 100 | 0 | 0 | 100 | 0 | 0
4922 | 679.95 | 0 | 27.4 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 30.6357 | 692.3489 | 0 | 0.05921 | 8.6126 | 0 | 0 | 195.7352 | 0 | off_peak | 679.95 | 0 | 100 | 0 | 0 | 100 | 0 | 0
4923 | 639.34 | 0 | 27.2 | 0 | 0 | 0 | 0 | 8.7263 | 8.7263 | 0 | 0 | 0 | 38.7984 | 648.0663 | 0 | 0.05921 | 8.0457 | 0 | 0 | 195.7352 | 0 | off_peak | 639.34 | 0 | 100 | 0 | 0 | 100 | 0 | 0
4924 | 643.82 | 0 | 27.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 38.7984 | 643.82 | 0 | 0.05921 | 7.2695 | 0 | 0 | 195.7352 | 0 | off_peak | 643.82 |  |  | 0 | 0 | 100 | 0 | 0
4925 | 634.61 | 0 | 27.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 38.7984 | 634.61 | 0 | 0.05921 | 6.5052 | 0 | 0 | 195.7352 | 0 | off_peak | 634.61 |  |  | 0 | 0 | 100 | 0 | 0
4926 | 703.4 | 0 | 27.6 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 50.3966 | 715.7989 | 0 | 0.05921 | 5.95 | 0 | 0 | 195.7352 | 0 | off_peak | 703.4 | 0 | 100 | 0 | 0 | 100 | 0 | 0
4927 | 785.48 | 92.2973 | 28.3 | 18.4682 | 6.0692 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 0 | 61.9947 | 779.4108 | 0 | 0.05921 | 5.4465 | 0 | 0 | 207.3334 | 6.0692 | off_peak | 779.4108 | 100 | 0 | 0.77 | 0 | 99.23 | 33.0558 | 0
4928 | 906.47 | 288.594 | 28.7 | 57.6619 | 57.6619 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 73.5928 | 861.2071 | 0 | 0.05921 | 5.1033 | 0 | 0 | 207.3334 | 57.6619 | off_peak | 848.8081 | 0 | 100 | 6.36 | 0 | 93.64 | 294.2634 | 0
4929 | 875.46 | 493.555 | 29 | 98.5057 | 98.5057 | 0 | 0 | 0.80079 | 0.80079 | 0 | 0 | 0 | 74.3419 | 777.7551 | 0 | 0.05921 | 4.8629 | 0 | 0 | 207.3334 | 98.5057 | off_peak | 776.9543 | 0 | 100 | 11.25 | 0 | 88.75 | 479.0276 | 0
4930 | 859.82 | 620.194 | 29.3 | 123.6452 | 123.6452 | 0 | 0 | 0.05172 | 0.05172 | 0 | 0 | 0 | 74.3903 | 736.2266 | 0 | 0.05921 | 4.7718 | 0 | 0 | 207.3334 | 123.6452 | off_peak | 736.1748 | 0 | 100 | 14.38 | 0 | 85.62 | 590.012 | 0
4931 | 867.88 | 705.67 | 29.4 | 140.6347 | 140.6347 | 0 | 0 | 0.0033404 | 0.0033404 | 0 | 0 | 0 | 74.3934 | 727.2487 | 0 | 0.05921 | 4.8586 | 0 | 0 | 207.3334 | 140.6347 | off_peak | 727.2453 | 0 | 100 | 16.2 | 0 | 83.8 | 683.2847 | 0
4932 | 956.9 | 656.041 | 29.5 | 130.6962 | 130.6962 | 0 | 0 | 0.00021574 | 0.00021574 | 0 | 0 | 0 | 74.3936 | 826.2041 | 0 | 0.05921 | 5.0798 | 0 | 0 | 207.3334 | 130.6962 | off_peak | 826.2038 | 0 | 100 | 13.66 | 0 | 86.34 | 663.9168 | 0
4933 | 878.57 | 771.347 | 29.5 | 153.6674 | 153.6674 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 724.9026 | 0 | 0.088511 | 5.1986 | 0 | 0 | 207.3334 | 153.6674 | on_peak | 724.9026 |  |  | 17.49 | 0 | 82.51 | 798.8481 | 0
4934 | 943.81 | 817.174 | 29.4 | 162.8566 | 162.8566 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 780.9534 | 0 | 0.088511 | 5.5102 | 0 | 0 | 207.3334 | 162.8566 | on_peak | 780.9534 |  |  | 17.26 | 0 | 82.74 | 897.3774 | 0
4935 | 986.76 | 467.909 | 29.3 | 93.2848 | 93.2848 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 893.4752 | 0 | 0.088511 | 5.8994 | 0 | 0 | 207.3334 | 93.2848 | on_peak | 893.4752 |  |  | 9.45 | 0 | 90.55 | 550.3232 | 0
4936 | 842.57 | 55.1 | 29.2 | 10.989 | 10.989 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 831.581 | 0 | 0.088511 | 6.4506 | 0 | 0 | 207.3334 | 10.989 | on_peak | 831.581 |  |  | 1.3 | 0 | 98.7 | 70.886 | 0
4937 | 883.02 | 328.542 | 29 | 65.5717 | 65.5717 | 0 | 0 | 0 | 0 | 62.63 | 62.63 | 0 | 7.4394 | 754.8183 | 0 | 0.088511 | 7.0726 | 0 | 0 | 207.3334 | 65.5717 | on_peak | 754.8183 |  |  | 7.43 | 7.09 | 85.48 | 463.7647 | 0
4938 | 871.9 | 263.785 | 28.8 | 52.6857 | 52.6857 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 819.2143 | 0 | 0.088511 | 7.7503 | 0 | 0 | 207.3334 | 52.6857 | on_peak | 819.2143 |  |  | 6.04 | 0 | 93.96 | 408.3295 | 0
4939 | 854.58 | 56.2851 | 28.6 | 11.25 | 11.25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 843.33 | 0 | 0.088511 | 8.082 | 0 | 0 | 207.3334 | 11.25 | on_peak | 843.33 |  |  | 1.32 | 0 | 98.68 | 90.9221 | 0
4940 | 860.48 | 0 | 28.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 860.48 | 0 | 0.088511 | 8.4149 | 0 | 0 | 207.3334 | 0 | on_peak | 860.48 |  |  | 0 | 0 | 100 | 0 | 0
4941 | 832.98 | 0 | 28.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 832.98 | 0 | 0.088511 | 8.653 | 0 | 0 | 207.3334 | 0 | on_peak | 832.98 |  |  | 0 | 0 | 100 | 0 | 0
4942 | 801.33 | 0 | 28.2 | 0 | 0 | 0 | 0 | 8.7263 | 8.7263 | 0 | 0 | 0 | 15.6021 | 810.0563 | 0 | 0.05921 | 8.7787 | 0 | 0 | 207.3334 | 0 | off_peak | 801.33 | 0 | 100 | 0 | 0 | 100 | 0 | 0
4943 | 869.16 | 0 | 28.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15.6021 | 869.16 | 0 | 0.05921 | 8.8007 | 0 | 0 | 207.3334 | 0 | off_peak | 869.16 |  |  | 0 | 0 | 100 | 0 | 0
4944 | 800.93 | 0 | 28.1 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 27.2003 | 813.3289 | 0 | 0.05921 | 8.8086 | 0 | 0 | 207.3334 | 0 | off_peak | 800.93 | 0 | 100 | 0 | 0 | 100 | 0 | 0
4945 | 757.32 | 0 | 28 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27.2003 | 757.32 | 0 | 0.05921 | 8.7087 | 0 | 0 | 207.3334 | 0 | off_peak | 757.32 |  |  | 0 | 0 | 100 | 0 | 0
4946 | 698.42 | 0 | 27.9 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 38.7984 | 710.8189 | 0 | 0.05921 | 8.5108 | 0 | 0 | 207.3334 | 0 | off_peak | 698.42 | 0 | 100 | 0 | 0 | 100 | 0 | 0
4947 | 646.35 | 0 | 27.8 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 50.3966 | 658.7489 | 0 | 0.05921 | 8.1447 | 0 | 0 | 207.3334 | 0 | off_peak | 646.35 | 0 | 100 | 0 | 0 | 100 | 0 | 0
4948 | 638.59 | 0 | 27.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50.3966 | 638.59 | 0 | 0.05921 | 7.4586 | 0 | 0 | 207.3334 | 0 | off_peak | 638.59 |  |  | 0 | 0 | 100 | 0 | 0
4949 | 672.42 | 0 | 27.7 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 61.9947 | 684.8189 | 0 | 0.05921 | 6.6189 | 0 | 0 | 207.3334 | 0 | off_peak | 672.42 | 0 | 100 | 0 | 0 | 100 | 0 | 0
4950 | 719.06 | 0 | 27.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 61.9947 | 719.06 | 0 | 0.05921 | 6.087 | 0 | 0 | 207.3334 | 0 | off_peak | 719.06 |  |  | 0 | 0 | 100 | 0 | 0
4951 | 779.72 | 88.6788 | 28.2 | 17.7506 | 5.3516 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 0 | 73.5928 | 774.3684 | 0 | 0.05921 | 5.4985 | 0 | 0 | 218.9315 | 5.3516 | off_peak | 774.3684 | 100 | 0 | 0.69 | 0 | 99.31 | 29.4258 | 0
4952 | 863.31 | 282.624 | 28.6 | 56.4896 | 56.4896 | 0 | 0 | 0.80079 | 0.80079 | 0 | 0 | 0 | 74.3419 | 807.6212 | 0 | 0.05921 | 5.1499 | 0 | 0 | 218.9315 | 56.4896 | off_peak | 806.8204 | 0 | 100 | 6.54 | 0 | 93.46 | 290.9156 | 0
4953 | 863.28 | 487.959 | 28.9 | 97.4244 | 97.4244 | 0 | 0 | 0.05172 | 0.05172 | 0 | 0 | 0 | 74.3903 | 765.9073 | 0 | 0.05921 | 4.9215 | 0 | 0 | 218.9315 | 97.4244 | off_peak | 765.8556 | 0 | 100 | 11.29 | 0 | 88.71 | 479.4788 | 0
4954 | 905.46 | 586.292 | 29.2 | 116.929 | 116.929 | 0 | 0 | 0.0033404 | 0.0033404 | 0 | 0 | 0 | 74.3934 | 788.5343 | 0 | 0.05921 | 4.8199 | 0 | 0 | 218.9315 | 116.929 | off_peak | 788.531 | 0 | 100 | 12.91 | 0 | 87.09 | 563.5903 | 0
4955 | 925.61 | 690.904 | 29.5 | 137.6415 | 137.6415 | 0 | 0 | 0.00021574 | 0.00021574 | 0 | 0 | 0 | 74.3936 | 787.9687 | 0 | 0.05921 | 4.3894 | 0 | 0 | 218.9315 | 137.6415 | off_peak | 787.9685 | 0 | 100 | 14.87 | 0 | 85.13 | 604.166 | 0
4956 | 964.05 | 257.355 | 29.6 | 51.2514 | 51.2514 | 0 | 0 | 1.3934e-05 | 1.3934e-05 | 0 | 0 | 0 | 74.3936 | 912.7986 | 0 | 0.05921 | 5.1601 | 0 | 0 | 218.9315 | 51.2514 | off_peak | 912.7986 | 0 | 100 | 5.32 | 0 | 94.68 | 264.4607 | 0
4957 | 927.53 | 546.458 | 29.7 | 108.7854 | 108.7854 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 818.7446 | 0 | 0.088511 | 5.4006 | 0 | 0 | 218.9315 | 108.7854 | on_peak | 818.7446 |  |  | 11.73 | 0 | 88.27 | 587.5013 | 0
4958 | 928.9 | 647.795 | 29.7 | 128.9589 | 128.9589 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 799.9411 | 0 | 0.088511 | 5.4858 | 0 | 0 | 218.9315 | 128.9589 | on_peak | 799.9411 |  |  | 13.88 | 0 | 86.12 | 707.445 | 0
4959 | 931.82 | 750.511 | 29.7 | 149.407 | 149.407 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 782.413 | 0 | 0.088511 | 5.6158 | 0 | 0 | 218.9315 | 149.407 | on_peak | 782.413 |  |  | 16.03 | 0 | 83.97 | 839.0343 | 0
4960 | 851.72 | 658.116 | 29.6 | 131.0616 | 131.0616 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 720.6584 | 0 | 0.088511 | 5.9699 | 0 | 0 | 218.9315 | 131.0616 | on_peak | 720.6584 |  |  | 15.39 | 0 | 84.61 | 782.4268 | 0
4961 | 853.72 | 473.216 | 29.3 | 94.3428 | 94.3428 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 759.3772 | 0 | 0.088511 | 6.3057 | 0 | 0 | 218.9315 | 94.3428 | on_peak | 759.3772 |  |  | 11.05 | 0 | 88.95 | 594.8966 | 0
4962 | 919 | 270.471 | 29 | 53.9817 | 53.9817 | 0 | 0 | 0 | 0 | 62.63 | 62.63 | 0 | 7.4394 | 802.3883 | 0 | 0.088511 | 6.7117 | 0 | 0 | 218.9315 | 53.9817 | on_peak | 802.3883 |  |  | 5.87 | 6.82 | 87.31 | 362.3084 | 0
4963 | 823.32 | 78.3703 | 28.8 | 15.6529 | 15.6529 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 807.6671 | 0 | 0.088511 | 7.2716 | 0 | 0 | 218.9315 | 15.6529 | on_peak | 807.6671 |  |  | 1.9 | 0 | 98.1 | 113.8221 | 0
4964 | 874.04 | 0 | 28.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 874.04 | 0 | 0.088511 | 7.4453 | 0 | 0 | 218.9315 | 0 | on_peak | 874.04 |  |  | 0 | 0 | 100 | 0 | 0
4965 | 832.99 | 0 | 28.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 832.99 | 0 | 0.088511 | 7.7357 | 0 | 0 | 218.9315 | 0 | on_peak | 832.99 |  |  | 0 | 0 | 100 | 0 | 0
4966 | 843.07 | 0 | 28.2 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 19.0375 | 855.4689 | 0 | 0.05921 | 7.8724 | 0 | 0 | 218.9315 | 0 | off_peak | 843.07 | 0 | 100 | 0 | 0 | 100 | 0 | 0
4967 | 844.29 | 0 | 28.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19.0375 | 844.29 | 0 | 0.05921 | 8.0315 | 0 | 0 | 218.9315 | 0 | off_peak | 844.29 |  |  | 0 | 0 | 100 | 0 | 0
4968 | 805.26 | 0 | 28 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19.0375 | 805.26 | 0 | 0.05921 | 8.105 | 0 | 0 | 218.9315 | 0 | off_peak | 805.26 |  |  | 0 | 0 | 100 | 0 | 0
4969 | 728.39 | 0 | 27.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19.0375 | 728.39 | 0 | 0.05921 | 7.7985 | 0 | 0 | 218.9315 | 0 | off_peak | 728.39 |  |  | 0 | 0 | 100 | 0 | 0
4970 | 752.4 | 0 | 27.8 | 0 | 0 | 0 | 0 | 8.7263 | 8.7263 | 0 | 0 | 0 | 27.2003 | 761.1263 | 0 | 0.05921 | 7.743 | 0 | 0 | 218.9315 | 0 | off_peak | 752.4 | 0 | 100 | 0 | 0 | 100 | 0 | 0
4971 | 703.17 | 0 | 27.7 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 38.7984 | 715.5689 | 0 | 0.05921 | 7.3849 | 0 | 0 | 218.9315 | 0 | off_peak | 703.17 | 0 | 100 | 0 | 0 | 100 | 0 | 0
4972 | 691.71 | 0 | 27.7 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 50.3966 | 704.1089 | 0 | 0.05921 | 6.8326 | 0 | 0 | 218.9315 | 0 | off_peak | 691.71 | 0 | 100 | 0 | 0 | 100 | 0 | 0
4973 | 702.35 | 0 | 27.6 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 61.9947 | 714.7489 | 0 | 0.05921 | 6.0659 | 0 | 0 | 218.9315 | 0 | off_peak | 702.35 | 0 | 100 | 0 | 0 | 100 | 0 | 0
4974 | 751.2 | 0 | 27.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 61.9947 | 751.2 | 0 | 0.05921 | 5.4996 | 0 | 0 | 218.9315 | 0 | off_peak | 751.2 |  |  | 0 | 0 | 100 | 0 | 0
4975 | 797.43 | 92.0092 | 28.4 | 18.4038 | 18.4038 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 73.5928 | 791.4251 | 0 | 0.05921 | 5.0368 | 0 | 0 | 218.9315 | 18.4038 | off_peak | 779.0262 | 0 | 100 | 2.31 | 0 | 97.69 | 92.6956 | 0
4976 | 857.44 | 290.403 | 28.8 | 58.0021 | 58.0021 | 0 | 0 | 0.80079 | 0.80079 | 0 | 0 | 0 | 74.3419 | 800.2387 | 0 | 0.05921 | 4.7107 | 0 | 0 | 218.9315 | 58.0021 | off_peak | 799.4379 | 0 | 100 | 6.76 | 0 | 93.24 | 273.2317 | 0
4977 | 871.96 | 498.655 | 29 | 99.5236 | 99.5236 | 0 | 0 | 0.05172 | 0.05172 | 0 | 0 | 0 | 74.3903 | 772.4882 | 0 | 0.05921 | 4.464 | 0 | 0 | 218.9315 | 99.5236 | off_peak | 772.4364 | 0 | 100 | 11.41 | 0 | 88.59 | 444.2685 | 0
4978 | 918.41 | 541.25 | 29.3 | 107.9065 | 107.9031 | 0 | 0.0033404 | 0.0033404 | 0 | 0 | 0 | 0 | 74.3934 | 810.5069 | 0 | 0.05921 | 4.3786 | 0 | 0 | 218.9346 | 107.9031 | off_peak | 810.5069 | 100 | 0 | 11.75 | 0 | 88.25 | 472.4634 | 0
4979 | 885.21 | 824.761 | 29.6 | 164.2483 | 164.2483 | 0 | 0 | 0.00021574 | 0.00021574 | 0 | 0 | 0 | 74.3936 | 720.9619 | 0 | 0.05921 | 4.5033 | 0 | 0 | 218.9346 | 164.2483 | off_peak | 720.9617 | 0 | 100 | 18.55 | 0 | 81.45 | 739.6589 | 0
4980 | 958.3 | 914.701 | 29.8 | 182.0262 | 182.0262 | 0 | 1.3934e-05 | 1.3934e-05 | 0 | 0 | 0 | 0 | 74.3936 | 776.2738 | 0 | 0.05921 | 4.7552 | 0 | 0 | 218.9346 | 182.0262 | off_peak | 776.2738 | 100 | 0 | 18.99 | 0 | 81.01 | 865.5732 | 0
4981 | 855.84 | 418.889 | 29.9 | 83.3287 | 83.3287 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 772.5113 | 0 | 0.088511 | 4.8639 | 0 | 0 | 218.9346 | 83.3287 | on_peak | 772.5113 |  |  | 9.74 | 0 | 90.26 | 405.3023 | 0
4982 | 887.7 | 910.132 | 29.9 | 181.0506 | 181.0506 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 706.6494 | 0 | 0.088511 | 5.0166 | 0 | 0 | 218.9346 | 181.0506 | on_peak | 706.6494 |  |  | 20.4 | 0 | 79.6 | 908.2615 | 0
4983 | 898.94 | 788.719 | 29.8 | 156.9557 | 156.9557 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 741.9843 | 0 | 0.088511 | 5.3996 | 0 | 0 | 218.9346 | 156.9557 | on_peak | 741.9843 |  |  | 17.46 | 0 | 82.54 | 847.5016 | 0
4984 | 860.49 | 586.748 | 29.7 | 116.8061 | 116.8061 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 743.6839 | 0 | 0.088511 | 5.7991 | 0 | 0 | 218.9346 | 116.8061 | on_peak | 743.6839 |  |  | 13.57 | 0 | 86.43 | 677.3714 | 0
4985 | 832.36 | 458.548 | 29.4 | 91.3851 | 91.3851 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 740.9749 | 0 | 0.088511 | 6.278 | 0 | 0 | 218.9346 | 91.3851 | on_peak | 740.9749 |  |  | 10.98 | 0 | 89.02 | 573.7128 | 0
4986 | 878.21 | 267.802 | 29 | 53.449 | 53.449 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 824.761 | 0 | 0.088511 | 6.7823 | 0 | 0 | 218.9346 | 53.449 | on_peak | 824.761 |  |  | 6.09 | 0 | 93.91 | 362.5071 | 0
4987 | 838.97 | 75.784 | 28.7 | 15.1418 | 15.1418 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 823.8282 | 0 | 0.088511 | 7.1186 | 0 | 0 | 218.9346 | 15.1418 | on_peak | 823.8282 |  |  | 1.8 | 0 | 98.2 | 107.7892 | 0
4988 | 841.23 | 0 | 28.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 841.23 | 0 | 0.088511 | 7.3015 | 0 | 0 | 218.9346 | 0 | on_peak | 841.23 |  |  | 0 | 0 | 100 | 0 | 0
4989 | 840.31 | 0 | 28 | 0 | 0 | 0 | 0 | 0 | 0 | 62.63 | 62.63 | 0 | 7.4394 | 777.68 | 0 | 0.088511 | 7.513 | 0 | 0 | 218.9346 | 0 | on_peak | 777.68 |  |  | 0 | 7.45 | 92.55 | 0 | 0
4990 | 796 | 0 | 27.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 796 | 0 | 0.05921 | 7.7721 | 0 | 0 | 218.9346 | 0 | off_peak | 796 |  |  | 0 | 0 | 100 | 0 | 0
4991 | 843.25 | 0 | 27.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 843.25 | 0 | 0.05921 | 7.7034 | 0 | 0 | 218.9346 | 0 | off_peak | 843.25 |  |  | 0 | 0 | 100 | 0 | 0
4992 | 843.69 | 0 | 27.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 843.69 | 0 | 0.05921 | 7.4874 | 0 | 0 | 218.9346 | 0 | off_peak | 843.69 |  |  | 0 | 0 | 100 | 0 | 0
4993 | 728.99 | 0 | 27.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 728.99 | 0 | 0.05921 | 7.1745 | 0 | 0 | 218.9346 | 0 | off_peak | 728.99 |  |  | 0 | 0 | 100 | 0 | 0
4994 | 700.22 | 0 | 27.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 700.22 | 0 | 0.05921 | 7.0924 | 0 | 0 | 218.9346 | 0 | off_peak | 700.22 |  |  | 0 | 0 | 100 | 0 | 0
4995 | 627.84 | 0 | 27.6 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 19.0375 | 640.2389 | 0 | 0.05921 | 6.8058 | 0 | 0 | 218.9346 | 0 | off_peak | 627.84 | 0 | 100 | 0 | 0 | 100 | 0 | 0
4996 | 644.3 | 0 | 27.7 | 0 | 0 | 0 | 0 | 8.7263 | 8.7263 | 0 | 0 | 0 | 27.2003 | 653.0263 | 0 | 0.05921 | 6.3455 | 0 | 0 | 218.9346 | 0 | off_peak | 644.3 | 0 | 100 | 0 | 0 | 100 | 0 | 0
4997 | 685.96 | 0 | 27.6 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 38.7984 | 698.3589 | 0 | 0.05921 | 5.8201 | 0 | 0 | 218.9346 | 0 | off_peak | 685.96 | 0 | 100 | 0 | 0 | 100 | 0 | 0
4998 | 710.25 | 0 | 27.7 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 50.3966 | 722.6489 | 0 | 0.05921 | 5.2911 | 0 | 0 | 218.9346 | 0 | off_peak | 710.25 | 0 | 100 | 0 | 0 | 100 | 0 | 0
4999 | 771.24 | 90.2758 | 28 | 18.0834 | 18.0834 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 61.9947 | 765.5555 | 0 | 0.05921 | 4.9044 | 0 | 0 | 218.9346 | 18.0834 | off_peak | 753.1566 | 0 | 100 | 2.34 | 0 | 97.66 | 88.6881 | 0
5000 | 859.14 | 288.85 | 28.3 | 57.7972 | 57.7972 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 73.5928 | 813.7417 | 0 | 0.05921 | 4.6473 | 0 | 0 | 218.9346 | 57.7972 | off_peak | 801.3428 | 0 | 100 | 6.73 | 0 | 93.27 | 268.6016 | 0
5001 | 864.63 | 496.453 | 28.6 | 99.2288 | 99.2288 | 0 | 0 | 0.80079 | 0.80079 | 0 | 0 | 0 | 74.3419 | 766.202 | 0 | 0.05921 | 4.4718 | 0 | 0 | 218.9346 | 99.2288 | off_peak | 765.4012 | 0 | 100 | 11.48 | 0 | 88.52 | 443.7292 | 0
5002 | 838.14 | 617.285 | 28.9 | 123.2452 | 123.2452 | 0 | 0 | 0.05172 | 0.05172 | 0 | 0 | 0 | 74.3903 | 714.9465 | 0 | 0.05921 | 4.4485 | 0 | 0 | 218.9346 | 123.2452 | off_peak | 714.8948 | 0 | 100 | 14.7 | 0 | 85.3 | 548.2533 | 0
5003 | 829.32 | 774.076 | 29.3 | 154.3239 | 154.3239 | 0 | 0 | 0.0033404 | 0.0033404 | 0 | 0 | 0 | 74.3934 | 674.9994 | 0 | 0.05921 | 4.5844 | 0 | 0 | 218.9346 | 154.3239 | off_peak | 674.9961 | 0 | 100 | 18.61 | 0 | 81.39 | 707.4878 | 0
5004 | 879.06 | 911.568 | 29.6 | 181.5357 | 181.5357 | 0 | 0 | 0.00021574 | 0.00021574 | 0 | 0 | 0 | 74.3936 | 697.5245 | 0 | 0.05921 | 4.8198 | 0 | 0 | 218.9346 | 181.5357 | off_peak | 697.5243 | 0 | 100 | 20.65 | 0 | 79.35 | 874.9727 | 0
5005 | 834.92 | 585.769 | 29.8 | 116.5685 | 116.5685 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 718.3515 | 0 | 0.088511 | 5.1215 | 0 | 0 | 218.9346 | 116.5685 | on_peak | 718.3515 |  |  | 13.96 | 0 | 86.04 | 597.0098 | 0
5006 | 889.96 | 430.849 | 30 | 85.6765 | 85.6765 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 804.2835 | 0 | 0.088511 | 5.3917 | 0 | 0 | 218.9346 | 85.6765 | on_peak | 804.2835 |  |  | 9.63 | 0 | 90.37 | 461.9447 | 0
5007 | 857.28 | 802.167 | 30 | 159.5149 | 159.5149 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 697.7651 | 0 | 0.088511 | 5.7174 | 0 | 0 | 218.9346 | 159.5149 | on_peak | 697.7651 |  |  | 18.61 | 0 | 81.39 | 912.0181 | 0
5008 | 815.03 | 654.505 | 29.8 | 130.247 | 130.247 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 684.783 | 0 | 0.088511 | 6.0707 | 0 | 0 | 218.9346 | 130.247 | on_peak | 684.783 |  |  | 15.98 | 0 | 84.02 | 790.6919 | 0
5009 | 803.74 | 448.247 | 29.6 | 89.2669 | 89.2669 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 714.4731 | 0 | 0.088511 | 6.5245 | 0 | 0 | 218.9346 | 89.2669 | on_peak | 714.4731 |  |  | 11.11 | 0 | 88.89 | 582.4175 | 0
5010 | 890.32 | 116.571 | 29.1 | 23.2572 | 23.2572 | 0 | 0 | 0 | 0 | 62.63 | 62.63 | 0 | 7.4394 | 804.4328 | 0 | 0.088511 | 6.8764 | 0 | 0 | 218.9346 | 23.2572 | on_peak | 804.4328 |  |  | 2.61 | 7.03 | 90.35 | 159.9262 | 0
5011 | 812.14 | 73.642 | 28.8 | 14.7085 | 14.7085 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 797.4315 | 0 | 0.088511 | 7.0324 | 0 | 0 | 218.9346 | 14.7085 | on_peak | 797.4315 |  |  | 1.81 | 0 | 98.19 | 103.4354 | 0
5012 | 887.33 | 0 | 28.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 887.33 | 0 | 0.088511 | 7.1853 | 0 | 0 | 218.9346 | 0 | on_peak | 887.33 |  |  | 0 | 0 | 100 | 0 | 0
5013 | 837.61 | 0 | 27.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 837.61 | 0 | 0.088511 | 7.3471 | 0 | 0 | 218.9346 | 0 | on_peak | 837.61 |  |  | 0 | 0 | 100 | 0 | 0
5014 | 777.48 | 0 | 27.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 777.48 | 0 | 0.05921 | 7.5708 | 0 | 0 | 218.9346 | 0 | off_peak | 777.48 |  |  | 0 | 0 | 100 | 0 | 0
5015 | 857.51 | 0 | 27.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 857.51 | 0 | 0.05921 | 7.6357 | 0 | 0 | 218.9346 | 0 | off_peak | 857.51 |  |  | 0 | 0 | 100 | 0 | 0
5016 | 803.58 | 0 | 27.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 803.58 | 0 | 0.05921 | 7.5217 | 0 | 0 | 218.9346 | 0 | off_peak | 803.58 |  |  | 0 | 0 | 100 | 0 | 0
5017 | 714.78 | 0 | 27.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 714.78 | 0 | 0.05921 | 7.3444 | 0 | 0 | 218.9346 | 0 | off_peak | 714.78 |  |  | 0 | 0 | 100 | 0 | 0
5018 | 662.83 | 0 | 27.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 662.83 | 0 | 0.05921 | 7.186 | 0 | 0 | 218.9346 | 0 | off_peak | 662.83 |  |  | 0 | 0 | 100 | 0 | 0
5019 | 658.1 | 0 | 27.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 658.1 | 0 | 0.05921 | 6.9699 | 0 | 0 | 218.9346 | 0 | off_peak | 658.1 |  |  | 0 | 0 | 100 | 0 | 0
5020 | 631.58 | 0 | 27.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 631.58 | 0 | 0.05921 | 6.5891 | 0 | 0 | 218.9346 | 0 | off_peak | 631.58 |  |  | 0 | 0 | 100 | 0 | 0
5021 | 631.6 | 0 | 27.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 631.6 | 0 | 0.05921 | 6.0229 | 0 | 0 | 218.9346 | 0 | off_peak | 631.6 |  |  | 0 | 0 | 100 | 0 | 0
5022 | 722.59 | 0 | 27.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 722.59 | 0 | 0.05921 | 5.5538 | 0 | 0 | 218.9346 | 0 | off_peak | 722.59 |  |  | 0 | 0 | 100 | 0 | 0
5023 | 709.62 | 88.2644 | 27.8 | 17.6934 | 17.6934 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 691.9266 | 0 | 0.05921 | 5.1379 | 0 | 0 | 218.9346 | 17.6934 | off_peak | 691.9266 |  |  | 2.49 | 0 | 97.51 | 90.9072 | 0
5024 | 751.08 | 171.118 | 28.2 | 34.2522 | 21.8533 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 0 | 19.0375 | 729.2267 | 0 | 0.05921 | 4.8501 | 0 | 0 | 230.5328 | 21.8533 | off_peak | 729.2267 | 100 | 0 | 2.91 | 0 | 97.09 | 105.9899 | 0
5025 | 776.15 | 450.705 | 28.4 | 90.1506 | 90.1506 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19.0375 | 685.9994 | 0 | 0.05921 | 4.6103 | 0 | 0 | 230.5328 | 90.1506 | off_peak | 685.9994 |  |  | 11.62 | 0 | 88.38 | 415.623 | 0
5026 | 773.23 | 673.77 | 28.7 | 134.6211 | 134.6211 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19.0375 | 638.6089 | 0 | 0.05921 | 4.488 | 0 | 0 | 230.5328 | 134.6211 | off_peak | 638.6089 |  |  | 17.41 | 0 | 82.59 | 604.1793 | 0
5027 | 746.5 | 729.246 | 29.1 | 145.4927 | 145.4927 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19.0375 | 601.0073 | 0 | 0.05921 | 4.4674 | 0 | 0 | 230.5328 | 145.4927 | off_peak | 601.0073 |  |  | 19.49 | 0 | 80.51 | 649.9729 | 0
5028 | 785.15 | 324.635 | 29.5 | 64.6736 | 64.6736 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19.0375 | 720.4764 | 0 | 0.05921 | 4.5225 | 0 | 0 | 230.5328 | 64.6736 | off_peak | 720.4764 |  |  | 8.24 | 0 | 91.76 | 292.4874 | 0
5029 | 752.28 | 710.667 | 29.8 | 141.4233 | 141.4233 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19.0375 | 610.8567 | 0 | 0.05921 | 4.6488 | 0 | 0 | 230.5328 | 141.4233 | off_peak | 610.8567 |  |  | 18.8 | 0 | 81.2 | 657.4448 | 0
5030 | 767.23 | 454.929 | 30 | 90.4649 | 90.4649 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19.0375 | 676.7651 | 0 | 0.05921 | 4.9608 | 0 | 0 | 230.5328 | 90.4649 | off_peak | 676.7651 |  |  | 11.79 | 0 | 88.21 | 448.78 | 0
5031 | 754.16 | 678.33 | 30 | 134.8893 | 134.8893 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 30.6357 | 631.6696 | 0 | 0.05921 | 5.4045 | 0 | 0 | 230.5328 | 134.8893 | off_peak | 619.2707 | 0 | 100 | 17.89 | 0 | 82.11 | 729.0153 | 0
5032 | 721.58 | 434.114 | 29.8 | 86.389 | 86.389 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30.6357 | 635.191 | 0 | 0.05921 | 6.0171 | 0 | 0 | 230.5328 | 86.389 | off_peak | 635.191 |  |  | 11.97 | 0 | 88.03 | 519.8109 | 0
5033 | 711.03 | 473.539 | 29.5 | 94.3382 | 94.3382 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30.6357 | 616.6918 | 0 | 0.05921 | 6.673 | 0 | 0 | 230.5328 | 94.3382 | off_peak | 616.6918 |  |  | 13.27 | 0 | 86.73 | 629.515 | 0
5034 | 666.82 | 266.833 | 29 | 53.2556 | 53.2556 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30.6357 | 613.5644 | 0 | 0.05921 | 7.3005 | 0 | 0 | 230.5328 | 53.2556 | off_peak | 613.5644 |  |  | 7.99 | 0 | 92.01 | 388.7937 | 0
5035 | 644.85 | 74.4832 | 28.7 | 14.8819 | 14.8819 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30.6357 | 629.9681 | 0 | 0.05921 | 7.7852 | 0 | 0 | 230.5328 | 14.8819 | off_peak | 629.9681 |  |  | 2.31 | 0 | 97.69 | 115.8582 | 0
5036 | 634.86 | 0 | 28.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30.6357 | 634.86 | 0 | 0.05921 | 8.0046 | 0 | 0 | 230.5328 | 0 | off_peak | 634.86 |  |  | 0 | 0 | 100 | 0 | 0
5037 | 608.94 | 0 | 27.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30.6357 | 608.94 | 0 | 0.05921 | 8.38 | 0 | 0 | 230.5328 | 0 | off_peak | 608.94 |  |  | 0 | 0 | 100 | 0 | 0
5038 | 601.96 | 0 | 27.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30.6357 | 601.96 | 0 | 0.05921 | 8.5484 | 0 | 0 | 230.5328 | 0 | off_peak | 601.96 |  |  | 0 | 0 | 100 | 0 | 0
5039 | 590.65 | 0 | 27.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30.6357 | 590.65 | 0 | 0.05921 | 8.3927 | 0 | 0 | 230.5328 | 0 | off_peak | 590.65 |  |  | 0 | 0 | 100 | 0 | 0
5040 | 596.25 | 0 | 27.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30.6357 | 596.25 | 0 | 0.05921 | 8.3438 | 0 | 0 | 230.5328 | 0 | off_peak | 596.25 |  |  | 0 | 0 | 100 | 0 | 0
5041 | 601.73 | 0 | 27.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30.6357 | 601.73 | 0 | 0.05921 | 8.1426 | 0 | 0 | 230.5328 | 0 | off_peak | 601.73 |  |  | 0 | 0 | 100 | 0 | 0
5042 | 625.37 | 0 | 27.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30.6357 | 625.37 | 0 | 0.05921 | 7.8782 | 0 | 0 | 230.5328 | 0 | off_peak | 625.37 |  |  | 0 | 0 | 100 | 0 | 0
5043 | 602.19 | 0 | 27.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30.6357 | 602.19 | 0 | 0.05921 | 7.4485 | 0 | 0 | 230.5328 | 0 | off_peak | 602.19 |  |  | 0 | 0 | 100 | 0 | 0
5044 | 602.25 | 0 | 27.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30.6357 | 602.25 | 0 | 0.05921 | 7.2231 | 0 | 0 | 230.5328 | 0 | off_peak | 602.25 |  |  | 0 | 0 | 100 | 0 | 0
5045 | 622.14 | 0 | 27.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30.6357 | 622.14 | 0 | 0.05921 | 6.7215 | 0 | 0 | 230.5328 | 0 | off_peak | 622.14 |  |  | 0 | 0 | 100 | 0 | 0
5046 | 679.67 | 0 | 27.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30.6357 | 679.67 | 0 | 0.05921 | 6.218 | 0 | 0 | 230.5328 | 0 | off_peak | 679.67 |  |  | 0 | 0 | 100 | 0 | 0
5047 | 722.14 | 57.2812 | 28.1 | 11.47 | 11.47 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 42.2338 | 723.0689 | 0 | 0.05921 | 5.7261 | 0 | 0 | 230.5328 | 11.47 | off_peak | 710.67 | 0 | 100 | 1.59 | 0 | 98.41 | 65.6787 | 0
5048 | 702.16 | 284.835 | 28.6 | 56.9316 | 56.9316 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 42.2338 | 645.2284 | 0 | 0.05921 | 5.3401 | 0 | 0 | 230.5328 | 56.9316 | off_peak | 645.2284 |  |  | 8.11 | 0 | 91.89 | 304.018 | 0
5049 | 763.49 | 467.778 | 28.9 | 93.3951 | 93.3951 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 42.2338 | 670.0949 | 0 | 0.05921 | 5.0334 | 0 | 0 | 230.5328 | 93.3951 | off_peak | 670.0949 |  |  | 12.23 | 0 | 87.77 | 470.0916 | 0
5050 | 735.98 | 676.013 | 29.1 | 134.8721 | 134.8721 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 42.2338 | 601.1079 | 0 | 0.05921 | 4.8471 | 0 | 0 | 230.5328 | 134.8721 | off_peak | 601.1079 |  |  | 18.33 | 0 | 81.67 | 653.7369 | 0
5051 | 759.07 | 820.336 | 29.4 | 163.4867 | 163.4867 | 0 | 0 | 3.9741 | 3.9741 | 0 | 0 | 0 | 45.9512 | 599.5574 | 0 | 0.05921 | 4.7499 | 0 | 0 | 230.5328 | 163.4867 | off_peak | 595.5833 | 0 | 100 | 21.54 | 0 | 78.46 | 776.5497 | 0
5052 | 734.47 | 378.41 | 29.6 | 75.3591 | 75.3591 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 45.9512 | 659.1109 | 0 | 0.05921 | 4.6843 | 0 | 0 | 230.5328 | 75.3591 | off_peak | 659.1109 |  |  | 10.26 | 0 | 89.74 | 353.003 | 0
5053 | 735.58 | 463.198 | 29.8 | 92.1768 | 92.1768 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 45.9512 | 643.4032 | 0 | 0.05921 | 4.7068 | 0 | 0 | 230.5328 | 92.1768 | off_peak | 643.4032 |  |  | 12.53 | 0 | 87.47 | 433.8622 | 0
5054 | 785.75 | 680.42 | 29.9 | 135.3545 | 122.9556 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 0 | 57.5494 | 662.7944 | 0 | 0.05921 | 4.9775 | 0 | 0 | 242.1309 | 122.9556 | off_peak | 662.7944 | 100 | 0 | 15.65 | 0 | 84.35 | 612.0101 | 0
5055 | 753.88 | 803.221 | 29.9 | 159.7831 | 159.7831 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 57.5494 | 594.0969 | 0 | 0.05921 | 5.3248 | 0 | 0 | 242.1309 | 159.7831 | off_peak | 594.0969 |  |  | 21.19 | 0 | 78.81 | 850.8188 | 0
5056 | 721.76 | 525.325 | 29.7 | 104.5784 | 104.5784 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 57.5494 | 617.1816 | 0 | 0.05921 | 5.9243 | 0 | 0 | 242.1309 | 104.5784 | off_peak | 617.1816 |  |  | 14.49 | 0 | 85.51 | 619.5552 | 0
5057 | 749.26 | 388.577 | 29.4 | 77.4404 | 77.4404 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 57.5494 | 671.8196 | 0 | 0.05921 | 6.5952 | 0 | 0 | 242.1309 | 77.4404 | off_peak | 671.8196 |  |  | 10.34 | 0 | 89.66 | 510.7385 | 0
5058 | 709.62 | 151.432 | 29 | 30.2234 | 30.2234 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 57.5494 | 679.3966 | 0 | 0.05921 | 7.181 | 0 | 0 | 242.1309 | 30.2234 | off_peak | 679.3966 |  |  | 4.26 | 0 | 95.74 | 217.0354 | 0
5059 | 680.68 | 31.4733 | 28.7 | 6.2885 | 6.2885 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 57.5494 | 674.3915 | 0 | 0.05921 | 7.7449 | 0 | 0 | 242.1309 | 6.2885 | off_peak | 674.3915 |  |  | 0.92 | 0 | 99.08 | 48.7037 | 0
5060 | 663.97 | 0 | 28.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 57.5494 | 663.97 | 0 | 0.05921 | 8.0904 | 0 | 0 | 242.1309 | 0 | off_peak | 663.97 |  |  | 0 | 0 | 100 | 0 | 0
5061 | 668.02 | 0 | 27.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 57.5494 | 668.02 | 0 | 0.05921 | 8.3571 | 0 | 0 | 242.1309 | 0 | off_peak | 668.02 |  |  | 0 | 0 | 100 | 0 | 0
5062 | 640.24 | 0 | 27.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 57.5494 | 640.24 | 0 | 0.05921 | 8.7513 | 0 | 0 | 242.1309 | 0 | off_peak | 640.24 |  |  | 0 | 0 | 100 | 0 | 0
5063 | 589.77 | 0 | 27.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 57.5494 | 589.77 | 0 | 0.05921 | 8.9811 | 0 | 0 | 242.1309 | 0 | off_peak | 589.77 |  |  | 0 | 0 | 100 | 0 | 0
5064 | 604.79 | 0 | 27.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 57.5494 | 604.79 | 0 | 0.05921 | 8.8092 | 0 | 0 | 242.1309 | 0 | off_peak | 604.79 |  |  | 0 | 0 | 100 | 0 | 0
5065 | 620.94 | 0 | 27.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 57.5494 | 620.94 | 0 | 0.05921 | 8.4827 | 0 | 0 | 242.1309 | 0 | off_peak | 620.94 |  |  | 0 | 0 | 100 | 0 | 0
5066 | 606.06 | 0 | 27.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 57.5494 | 606.06 | 0 | 0.05921 | 8.3123 | 0 | 0 | 242.1309 | 0 | off_peak | 606.06 |  |  | 0 | 0 | 100 | 0 | 0
5067 | 582.4 | 0 | 27.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 57.5494 | 582.4 | 0 | 0.05921 | 7.9912 | 0 | 0 | 242.1309 | 0 | off_peak | 582.4 |  |  | 0 | 0 | 100 | 0 | 0
5068 | 591.98 | 0 | 27.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 57.5494 | 591.98 | 0 | 0.05921 | 7.3997 | 0 | 0 | 242.1309 | 0 | off_peak | 591.98 |  |  | 0 | 0 | 100 | 0 | 0
5069 | 601.91 | 0 | 27.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 57.5494 | 601.91 | 0 | 0.05921 | 6.7986 | 0 | 0 | 242.1309 | 0 | off_peak | 601.91 |  |  | 0 | 0 | 100 | 0 | 0
5070 | 723.22 | 0 | 28 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 57.5494 | 723.22 | 0 | 0.05921 | 6.0784 | 0 | 0 | 242.1309 | 0 | off_peak | 723.22 |  |  | 0 | 0 | 100 | 0 | 0
5071 | 790.44 | 23.75 | 28.3 | 4.7522 | 0 | 0 | 4.7522 | 4.7522 | 0 | 0 | 0 | 0 | 61.9947 | 790.44 | 0 | 0.05921 | 5.5508 | 0 | 0 | 246.5762 | 0 | off_peak | 790.44 | 100 | 0 | 0 | 0 | 100 | 0 | 0
5072 | 862.14 | 69.698 | 28.8 | 13.9208 | 13.9208 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 73.5928 | 860.6182 | 0 | 0.05921 | 5.1367 | 0 | 0 | 246.5762 | 13.9208 | off_peak | 848.2192 | 0 | 100 | 1.61 | 0 | 98.39 | 71.5061 | 0
5073 | 846.65 | 87.9428 | 29.1 | 17.5456 | 16.7448 | 0 | 0.80079 | 0.80079 | 0 | 0 | 0 | 0 | 74.3419 | 829.9052 | 0 | 0.05921 | 4.8926 | 0 | 0 | 247.3253 | 16.7448 | off_peak | 829.9052 | 100 | 0 | 1.98 | 0 | 98.02 | 81.9252 | 0
5074 | 866.19 | 162.919 | 29.4 | 32.4685 | 32.4685 | 0 | 0 | 0.05172 | 0.05172 | 0 | 0 | 0 | 74.3903 | 833.7732 | 0 | 0.05921 | 4.7925 | 0 | 0 | 247.3253 | 32.4685 | off_peak | 833.7215 | 0 | 100 | 3.75 | 0 | 96.25 | 155.6045 | 0
5075 | 840.68 | 277.67 | 29.7 | 55.2768 | 55.2768 | 0 | 0 | 0.0033404 | 0.0033404 | 0 | 0 | 0 | 74.3934 | 785.4065 | 0 | 0.05921 | 4.886 | 0 | 0 | 247.3253 | 55.2768 | off_peak | 785.4032 | 0 | 100 | 6.58 | 0 | 93.42 | 270.0808 | 0
5076 | 915.14 | 194.716 | 29.9 | 38.7344 | 38.7344 | 0 | 0 | 0.00021574 | 0.00021574 | 0 | 0 | 0 | 74.3936 | 876.4058 | 0 | 0.05921 | 5.0831 | 0 | 0 | 247.3253 | 38.7344 | off_peak | 876.4056 | 0 | 100 | 4.23 | 0 | 95.77 | 196.8894 | 0
5077 | 882.81 | 216.591 | 30 | 43.0702 | 43.0702 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 839.7398 | 0 | 0.088511 | 5.2437 | 0 | 0 | 247.3253 | 43.0702 | on_peak | 839.7398 |  |  | 4.88 | 0 | 95.12 | 225.8485 | 0
5078 | 918.78 | 394.233 | 30.1 | 78.3665 | 78.3665 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 840.4135 | 0 | 0.088511 | 5.4852 | 0 | 0 | 247.3253 | 78.3665 | on_peak | 840.4135 |  |  | 8.53 | 0 | 91.47 | 429.8593 | 0
5079 | 943.28 | 257.303 | 30 | 51.166 | 51.166 | 0 | 0 | 0 | 0 | 62.63 | 62.63 | 0 | 7.4394 | 829.484 | 0 | 0.088511 | 5.8156 | 0 | 0 | 247.3253 | 51.166 | on_peak | 829.484 |  |  | 5.42 | 6.64 | 87.94 | 297.5613 | 0
5080 | 844.37 | 252.961 | 29.8 | 50.3394 | 50.3394 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 794.0306 | 0 | 0.088511 | 6.3716 | 0 | 0 | 247.3253 | 50.3394 | on_peak | 794.0306 |  |  | 5.96 | 0 | 94.04 | 320.7428 | 0
5081 | 881.83 | 99.3276 | 29.6 | 19.7808 | 19.7808 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 862.0492 | 0 | 0.088511 | 6.8464 | 0 | 0 | 247.3253 | 19.7808 | on_peak | 862.0492 |  |  | 2.24 | 0 | 97.76 | 135.4268 | 0
5082 | 900.77 | 25.65 | 29.2 | 5.1156 | 5.1156 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 895.6544 | 0 | 0.088511 | 7.3437 | 0 | 0 | 247.3253 | 5.1156 | on_peak | 895.6544 |  |  | 0.57 | 0 | 99.43 | 37.5672 | 0
5083 | 898.75 | 33.25 | 29 | 6.6362 | 6.6362 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 892.1138 | 0 | 0.088511 | 7.8253 | 0 | 0 | 247.3253 | 6.6362 | on_peak | 892.1138 |  |  | 0.74 | 0 | 99.26 | 51.93 | 0
5084 | 887.89 | 0 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 887.89 | 0 | 0.088511 | 8.1503 | 0 | 0 | 247.3253 | 0 | on_peak | 887.89 |  |  | 0 | 0 | 100 | 0 | 0
5085 | 871.14 | 0 | 29.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 871.14 | 0 | 0.088511 | 8.3732 | 0 | 0 | 247.3253 | 0 | on_peak | 871.14 |  |  | 0 | 0 | 100 | 0 | 0
5086 | 856.17 | 0 | 29.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 856.17 | 0 | 0.05921 | 8.4156 | 0 | 0 | 247.3253 | 0 | off_peak | 856.17 |  |  | 0 | 0 | 100 | 0 | 0
5087 | 872.31 | 0 | 29.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 872.31 | 0 | 0.05921 | 8.2402 | 0 | 0 | 247.3253 | 0 | off_peak | 872.31 |  |  | 0 | 0 | 100 | 0 | 0
5088 | 853.22 | 0 | 29.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 853.22 | 0 | 0.05921 | 7.8999 | 0 | 0 | 247.3253 | 0 | off_peak | 853.22 |  |  | 0 | 0 | 100 | 0 | 0
5089 | 789.24 | 0 | 29.2 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 19.0375 | 801.6389 | 0 | 0.05921 | 7.7104 | 0 | 0 | 247.3253 | 0 | off_peak | 789.24 | 0 | 100 | 0 | 0 | 100 | 0 | 0
5090 | 757.5 | 0 | 29 | 0 | 0 | 0 | 0 | 8.7263 | 8.7263 | 0 | 0 | 0 | 27.2003 | 766.2263 | 0 | 0.05921 | 7.3136 | 0 | 0 | 247.3253 | 0 | off_peak | 757.5 | 0 | 100 | 0 | 0 | 100 | 0 | 0
5091 | 695.39 | 0 | 28.8 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 38.7984 | 707.7889 | 0 | 0.05921 | 6.8051 | 0 | 0 | 247.3253 | 0 | off_peak | 695.39 | 0 | 100 | 0 | 0 | 100 | 0 | 0
5092 | 688.11 | 0 | 28.8 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 50.3966 | 700.5089 | 0 | 0.05921 | 6.3132 | 0 | 0 | 247.3253 | 0 | off_peak | 688.11 | 0 | 100 | 0 | 0 | 100 | 0 | 0
5093 | 700.96 | 0 | 28.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50.3966 | 700.96 | 0 | 0.05921 | 5.8131 | 0 | 0 | 247.3253 | 0 | off_peak | 700.96 |  |  | 0 | 0 | 100 | 0 | 0
5094 | 746.76 | 0 | 29 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50.3966 | 746.76 | 0 | 0.05921 | 5.1773 | 0 | 0 | 247.3253 | 0 | off_peak | 746.76 |  |  | 0 | 0 | 100 | 0 | 0
5095 | 761.96 | 79.2773 | 29.5 | 15.7936 | 3.3946 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 0 | 61.9947 | 758.5654 | 0 | 0.05921 | 4.6293 | 0 | 0 | 258.9235 | 3.3946 | off_peak | 758.5654 | 100 | 0 | 0.45 | 0 | 99.55 | 15.715 | 0
5096 | 849.47 | 199.001 | 29.9 | 39.5869 | 39.5869 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 73.5928 | 822.2821 | 0 | 0.05921 | 4.3479 | 0 | 0 | 258.9235 | 39.5869 | off_peak | 809.8831 | 0 | 100 | 4.66 | 0 | 95.34 | 172.1216 | 0
5097 | 863.2 | 166.042 | 30.2 | 32.9941 | 32.9941 | 0 | 0 | 0.80079 | 0.80079 | 0 | 0 | 0 | 74.3419 | 831.0067 | 0 | 0.05921 | 4.1536 | 0 | 0 | 258.9235 | 32.9941 | off_peak | 830.2059 | 0 | 100 | 3.82 | 0 | 96.18 | 137.0445 | 0
5098 | 933.45 | 603.034 | 30.6 | 119.6526 | 119.6526 | 0 | 0 | 0.05172 | 0.05172 | 0 | 0 | 0 | 74.3903 | 813.8492 | 0 | 0.05921 | 4.084 | 0 | 0 | 258.9235 | 119.6526 | off_peak | 813.7974 | 0 | 100 | 12.82 | 0 | 87.18 | 488.6594 | 0
5099 | 919.63 | 766.727 | 31 | 151.9086 | 151.9086 | 0 | 0 | 0.0033404 | 0.0033404 | 0 | 0 | 0 | 74.3934 | 767.7248 | 0 | 0.05921 | 4.219 | 0 | 0 | 258.9235 | 151.9086 | off_peak | 767.7214 | 0 | 100 | 16.52 | 0 | 83.48 | 640.9085 | 0
5100 | 900.79 | 483.88 | 31.3 | 95.7634 | 95.7634 | 0 | 0 | 0.00021574 | 0.00021574 | 0 | 0 | 0 | 74.3936 | 805.0268 | 0 | 0.05921 | 4.4947 | 0 | 0 | 258.9235 | 95.7634 | off_peak | 805.0266 | 0 | 100 | 10.63 | 0 | 89.37 | 430.427 | 0
5101 | 881.94 | 909.507 | 31.5 | 179.8655 | 179.8655 | 0 | 0 | 0 | 0 | 21.8535 | 21.8535 | 0 | 51.0313 | 680.2211 | 0 | 0.088511 | 4.7127 | 0 | 0 | 258.9235 | 179.8655 | on_peak | 680.2211 |  |  | 20.39 | 2.48 | 77.13 | 847.6581 | 0
5102 | 956.79 | 123.5 | 31.6 | 24.4145 | 24.4145 | 0 | 0 | 0 | 0 | 34.1324 | 34.1324 | 0 | 14.5422 | 898.2431 | 0 | 0.088511 | 4.9824 | 0 | 0 | 258.9235 | 24.4145 | on_peak | 898.2431 |  |  | 2.55 | 3.57 | 93.88 | 121.6441 | 0
5103 | 964.77 | 302.915 | 31.6 | 59.8828 | 59.8828 | 0 | 0 | 0 | 0 | 6.6441 | 6.6441 | 0 | 7.4394 | 898.2431 | 0 | 0.088511 | 5.3108 | 0 | 0 | 258.9235 | 59.8828 | on_peak | 898.2431 |  |  | 6.21 | 0.69 | 93.1 | 318.023 | 0
5104 | 853.73 | 347.51 | 31.4 | 68.7494 | 68.7494 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 784.9806 | 0 | 0.088511 | 5.8346 | 0 | 0 | 258.9235 | 68.7494 | on_peak | 784.9806 |  |  | 8.05 | 0 | 91.95 | 401.1253 | 0
5105 | 826.13 | 338.388 | 31.1 | 67.0188 | 67.0188 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 759.1112 | 0 | 0.088511 | 6.4072 | 0 | 0 | 258.9235 | 67.0188 | on_peak | 759.1112 |  |  | 8.11 | 0 | 91.89 | 429.4054 | 0
5106 | 876.42 | 205.057 | 30.7 | 40.672 | 40.672 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 835.748 | 0 | 0.088511 | 6.7912 | 0 | 0 | 258.9235 | 40.672 | on_peak | 835.748 |  |  | 4.64 | 0 | 95.36 | 276.2096 | 0
5107 | 823.83 | 19 | 30.5 | 3.7713 | 3.7713 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 820.0587 | 0 | 0.088511 | 7.1514 | 0 | 0 | 258.9235 | 3.7713 | on_peak | 820.0587 |  |  | 0.46 | 0 | 99.54 | 26.9701 | 0
5108 | 856.17 | 0 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 856.17 | 0 | 0.088511 | 7.304 | 0 | 0 | 258.9235 | 0 | on_peak | 856.17 |  |  | 0 | 0 | 100 | 0 | 0
5109 | 842.73 | 0 | 29.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 842.73 | 0 | 0.088511 | 7.4352 | 0 | 0 | 258.9235 | 0 | on_peak | 842.73 |  |  | 0 | 0 | 100 | 0 | 0
5110 | 799.18 | 0 | 29.7 | 0 | 0 | 0 | 0 | 8.7263 | 8.7263 | 0 | 0 | 0 | 15.6021 | 807.9063 | 0 | 0.05921 | 7.7741 | 0 | 0 | 258.9235 | 0 | off_peak | 799.18 | 0 | 100 | 0 | 0 | 100 | 0 | 0
5111 | 832.88 | 0 | 29.6 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 27.2003 | 845.2789 | 0 | 0.05921 | 7.6997 | 0 | 0 | 258.9235 | 0 | off_peak | 832.88 | 0 | 100 | 0 | 0 | 100 | 0 | 0
5112 | 794.19 | 0 | 29.5 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 38.7984 | 806.5889 | 0 | 0.05921 | 7.5146 | 0 | 0 | 258.9235 | 0 | off_peak | 794.19 | 0 | 100 | 0 | 0 | 100 | 0 | 0
5113 | 790.19 | 0 | 29.4 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 50.3966 | 802.5889 | 0 | 0.05921 | 7.3455 | 0 | 0 | 258.9235 | 0 | off_peak | 790.19 | 0 | 100 | 0 | 0 | 100 | 0 | 0
5114 | 659.76 | 0 | 29.3 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 61.9947 | 672.1589 | 0 | 0.05921 | 7.166 | 0 | 0 | 258.9235 | 0 | off_peak | 659.76 | 0 | 100 | 0 | 0 | 100 | 0 | 0
5115 | 634.98 | 0 | 29.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 61.9947 | 634.98 | 0 | 0.05921 | 6.7772 | 0 | 0 | 258.9235 | 0 | off_peak | 634.98 |  |  | 0 | 0 | 100 | 0 | 0
5116 | 638.61 | 0 | 29.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 61.9947 | 638.61 | 0 | 0.05921 | 6.2554 | 0 | 0 | 258.9235 | 0 | off_peak | 638.61 |  |  | 0 | 0 | 100 | 0 | 0
5117 | 647.99 | 0 | 29.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 61.9947 | 647.99 | 0 | 0.05921 | 5.6827 | 0 | 0 | 258.9235 | 0 | off_peak | 647.99 |  |  | 0 | 0 | 100 | 0 | 0
5118 | 701.72 | 0 | 29.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 61.9947 | 701.72 | 0 | 0.05921 | 5.1232 | 0 | 0 | 258.9235 | 0 | off_peak | 701.72 |  |  | 0 | 0 | 100 | 0 | 0
5119 | 716.75 | 42.8857 | 29.5 | 8.5437 | 8.5437 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 73.5928 | 720.6053 | 0 | 0.05921 | 4.6341 | 0 | 0 | 258.9235 | 8.5437 | off_peak | 708.2063 | 0 | 100 | 1.19 | 0 | 98.81 | 39.5919 | 0
5120 | 825.2 | 177.374 | 29.8 | 35.2976 | 35.2976 | 0 | 0 | 0.80079 | 0.80079 | 0 | 0 | 0 | 74.3419 | 790.7032 | 0 | 0.05921 | 4.336 | 0 | 0 | 258.9235 | 35.2976 | off_peak | 789.9024 | 0 | 100 | 4.28 | 0 | 95.72 | 153.0513 | 0
5121 | 889.06 | 132.722 | 29.9 | 26.4021 | 26.3504 | 0 | 0.05172 | 0.05172 | 0 | 0 | 0 | 0 | 74.3903 | 862.7096 | 0 | 0.05921 | 4.1058 | 0 | 0 | 258.9718 | 26.3504 | off_peak | 862.7096 | 100 | 0 | 2.96 | 0 | 97.04 | 108.1905 | 0
5122 | 883.93 | 345.293 | 30 | 68.6632 | 68.6632 | 0 | 0 | 0.0033404 | 0.0033404 | 0 | 0 | 0 | 74.3934 | 815.2701 | 0 | 0.05921 | 4.0426 | 0 | 0 | 258.9718 | 68.6632 | off_peak | 815.2668 | 0 | 100 | 7.77 | 0 | 92.23 | 277.5748 | 0
5123 | 848.57 | 343.883 | 30.2 | 68.3327 | 68.3327 | 0 | 0 | 0.00021574 | 0.00021574 | 0 | 0 | 0 | 74.3936 | 780.2375 | 0 | 0.05921 | 4.1442 | 0 | 0 | 258.9718 | 68.3327 | off_peak | 780.2373 | 0 | 100 | 8.05 | 0 | 91.95 | 283.1873 | 0
5124 | 871.28 | 477.221 | 30.3 | 94.7934 | 94.7934 | 0 | 1.3934e-05 | 1.3934e-05 | 0 | 0 | 0 | 0 | 74.3936 | 776.4866 | 0 | 0.05921 | 4.4263 | 0 | 0 | 258.9719 | 94.7934 | off_peak | 776.4866 | 100 | 0 | 10.88 | 0 | 89.12 | 419.5842 | 0
5125 | 773.7 | 537.558 | 30.3 | 106.7785 | 106.7785 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 666.9215 | 0 | 0.088511 | 4.6632 | 0 | 0 | 258.9719 | 106.7785 | on_peak | 666.9215 |  |  | 13.8 | 0 | 86.2 | 497.9268 | 0
5126 | 838.02 | 429.77 | 30.2 | 85.3993 | 85.3993 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 752.6207 | 0 | 0.088511 | 4.9665 | 0 | 0 | 258.9719 | 85.3993 | on_peak | 752.6207 |  |  | 10.19 | 0 | 89.81 | 424.1356 | 0
5127 | 839.88 | 415.606 | 30.1 | 82.615 | 82.615 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 757.265 | 0 | 0.088511 | 5.3021 | 0 | 0 | 258.9719 | 82.615 | on_peak | 757.265 |  |  | 9.84 | 0 | 90.16 | 438.0356 | 0
5128 | 804.01 | 395.044 | 29.9 | 78.5853 | 78.5853 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 725.4247 | 0 | 0.088511 | 5.797 | 0 | 0 | 258.9719 | 78.5853 | on_peak | 725.4247 |  |  | 9.77 | 0 | 90.23 | 455.559 | 0
5129 | 758.43 | 307.281 | 29.6 | 61.194 | 61.194 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 697.236 | 0 | 0.088511 | 6.4344 | 0 | 0 | 258.9719 | 61.194 | on_peak | 697.236 |  |  | 8.07 | 0 | 91.93 | 393.7439 | 0
5130 | 788.07 | 153.621 | 29.3 | 30.6267 | 30.6267 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 757.4433 | 0 | 0.088511 | 7.0436 | 0 | 0 | 258.9719 | 30.6267 | on_peak | 757.4433 |  |  | 3.89 | 0 | 96.11 | 215.7209 | 0
5131 | 753.09 | 42.0337 | 29.2 | 8.3831 | 8.3831 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 744.7069 | 0 | 0.088511 | 7.6296 | 0 | 0 | 258.9719 | 8.3831 | on_peak | 744.7069 |  |  | 1.11 | 0 | 98.89 | 63.9596 | 0
5132 | 759.02 | 0 | 29 | 0 | 0 | 0 | 0 | 0 | 0 | 62.63 | 62.63 | 0 | 7.4394 | 696.39 | 0 | 0.088511 | 7.8281 | 62.63 | 0 | 192.0176 | 62.63 | on_peak | 696.39 |  |  | 0 | 8.25 | 91.75 | 490.2748 | 0
5133 | 755.9 | 0 | 29 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 755.9 | 0 | 0.088511 | 7.9732 | 0 | 0 | 192.0176 | 0 | on_peak | 755.9 |  |  | 0 | 0 | 100 | 0 | 0
5134 | 718.25 | 0 | 29 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 19.0375 | 730.6489 | 0 | 0.05921 | 8.3095 | 0 | 0 | 192.0176 | 0 | off_peak | 718.25 | 0 | 100 | 0 | 0 | 100 | 0 | 0
5135 | 730.11 | 0 | 29 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19.0375 | 730.11 | 0 | 0.05921 | 8.2686 | 0 | 0 | 192.0176 | 0 | off_peak | 730.11 |  |  | 0 | 0 | 100 | 0 | 0
5136 | 753.25 | 0 | 29 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19.0375 | 753.25 | 0 | 0.05921 | 8.0338 | 0 | 0 | 192.0176 | 0 | off_peak | 753.25 |  |  | 0 | 0 | 100 | 0 | 0
5137 | 646.3 | 0 | 28.9 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 30.6357 | 658.6989 | 0 | 0.05921 | 7.9402 | 0 | 0 | 192.0176 | 0 | off_peak | 646.3 | 0 | 100 | 0 | 0 | 100 | 0 | 0
5138 | 560.61 | 0 | 28.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30.6357 | 560.61 | 0 | 0.05921 | 7.7382 | 0 | 0 | 192.0176 | 0 | off_peak | 560.61 |  |  | 0 | 0 | 100 | 0 | 0
5139 | 548.31 | 0 | 28.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30.6357 | 548.31 | 0 | 0.05921 | 7.1543 | 0 | 0 | 192.0176 | 0 | off_peak | 548.31 |  |  | 0 | 0 | 100 | 0 | 0
5140 | 575.73 | 0 | 28.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30.6357 | 575.73 | 0 | 0.05921 | 6.612 | 0 | 0 | 192.0176 | 0 | off_peak | 575.73 |  |  | 0 | 0 | 100 | 0 | 0
5141 | 558.15 | 0 | 28.8 | 0 | 0 | 0 | 0 | 8.7263 | 8.7263 | 0 | 0 | 0 | 38.7984 | 566.8763 | 0 | 0.05921 | 5.8875 | 0 | 0 | 192.0176 | 0 | off_peak | 558.15 | 0 | 100 | 0 | 0 | 100 | 0 | 0
5142 | 640.32 | 0 | 28.9 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 50.3966 | 652.7189 | 0 | 0.05921 | 5.4155 | 0 | 0 | 192.0176 | 0 | off_peak | 640.32 | 0 | 100 | 0 | 0 | 100 | 0 | 0
5143 | 697.81 | 58.3424 | 29.1 | 11.64 | 11.64 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 61.9947 | 698.569 | 0 | 0.05921 | 5.0413 | 0 | 0 | 192.0176 | 11.64 | off_peak | 686.17 | 0 | 100 | 1.67 | 0 | 98.33 | 58.6804 | 0
5144 | 855.32 | 249.529 | 29.4 | 49.7292 | 37.3303 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 0 | 73.5928 | 817.9897 | 0 | 0.05921 | 4.7621 | 0 | 0 | 203.6157 | 37.3303 | off_peak | 817.9897 | 100 | 0 | 4.36 | 0 | 95.64 | 177.7709 | 0
5145 | 863.1 | 379.892 | 29.6 | 75.6542 | 75.6542 | 0 | 0 | 0.80079 | 0.80079 | 0 | 0 | 0 | 74.3419 | 788.2466 | 0 | 0.05921 | 4.5163 | 0 | 0 | 203.6157 | 75.6542 | off_peak | 787.4458 | 0 | 100 | 8.77 | 0 | 91.23 | 341.6758 | 0
5146 | 900.9 | 542.637 | 29.7 | 108.0248 | 108.0248 | 0 | 0 | 0.05172 | 0.05172 | 0 | 0 | 0 | 74.3903 | 792.927 | 0 | 0.05921 | 4.4536 | 0 | 0 | 203.6157 | 108.0248 | off_peak | 792.8752 | 0 | 100 | 11.99 | 0 | 88.01 | 481.0999 | 0
5147 | 841.52 | 565.897 | 29.7 | 112.6552 | 112.6552 | 0 | 0 | 0.0033404 | 0.0033404 | 0 | 0 | 0 | 74.3934 | 728.8681 | 0 | 0.05921 | 4.5866 | 0 | 0 | 203.6157 | 112.6552 | off_peak | 728.8648 | 0 | 100 | 13.39 | 0 | 86.61 | 516.7065 | 0
5148 | 887.76 | 472.304 | 29.7 | 94.0233 | 94.0233 | 0 | 0 | 0.00021574 | 0.00021574 | 0 | 0 | 0 | 74.3936 | 793.7369 | 0 | 0.05921 | 4.8682 | 0 | 0 | 203.6157 | 94.0233 | off_peak | 793.7367 | 0 | 100 | 10.59 | 0 | 89.41 | 457.7241 | 0
5149 | 896.33 | 583.371 | 29.7 | 116.1338 | 116.1338 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 780.1962 | 0 | 0.088511 | 5.1362 | 0 | 0 | 203.6157 | 116.1338 | on_peak | 780.1962 |  |  | 12.96 | 0 | 87.04 | 596.4855 | 0
5150 | 888.79 | 571.745 | 29.6 | 113.8611 | 113.8611 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 774.9289 | 0 | 0.088511 | 5.3873 | 0 | 0 | 203.6157 | 113.8611 | on_peak | 774.9289 |  |  | 12.81 | 0 | 87.19 | 613.4016 | 0
5151 | 900.66 | 491.719 | 29.6 | 97.9242 | 97.9242 | 0 | 0 | 0 | 0 | 62.63 | 62.63 | 0 | 7.4394 | 740.1059 | 0 | 0.088511 | 5.5751 | 0 | 0 | 203.6157 | 97.9242 | on_peak | 740.1059 |  |  | 10.87 | 6.95 | 82.17 | 545.9412 | 0
5152 | 815.51 | 460.187 | 29.4 | 91.7118 | 91.7118 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 723.7982 | 0 | 0.088511 | 5.992 | 0 | 0 | 203.6157 | 91.7118 | on_peak | 723.7982 |  |  | 11.25 | 0 | 88.75 | 549.5339 | 0
5153 | 832.51 | 144.688 | 29.1 | 28.8669 | 28.8669 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 803.6431 | 0 | 0.088511 | 6.6214 | 0 | 0 | 203.6157 | 28.8669 | on_peak | 803.6431 |  |  | 3.47 | 0 | 96.53 | 191.1383 | 0
5154 | 858.07 | 82.0768 | 28.6 | 16.4051 | 16.4051 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 841.6649 | 0 | 0.088511 | 7.2641 | 0 | 0 | 203.6157 | 16.4051 | on_peak | 841.6649 |  |  | 1.91 | 0 | 98.09 | 119.1682 | 0
5155 | 826.11 | 19 | 28.4 | 3.8004 | 3.8004 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 822.3096 | 0 | 0.088511 | 7.7913 | 0 | 0 | 203.6157 | 3.8004 | on_peak | 822.3096 |  |  | 0.46 | 0 | 99.54 | 29.61 | 0
5156 | 829.74 | 0 | 28 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 829.74 | 0 | 0.088511 | 8.0939 | 0 | 0 | 203.6157 | 0 | on_peak | 829.74 |  |  | 0 | 0 | 100 | 0 | 0
5157 | 816.85 | 0 | 27.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 816.85 | 0 | 0.088511 | 8.2687 | 0 | 0 | 203.6157 | 0 | on_peak | 816.85 |  |  | 0 | 0 | 100 | 0 | 0
5158 | 802.19 | 0 | 27.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 802.19 | 0 | 0.05921 | 8.2298 | 0 | 0 | 203.6157 | 0 | off_peak | 802.19 |  |  | 0 | 0 | 100 | 0 | 0
5159 | 808.21 | 0 | 27.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 808.21 | 0 | 0.05921 | 8.1398 | 0 | 0 | 203.6157 | 0 | off_peak | 808.21 |  |  | 0 | 0 | 100 | 0 | 0
5160 | 763.59 | 0 | 27.7 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 19.0375 | 775.9889 | 0 | 0.05921 | 8.0325 | 0 | 0 | 203.6157 | 0 | off_peak | 763.59 | 0 | 100 | 0 | 0 | 100 | 0 | 0
5161 | 715.51 | 0 | 27.7 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 30.6357 | 727.9089 | 0 | 0.05921 | 8.0086 | 0 | 0 | 203.6157 | 0 | off_peak | 715.51 | 0 | 100 | 0 | 0 | 100 | 0 | 0
5162 | 615.63 | 0 | 27.7 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 42.2338 | 628.0289 | 0 | 0.05921 | 7.8974 | 0 | 0 | 203.6157 | 0 | off_peak | 615.63 | 0 | 100 | 0 | 0 | 100 | 0 | 0
5163 | 621.79 | 0 | 27.7 | 0 | 0 | 0 | 0 | 8.7263 | 8.7263 | 0 | 0 | 0 | 50.3966 | 630.5163 | 0 | 0.05921 | 7.4342 | 0 | 0 | 203.6157 | 0 | off_peak | 621.79 | 0 | 100 | 0 | 0 | 100 | 0 | 0
5164 | 622.99 | 0 | 27.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50.3966 | 622.99 | 0 | 0.05921 | 6.924 | 0 | 0 | 203.6157 | 0 | off_peak | 622.99 |  |  | 0 | 0 | 100 | 0 | 0
5165 | 649.31 | 0 | 27.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50.3966 | 649.31 | 0 | 0.05921 | 6.2064 | 0 | 0 | 203.6157 | 0 | off_peak | 649.31 |  |  | 0 | 0 | 100 | 0 | 0
5166 | 690.39 | 0 | 28.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50.3966 | 690.39 | 0 | 0.05921 | 5.5733 | 0 | 0 | 203.6157 | 0 | off_peak | 690.39 |  |  | 0 | 0 | 100 | 0 | 0
5167 | 792.26 | 72.5217 | 28.5 | 14.5006 | 2.1017 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 0 | 61.9947 | 790.1583 | 0 | 0.05921 | 5.1848 | 0 | 0 | 215.2139 | 2.1017 | off_peak | 790.1583 | 100 | 0 | 0.27 | 0 | 99.73 | 10.8967 | 0
5168 | 850.24 | 262.16 | 29 | 52.3229 | 52.3229 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 73.5928 | 810.316 | 0 | 0.05921 | 4.8703 | 0 | 0 | 215.2139 | 52.3229 | off_peak | 797.9171 | 0 | 100 | 6.15 | 0 | 93.85 | 254.8277 | 0
5169 | 925.28 | 470.403 | 29.2 | 93.8163 | 93.8163 | 0 | 0 | 0.80079 | 0.80079 | 0 | 0 | 0 | 74.3419 | 832.2645 | 0 | 0.05921 | 4.6596 | 0 | 0 | 215.2139 | 93.8163 | off_peak | 831.4637 | 0 | 100 | 10.14 | 0 | 89.86 | 437.1436 | 0
5170 | 943.49 | 657.029 | 29.3 | 130.9888 | 130.9888 | 0 | 0 | 0.05172 | 0.05172 | 0 | 0 | 0 | 74.3903 | 812.5529 | 0 | 0.05921 | 4.5452 | 0 | 0 | 215.2139 | 130.9888 | off_peak | 812.5012 | 0 | 100 | 13.88 | 0 | 86.12 | 595.3678 | 0
5171 | 896.51 | 645.856 | 29.3 | 128.7613 | 128.7613 | 0 | 0 | 0.0033404 | 0.0033404 | 0 | 0 | 0 | 74.3934 | 767.7521 | 0 | 0.05921 | 4.5788 | 0 | 0 | 215.2139 | 128.7613 | off_peak | 767.7487 | 0 | 100 | 14.36 | 0 | 85.64 | 589.566 | 0
5172 | 935.07 | 342.316 | 29.1 | 68.2958 | 68.2958 | 0 | 0 | 0.00021574 | 0.00021574 | 0 | 0 | 0 | 74.3936 | 866.7744 | 0 | 0.05921 | 4.8303 | 0 | 0 | 215.2139 | 68.2958 | off_peak | 866.7742 | 0 | 100 | 7.3 | 0 | 92.7 | 329.8912 | 0
5173 | 826.89 | 137.75 | 29 | 27.4927 | 27.4927 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 799.3973 | 0 | 0.088511 | 5.155 | 0 | 0 | 215.2139 | 27.4927 | on_peak | 799.3973 |  |  | 3.32 | 0 | 96.68 | 141.7253 | 0
5174 | 884.07 | 261.53 | 28.8 | 52.2353 | 52.2353 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 831.8347 | 0 | 0.088511 | 5.4593 | 0 | 0 | 215.2139 | 52.2353 | on_peak | 831.8347 |  |  | 5.91 | 0 | 94.09 | 285.1675 | 0
5175 | 889.17 | 618.869 | 28.6 | 123.6968 | 123.6968 | 0 | 0 | 0 | 0 | 62.63 | 62.63 | 0 | 7.4394 | 702.8432 | 0 | 0.088511 | 5.8977 | 0 | 0 | 215.2139 | 123.6968 | on_peak | 702.8432 |  |  | 13.91 | 7.04 | 79.04 | 729.5259 | 0
5176 | 830.1 | 574.163 | 28.5 | 114.803 | 114.803 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 715.297 | 0 | 0.088511 | 6.391 | 0 | 0 | 215.2139 | 114.803 | on_peak | 715.297 |  |  | 13.83 | 0 | 86.17 | 733.7108 | 0
5177 | 844.89 | 414.463 | 28.4 | 82.9015 | 82.9015 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 761.9885 | 0 | 0.088511 | 6.8541 | 0 | 0 | 215.2139 | 82.9015 | on_peak | 761.9885 |  |  | 9.81 | 0 | 90.19 | 568.2152 | 0
5178 | 834.8 | 245.705 | 28.3 | 49.1642 | 49.1642 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 785.6358 | 0 | 0.088511 | 7.3708 | 0 | 0 | 215.2139 | 49.1642 | on_peak | 785.6358 |  |  | 5.89 | 0 | 94.11 | 362.3774 | 0
5179 | 825.32 | 47.3379 | 28.2 | 9.4755 | 9.4755 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 815.8445 | 0 | 0.088511 | 7.9719 | 0 | 0 | 215.2139 | 9.4755 | on_peak | 815.8445 |  |  | 1.15 | 0 | 98.85 | 75.5379 | 0
5180 | 806.77 | 0 | 28.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 806.77 | 0 | 0.088511 | 8.4168 | 0 | 0 | 215.2139 | 0 | on_peak | 806.77 |  |  | 0 | 0 | 100 | 0 | 0
5181 | 840.72 | 0 | 28.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 840.72 | 0 | 0.088511 | 8.5206 | 0 | 0 | 215.2139 | 0 | on_peak | 840.72 |  |  | 0 | 0 | 100 | 0 | 0
5182 | 784.59 | 0 | 28.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 784.59 | 0 | 0.05921 | 8.7176 | 0 | 0 | 215.2139 | 0 | off_peak | 784.59 |  |  | 0 | 0 | 100 | 0 | 0
5183 | 782.19 | 0 | 28.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 782.19 | 0 | 0.05921 | 8.6867 | 0 | 0 | 215.2139 | 0 | off_peak | 782.19 |  |  | 0 | 0 | 100 | 0 | 0
5184 | 783.16 | 0 | 28.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 783.16 | 0 | 0.05921 | 8.5816 | 0 | 0 | 215.2139 | 0 | off_peak | 783.16 |  |  | 0 | 0 | 100 | 0 | 0
5185 | 716.39 | 0 | 28.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 716.39 | 0 | 0.05921 | 8.452 | 0 | 0 | 215.2139 | 0 | off_peak | 716.39 |  |  | 0 | 0 | 100 | 0 | 0
5186 | 646.46 | 0 | 28.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 646.46 | 0 | 0.05921 | 8.241 | 0 | 0 | 215.2139 | 0 | off_peak | 646.46 |  |  | 0 | 0 | 100 | 0 | 0
5187 | 594.29 | 0 | 28.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 594.29 | 0 | 0.05921 | 7.727 | 0 | 0 | 215.2139 | 0 | off_peak | 594.29 |  |  | 0 | 0 | 100 | 0 | 0
5188 | 628.74 | 0 | 28.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 628.74 | 0 | 0.05921 | 7.272 | 0 | 0 | 215.2139 | 0 | off_peak | 628.74 |  |  | 0 | 0 | 100 | 0 | 0
5189 | 629.08 | 0 | 28.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 629.08 | 0 | 0.05921 | 6.7386 | 0 | 0 | 215.2139 | 0 | off_peak | 629.08 |  |  | 0 | 0 | 100 | 0 | 0
5190 | 710.26 | 0 | 28.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 710.26 | 0 | 0.05921 | 6.1533 | 0 | 0 | 215.2139 | 0 | off_peak | 710.26 |  |  | 0 | 0 | 100 | 0 | 0
5191 | 744.33 | 79.9684 | 28.9 | 15.9662 | 15.9662 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 728.3638 | 0 | 0.05921 | 5.6849 | 0 | 0 | 215.2139 | 15.9662 | off_peak | 728.3638 |  |  | 2.15 | 0 | 97.85 | 90.7672 | 0
5192 | 805.51 | 272.684 | 29.4 | 54.3438 | 54.3438 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 751.1662 | 0 | 0.05921 | 5.3465 | 0 | 0 | 215.2139 | 54.3438 | off_peak | 751.1662 |  |  | 6.75 | 0 | 93.25 | 290.547 | 0
5193 | 793.21 | 329.341 | 29.6 | 65.5871 | 65.5871 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 727.6229 | 0 | 0.05921 | 5.1042 | 0 | 0 | 215.2139 | 65.5871 | off_peak | 727.6229 |  |  | 8.27 | 0 | 91.73 | 334.77 | 0
5194 | 794.26 | 489.048 | 29.8 | 97.3209 | 97.3209 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 696.9391 | 0 | 0.05921 | 4.9867 | 0 | 0 | 215.2139 | 97.3209 | off_peak | 696.9391 |  |  | 12.25 | 0 | 87.75 | 485.311 | 0
5195 | 798.79 | 263.567 | 30.1 | 52.3924 | 52.3924 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 746.3976 | 0 | 0.05921 | 4.9518 | 0 | 0 | 215.2139 | 52.3924 | off_peak | 746.3976 |  |  | 6.56 | 0 | 93.44 | 259.4383 | 0
5196 | 776.56 | 504.715 | 30.4 | 100.2179 | 100.2179 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 676.3421 | 0 | 0.05921 | 5.0046 | 0 | 0 | 215.2139 | 100.2179 | off_peak | 676.3421 |  |  | 12.91 | 0 | 87.09 | 501.5529 | 0
5197 | 773.82 | 636.094 | 30.6 | 126.2122 | 126.2122 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 647.6078 | 0 | 0.05921 | 5.1436 | 0 | 0 | 215.2139 | 126.2122 | off_peak | 647.6078 |  |  | 16.31 | 0 | 83.69 | 649.1895 | 0
5198 | 746.94 | 724.111 | 30.8 | 143.5708 | 143.5708 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 603.3692 | 0 | 0.05921 | 5.6243 | 0 | 0 | 215.2139 | 143.5708 | off_peak | 603.3692 |  |  | 19.22 | 0 | 80.78 | 807.4922 | 0
5199 | 725.54 | 687.222 | 30.8 | 136.2567 | 136.2567 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 589.2833 | 0 | 0.05921 | 6.0832 | 0 | 0 | 215.2139 | 136.2567 | off_peak | 589.2833 |  |  | 18.78 | 0 | 81.22 | 828.8747 | 0
5200 | 685.56 | 635.662 | 30.8 | 126.0338 | 126.0338 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 559.5262 | 0 | 0.05921 | 6.6279 | 0 | 0 | 215.2139 | 126.0338 | off_peak | 559.5262 |  |  | 18.38 | 0 | 81.62 | 835.3457 | 0
5201 | 724.39 | 449.07 | 30.6 | 89.1034 | 89.1034 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 635.2866 | 0 | 0.05921 | 7.0979 | 0 | 0 | 215.2139 | 89.1034 | off_peak | 635.2866 |  |  | 12.3 | 0 | 87.7 | 632.4463 | 0
5202 | 691.32 | 209.918 | 30.4 | 41.682 | 41.682 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 649.638 | 0 | 0.05921 | 7.4329 | 0 | 0 | 215.2139 | 41.682 | off_peak | 649.638 |  |  | 6.03 | 0 | 93.97 | 309.8168 | 0
5203 | 636.81 | 34.3103 | 30.2 | 6.8178 | 0 | 0 | 6.8178 | 12.3989 | 5.5812 | 0 | 0 | 0 | 19.0375 | 642.3912 | 0 | 0.05921 | 7.6191 | 0 | 0 | 221.5913 | 0 | off_peak | 636.81 | 54.99 | 45.01 | 0 | 0 | 100 | 0 | 0
5204 | 653.56 | 0 | 29.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19.0375 | 653.56 | 0 | 0.05921 | 7.7691 | 0 | 0 | 221.5913 | 0 | off_peak | 653.56 |  |  | 0 | 0 | 100 | 0 | 0
5205 | 633.79 | 0 | 29.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19.0375 | 633.79 | 0 | 0.05921 | 7.8472 | 0 | 0 | 221.5913 | 0 | off_peak | 633.79 |  |  | 0 | 0 | 100 | 0 | 0
5206 | 639.07 | 0 | 29.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19.0375 | 639.07 | 0 | 0.05921 | 8.0894 | 0 | 0 | 221.5913 | 0 | off_peak | 639.07 |  |  | 0 | 0 | 100 | 0 | 0
5207 | 638.27 | 0 | 28.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19.0375 | 638.27 | 0 | 0.05921 | 8.0533 | 0 | 0 | 221.5913 | 0 | off_peak | 638.27 |  |  | 0 | 0 | 100 | 0 | 0
5208 | 623.32 | 0 | 28.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19.0375 | 623.32 | 0 | 0.05921 | 8.0246 | 0 | 0 | 221.5913 | 0 | off_peak | 623.32 |  |  | 0 | 0 | 100 | 0 | 0
5209 | 640.68 | 0 | 28.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19.0375 | 640.68 | 0 | 0.05921 | 7.8905 | 0 | 0 | 221.5913 | 0 | off_peak | 640.68 |  |  | 0 | 0 | 100 | 0 | 0
5210 | 626.41 | 0 | 28.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19.0375 | 626.41 | 0 | 0.05921 | 7.8059 | 0 | 0 | 221.5913 | 0 | off_peak | 626.41 |  |  | 0 | 0 | 100 | 0 | 0
5211 | 632.59 | 0 | 28.4 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 30.6357 | 644.9889 | 0 | 0.05921 | 7.5718 | 0 | 0 | 221.5913 | 0 | off_peak | 632.59 | 0 | 100 | 0 | 0 | 100 | 0 | 0
5212 | 615.67 | 0 | 28.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30.6357 | 615.67 | 0 | 0.05921 | 7.1061 | 0 | 0 | 221.5913 | 0 | off_peak | 615.67 |  |  | 0 | 0 | 100 | 0 | 0
5213 | 661.79 | 0 | 28.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30.6357 | 661.79 | 0 | 0.05921 | 6.7125 | 0 | 0 | 221.5913 | 0 | off_peak | 661.79 |  |  | 0 | 0 | 100 | 0 | 0
5214 | 695.15 | 0 | 28.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30.6357 | 695.15 | 0 | 0.05921 | 6.1274 | 0 | 0 | 221.5913 | 0 | off_peak | 695.15 |  |  | 0 | 0 | 100 | 0 | 0
5215 | 755.7 | 80.6186 | 29.1 | 16.0843 | 16.0843 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30.6357 | 739.6157 | 0 | 0.05921 | 5.6479 | 0 | 0 | 221.5913 | 16.0843 | off_peak | 739.6157 |  |  | 2.13 | 0 | 97.87 | 90.8418 | 0
5216 | 765.83 | 277.012 | 29.6 | 55.166 | 55.166 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30.6357 | 710.664 | 0 | 0.05921 | 5.3036 | 0 | 0 | 221.5913 | 55.166 | off_peak | 710.664 |  |  | 7.2 | 0 | 92.8 | 292.5771 | 0
5217 | 768.7 | 485.594 | 29.9 | 96.5982 | 96.5982 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30.6357 | 672.1018 | 0 | 0.05921 | 5.0905 | 0 | 0 | 221.5913 | 96.5982 | off_peak | 672.1018 |  |  | 12.57 | 0 | 87.43 | 491.7333 | 0
5218 | 773.8 | 670.882 | 30.2 | 133.3104 | 133.3104 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30.6357 | 640.4896 | 0 | 0.05921 | 4.9537 | 0 | 0 | 221.5913 | 133.3104 | off_peak | 640.4896 |  |  | 17.23 | 0 | 82.77 | 660.3809 | 0
5219 | 785.25 | 812.949 | 30.5 | 161.3627 | 161.3627 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30.6357 | 623.8873 | 0 | 0.05921 | 4.8876 | 0 | 0 | 221.5913 | 161.3627 | off_peak | 623.8873 |  |  | 20.55 | 0 | 79.45 | 788.671 | 0
5220 | 803.67 | 667.985 | 30.8 | 132.4426 | 132.4426 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 42.2338 | 683.6264 | 0 | 0.05921 | 4.9042 | 0 | 0 | 221.5913 | 132.4426 | off_peak | 671.2274 | 0 | 100 | 16.48 | 0 | 83.52 | 649.5234 | 0
5221 | 754.15 | 432.297 | 30.9 | 85.6808 | 85.6808 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 53.832 | 680.8682 | 0 | 0.05921 | 4.9984 | 0 | 0 | 221.5913 | 85.6808 | off_peak | 668.4692 | 0 | 100 | 11.36 | 0 | 88.64 | 428.2685 | 0
5222 | 731.01 | 545.749 | 31 | 108.1271 | 108.1271 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 65.4301 | 635.2819 | 0 | 0.05921 | 5.4162 | 0 | 0 | 221.5913 | 108.1271 | off_peak | 622.8829 | 0 | 100 | 14.79 | 0 | 85.21 | 585.6361 | 0
5223 | 746.71 | 665.152 | 31 | 131.7839 | 131.7839 | 0 | 0 | 0.58163 | 0.58163 | 0 | 0 | 0 | 65.9742 | 615.5077 | 0 | 0.05921 | 5.9333 | 0 | 0 | 221.5913 | 131.7839 | off_peak | 614.9261 | 0 | 100 | 17.65 | 0 | 82.35 | 781.9194 | 0
5224 | 752.07 | 419.882 | 30.8 | 83.2508 | 83.2508 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 65.9742 | 668.8192 | 0 | 0.05921 | 6.4725 | 0 | 0 | 221.5913 | 83.2508 | off_peak | 668.8192 |  |  | 11.07 | 0 | 88.93 | 538.837 | 0
5225 | 731.32 | 153.466 | 30.5 | 30.4615 | 30.4615 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 65.9742 | 700.8585 | 0 | 0.05921 | 7.1014 | 0 | 0 | 221.5913 | 30.4615 | off_peak | 700.8585 |  |  | 4.17 | 0 | 95.83 | 216.3189 | 0
5226 | 686.03 | 201.777 | 30.2 | 40.0949 | 40.0949 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 65.9742 | 645.9351 | 0 | 0.05921 | 7.6448 | 0 | 0 | 221.5913 | 40.0949 | off_peak | 645.9351 |  |  | 5.84 | 0 | 94.16 | 306.5194 | 0
5227 | 629.14 | 42.3398 | 30 | 8.4195 | 0 | 0 | 8.4195 | 8.4195 | 0 | 0 | 0 | 0 | 73.8499 | 629.14 | 0 | 0.05921 | 8.0584 | 0 | 0 | 229.467 | 0 | off_peak | 629.14 | 100 | 0 | 0 | 0 | 100 | 0 | 0
5228 | 614.55 | 0 | 29.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 73.8499 | 614.55 | 0 | 0.05921 | 8.2516 | 0 | 0 | 229.467 | 0 | off_peak | 614.55 |  |  | 0 | 0 | 100 | 0 | 0
5229 | 620.99 | 0 | 29.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 73.8499 | 620.99 | 0 | 0.05921 | 8.288 | 0 | 0 | 229.467 | 0 | off_peak | 620.99 |  |  | 0 | 0 | 100 | 0 | 0
5230 | 620.37 | 0 | 29.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 73.8499 | 620.37 | 0 | 0.05921 | 8.4856 | 0 | 0 | 229.467 | 0 | off_peak | 620.37 |  |  | 0 | 0 | 100 | 0 | 0
5231 | 630.33 | 0 | 29.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 73.8499 | 630.33 | 0 | 0.05921 | 8.7487 | 0 | 0 | 229.467 | 0 | off_peak | 630.33 |  |  | 0 | 0 | 100 | 0 | 0
5232 | 605.23 | 0 | 29.1 | 0 | 0 | 0 | 0 | 0.54378 | 0.54378 | 0 | 0 | 0 | 74.3585 | 605.7738 | 0 | 0.05921 | 8.9716 | 0 | 0 | 229.467 | 0 | off_peak | 605.23 | 0 | 100 | 0 | 0 | 100 | 0 | 0
5233 | 617.98 | 0 | 29 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3585 | 617.98 | 0 | 0.05921 | 8.8041 | 0 | 0 | 229.467 | 0 | off_peak | 617.98 |  |  | 0 | 0 | 100 | 0 | 0
5234 | 603.11 | 0 | 28.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3585 | 603.11 | 0 | 0.05921 | 8.6397 | 0 | 0 | 229.467 | 0 | off_peak | 603.11 |  |  | 0 | 0 | 100 | 0 | 0
5235 | 638.35 | 0 | 28.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3585 | 638.35 | 0 | 0.05921 | 8.3001 | 0 | 0 | 229.467 | 0 | off_peak | 638.35 |  |  | 0 | 0 | 100 | 0 | 0
5236 | 592.96 | 0 | 28.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3585 | 592.96 | 0 | 0.05921 | 7.6856 | 0 | 0 | 229.467 | 0 | off_peak | 592.96 |  |  | 0 | 0 | 100 | 0 | 0
5237 | 665.82 | 0 | 28.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3585 | 665.82 | 0 | 0.05921 | 6.8829 | 0 | 0 | 229.467 | 0 | off_peak | 665.82 |  |  | 0 | 0 | 100 | 0 | 0
5238 | 685.51 | 0 | 28.6 | 0 | 0 | 0 | 0 | 0.03512 | 0.03512 | 0 | 0 | 0 | 74.3914 | 685.5451 | 0 | 0.05921 | 6.3358 | 0 | 0 | 229.467 | 0 | off_peak | 685.51 | 0 | 100 | 0 | 0 | 100 | 0 | 0
5239 | 740.97 | 79.1276 | 29.1 | 15.7868 | 15.7868 | 0 | 0 | 0.0022683 | 0.0022683 | 0 | 0 | 0 | 74.3935 | 725.1854 | 0 | 0.05921 | 5.8421 | 0 | 0 | 229.467 | 15.7868 | off_peak | 725.1832 | 0 | 100 | 2.13 | 0 | 97.87 | 92.2277 | 0
5240 | 811.4 | 272.569 | 29.5 | 54.3011 | 54.3011 | 0 | 0 | 0.0001465 | 0.0001465 | 0 | 0 | 0 | 74.3936 | 757.0991 | 0 | 0.05921 | 5.5231 | 0 | 0 | 229.467 | 54.3011 | off_peak | 757.0989 | 0 | 100 | 6.69 | 0 | 93.31 | 299.9106 | 0
5241 | 880.71 | 480.046 | 29.9 | 95.4945 | 95.4945 | 0 | 0 | 9.4616e-06 | 9.4616e-06 | 0 | 0 | 0 | 74.3936 | 785.2155 | 0 | 0.05921 | 5.2905 | 0 | 0 | 229.467 | 95.4945 | off_peak | 785.2155 | 0 | 100 | 10.84 | 0 | 89.16 | 505.2111 | 0
5242 | 824.4 | 667.258 | 30.2 | 132.5903 | 132.5903 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 691.8097 | 0 | 0.05921 | 5.2171 | 0 | 0 | 229.467 | 132.5903 | off_peak | 691.8097 |  |  | 16.08 | 0 | 83.92 | 691.7355 | 0
5243 | 833.34 | 811.778 | 30.5 | 161.1302 | 161.1302 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 672.2098 | 0 | 0.05921 | 5.3271 | 0 | 0 | 229.467 | 161.1302 | off_peak | 672.2098 |  |  | 19.34 | 0 | 80.66 | 858.3624 | 0
5244 | 890.2 | 903.687 | 30.8 | 179.1756 | 179.1756 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 711.0244 | 0 | 0.05921 | 5.4982 | 0 | 0 | 229.467 | 179.1756 | off_peak | 711.0244 |  |  | 20.13 | 0 | 79.87 | 985.1413 | 0
5245 | 812.82 | 931.615 | 31 | 184.5772 | 184.5772 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 628.2428 | 0 | 0.088511 | 5.6345 | 0 | 0 | 229.467 | 184.5772 | on_peak | 628.2428 |  |  | 22.71 | 0 | 77.29 | 1040.0034 | 0
5246 | 871.48 | 895.124 | 31 | 177.3473 | 177.3473 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 694.1327 | 0 | 0.088511 | 5.9465 | 0 | 0 | 229.467 | 177.3473 | on_peak | 694.1327 |  |  | 20.35 | 0 | 79.65 | 1054.5916 | 0
5247 | 873.75 | 797.326 | 31 | 157.971 | 157.971 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 715.779 | 0 | 0.088511 | 6.4105 | 0 | 0 | 229.467 | 157.971 | on_peak | 715.779 |  |  | 18.08 | 0 | 81.92 | 1012.6733 | 0
5248 | 844.12 | 646.739 | 30.9 | 128.183 | 128.183 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 715.937 | 0 | 0.088511 | 7.0774 | 0 | 0 | 229.467 | 128.183 | on_peak | 715.937 |  |  | 15.19 | 0 | 84.81 | 907.2017 | 0
5249 | 843.23 | 457.378 | 30.6 | 90.7518 | 90.7518 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 752.4782 | 0 | 0.088511 | 7.7249 | 0 | 0 | 229.467 | 90.7518 | on_peak | 752.4782 |  |  | 10.76 | 0 | 89.24 | 701.0458 | 0
5250 | 844.37 | 248.569 | 30.2 | 49.3929 | 49.3929 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 794.9771 | 0 | 0.088511 | 8.2406 | 0 | 0 | 229.467 | 49.3929 | on_peak | 794.9771 |  |  | 5.85 | 0 | 94.15 | 407.0294 | 0
5251 | 848.37 | 61.5389 | 30 | 12.2373 | 12.2373 | 0 | 0 | 0 | 0 | 62.63 | 62.63 | 0 | 7.4394 | 773.5027 | 0 | 0.088511 | 8.712 | 0 | 0 | 229.467 | 12.2373 | on_peak | 773.5027 |  |  | 1.44 | 7.38 | 91.18 | 106.6115 | 0
5252 | 855.88 | 0 | 29.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 855.88 | 0 | 0.088511 | 9.0542 | 0 | 0 | 229.467 | 0 | on_peak | 855.88 |  |  | 0 | 0 | 100 | 0 | 0
5253 | 830.24 | 0 | 29.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 830.24 | 0 | 0.088511 | 8.9808 | 0 | 0 | 229.467 | 0 | on_peak | 830.24 |  |  | 0 | 0 | 100 | 0 | 0
5254 | 832.8 | 0 | 29.3 | 0 | 0 | 0 | 0 | 8.7263 | 8.7263 | 0 | 0 | 0 | 15.6021 | 841.5263 | 0 | 0.05921 | 8.8558 | 0 | 0 | 229.467 | 0 | off_peak | 832.8 | 0 | 100 | 0 | 0 | 100 | 0 | 0
5255 | 872.84 | 0 | 29.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15.6021 | 872.84 | 0 | 0.05921 | 8.967 | 0 | 0 | 229.467 | 0 | off_peak | 872.84 |  |  | 0 | 0 | 100 | 0 | 0
5256 | 816.46 | 0 | 29 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15.6021 | 816.46 | 0 | 0.05921 | 9.057 | 0 | 0 | 229.467 | 0 | off_peak | 816.46 |  |  | 0 | 0 | 100 | 0 | 0
5257 | 774.58 | 0 | 28.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15.6021 | 774.58 | 0 | 0.05921 | 9.0684 | 0 | 0 | 229.467 | 0 | off_peak | 774.58 |  |  | 0 | 0 | 100 | 0 | 0
5258 | 704.44 | 0 | 28.8 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 27.2003 | 716.8389 | 0 | 0.05921 | 8.9796 | 0 | 0 | 229.467 | 0 | off_peak | 704.44 | 0 | 100 | 0 | 0 | 100 | 0 | 0
5259 | 687.58 | 0 | 28.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27.2003 | 687.58 | 0 | 0.05921 | 8.7383 | 0 | 0 | 229.467 | 0 | off_peak | 687.58 |  |  | 0 | 0 | 100 | 0 | 0
5260 | 686.76 | 0 | 28.7 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 38.7984 | 699.1589 | 0 | 0.05921 | 8.0899 | 0 | 0 | 229.467 | 0 | off_peak | 686.76 | 0 | 100 | 0 | 0 | 100 | 0 | 0
5261 | 656.25 | 0 | 28.7 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 50.3966 | 668.6489 | 0 | 0.05921 | 7.3993 | 0 | 0 | 229.467 | 0 | off_peak | 656.25 | 0 | 100 | 0 | 0 | 100 | 0 | 0
5262 | 705.35 | 0 | 28.8 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 61.9947 | 717.7489 | 0 | 0.05921 | 6.723 | 0 | 0 | 229.467 | 0 | off_peak | 705.35 | 0 | 100 | 0 | 0 | 100 | 0 | 0
5263 | 740.42 | 81.7191 | 29.2 | 16.2979 | 3.899 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 0 | 73.5928 | 736.521 | 0 | 0.05921 | 6.204 | 0 | 0 | 241.0652 | 3.899 | off_peak | 736.521 | 100 | 0 | 0.53 | 0 | 99.47 | 24.1891 | 0
5264 | 819.4 | 280.289 | 29.6 | 55.8186 | 55.8186 | 0 | 0 | 0.80079 | 0.80079 | 0 | 0 | 0 | 74.3419 | 764.3822 | 0 | 0.05921 | 5.8198 | 0 | 0 | 241.0652 | 55.8186 | off_peak | 763.5814 | 0 | 100 | 6.81 | 0 | 93.19 | 324.8513 | 0
5265 | 827.27 | 488.95 | 29.8 | 97.3014 | 97.2497 | 0 | 0.05172 | 0.05172 | 0 | 0 | 0 | 0 | 74.3903 | 730.0203 | 0 | 0.05921 | 5.5292 | 0 | 0 | 241.1135 | 97.2497 | off_peak | 730.0203 | 100 | 0 | 11.76 | 0 | 88.24 | 537.716 | 0
5266 | 871.06 | 653.952 | 30.2 | 129.9463 | 129.9463 | 0 | 0 | 0.0033404 | 0.0033404 | 0 | 0 | 0 | 74.3934 | 741.1171 | 0 | 0.05921 | 5.4057 | 0 | 0 | 241.1135 | 129.9463 | off_peak | 741.1137 | 0 | 100 | 14.92 | 0 | 85.08 | 702.455 | 0
5267 | 852.8 | 501.124 | 30.5 | 99.4684 | 99.4681 | 0 | 0.00021574 | 0.00021574 | 0 | 0 | 0 | 0 | 74.3936 | 753.3319 | 0 | 0.05921 | 5.4761 | 0 | 0 | 241.1137 | 99.4681 | off_peak | 753.3319 | 100 | 0 | 11.66 | 0 | 88.34 | 544.6992 | 0
5268 | 889.01 | 854.529 | 30.7 | 169.4913 | 169.4913 | 0 | 0 | 1.3934e-05 | 1.3934e-05 | 0 | 0 | 0 | 74.3936 | 719.5187 | 0 | 0.05921 | 5.6944 | 0 | 0 | 241.1137 | 169.4913 | off_peak | 719.5187 | 0 | 100 | 19.07 | 0 | 80.93 | 965.1578 | 0
5269 | 862.69 | 935.417 | 30.8 | 185.4668 | 185.4668 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 677.2232 | 0 | 0.088511 | 5.8575 | 0 | 0 | 241.1137 | 185.4668 | on_peak | 677.2232 |  |  | 21.5 | 0 | 78.5 | 1086.374 | 0
5270 | 881.1 | 897.538 | 30.8 | 177.9565 | 177.9565 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 703.1435 | 0 | 0.088511 | 6.1756 | 0 | 0 | 241.1137 | 177.9565 | on_peak | 703.1435 |  |  | 20.2 | 0 | 79.8 | 1098.9948 | 0
5271 | 831.85 | 799.5 | 30.8 | 158.5183 | 158.5183 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 673.3317 | 0 | 0.088511 | 6.6061 | 0 | 0 | 241.1137 | 158.5183 | on_peak | 673.3317 |  |  | 19.06 | 0 | 80.94 | 1047.1818 | 0
5272 | 806.86 | 647.412 | 30.7 | 128.4107 | 128.4107 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 678.4493 | 0 | 0.088511 | 7.2062 | 0 | 0 | 241.1137 | 128.4107 | on_peak | 678.4493 |  |  | 15.91 | 0 | 84.09 | 925.352 | 0
5273 | 835.68 | 457.523 | 30.5 | 90.814 | 90.814 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 744.866 | 0 | 0.088511 | 7.7322 | 0 | 0 | 241.1137 | 90.814 | on_peak | 744.866 |  |  | 10.87 | 0 | 89.13 | 702.1896 | 0
5274 | 874.77 | 248.631 | 30.2 | 49.4053 | 49.4053 | 0 | 0 | 0 | 0 | 62.63 | 62.63 | 0 | 7.4394 | 762.7347 | 0 | 0.088511 | 8.2542 | 0 | 0 | 241.1137 | 49.4053 | on_peak | 762.7347 |  |  | 5.65 | 7.16 | 87.19 | 407.8023 | 0
5275 | 808.22 | 60.2016 | 30 | 11.9714 | 11.9714 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 796.2486 | 0 | 0.088511 | 8.6262 | 0 | 0 | 241.1137 | 11.9714 | on_peak | 796.2486 |  |  | 1.48 | 0 | 98.52 | 103.2678 | 0
5276 | 845.54 | 0 | 29.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 845.54 | 0 | 0.088511 | 9.0003 | 0 | 0 | 241.1137 | 0 | on_peak | 845.54 |  |  | 0 | 0 | 100 | 0 | 0
5277 | 800.84 | 0 | 29.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 800.84 | 0 | 0.088511 | 9.1783 | 0 | 0 | 241.1137 | 0 | on_peak | 800.84 |  |  | 0 | 0 | 100 | 0 | 0
5278 | 788.13 | 0 | 29.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 788.13 | 0 | 0.05921 | 9.2545 | 0 | 0 | 241.1137 | 0 | off_peak | 788.13 |  |  | 0 | 0 | 100 | 0 | 0
5279 | 798.93 | 0 | 29.2 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 19.0375 | 811.3289 | 0 | 0.05921 | 9.5411 | 0 | 0 | 241.1137 | 0 | off_peak | 798.93 | 0 | 100 | 0 | 0 | 100 | 0 | 0
5280 | 765.69 | 0 | 29 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 30.6357 | 778.0889 | 0 | 0.05921 | 9.4332 | 0 | 0 | 241.1137 | 0 | off_peak | 765.69 | 0 | 100 | 0 | 0 | 100 | 0 | 0
5281 | 715.25 | 0 | 28.9 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 42.2338 | 727.6489 | 0 | 0.05921 | 9.1974 | 0 | 0 | 241.1137 | 0 | off_peak | 715.25 | 0 | 100 | 0 | 0 | 100 | 0 | 0
5282 | 616.02 | 0 | 28.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 42.2338 | 616.02 | 0 | 0.05921 | 8.9087 | 0 | 0 | 241.1137 | 0 | off_peak | 616.02 |  |  | 0 | 0 | 100 | 0 | 0
5283 | 579.08 | 0 | 28.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 42.2338 | 579.08 | 0 | 0.05921 | 8.5001 | 0 | 0 | 241.1137 | 0 | off_peak | 579.08 |  |  | 0 | 0 | 100 | 0 | 0
5284 | 547.62 | 0 | 28.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 42.2338 | 547.62 | 0 | 0.05921 | 7.6565 | 0 | 0 | 241.1137 | 0 | off_peak | 547.62 |  |  | 0 | 0 | 100 | 0 | 0
5285 | 575.27 | 0 | 28.9 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 53.832 | 587.6689 | 0 | 0.05921 | 6.8206 | 0 | 0 | 241.1137 | 0 | off_peak | 575.27 | 0 | 100 | 0 | 0 | 100 | 0 | 0
5286 | 674.72 | 0 | 29.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 53.832 | 674.72 | 0 | 0.05921 | 6.3634 | 0 | 0 | 241.1137 | 0 | off_peak | 674.72 |  |  | 0 | 0 | 100 | 0 | 0
5287 | 703.25 | 77.6385 | 29.6 | 15.4614 | 6.7351 | 0 | 8.7263 | 8.7263 | 0 | 0 | 0 | 0 | 61.9947 | 696.5149 | 0 | 0.05921 | 5.9987 | 0 | 0 | 249.2765 | 6.7351 | off_peak | 696.5149 | 100 | 0 | 0.96 | 0 | 99.04 | 40.4021 | 0
5288 | 790.16 | 274.171 | 30 | 54.5203 | 42.1213 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 0 | 73.5928 | 748.0387 | 0 | 0.05921 | 5.7029 | 0 | 0 | 260.8746 | 42.1213 | off_peak | 748.0387 | 100 | 0 | 5.33 | 0 | 94.67 | 240.2158 | 0
5289 | 836.98 | 403.114 | 30.3 | 80.0731 | 80.0731 | 0 | 0 | 0.80079 | 0.80079 | 0 | 0 | 0 | 74.3419 | 757.7077 | 0 | 0.05921 | 5.4845 | 0 | 0 | 260.8746 | 80.0731 | off_peak | 756.9069 | 0 | 100 | 9.57 | 0 | 90.43 | 439.1598 | 0
5290 | 883.76 | 456.026 | 30.6 | 90.4836 | 90.4836 | 0 | 0 | 0.05172 | 0.05172 | 0 | 0 | 0 | 74.3903 | 793.3281 | 0 | 0.05921 | 5.3892 | 0 | 0 | 260.8746 | 90.4836 | off_peak | 793.2764 | 0 | 100 | 10.24 | 0 | 89.76 | 487.6366 | 0
5291 | 832.89 | 776.309 | 30.9 | 153.8636 | 153.8636 | 0 | 0 | 0.0033404 | 0.0033404 | 0 | 0 | 0 | 74.3934 | 679.0298 | 0 | 0.05921 | 5.4578 | 0 | 0 | 260.8746 | 153.8636 | off_peak | 679.0264 | 0 | 100 | 18.47 | 0 | 81.53 | 839.7523 | 0
5292 | 910.17 | 827.631 | 31 | 163.9752 | 163.9752 | 0 | 0 | 0.00021574 | 0.00021574 | 0 | 0 | 0 | 74.3936 | 746.195 | 0 | 0.05921 | 5.6337 | 0 | 0 | 260.8746 | 163.9752 | off_peak | 746.1948 | 0 | 100 | 18.02 | 0 | 81.98 | 923.7912 | 0
5293 | 849.44 | 929.2 | 31 | 184.0987 | 184.0987 | 0 | 0 | 0 | 0 | 62.63 | 62.63 | 0 | 7.4394 | 602.7113 | 0 | 0.088511 | 5.7839 | 62.63 | 0 | 193.9204 | 246.7287 | on_peak | 602.7113 |  |  | 21.67 | 7.37 | 70.95 | 1427.0541 | 0
5294 | 853.22 | 890.789 | 30.9 | 176.5534 | 176.5534 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 676.6666 | 0 | 0.088511 | 6.1073 | 0 | 0 | 193.9204 | 176.5534 | on_peak | 676.6666 |  |  | 20.69 | 0 | 79.31 | 1078.2561 | 0
5295 | 909.56 | 784.805 | 30.8 | 155.6047 | 155.6047 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 753.9553 | 0 | 0.088511 | 6.5181 | 0 | 0 | 193.9204 | 155.6047 | on_peak | 753.9553 |  |  | 17.11 | 0 | 82.89 | 1014.2502 | 0
5296 | 824.62 | 642.923 | 30.5 | 127.6141 | 127.6141 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 697.0059 | 0 | 0.088511 | 7.0128 | 0 | 0 | 193.9204 | 127.6141 | on_peak | 697.0059 |  |  | 15.48 | 0 | 84.52 | 894.9346 | 0
5297 | 828.74 | 454.416 | 30.2 | 90.2966 | 90.2966 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 738.4434 | 0 | 0.088511 | 7.5576 | 0 | 0 | 193.9204 | 90.2966 | on_peak | 738.4434 |  |  | 10.9 | 0 | 89.1 | 682.4244 | 0
5298 | 830.23 | 247.078 | 29.9 | 49.1507 | 49.1507 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 781.0793 | 0 | 0.088511 | 8.0717 | 0 | 0 | 193.9204 | 49.1507 | on_peak | 781.0793 |  |  | 5.92 | 0 | 94.08 | 396.7298 | 0
5299 | 828.55 | 50.5145 | 29.7 | 10.0561 | 10.0561 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 818.4939 | 0 | 0.088511 | 8.3748 | 0 | 0 | 193.9204 | 10.0561 | on_peak | 818.4939 |  |  | 1.21 | 0 | 98.79 | 84.2184 | 0
5300 | 803.79 | 0 | 29.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 803.79 | 0 | 0.088511 | 8.8082 | 0 | 0 | 193.9204 | 0 | on_peak | 803.79 |  |  | 0 | 0 | 100 | 0 | 0
5301 | 855.62 | 0 | 29.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 855.62 | 0 | 0.088511 | 9.1995 | 0 | 0 | 193.9204 | 0 | on_peak | 855.62 |  |  | 0 | 0 | 100 | 0 | 0
5302 | 794.93 | 0 | 29.3 | 0 | 0 | 0 | 0 | 8.7263 | 8.7263 | 0 | 0 | 0 | 15.6021 | 803.6563 | 0 | 0.05921 | 9.121 | 0 | 0 | 193.9204 | 0 | off_peak | 794.93 | 0 | 100 | 0 | 0 | 100 | 0 | 0
5303 | 843.4 | 0 | 29.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15.6021 | 843.4 | 0 | 0.05921 | 8.926 | 0 | 0 | 193.9204 | 0 | off_peak | 843.4 |  |  | 0 | 0 | 100 | 0 | 0
5304 | 837.94 | 0 | 29.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15.6021 | 837.94 | 0 | 0.05921 | 8.8664 | 0 | 0 | 193.9204 | 0 | off_peak | 837.94 |  |  | 0 | 0 | 100 | 0 | 0
5305 | 742.54 | 0 | 29 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15.6021 | 742.54 | 0 | 0.05921 | 8.8825 | 0 | 0 | 193.9204 | 0 | off_peak | 742.54 |  |  | 0 | 0 | 100 | 0 | 0
5306 | 696.67 | 0 | 29 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15.6021 | 696.67 | 0 | 0.05921 | 8.6763 | 0 | 0 | 193.9204 | 0 | off_peak | 696.67 |  |  | 0 | 0 | 100 | 0 | 0
5307 | 644.74 | 0 | 28.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15.6021 | 644.74 | 0 | 0.05921 | 8.3125 | 0 | 0 | 193.9204 | 0 | off_peak | 644.74 |  |  | 0 | 0 | 100 | 0 | 0
5308 | 628.93 | 0 | 28.8 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 27.2003 | 641.3289 | 0 | 0.05921 | 7.6488 | 0 | 0 | 193.9204 | 0 | off_peak | 628.93 | 0 | 100 | 0 | 0 | 100 | 0 | 0
5309 | 628.32 | 0 | 28.7 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 38.7984 | 640.7189 | 0 | 0.05921 | 6.9316 | 0 | 0 | 193.9204 | 0 | off_peak | 628.32 | 0 | 100 | 0 | 0 | 100 | 0 | 0
5310 | 699.2 | 0 | 28.8 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 50.3966 | 711.5989 | 0 | 0.05921 | 6.3634 | 0 | 0 | 193.9204 | 0 | off_peak | 699.2 | 0 | 100 | 0 | 0 | 100 | 0 | 0
5311 | 745.89 | 79.5752 | 29.2 | 15.8703 | 3.4714 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 0 | 61.9947 | 742.4186 | 0 | 0.05921 | 5.9317 | 0 | 0 | 205.5185 | 3.4714 | off_peak | 742.4186 | 100 | 0 | 0.47 | 0 | 99.53 | 20.5912 | 0
5312 | 768.67 | 278.374 | 29.6 | 55.4372 | 55.4372 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 73.5928 | 725.6317 | 0 | 0.05921 | 5.6056 | 0 | 0 | 205.5185 | 55.4372 | off_peak | 713.2328 | 0 | 100 | 7.21 | 0 | 92.79 | 310.7578 | 0
5313 | 837.69 | 487.652 | 29.9 | 97.0076 | 96.2068 | 0 | 0.80079 | 0.80079 | 0 | 0 | 0 | 0 | 74.3419 | 741.4832 | 0 | 0.05921 | 5.3336 | 0 | 0 | 206.2676 | 96.2068 | off_peak | 741.4832 | 100 | 0 | 11.48 | 0 | 88.52 | 513.13 | 0
5314 | 859.29 | 673.496 | 30.3 | 133.7808 | 133.7808 | 0 | 0 | 0.05172 | 0.05172 | 0 | 0 | 0 | 74.3903 | 725.561 | 0 | 0.05921 | 5.1815 | 0 | 0 | 206.2676 | 133.7808 | off_peak | 725.5092 | 0 | 100 | 15.57 | 0 | 84.43 | 693.1862 | 0
5315 | 858.96 | 817.856 | 30.6 | 162.277 | 162.277 | 0 | 0 | 0.0033404 | 0.0033404 | 0 | 0 | 0 | 74.3934 | 696.6863 | 0 | 0.05921 | 5.2861 | 0 | 0 | 206.2676 | 162.277 | off_peak | 696.683 | 0 | 100 | 18.89 | 0 | 81.11 | 857.8078 | 0
5316 | 865.14 | 909.41 | 30.8 | 180.3104 | 180.3104 | 0 | 0 | 0.00021574 | 0.00021574 | 0 | 0 | 0 | 74.3936 | 684.8299 | 0 | 0.05921 | 5.5559 | 0 | 0 | 206.2676 | 180.3104 | off_peak | 684.8296 | 0 | 100 | 20.84 | 0 | 79.16 | 1001.7862 | 0
5317 | 829.3 | 935.806 | 30.9 | 185.4757 | 185.4757 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 643.8243 | 0 | 0.088511 | 5.7652 | 0 | 0 | 206.2676 | 185.4757 | on_peak | 643.8243 |  |  | 22.37 | 0 | 77.63 | 1069.2969 | 0
5318 | 929 | 897.617 | 30.9 | 177.9067 | 177.9067 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 751.0933 | 0 | 0.088511 | 5.9908 | 0 | 0 | 206.2676 | 177.9067 | on_peak | 751.0933 |  |  | 19.15 | 0 | 80.85 | 1065.7953 | 0
5319 | 881.73 | 799.632 | 30.8 | 158.5445 | 158.5445 | 0 | 0 | 0 | 0 | 62.63 | 62.63 | 0 | 7.4394 | 660.5555 | 0 | 0.088511 | 6.3834 | 0 | 0 | 206.2676 | 158.5445 | on_peak | 660.5555 |  |  | 17.98 | 7.1 | 74.92 | 1012.0459 | 0
5320 | 866.14 | 647.912 | 30.6 | 128.5571 | 128.5571 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 737.5829 | 0 | 0.088511 | 6.9569 | 0 | 0 | 206.2676 | 128.5571 | on_peak | 737.5829 |  |  | 14.84 | 0 | 85.16 | 894.3577 | 0
5321 | 838.39 | 456.743 | 30.4 | 90.6924 | 90.6924 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 747.6976 | 0 | 0.088511 | 7.4956 | 0 | 0 | 206.2676 | 90.6924 | on_peak | 747.6976 |  |  | 10.82 | 0 | 89.18 | 679.7921 | 0
5322 | 869.69 | 230.723 | 30 | 45.8804 | 45.8804 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 823.8096 | 0 | 0.088511 | 7.7495 | 0 | 0 | 206.2676 | 45.8804 | on_peak | 823.8096 |  |  | 5.28 | 0 | 94.72 | 355.5517 | 0
5323 | 809.18 | 39.3419 | 29.7 | 7.8319 | 7.8319 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 801.3481 | 0 | 0.088511 | 8.3428 | 0 | 0 | 206.2676 | 7.8319 | on_peak | 801.3481 |  |  | 0.97 | 0 | 99.03 | 65.3406 | 0
5324 | 871.94 | 0 | 29.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 871.94 | 0 | 0.088511 | 8.6804 | 0 | 0 | 206.2676 | 0 | on_peak | 871.94 |  |  | 0 | 0 | 100 | 0 | 0
5325 | 842.7 | 0 | 29.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 842.7 | 0 | 0.088511 | 8.9415 | 0 | 0 | 206.2676 | 0 | on_peak | 842.7 |  |  | 0 | 0 | 100 | 0 | 0
5326 | 812.32 | 0 | 29.1 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 19.0375 | 824.7189 | 0 | 0.05921 | 9.271 | 0 | 0 | 206.2676 | 0 | off_peak | 812.32 | 0 | 100 | 0 | 0 | 100 | 0 | 0
5327 | 831.6 | 0 | 29 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19.0375 | 831.6 | 0 | 0.05921 | 9.0779 | 0 | 0 | 206.2676 | 0 | off_peak | 831.6 |  |  | 0 | 0 | 100 | 0 | 0
5328 | 791.62 | 0 | 28.9 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 30.6357 | 804.0189 | 0 | 0.05921 | 8.5373 | 0 | 0 | 206.2676 | 0 | off_peak | 791.62 | 0 | 100 | 0 | 0 | 100 | 0 | 0
5329 | 709.34 | 0 | 28.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30.6357 | 709.34 | 0 | 0.05921 | 8.3582 | 0 | 0 | 206.2676 | 0 | off_peak | 709.34 |  |  | 0 | 0 | 100 | 0 | 0
5330 | 640.66 | 0 | 28.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30.6357 | 640.66 | 0 | 0.05921 | 8.0811 | 0 | 0 | 206.2676 | 0 | off_peak | 640.66 |  |  | 0 | 0 | 100 | 0 | 0
5331 | 606.71 | 0 | 28.6 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 42.2338 | 619.1089 | 0 | 0.05921 | 7.6097 | 0 | 0 | 206.2676 | 0 | off_peak | 606.71 | 0 | 100 | 0 | 0 | 100 | 0 | 0
5332 | 568.95 | 0 | 28.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 42.2338 | 568.95 | 0 | 0.05921 | 7.1219 | 0 | 0 | 206.2676 | 0 | off_peak | 568.95 |  |  | 0 | 0 | 100 | 0 | 0
5333 | 587.01 | 0 | 28.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 42.2338 | 587.01 | 0 | 0.05921 | 6.5854 | 0 | 0 | 206.2676 | 0 | off_peak | 587.01 |  |  | 0 | 0 | 100 | 0 | 0
5334 | 689.67 | 0 | 28.7 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 53.832 | 702.0689 | 0 | 0.05921 | 5.9626 | 0 | 0 | 206.2676 | 0 | off_peak | 689.67 | 0 | 100 | 0 | 0 | 100 | 0 | 0
5335 | 743.9 | 77.6051 | 29.1 | 15.4831 | 3.0841 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 0 | 65.4301 | 740.8159 | 0 | 0.05921 | 5.5002 | 0 | 0 | 217.8657 | 3.0841 | off_peak | 740.8159 | 100 | 0 | 0.41 | 0 | 99.59 | 16.9635 | 0
5336 | 836.18 | 275.222 | 29.5 | 54.8296 | 54.8296 | 0 | 0 | 8.9635 | 8.9635 | 0 | 0 | 0 | 73.8147 | 790.314 | 0 | 0.05921 | 5.206 | 0 | 0 | 217.8657 | 54.8296 | off_peak | 781.3504 | 0 | 100 | 6.56 | 0 | 93.44 | 285.4401 | 0
5337 | 873.73 | 484.554 | 29.8 | 96.4266 | 96.4266 | 0 | 0 | 0.57892 | 0.57892 | 0 | 0 | 0 | 74.3563 | 777.8823 | 0 | 0.05921 | 5.0016 | 0 | 0 | 217.8657 | 96.4266 | off_peak | 777.3034 | 0 | 100 | 11.04 | 0 | 88.96 | 482.2895 | 0
5338 | 882.64 | 422.381 | 30 | 83.9926 | 83.9926 | 0 | 0 | 0.03739 | 0.03739 | 0 | 0 | 0 | 74.3912 | 798.6848 | 0 | 0.05921 | 4.9368 | 0 | 0 | 217.8657 | 83.9926 | off_peak | 798.6474 | 0 | 100 | 9.52 | 0 | 90.48 | 414.6584 | 0
5339 | 855.01 | 644.242 | 30.3 | 127.9698 | 127.9698 | 0 | 0 | 0.0024148 | 0.0024148 | 0 | 0 | 0 | 74.3935 | 727.0426 | 0 | 0.05921 | 5.0632 | 0 | 0 | 217.8657 | 127.9698 | off_peak | 727.0402 | 0 | 100 | 14.97 | 0 | 85.03 | 647.9379 | 0
5340 | 930.4 | 835.741 | 30.4 | 165.9476 | 165.9476 | 0 | 0 | 0.00015596 | 0.00015596 | 0 | 0 | 0 | 74.3936 | 764.4526 | 0 | 0.05921 | 5.3013 | 0 | 0 | 217.8657 | 165.9476 | off_peak | 764.4524 | 0 | 100 | 17.84 | 0 | 82.16 | 879.7355 | 0
5341 | 829.33 | 892.975 | 30.5 | 177.2471 | 177.2471 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 652.0829 | 0 | 0.088511 | 5.4246 | 0 | 0 | 217.8657 | 177.2471 | on_peak | 652.0829 |  |  | 21.37 | 0 | 78.63 | 961.4987 | 0
5342 | 908.29 | 897.304 | 30.5 | 178.1063 | 178.1063 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 730.1837 | 0 | 0.088511 | 5.741 | 0 | 0 | 217.8657 | 178.1063 | on_peak | 730.1837 |  |  | 19.61 | 0 | 80.39 | 1022.5034 | 0
5343 | 865.76 | 797.516 | 30.4 | 158.3575 | 158.3575 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 707.4025 | 0 | 0.088511 | 6.1707 | 0 | 0 | 217.8657 | 158.3575 | on_peak | 707.4025 |  |  | 18.29 | 0 | 81.71 | 977.1826 | 0
5344 | 833.16 | 641.995 | 30.2 | 127.5703 | 127.5703 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 705.5897 | 0 | 0.088511 | 6.7287 | 0 | 0 | 217.8657 | 127.5703 | on_peak | 705.5897 |  |  | 15.31 | 0 | 84.69 | 858.377 | 0
5345 | 832.81 | 415.47 | 30 | 82.6183 | 82.6183 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 750.1917 | 0 | 0.088511 | 7.2396 | 0 | 0 | 217.8657 | 82.6183 | on_peak | 750.1917 |  |  | 9.92 | 0 | 90.08 | 598.1272 | 0
5346 | 833.19 | 238.909 | 29.6 | 47.5779 | 47.5779 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 785.6121 | 0 | 0.088511 | 7.7839 | 0 | 0 | 217.8657 | 47.5779 | on_peak | 785.6121 |  |  | 5.71 | 0 | 94.29 | 370.3408 | 0
5347 | 846.41 | 43.6259 | 29.3 | 8.6975 | 8.6975 | 0 | 0 | 0 | 0 | 62.63 | 62.63 | 0 | 7.4394 | 775.0825 | 0 | 0.088511 | 8.1568 | 0 | 0 | 217.8657 | 8.6975 | on_peak | 775.0825 |  |  | 1.03 | 7.4 | 91.57 | 70.9436 | 0
5348 | 822.79 | 0 | 29 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 822.79 | 0 | 0.088511 | 8.5748 | 0 | 0 | 217.8657 | 0 | on_peak | 822.79 |  |  | 0 | 0 | 100 | 0 | 0
5349 | 788.48 | 0 | 28.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 788.48 | 0 | 0.088511 | 8.8249 | 0 | 0 | 217.8657 | 0 | on_peak | 788.48 |  |  | 0 | 0 | 100 | 0 | 0
5350 | 809.33 | 0 | 28.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 809.33 | 0 | 0.05921 | 9.0755 | 0 | 0 | 217.8657 | 0 | off_peak | 809.33 |  |  | 0 | 0 | 100 | 0 | 0
5351 | 791.04 | 0 | 28.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 791.04 | 0 | 0.05921 | 9.3334 | 0 | 0 | 217.8657 | 0 | off_peak | 791.04 |  |  | 0 | 0 | 100 | 0 | 0
5352 | 751.13 | 0 | 28.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 751.13 | 0 | 0.05921 | 9.4119 | 0 | 0 | 217.8657 | 0 | off_peak | 751.13 |  |  | 0 | 0 | 100 | 0 | 0
5353 | 679.84 | 0 | 28.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 679.84 | 0 | 0.05921 | 9.3472 | 0 | 0 | 217.8657 | 0 | off_peak | 679.84 |  |  | 0 | 0 | 100 | 0 | 0
5354 | 573.79 | 0 | 28.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 573.79 | 0 | 0.05921 | 9.0466 | 0 | 0 | 217.8657 | 0 | off_peak | 573.79 |  |  | 0 | 0 | 100 | 0 | 0
5355 | 594.8 | 0 | 28.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 594.8 | 0 | 0.05921 | 8.4917 | 0 | 0 | 217.8657 | 0 | off_peak | 594.8 |  |  | 0 | 0 | 100 | 0 | 0
5356 | 591.06 | 0 | 28.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 591.06 | 0 | 0.05921 | 7.8082 | 0 | 0 | 217.8657 | 0 | off_peak | 591.06 |  |  | 0 | 0 | 100 | 0 | 0
5357 | 627.88 | 0 | 28.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 627.88 | 0 | 0.05921 | 7.2604 | 0 | 0 | 217.8657 | 0 | off_peak | 627.88 |  |  | 0 | 0 | 100 | 0 | 0
5358 | 697.79 | 0 | 28.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 697.79 | 0 | 0.05921 | 6.677 | 0 | 0 | 217.8657 | 0 | off_peak | 697.79 |  |  | 0 | 0 | 100 | 0 | 0
5359 | 705.97 | 48.8132 | 29 | 9.7423 | 9.7423 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 19.0375 | 708.6266 | 0 | 0.05921 | 6.2178 | 0 | 0 | 217.8657 | 9.7423 | off_peak | 696.2277 | 0 | 100 | 1.38 | 0 | 98.62 | 60.5758 | 0
5360 | 756.86 | 13.3 | 29.4 | 2.6506 | 0 | 0 | 2.6506 | 2.6506 | 0 | 0 | 0 | 0 | 21.5169 | 756.86 | 0 | 0.05921 | 5.8376 | 0 | 0 | 220.3451 | 0 | off_peak | 756.86 | 100 | 0 | 0 | 0 | 100 | 0 | 0
5361 | 839.47 | 120.316 | 29.7 | 23.9518 | 23.9518 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21.5169 | 815.5182 | 0 | 0.05921 | 5.5766 | 0 | 0 | 220.3451 | 23.9518 | off_peak | 815.5182 |  |  | 2.85 | 0 | 97.15 | 133.5702 | 0
5362 | 768.85 | 344.536 | 30 | 68.5127 | 68.5127 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21.5169 | 700.3373 | 0 | 0.05921 | 5.3685 | 0 | 0 | 220.3451 | 68.5127 | off_peak | 700.3373 |  |  | 8.91 | 0 | 91.09 | 367.8111 | 0
5363 | 847.94 | 243.541 | 30.3 | 48.3761 | 48.3761 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21.5169 | 799.5639 | 0 | 0.05921 | 5.2698 | 0 | 0 | 220.3451 | 48.3761 | off_peak | 799.5639 |  |  | 5.71 | 0 | 94.29 | 254.9309 | 0
5364 | 791.01 | 393.579 | 30.5 | 78.1217 | 78.1217 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21.5169 | 712.8883 | 0 | 0.05921 | 5.2757 | 0 | 0 | 220.3451 | 78.1217 | off_peak | 712.8883 |  |  | 9.88 | 0 | 90.12 | 412.1495 | 0
5365 | 760.4 | 708.693 | 30.5 | 140.6688 | 140.6688 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21.5169 | 619.7312 | 0 | 0.05921 | 5.3396 | 0 | 0 | 220.3451 | 140.6688 | off_peak | 619.7312 |  |  | 18.5 | 0 | 81.5 | 751.1188 | 0
5366 | 777.5 | 739.369 | 30.5 | 146.7577 | 146.7577 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21.5169 | 630.7423 | 0 | 0.05921 | 5.7169 | 0 | 0 | 220.3451 | 146.7577 | off_peak | 630.7423 |  |  | 18.88 | 0 | 81.12 | 839.0034 | 0
5367 | 743.47 | 680.759 | 30.4 | 135.1738 | 135.1738 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21.5169 | 608.2962 | 0 | 0.05921 | 6.1709 | 0 | 0 | 220.3451 | 135.1738 | off_peak | 608.2962 |  |  | 18.18 | 0 | 81.82 | 834.1465 | 0
5368 | 774.87 | 588.193 | 30.2 | 116.8794 | 116.8794 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21.5169 | 657.9906 | 0 | 0.05921 | 6.7541 | 0 | 0 | 220.3451 | 116.8794 | off_peak | 657.9906 |  |  | 15.08 | 0 | 84.92 | 789.4112 | 0
5369 | 744.69 | 311.873 | 29.8 | 62.063 | 62.063 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21.5169 | 682.627 | 0 | 0.05921 | 7.3215 | 0 | 0 | 220.3451 | 62.063 | off_peak | 682.627 |  |  | 8.33 | 0 | 91.67 | 454.3944 | 0
5370 | 673.61 | 188.72 | 29.3 | 37.6242 | 37.6242 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21.5169 | 635.9858 | 0 | 0.05921 | 7.7948 | 0 | 0 | 220.3451 | 37.6242 | off_peak | 635.9858 |  |  | 5.59 | 0 | 94.41 | 293.2727 | 0
5371 | 607.67 | 51.6548 | 29.1 | 10.3057 | 10.3057 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21.5169 | 597.3643 | 0 | 0.05921 | 8.2495 | 0 | 0 | 220.3451 | 10.3057 | off_peak | 597.3643 |  |  | 1.7 | 0 | 98.3 | 85.017 | 0
5372 | 611.21 | 0 | 28.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21.5169 | 611.21 | 0 | 0.05921 | 8.6153 | 0 | 0 | 220.3451 | 0 | off_peak | 611.21 |  |  | 0 | 0 | 100 | 0 | 0
5373 | 575.83 | 0 | 28.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21.5169 | 575.83 | 0 | 0.05921 | 8.8285 | 0 | 0 | 220.3451 | 0 | off_peak | 575.83 |  |  | 0 | 0 | 100 | 0 | 0
5374 | 603.19 | 0 | 28.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21.5169 | 603.19 | 0 | 0.05921 | 9.0178 | 0 | 0 | 220.3451 | 0 | off_peak | 603.19 |  |  | 0 | 0 | 100 | 0 | 0
5375 | 586.71 | 0 | 28.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21.5169 | 586.71 | 0 | 0.05921 | 9.2863 | 0 | 0 | 220.3451 | 0 | off_peak | 586.71 |  |  | 0 | 0 | 100 | 0 | 0
5376 | 565.19 | 0 | 28.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21.5169 | 565.19 | 0 | 0.05921 | 9.3149 | 0 | 0 | 220.3451 | 0 | off_peak | 565.19 |  |  | 0 | 0 | 100 | 0 | 0
5377 | 594.72 | 0 | 28.1 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 33.1151 | 607.1189 | 0 | 0.05921 | 8.9503 | 0 | 0 | 220.3451 | 0 | off_peak | 594.72 | 0 | 100 | 0 | 0 | 100 | 0 | 0
5378 | 562.95 | 0 | 28 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 33.1151 | 562.95 | 0 | 0.05921 | 8.66 | 0 | 0 | 220.3451 | 0 | off_peak | 562.95 |  |  | 0 | 0 | 100 | 0 | 0
5379 | 595.26 | 0 | 27.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 33.1151 | 595.26 | 0 | 0.05921 | 8.2627 | 0 | 0 | 220.3451 | 0 | off_peak | 595.26 |  |  | 0 | 0 | 100 | 0 | 0
5380 | 552.52 | 0 | 27.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 33.1151 | 552.52 | 0 | 0.05921 | 7.7919 | 0 | 0 | 220.3451 | 0 | off_peak | 552.52 |  |  | 0 | 0 | 100 | 0 | 0
5381 | 595.12 | 0 | 27.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 33.1151 | 595.12 | 0 | 0.05921 | 7.168 | 0 | 0 | 220.3451 | 0 | off_peak | 595.12 |  |  | 0 | 0 | 100 | 0 | 0
5382 | 617.97 | 0 | 28.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 33.1151 | 617.97 | 0 | 0.05921 | 6.5936 | 0 | 0 | 220.3451 | 0 | off_peak | 617.97 |  |  | 0 | 0 | 100 | 0 | 0
5383 | 651.79 | 71.9521 | 28.5 | 14.3867 | 14.3867 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 33.1151 | 637.4033 | 0 | 0.05921 | 6.0678 | 0 | 0 | 220.3451 | 14.3867 | off_peak | 637.4033 |  |  | 2.21 | 0 | 97.79 | 87.2952 | 0
5384 | 706.59 | 267.199 | 28.9 | 53.3481 | 40.9492 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 0 | 44.7132 | 665.6408 | 0 | 0.05921 | 5.6961 | 0 | 0 | 231.9433 | 40.9492 | off_peak | 665.6408 | 100 | 0 | 5.8 | 0 | 94.2 | 233.2494 | 0
5385 | 735.49 | 463.567 | 29.3 | 92.4192 | 92.4192 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 44.7132 | 643.0708 | 0 | 0.05921 | 5.4443 | 0 | 0 | 231.9433 | 92.4192 | off_peak | 643.0708 |  |  | 12.57 | 0 | 87.43 | 503.1583 | 0
5386 | 738.34 | 655.569 | 29.7 | 130.5065 | 130.5065 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 44.7132 | 607.8335 | 0 | 0.05921 | 5.285 | 0 | 0 | 231.9433 | 130.5065 | off_peak | 607.8335 |  |  | 17.68 | 0 | 82.32 | 689.7269 | 0
5387 | 705.95 | 809.712 | 29.9 | 161.0743 | 161.0743 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 44.7132 | 544.8757 | 0 | 0.05921 | 5.1736 | 0 | 0 | 231.9433 | 161.0743 | off_peak | 544.8757 |  |  | 22.82 | 0 | 77.18 | 833.3277 | 0
5388 | 731.61 | 900.346 | 30.1 | 178.9727 | 178.9727 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 44.7132 | 552.6373 | 0 | 0.05921 | 5.1352 | 0 | 0 | 231.9433 | 178.9727 | off_peak | 552.6373 |  |  | 24.46 | 0 | 75.54 | 919.0617 | 0
5389 | 715.28 | 807.315 | 30.1 | 160.4798 | 160.4798 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 44.7132 | 554.8002 | 0 | 0.05921 | 5.1364 | 0 | 0 | 231.9433 | 160.4798 | off_peak | 554.8002 |  |  | 22.44 | 0 | 77.56 | 824.2882 | 0
5390 | 707.07 | 830.059 | 30 | 165.0614 | 165.0614 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 44.7132 | 542.0086 | 0 | 0.05921 | 5.4608 | 0 | 0 | 231.9433 | 165.0614 | off_peak | 542.0086 |  |  | 23.34 | 0 | 76.66 | 901.3593 | 0
5391 | 723.52 | 791.395 | 29.9 | 157.4305 | 157.4305 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 56.3114 | 578.4884 | 0 | 0.05921 | 5.9287 | 0 | 0 | 231.9433 | 157.4305 | off_peak | 566.0895 | 0 | 100 | 21.76 | 0 | 78.24 | 933.3549 | 0
5392 | 696.51 | 639.371 | 29.8 | 127.2353 | 127.2353 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 56.3114 | 569.2747 | 0 | 0.05921 | 6.5085 | 0 | 0 | 231.9433 | 127.2353 | off_peak | 569.2747 |  |  | 18.27 | 0 | 81.73 | 828.1173 | 0
5393 | 691.62 | 447.881 | 29.6 | 89.194 | 89.194 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 56.3114 | 602.426 | 0 | 0.05921 | 7.0567 | 0 | 0 | 231.9433 | 89.194 | off_peak | 602.426 |  |  | 12.9 | 0 | 87.1 | 629.417 | 0
5394 | 644.09 | 237.414 | 29.3 | 47.3321 | 47.3321 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 56.3114 | 596.7579 | 0 | 0.05921 | 7.5259 | 0 | 0 | 231.9433 | 47.3321 | off_peak | 596.7579 |  |  | 7.35 | 0 | 92.65 | 356.2182 | 0
5395 | 608.21 | 51.0324 | 29.2 | 10.1778 | 10.1778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 56.3114 | 598.0322 | 0 | 0.05921 | 7.9036 | 0 | 0 | 231.9433 | 10.1778 | off_peak | 598.0322 |  |  | 1.67 | 0 | 98.33 | 80.4411 | 0
5396 | 580.3 | 0 | 29.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 56.3114 | 580.3 | 0 | 0.05921 | 8.3066 | 0 | 0 | 231.9433 | 0 | off_peak | 580.3 |  |  | 0 | 0 | 100 | 0 | 0
5397 | 568.89 | 0 | 29.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 56.3114 | 568.89 | 0 | 0.05921 | 8.5733 | 0 | 0 | 231.9433 | 0 | off_peak | 568.89 |  |  | 0 | 0 | 100 | 0 | 0
5398 | 587.77 | 0 | 28.9 | 0 | 0 | 0 | 0 | 6.0758 | 6.0758 | 0 | 0 | 0 | 61.9947 | 593.8458 | 0 | 0.05921 | 8.6059 | 0 | 0 | 231.9433 | 0 | off_peak | 587.77 | 0 | 100 | 0 | 0 | 100 | 0 | 0
5399 | 544.6 | 0 | 28.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 61.9947 | 544.6 | 0 | 0.05921 | 8.525 | 0 | 0 | 231.9433 | 0 | off_peak | 544.6 |  |  | 0 | 0 | 100 | 0 | 0
5400 | 565.68 | 0 | 28.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 61.9947 | 565.68 | 0 | 0.05921 | 8.4572 | 0 | 0 | 231.9433 | 0 | off_peak | 565.68 |  |  | 0 | 0 | 100 | 0 | 0
5401 | 570.59 | 0 | 28.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 61.9947 | 570.59 | 0 | 0.05921 | 8.4116 | 0 | 0 | 231.9433 | 0 | off_peak | 570.59 |  |  | 0 | 0 | 100 | 0 | 0
5402 | 584.88 | 0 | 27.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 61.9947 | 584.88 | 0 | 0.05921 | 8.1811 | 0 | 0 | 231.9433 | 0 | off_peak | 584.88 |  |  | 0 | 0 | 100 | 0 | 0
5403 | 525.58 | 0 | 27.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 61.9947 | 525.58 | 0 | 0.05921 | 7.7026 | 0 | 0 | 231.9433 | 0 | off_peak | 525.58 |  |  | 0 | 0 | 100 | 0 | 0
5404 | 557.86 | 0 | 27 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 61.9947 | 557.86 | 0 | 0.05921 | 7.256 | 0 | 0 | 231.9433 | 0 | off_peak | 557.86 |  |  | 0 | 0 | 100 | 0 | 0
5405 | 570.12 | 0 | 27 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 61.9947 | 570.12 | 0 | 0.05921 | 6.6269 | 0 | 0 | 231.9433 | 0 | off_peak | 570.12 |  |  | 0 | 0 | 100 | 0 | 0
5406 | 670.8 | 0 | 27.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 61.9947 | 670.8 | 0 | 0.05921 | 6.0144 | 0 | 0 | 231.9433 | 0 | off_peak | 670.8 |  |  | 0 | 0 | 100 | 0 | 0
5407 | 691.73 | 44.1727 | 27.5 | 8.8645 | 8.8645 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 73.5928 | 695.2645 | 0 | 0.05921 | 5.5754 | 0 | 0 | 231.9433 | 8.8645 | off_peak | 682.8655 | 0 | 100 | 1.28 | 0 | 98.72 | 49.4234 | 0
5408 | 821.02 | 252.427 | 27.9 | 50.5828 | 50.5828 | 0 | 0 | 0.80079 | 0.80079 | 0 | 0 | 0 | 74.3419 | 771.238 | 0 | 0.05921 | 5.2789 | 0 | 0 | 231.9433 | 50.5828 | off_peak | 770.4372 | 0 | 100 | 6.16 | 0 | 93.84 | 267.021 | 0
5409 | 817.97 | 472.761 | 28.2 | 94.6312 | 94.6312 | 0 | 0 | 0.05172 | 0.05172 | 0 | 0 | 0 | 74.3903 | 723.3905 | 0 | 0.05921 | 5.1335 | 0 | 0 | 231.9433 | 94.6312 | off_peak | 723.3388 | 0 | 100 | 11.57 | 0 | 88.43 | 485.7897 | 0
5410 | 847.97 | 661.823 | 28.4 | 132.3788 | 132.3754 | 0 | 0.0033404 | 0.0033404 | 0 | 0 | 0 | 0 | 74.3934 | 715.5946 | 0 | 0.05921 | 5.0691 | 0 | 0 | 231.9464 | 132.3754 | off_peak | 715.5946 | 100 | 0 | 15.61 | 0 | 84.39 | 671.02 | 0
5411 | 807.7 | 727.136 | 28.4 | 145.4428 | 145.4428 | 0 | 0 | 0.00021574 | 0.00021574 | 0 | 0 | 0 | 74.3936 | 662.2575 | 0 | 0.05921 | 5.2426 | 0 | 0 | 231.9464 | 145.4428 | off_peak | 662.2572 | 0 | 100 | 18.01 | 0 | 81.99 | 762.4978 | 0
5412 | 923.51 | 825.597 | 28.3 | 165.1973 | 165.1973 | 0 | 0 | 1.3934e-05 | 1.3934e-05 | 0 | 0 | 0 | 74.3936 | 758.3128 | 0 | 0.05921 | 5.5112 | 0 | 0 | 231.9464 | 165.1973 | off_peak | 758.3127 | 0 | 100 | 17.89 | 0 | 82.11 | 910.4281 | 0
5413 | 839.33 | 917.327 | 28.2 | 183.6188 | 183.6188 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 655.7112 | 0 | 0.088511 | 5.6505 | 0 | 0 | 231.9464 | 183.6188 | on_peak | 655.7112 |  |  | 21.88 | 0 | 78.12 | 1037.5364 | 0
5414 | 905.79 | 857.404 | 28.1 | 171.6867 | 171.6867 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 734.1033 | 0 | 0.088511 | 5.9128 | 0 | 0 | 231.9464 | 171.6867 | on_peak | 734.1033 |  |  | 18.95 | 0 | 81.05 | 1015.148 | 0
5415 | 886.76 | 781.598 | 28 | 156.5642 | 156.5642 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 730.1958 | 0 | 0.088511 | 6.2967 | 0 | 0 | 231.9464 | 156.5642 | on_peak | 730.1958 |  |  | 17.66 | 0 | 82.34 | 985.8389 | 0
5416 | 812.9 | 629.762 | 27.9 | 126.1954 | 126.1954 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 686.7046 | 0 | 0.088511 | 6.7636 | 0 | 0 | 231.9464 | 126.1954 | on_peak | 686.7046 |  |  | 15.52 | 0 | 84.48 | 853.54 | 0
5417 | 888.59 | 438.394 | 27.7 | 87.9119 | 87.9119 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 800.6781 | 0 | 0.088511 | 7.3539 | 0 | 0 | 231.9464 | 87.9119 | on_peak | 800.6781 |  |  | 9.89 | 0 | 90.11 | 646.4967 | 0
5418 | 870.27 | 229.017 | 27.6 | 45.9419 | 45.9419 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 824.3281 | 0 | 0.088511 | 7.9325 | 0 | 0 | 231.9464 | 45.9419 | on_peak | 824.3281 |  |  | 5.28 | 0 | 94.72 | 364.4349 | 0
5419 | 843.4 | 46.7174 | 27.5 | 9.3751 | 9.3751 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 834.0249 | 0 | 0.088511 | 8.2517 | 0 | 0 | 231.9464 | 9.3751 | on_peak | 834.0249 |  |  | 1.11 | 0 | 98.89 | 77.3609 | 0
5420 | 873.66 | 0 | 27.5 | 0 | 0 | 0 | 0 | 0 | 0 | 41.5752 | 41.5752 | 0 | 29.9479 | 832.0848 | 0 | 0.088511 | 8.5946 | 0 | 0 | 231.9464 | 0 | on_peak | 832.0848 |  |  | 0 | 4.76 | 95.24 | 0 | 0
5421 | 836.44 | 0 | 27.6 | 0 | 0 | 0 | 0 | 0 | 0 | 21.0548 | 21.0548 | 0 | 7.4394 | 815.3852 | 0 | 0.088511 | 8.7805 | 21.0548 | 0 | 209.4378 | 21.0548 | on_peak | 815.3852 |  |  | 0 | 2.52 | 97.48 | 184.8727 | 0
5422 | 826.97 | 0 | 27.8 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 19.0375 | 839.3689 | 0 | 0.05921 | 8.9952 | 0 | 0 | 209.4378 | 0 | off_peak | 826.97 | 0 | 100 | 0 | 0 | 100 | 0 | 0
5423 | 820.53 | 0 | 27.9 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 30.6357 | 832.9289 | 0 | 0.05921 | 9.211 | 0 | 0 | 209.4378 | 0 | off_peak | 820.53 | 0 | 100 | 0 | 0 | 100 | 0 | 0
5424 | 775.34 | 0 | 27.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30.6357 | 775.34 | 0 | 0.05921 | 9.0862 | 0 | 0 | 209.4378 | 0 | off_peak | 775.34 |  |  | 0 | 0 | 100 | 0 | 0
5425 | 721.9 | 0 | 27.9 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 42.2338 | 734.2989 | 0 | 0.05921 | 8.8964 | 0 | 0 | 209.4378 | 0 | off_peak | 721.9 | 0 | 100 | 0 | 0 | 100 | 0 | 0
5426 | 646.4 | 0 | 27.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 42.2338 | 646.4 | 0 | 0.05921 | 8.6169 | 0 | 0 | 209.4378 | 0 | off_peak | 646.4 |  |  | 0 | 0 | 100 | 0 | 0
5427 | 622.67 | 0 | 27.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 42.2338 | 622.67 | 0 | 0.05921 | 8.1499 | 0 | 0 | 209.4378 | 0 | off_peak | 622.67 |  |  | 0 | 0 | 100 | 0 | 0
5428 | 635.04 | 0 | 27.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 42.2338 | 635.04 | 0 | 0.05921 | 7.5797 | 0 | 0 | 209.4378 | 0 | off_peak | 635.04 |  |  | 0 | 0 | 100 | 0 | 0
5429 | 623.66 | 0 | 27.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 42.2338 | 623.66 | 0 | 0.05921 | 6.9449 | 0 | 0 | 209.4378 | 0 | off_peak | 623.66 |  |  | 0 | 0 | 100 | 0 | 0
5430 | 688.83 | 0 | 28.1 | 0 | 0 | 0 | 0 | 8.7263 | 8.7263 | 0 | 0 | 0 | 50.3966 | 697.5563 | 0 | 0.05921 | 6.2979 | 0 | 0 | 209.4378 | 0 | off_peak | 688.83 | 0 | 100 | 0 | 0 | 100 | 0 | 0
5431 | 747.4 | 63.7952 | 28.4 | 12.7604 | 0.36146 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 0 | 61.9947 | 747.0385 | 0 | 0.05921 | 5.8582 | 0 | 0 | 221.036 | 0.36146 | off_peak | 747.0385 | 100 | 0 | 0.05 | 0 | 99.95 | 2.1176 | 0
5432 | 794.33 | 242.723 | 28.7 | 48.4967 | 48.4967 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 73.5928 | 758.2322 | 0 | 0.05921 | 5.5041 | 0 | 0 | 221.036 | 48.4967 | off_peak | 745.8333 | 0 | 100 | 6.11 | 0 | 93.89 | 266.9308 | 0
5433 | 840.34 | 456.742 | 28.9 | 91.1917 | 91.1917 | 0 | 0 | 0.80079 | 0.80079 | 0 | 0 | 0 | 74.3419 | 749.9491 | 0 | 0.05921 | 5.2731 | 0 | 0 | 221.036 | 91.1917 | off_peak | 749.1483 | 0 | 100 | 10.85 | 0 | 89.15 | 480.8608 | 0
5434 | 858.84 | 462.325 | 29 | 92.2727 | 92.2727 | 0 | 0 | 0.05172 | 0.05172 | 0 | 0 | 0 | 74.3903 | 766.619 | 0 | 0.05921 | 5.1785 | 0 | 0 | 221.036 | 92.2727 | off_peak | 766.5673 | 0 | 100 | 10.74 | 0 | 89.26 | 477.8345 | 0
5435 | 811.21 | 188.135 | 29 | 37.5487 | 37.5487 | 0 | 0 | 0.0033404 | 0.0033404 | 0 | 0 | 0 | 74.3934 | 773.6646 | 0 | 0.05921 | 5.2889 | 0 | 0 | 221.036 | 37.5487 | off_peak | 773.6613 | 0 | 100 | 4.63 | 0 | 95.37 | 198.5901 | 0
5436 | 888.19 | 475.838 | 29 | 94.9697 | 94.9697 | 0 | 0 | 0.00021574 | 0.00021574 | 0 | 0 | 0 | 74.3936 | 793.2206 | 0 | 0.05921 | 5.5786 | 0 | 0 | 221.036 | 94.9697 | off_peak | 793.2203 | 0 | 100 | 10.69 | 0 | 89.31 | 529.8002 | 0
5437 | 865.88 | 853.631 | 29 | 170.3711 | 170.3711 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 695.5089 | 0 | 0.088511 | 5.6306 | 0 | 0 | 221.036 | 170.3711 | on_peak | 695.5089 |  |  | 19.68 | 0 | 80.32 | 959.2973 | 0
5438 | 923.43 | 420.598 | 28.9 | 83.9753 | 83.9753 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 839.4547 | 0 | 0.088511 | 5.8902 | 0 | 0 | 221.036 | 83.9753 | on_peak | 839.4547 |  |  | 9.09 | 0 | 90.91 | 494.6337 | 0
5439 | 938.04 | 507.391 | 28.8 | 101.3411 | 101.3411 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 836.6989 | 0 | 0.088511 | 6.2616 | 0 | 0 | 221.036 | 101.3411 | on_peak | 836.6989 |  |  | 10.8 | 0 | 89.2 | 634.5535 | 0
5440 | 810.47 | 639.311 | 28.7 | 127.7361 | 127.7361 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 682.7339 | 0 | 0.088511 | 6.778 | 0 | 0 | 221.036 | 127.7361 | on_peak | 682.7339 |  |  | 15.76 | 0 | 84.24 | 865.7912 | 0
5441 | 832.5 | 412.118 | 28.7 | 82.3423 | 82.3423 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 750.1577 | 0 | 0.088511 | 7.3895 | 0 | 0 | 221.036 | 82.3423 | on_peak | 750.1577 |  |  | 9.89 | 0 | 90.11 | 608.468 | 0
5442 | 828.51 | 226.539 | 28.5 | 45.2961 | 45.2961 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 783.2139 | 0 | 0.088511 | 7.8893 | 0 | 0 | 221.036 | 45.2961 | on_peak | 783.2139 |  |  | 5.47 | 0 | 94.53 | 357.355 | 0
5443 | 790.57 | 47.887 | 28.4 | 9.5784 | 9.5784 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 780.9916 | 0 | 0.088511 | 8.4489 | 0 | 0 | 221.036 | 9.5784 | on_peak | 780.9916 |  |  | 1.21 | 0 | 98.79 | 80.9272 | 0
5444 | 829.48 | 0 | 28.3 | 0 | 0 | 0 | 0 | 0 | 0 | 62.63 | 62.63 | 0 | 7.4394 | 766.85 | 0 | 0.088511 | 8.6474 | 62.63 | 0 | 154.0817 | 62.63 | on_peak | 766.85 |  |  | 0 | 7.55 | 92.45 | 541.5888 | 0
5445 | 821.18 | 0 | 28.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 821.18 | 0 | 0.088511 | 8.6274 | 0 | 0 | 154.0817 | 0 | on_peak | 821.18 |  |  | 0 | 0 | 100 | 0 | 0
5446 | 764.39 | 0 | 28.3 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 19.0375 | 776.7889 | 0 | 0.05921 | 8.6039 | 0 | 0 | 154.0817 | 0 | off_peak | 764.39 | 0 | 100 | 0 | 0 | 100 | 0 | 0
5447 | 799.73 | 0 | 28.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19.0375 | 799.73 | 0 | 0.05921 | 8.545 | 0 | 0 | 154.0817 | 0 | off_peak | 799.73 |  |  | 0 | 0 | 100 | 0 | 0
5448 | 790.62 | 0 | 28.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19.0375 | 790.62 | 0 | 0.05921 | 8.4654 | 0 | 0 | 154.0817 | 0 | off_peak | 790.62 |  |  | 0 | 0 | 100 | 0 | 0
5449 | 745.87 | 0 | 28.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19.0375 | 745.87 | 0 | 0.05921 | 8.4749 | 0 | 0 | 154.0817 | 0 | off_peak | 745.87 |  |  | 0 | 0 | 100 | 0 | 0
5450 | 659.5 | 0 | 28 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 30.6357 | 671.8989 | 0 | 0.05921 | 8.2775 | 0 | 0 | 154.0817 | 0 | off_peak | 659.5 | 0 | 100 | 0 | 0 | 100 | 0 | 0
5451 | 626.72 | 0 | 28 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 42.2338 | 639.1189 | 0 | 0.05921 | 7.8401 | 0 | 0 | 154.0817 | 0 | off_peak | 626.72 | 0 | 100 | 0 | 0 | 100 | 0 | 0
5452 | 609.08 | 0 | 28 | 0 | 0 | 0 | 0 | 8.7263 | 8.7263 | 0 | 0 | 0 | 50.3966 | 617.8063 | 0 | 0.05921 | 7.2581 | 0 | 0 | 154.0817 | 0 | off_peak | 609.08 | 0 | 100 | 0 | 0 | 100 | 0 | 0
5453 | 620.18 | 0 | 28.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50.3966 | 620.18 | 0 | 0.05921 | 6.5663 | 0 | 0 | 154.0817 | 0 | off_peak | 620.18 |  |  | 0 | 0 | 100 | 0 | 0
5454 | 712.16 | 0 | 28.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50.3966 | 712.16 | 0 | 0.05921 | 5.9398 | 0 | 0 | 154.0817 | 0 | off_peak | 712.16 |  |  | 0 | 0 | 100 | 0 | 0
5455 | 757.8 | 52.7814 | 28.5 | 10.5536 | 10.5536 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 61.9947 | 759.6454 | 0 | 0.05921 | 5.5192 | 0 | 0 | 154.0817 | 10.5536 | off_peak | 747.2464 | 0 | 100 | 1.39 | 0 | 98.61 | 58.2474 | 0
5456 | 818.02 | 227.172 | 28.9 | 45.3565 | 45.3565 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 73.5928 | 785.0625 | 0 | 0.05921 | 5.198 | 0 | 0 | 154.0817 | 45.3565 | off_peak | 772.6635 | 0 | 100 | 5.54 | 0 | 94.46 | 235.7649 | 0
5457 | 854.29 | 479.337 | 29.2 | 95.5981 | 95.5981 | 0 | 0 | 0.80079 | 0.80079 | 0 | 0 | 0 | 74.3419 | 759.4927 | 0 | 0.05921 | 5.0076 | 0 | 0 | 154.0817 | 95.5981 | off_peak | 758.6919 | 0 | 100 | 11.19 | 0 | 88.81 | 478.7145 | 0
5458 | 832.37 | 570.345 | 29.5 | 113.6238 | 113.6238 | 0 | 0 | 0.05172 | 0.05172 | 0 | 0 | 0 | 74.3903 | 718.7979 | 0 | 0.05921 | 4.9075 | 0 | 0 | 154.0817 | 113.6238 | off_peak | 718.7462 | 0 | 100 | 13.65 | 0 | 86.35 | 557.6144 | 0
5459 | 879.13 | 701.386 | 29.9 | 139.5252 | 139.5252 | 0 | 0 | 0.0033404 | 0.0033404 | 0 | 0 | 0 | 74.3934 | 739.6081 | 0 | 0.05921 | 4.9974 | 0 | 0 | 154.0817 | 139.5252 | off_peak | 739.6048 | 0 | 100 | 15.87 | 0 | 84.13 | 697.2606 | 0
5460 | 895.73 | 741.559 | 30.2 | 147.3546 | 147.3546 | 0 | 0 | 0.00021574 | 0.00021574 | 0 | 0 | 0 | 74.3936 | 748.3756 | 0 | 0.05921 | 5.2518 | 0 | 0 | 154.0817 | 147.3546 | off_peak | 748.3754 | 0 | 100 | 16.45 | 0 | 83.55 | 773.8706 | 0
5461 | 840.08 | 425.751 | 30.4 | 84.5386 | 84.5386 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 755.5414 | 0 | 0.088511 | 5.2974 | 0 | 0 | 154.0817 | 84.5386 | on_peak | 755.5414 |  |  | 10.06 | 0 | 89.94 | 447.8337 | 0
5462 | 873.59 | 465.752 | 30.5 | 92.4473 | 92.4473 | 0 | 0 | 0 | 0 | 62.63 | 62.63 | 0 | 7.4394 | 718.5127 | 0 | 0.088511 | 5.51 | 0 | 0 | 154.0817 | 92.4473 | on_peak | 718.5127 |  |  | 10.58 | 7.17 | 82.25 | 509.3885 | 0
5463 | 872.32 | 410.769 | 30.5 | 81.5337 | 81.5337 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 790.7863 | 0 | 0.088511 | 5.8605 | 0 | 0 | 154.0817 | 81.5337 | on_peak | 790.7863 |  |  | 9.35 | 0 | 90.65 | 477.829 | 0
5464 | 799.63 | 623.95 | 30.3 | 123.9391 | 123.9391 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 675.6909 | 0 | 0.088511 | 6.4511 | 0 | 0 | 154.0817 | 123.9391 | on_peak | 675.6909 |  |  | 15.5 | 0 | 84.5 | 799.5412 | 0
5465 | 810.87 | 449.864 | 29.9 | 89.4905 | 89.4905 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 721.3795 | 0 | 0.088511 | 6.9715 | 0 | 0 | 154.0817 | 89.4905 | on_peak | 721.3795 |  |  | 11.04 | 0 | 88.96 | 623.8821 | 0
5466 | 818.23 | 236.922 | 29.5 | 47.1995 | 47.1995 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 771.0305 | 0 | 0.088511 | 7.3899 | 0 | 0 | 154.0817 | 47.1995 | on_peak | 771.0305 |  |  | 5.77 | 0 | 94.23 | 348.7985 | 0
5467 | 792.26 | 47.8552 | 29.2 | 9.5442 | 9.5442 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 782.7158 | 0 | 0.088511 | 7.8463 | 0 | 0 | 154.0817 | 9.5442 | on_peak | 782.7158 |  |  | 1.2 | 0 | 98.8 | 74.8859 | 0
5468 | 827.41 | 0 | 28.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 827.41 | 0 | 0.088511 | 8.1472 | 0 | 0 | 154.0817 | 0 | on_peak | 827.41 |  |  | 0 | 0 | 100 | 0 | 0
5469 | 784.84 | 0 | 28.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 784.84 | 0 | 0.088511 | 8.029 | 0 | 0 | 154.0817 | 0 | on_peak | 784.84 |  |  | 0 | 0 | 100 | 0 | 0
5470 | 758.35 | 0 | 28.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 758.35 | 0 | 0.05921 | 7.9183 | 0 | 0 | 154.0817 | 0 | off_peak | 758.35 |  |  | 0 | 0 | 100 | 0 | 0
5471 | 806.42 | 0 | 28.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 806.42 | 0 | 0.05921 | 7.9199 | 0 | 0 | 154.0817 | 0 | off_peak | 806.42 |  |  | 0 | 0 | 100 | 0 | 0
5472 | 775.08 | 0 | 28.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 775.08 | 0 | 0.05921 | 7.8753 | 0 | 0 | 154.0817 | 0 | off_peak | 775.08 |  |  | 0 | 0 | 100 | 0 | 0
5473 | 706.22 | 0 | 28.5 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 19.0375 | 718.6189 | 0 | 0.05921 | 7.7131 | 0 | 0 | 154.0817 | 0 | off_peak | 706.22 | 0 | 100 | 0 | 0 | 100 | 0 | 0
5474 | 628.84 | 0 | 28.5 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 30.6357 | 641.2389 | 0 | 0.05921 | 7.3065 | 0 | 0 | 154.0817 | 0 | off_peak | 628.84 | 0 | 100 | 0 | 0 | 100 | 0 | 0
5475 | 609.94 | 0 | 28.4 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 42.2338 | 622.3389 | 0 | 0.05921 | 6.8551 | 0 | 0 | 154.0817 | 0 | off_peak | 609.94 | 0 | 100 | 0 | 0 | 100 | 0 | 0
5476 | 579.14 | 0 | 28.4 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 53.832 | 591.5389 | 0 | 0.05921 | 6.2966 | 0 | 0 | 154.0817 | 0 | off_peak | 579.14 | 0 | 100 | 0 | 0 | 100 | 0 | 0
5477 | 594.73 | 0 | 28.4 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 65.4301 | 607.1289 | 0 | 0.05921 | 5.8115 | 0 | 0 | 154.0817 | 0 | off_peak | 594.73 | 0 | 100 | 0 | 0 | 100 | 0 | 0
5478 | 688.36 | 0 | 28.6 | 0 | 0 | 0 | 0 | 8.9635 | 8.9635 | 0 | 0 | 0 | 73.8147 | 697.3235 | 0 | 0.05921 | 5.1794 | 0 | 0 | 154.0817 | 0 | off_peak | 688.36 | 0 | 100 | 0 | 0 | 100 | 0 | 0
5479 | 745.07 | 68.8592 | 28.9 | 13.7482 | 13.1693 | 0 | 0.57892 | 0.57892 | 0 | 0 | 0 | 0 | 74.3563 | 731.9007 | 0 | 0.05921 | 4.7536 | 0 | 0 | 154.6233 | 13.1693 | off_peak | 731.9007 | 100 | 0 | 1.77 | 0 | 98.23 | 62.601 | 0
5480 | 860.47 | 264.34 | 29.3 | 52.7002 | 52.7002 | 0 | 0 | 0.03739 | 0.03739 | 0 | 0 | 0 | 74.3912 | 807.8072 | 0 | 0.05921 | 4.4784 | 0 | 0 | 154.6233 | 52.7002 | off_peak | 807.7698 | 0 | 100 | 6.12 | 0 | 93.88 | 236.0144 | 0
5481 | 913.02 | 475.231 | 29.5 | 94.6753 | 94.6753 | 0 | 0 | 0.0024148 | 0.0024148 | 0 | 0 | 0 | 74.3935 | 818.3471 | 0 | 0.05921 | 4.3343 | 0 | 0 | 154.6233 | 94.6753 | off_peak | 818.3447 | 0 | 100 | 10.37 | 0 | 89.63 | 410.3509 | 0
5482 | 894.15 | 558.789 | 29.7 | 111.2402 | 111.2402 | 0 | 0 | 0.00015596 | 0.00015596 | 0 | 0 | 0 | 74.3936 | 782.91 | 0 | 0.05921 | 4.2753 | 0 | 0 | 154.6233 | 111.2402 | off_peak | 782.9098 | 0 | 100 | 12.44 | 0 | 87.56 | 475.5839 | 0
5483 | 852.98 | 674.118 | 29.9 | 134.1009 | 134.1009 | 0 | 0 | 1.0073e-05 | 1.0073e-05 | 0 | 0 | 0 | 74.3936 | 718.8791 | 0 | 0.05921 | 4.4528 | 0 | 0 | 154.6233 | 134.1009 | off_peak | 718.8791 | 0 | 100 | 15.72 | 0 | 84.28 | 597.1181 | 0
5484 | 948.93 | 790.449 | 30.1 | 157.1271 | 157.1271 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 791.8029 | 0 | 0.05921 | 4.8004 | 0 | 0 | 154.6233 | 157.1271 | off_peak | 791.8029 |  |  | 16.56 | 0 | 83.44 | 754.274 | 0
5485 | 915.7 | 717.883 | 30.1 | 142.7023 | 142.7023 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 772.9977 | 0 | 0.088511 | 4.8613 | 0 | 0 | 154.6233 | 142.7023 | on_peak | 772.9977 |  |  | 15.58 | 0 | 84.42 | 693.7179 | 0
5486 | 928.17 | 873.261 | 30.1 | 173.5887 | 173.5887 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 754.5813 | 0 | 0.088511 | 4.9721 | 0 | 0 | 154.6233 | 173.5887 | on_peak | 754.5813 |  |  | 18.7 | 0 | 81.3 | 863.0931 | 0
5487 | 972.24 | 788.157 | 30 | 156.729 | 156.729 | 0 | 0 | 0 | 0 | 62.63 | 62.63 | 0 | 7.4394 | 752.881 | 0 | 0.088511 | 5.1737 | 0 | 0 | 154.6233 | 156.729 | on_peak | 752.881 |  |  | 16.12 | 6.44 | 77.44 | 810.8655 | 0
5488 | 900.47 | 634.129 | 29.9 | 126.146 | 126.146 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 774.324 | 0 | 0.088511 | 5.6746 | 0 | 0 | 154.6233 | 126.146 | on_peak | 774.324 |  |  | 14.01 | 0 | 85.99 | 715.827 | 0
5489 | 873.75 | 432.429 | 29.7 | 86.0852 | 86.0852 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 787.6648 | 0 | 0.088511 | 6.4077 | 0 | 0 | 154.6233 | 86.0852 | on_peak | 787.6648 |  |  | 9.85 | 0 | 90.15 | 551.6042 | 0
5490 | 890.09 | 139.662 | 29.5 | 27.8234 | 27.8234 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 862.2666 | 0 | 0.088511 | 7.0286 | 0 | 0 | 154.6233 | 27.8234 | on_peak | 862.2666 |  |  | 3.13 | 0 | 96.87 | 195.5596 | 0
5491 | 817.23 | 18.05 | 29.3 | 3.5985 | 3.5985 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 813.6315 | 0 | 0.088511 | 7.7496 | 0 | 0 | 154.6233 | 3.5985 | on_peak | 813.6315 |  |  | 0.44 | 0 | 99.56 | 27.8872 | 0
5492 | 893.97 | 0 | 29.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 893.97 | 0 | 0.088511 | 7.9341 | 0 | 0 | 154.6233 | 0 | on_peak | 893.97 |  |  | 0 | 0 | 100 | 0 | 0
5493 | 868.36 | 0 | 29.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 868.36 | 0 | 0.088511 | 7.8248 | 0 | 0 | 154.6233 | 0 | on_peak | 868.36 |  |  | 0 | 0 | 100 | 0 | 0
5494 | 802.27 | 0 | 29.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 802.27 | 0 | 0.05921 | 7.5385 | 0 | 0 | 154.6233 | 0 | off_peak | 802.27 |  |  | 0 | 0 | 100 | 0 | 0
5495 | 835.78 | 0 | 29 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 835.78 | 0 | 0.05921 | 7.3968 | 0 | 0 | 154.6233 | 0 | off_peak | 835.78 |  |  | 0 | 0 | 100 | 0 | 0
5496 | 795.45 | 0 | 28.8 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 19.0375 | 807.8489 | 0 | 0.05921 | 7.1678 | 0 | 0 | 154.6233 | 0 | off_peak | 795.45 | 0 | 100 | 0 | 0 | 100 | 0 | 0
5497 | 756.98 | 0 | 28.7 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 30.6357 | 769.3789 | 0 | 0.05921 | 7.0782 | 0 | 0 | 154.6233 | 0 | off_peak | 756.98 | 0 | 100 | 0 | 0 | 100 | 0 | 0
5498 | 711.05 | 0 | 28.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30.6357 | 711.05 | 0 | 0.05921 | 6.974 | 0 | 0 | 154.6233 | 0 | off_peak | 711.05 |  |  | 0 | 0 | 100 | 0 | 0
5499 | 621.96 | 0 | 28.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30.6357 | 621.96 | 0 | 0.05921 | 6.6098 | 0 | 0 | 154.6233 | 0 | off_peak | 621.96 |  |  | 0 | 0 | 100 | 0 | 0
5500 | 657.38 | 0 | 28.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30.6357 | 657.38 | 0 | 0.05921 | 6.1081 | 0 | 0 | 154.6233 | 0 | off_peak | 657.38 |  |  | 0 | 0 | 100 | 0 | 0
5501 | 641.62 | 0 | 28.5 | 0 | 0 | 0 | 0 | 8.7263 | 8.7263 | 0 | 0 | 0 | 38.7984 | 650.3463 | 0 | 0.05921 | 5.4833 | 0 | 0 | 154.6233 | 0 | off_peak | 641.62 | 0 | 100 | 0 | 0 | 100 | 0 | 0
5502 | 741.98 | 0 | 28.6 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 50.3966 | 754.3789 | 0 | 0.05921 | 5.001 | 0 | 0 | 154.6233 | 0 | off_peak | 741.98 | 0 | 100 | 0 | 0 | 100 | 0 | 0
5503 | 824.71 | 67.4604 | 29.1 | 13.4591 | 1.0602 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 0 | 61.9947 | 823.6498 | 0 | 0.05921 | 4.6145 | 0 | 0 | 166.2214 | 1.0602 | off_peak | 823.6498 | 100 | 0 | 0.13 | 0 | 99.87 | 4.8921 | 0
5504 | 839.56 | 264.347 | 29.5 | 52.6631 | 52.6631 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 73.5928 | 799.2959 | 0 | 0.05921 | 4.3323 | 0 | 0 | 166.2214 | 52.6631 | off_peak | 786.8969 | 0 | 100 | 6.27 | 0 | 93.73 | 228.1526 | 0
5505 | 918.22 | 472.933 | 29.9 | 94.0796 | 94.0796 | 0 | 0 | 0.80079 | 0.80079 | 0 | 0 | 0 | 74.3419 | 824.9412 | 0 | 0.05921 | 4.1422 | 0 | 0 | 166.2214 | 94.0796 | off_peak | 824.1404 | 0 | 100 | 10.25 | 0 | 89.75 | 389.6943 | 0
5506 | 880.15 | 617.057 | 30.2 | 122.6149 | 122.6149 | 0 | 0 | 0.05172 | 0.05172 | 0 | 0 | 0 | 74.3903 | 757.5868 | 0 | 0.05921 | 4.098 | 0 | 0 | 166.2214 | 122.6149 | off_peak | 757.5351 | 0 | 100 | 13.93 | 0 | 86.07 | 502.4766 | 0
5507 | 844.63 | 503.91 | 30.5 | 100.0213 | 100.0213 | 0 | 0 | 0.0033404 | 0.0033404 | 0 | 0 | 0 | 74.3934 | 744.612 | 0 | 0.05921 | 4.3275 | 0 | 0 | 166.2214 | 100.0213 | off_peak | 744.6087 | 0 | 100 | 11.84 | 0 | 88.16 | 432.8442 | 0
5508 | 924.29 | 612.166 | 30.6 | 121.4645 | 121.4645 | 0 | 0 | 0.00021574 | 0.00021574 | 0 | 0 | 0 | 74.3936 | 802.8257 | 0 | 0.05921 | 4.6471 | 0 | 0 | 166.2214 | 121.4645 | off_peak | 802.8255 | 0 | 100 | 13.14 | 0 | 86.86 | 564.457 | 0
5509 | 875.66 | 671.396 | 30.7 | 133.1678 | 133.1678 | 0 | 0 | 0 | 0 | 52.5697 | 52.5697 | 0 | 18.1943 | 689.9225 | 0 | 0.088511 | 4.7578 | 0 | 0 | 166.2214 | 133.1678 | on_peak | 689.9225 |  |  | 15.21 | 6 | 78.79 | 633.5915 | 0
5510 | 908.86 | 876.127 | 30.6 | 173.839 | 173.839 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18.1943 | 735.021 | 0 | 0.088511 | 4.8945 | 0 | 0 | 166.2214 | 173.839 | on_peak | 735.021 |  |  | 19.13 | 0 | 80.87 | 850.8485 | 0
5511 | 953.14 | 225.888 | 30.5 | 44.8366 | 44.8366 | 0 | 0 | 0 | 0 | 10.0603 | 10.0603 | 0 | 7.4394 | 898.2431 | 0 | 0.088511 | 5.1283 | 0 | 0 | 166.2214 | 44.8366 | on_peak | 898.2431 |  |  | 4.7 | 1.06 | 94.24 | 229.9346 | 0
5512 | 869.78 | 588.183 | 30.4 | 116.7916 | 116.7916 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 752.9884 | 0 | 0.088511 | 5.4097 | 0 | 0 | 166.2214 | 116.7916 | on_peak | 752.9884 |  |  | 13.43 | 0 | 86.57 | 631.8079 | 0
5513 | 872.38 | 397.852 | 30.1 | 79.0859 | 79.0859 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 793.2941 | 0 | 0.088511 | 5.8204 | 0 | 0 | 166.2214 | 79.0859 | on_peak | 793.2941 |  |  | 9.07 | 0 | 90.93 | 460.3129 | 0
5514 | 896.18 | 224.629 | 29.8 | 44.7014 | 44.7014 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 851.4786 | 0 | 0.088511 | 6.1756 | 0 | 0 | 166.2214 | 44.7014 | on_peak | 851.4786 |  |  | 4.99 | 0 | 95.01 | 276.0557 | 0
5515 | 842.31 | 20.9654 | 29.5 | 4.1767 | 4.1767 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 838.1333 | 0 | 0.088511 | 6.7045 | 0 | 0 | 166.2214 | 4.1767 | on_peak | 838.1333 |  |  | 0.5 | 0 | 99.5 | 28.003 | 0
5516 | 855.96 | 0 | 29.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 855.96 | 0 | 0.088511 | 7.0274 | 0 | 0 | 166.2214 | 0 | on_peak | 855.96 |  |  | 0 | 0 | 100 | 0 | 0
5517 | 879.64 | 0 | 29 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 879.64 | 0 | 0.088511 | 7.2654 | 0 | 0 | 166.2214 | 0 | on_peak | 879.64 |  |  | 0 | 0 | 100 | 0 | 0
5518 | 812.34 | 0 | 28.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 812.34 | 0 | 0.05921 | 7.4918 | 0 | 0 | 166.2214 | 0 | off_peak | 812.34 |  |  | 0 | 0 | 100 | 0 | 0
5519 | 835.44 | 0 | 28.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 835.44 | 0 | 0.05921 | 7.5046 | 0 | 0 | 166.2214 | 0 | off_peak | 835.44 |  |  | 0 | 0 | 100 | 0 | 0
5520 | 805.32 | 0 | 28.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 805.32 | 0 | 0.05921 | 7.3859 | 0 | 0 | 166.2214 | 0 | off_peak | 805.32 |  |  | 0 | 0 | 100 | 0 | 0
5521 | 714 | 0 | 28.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 714 | 0 | 0.05921 | 7.3166 | 0 | 0 | 166.2214 | 0 | off_peak | 714 |  |  | 0 | 0 | 100 | 0 | 0
5522 | 607.72 | 0 | 28.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 607.72 | 0 | 0.05921 | 7.2098 | 0 | 0 | 166.2214 | 0 | off_peak | 607.72 |  |  | 0 | 0 | 100 | 0 | 0
5523 | 611.31 | 0 | 28.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 611.31 | 0 | 0.05921 | 6.8545 | 0 | 0 | 166.2214 | 0 | off_peak | 611.31 |  |  | 0 | 0 | 100 | 0 | 0
5524 | 622.87 | 0 | 28.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 622.87 | 0 | 0.05921 | 6.4108 | 0 | 0 | 166.2214 | 0 | off_peak | 622.87 |  |  | 0 | 0 | 100 | 0 | 0
5525 | 635.54 | 0 | 28.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 635.54 | 0 | 0.05921 | 5.7987 | 0 | 0 | 166.2214 | 0 | off_peak | 635.54 |  |  | 0 | 0 | 100 | 0 | 0
5526 | 699.62 | 0 | 28.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 699.62 | 0 | 0.05921 | 5.2883 | 0 | 0 | 166.2214 | 0 | off_peak | 699.62 |  |  | 0 | 0 | 100 | 0 | 0
5527 | 763.43 | 46.0441 | 28.9 | 9.193 | 9.193 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 754.237 | 0 | 0.05921 | 4.9156 | 0 | 0 | 166.2214 | 9.193 | off_peak | 754.237 |  |  | 1.2 | 0 | 98.8 | 45.1889 | 0
5528 | 753.31 | 238.699 | 29.4 | 47.5709 | 47.5709 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 19.0375 | 718.138 | 0 | 0.05921 | 4.6381 | 0 | 0 | 166.2214 | 47.5709 | off_peak | 705.7391 | 0 | 100 | 6.31 | 0 | 93.69 | 220.6367 | 0
5529 | 788.44 | 217.703 | 29.7 | 43.3389 | 43.3389 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19.0375 | 745.1011 | 0 | 0.05921 | 4.3873 | 0 | 0 | 166.2214 | 43.3389 | off_peak | 745.1011 |  |  | 5.5 | 0 | 94.5 | 190.1427 | 0
5530 | 787.86 | 147.687 | 30.1 | 29.3575 | 29.3575 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19.0375 | 758.5025 | 0 | 0.05921 | 4.2673 | 0 | 0 | 166.2214 | 29.3575 | off_peak | 758.5025 |  |  | 3.73 | 0 | 96.27 | 125.2762 | 0
5531 | 758.63 | 176.572 | 30.4 | 35.0607 | 35.0607 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19.0375 | 723.5693 | 0 | 0.05921 | 4.2504 | 0 | 0 | 166.2214 | 35.0607 | off_peak | 723.5693 |  |  | 4.62 | 0 | 95.38 | 149.0222 | 0
5532 | 821.31 | 416.725 | 30.7 | 82.6552 | 82.6552 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19.0375 | 738.6548 | 0 | 0.05921 | 4.3366 | 0 | 0 | 166.2214 | 82.6552 | off_peak | 738.6548 |  |  | 10.06 | 0 | 89.94 | 358.4412 | 0
5533 | 746.07 | 851.472 | 30.9 | 168.7608 | 168.7608 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19.0375 | 577.3092 | 0 | 0.05921 | 4.4627 | 0 | 0 | 166.2214 | 168.7608 | off_peak | 577.3092 |  |  | 22.62 | 0 | 77.38 | 753.1331 | 0
5534 | 715.21 | 750.569 | 30.9 | 148.762 | 148.762 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19.0375 | 566.448 | 0 | 0.05921 | 4.7341 | 0 | 0 | 166.2214 | 148.762 | off_peak | 566.448 |  |  | 20.8 | 0 | 79.2 | 704.2587 | 0
5535 | 727.59 | 201.444 | 30.9 | 39.926 | 39.926 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19.0375 | 687.664 | 0 | 0.05921 | 5.1238 | 0 | 0 | 166.2214 | 39.926 | off_peak | 687.664 |  |  | 5.49 | 0 | 94.51 | 204.5745 | 0
5536 | 744.77 | 22.8 | 30.7 | 4.5223 | 0 | 0 | 4.5223 | 4.5223 | 0 | 0 | 0 | 0 | 23.2677 | 744.77 | 0 | 0.05921 | 5.7546 | 0 | 0 | 170.4516 | 0 | off_peak | 744.77 | 100 | 0 | 0 | 0 | 100 | 0 | 0
5537 | 733.79 | 84.2078 | 30.4 | 16.7206 | 16.7206 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 23.2677 | 717.0694 | 0 | 0.05921 | 6.3604 | 0 | 0 | 170.4516 | 16.7206 | off_peak | 717.0694 |  |  | 2.28 | 0 | 97.72 | 106.3499 | 0
5538 | 643.84 | 55.0103 | 29.9 | 10.9431 | 10.9431 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 23.2677 | 632.8969 | 0 | 0.05921 | 6.738 | 0 | 0 | 170.4516 | 10.9431 | off_peak | 632.8969 |  |  | 1.7 | 0 | 98.3 | 73.7347 | 0
5539 | 630.79 | 21.8838 | 29.6 | 4.3581 | 0 | 0 | 4.3581 | 4.3581 | 0 | 0 | 0 | 0 | 27.3443 | 630.79 | 0 | 0.05921 | 7.1478 | 0 | 0 | 174.5282 | 0 | off_peak | 630.79 | 100 | 0 | 0 | 0 | 100 | 0 | 0
5540 | 600.92 | 0 | 29 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27.3443 | 600.92 | 0 | 0.05921 | 7.6276 | 0 | 0 | 174.5282 | 0 | off_peak | 600.92 |  |  | 0 | 0 | 100 | 0 | 0
5541 | 571.67 | 0 | 28.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27.3443 | 571.67 | 0 | 0.05921 | 8.0352 | 0 | 0 | 174.5282 | 0 | off_peak | 571.67 |  |  | 0 | 0 | 100 | 0 | 0
5542 | 569.22 | 0 | 28.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27.3443 | 569.22 | 0 | 0.05921 | 8.2424 | 0 | 0 | 174.5282 | 0 | off_peak | 569.22 |  |  | 0 | 0 | 100 | 0 | 0
5543 | 592.7 | 0 | 28.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27.3443 | 592.7 | 0 | 0.05921 | 8.2908 | 0 | 0 | 174.5282 | 0 | off_peak | 592.7 |  |  | 0 | 0 | 100 | 0 | 0
5544 | 585.25 | 0 | 28.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27.3443 | 585.25 | 0 | 0.05921 | 8.0229 | 0 | 0 | 174.5282 | 0 | off_peak | 585.25 |  |  | 0 | 0 | 100 | 0 | 0
5545 | 568.92 | 0 | 28.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27.3443 | 568.92 | 0 | 0.05921 | 7.9049 | 0 | 0 | 174.5282 | 0 | off_peak | 568.92 |  |  | 0 | 0 | 100 | 0 | 0
5546 | 587.55 | 0 | 28.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27.3443 | 587.55 | 0 | 0.05921 | 7.7691 | 0 | 0 | 174.5282 | 0 | off_peak | 587.55 |  |  | 0 | 0 | 100 | 0 | 0
5547 | 572.22 | 0 | 28.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27.3443 | 572.22 | 0 | 0.05921 | 7.2745 | 0 | 0 | 174.5282 | 0 | off_peak | 572.22 |  |  | 0 | 0 | 100 | 0 | 0
5548 | 584.48 | 0 | 28 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27.3443 | 584.48 | 0 | 0.05921 | 6.7221 | 0 | 0 | 174.5282 | 0 | off_peak | 584.48 |  |  | 0 | 0 | 100 | 0 | 0
5549 | 599.48 | 0 | 27.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27.3443 | 599.48 | 0 | 0.05921 | 6.1142 | 0 | 0 | 174.5282 | 0 | off_peak | 599.48 |  |  | 0 | 0 | 100 | 0 | 0
5550 | 658.9 | 0 | 28 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27.3443 | 658.9 | 0 | 0.05921 | 5.6009 | 0 | 0 | 174.5282 | 0 | off_peak | 658.9 |  |  | 0 | 0 | 100 | 0 | 0
5551 | 711.36 | 37.2692 | 28.3 | 7.4574 | 0 | 0 | 7.4574 | 7.4574 | 0 | 0 | 0 | 0 | 34.32 | 711.36 | 0 | 0.05921 | 5.1619 | 0 | 0 | 181.5039 | 0 | off_peak | 711.36 | 100 | 0 | 0 | 0 | 100 | 0 | 0
5552 | 748.49 | 86.9221 | 28.7 | 17.3673 | 17.3673 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 34.32 | 731.1227 | 0 | 0.05921 | 4.8489 | 0 | 0 | 181.5039 | 17.3673 | off_peak | 731.1227 |  |  | 2.32 | 0 | 97.68 | 84.2127 | 0
5553 | 755.96 | 402.277 | 29.2 | 80.2294 | 80.2294 | 0 | 0 | 9.6767 | 9.6767 | 0 | 0 | 0 | 43.3718 | 685.4073 | 0 | 0.05921 | 4.6117 | 0 | 0 | 181.5039 | 80.2294 | off_peak | 675.7306 | 0 | 100 | 10.61 | 0 | 89.39 | 369.996 | 0
5554 | 729.46 | 585.295 | 29.8 | 116.4742 | 116.4742 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 43.3718 | 612.9858 | 0 | 0.05921 | 4.4751 | 0 | 0 | 181.5039 | 116.4742 | off_peak | 612.9858 |  |  | 15.97 | 0 | 84.03 | 521.2326 | 0
5555 | 725.02 | 451.504 | 30.4 | 89.6522 | 89.6522 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 43.3718 | 635.3678 | 0 | 0.05921 | 4.4511 | 0 | 0 | 181.5039 | 89.6522 | off_peak | 635.3678 |  |  | 12.37 | 0 | 87.63 | 399.0468 | 0
5556 | 729.86 | 108.3 | 30.9 | 21.4649 | 9.066 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 0 | 54.9699 | 720.794 | 0 | 0.05921 | 4.5015 | 0 | 0 | 193.1021 | 9.066 | off_peak | 720.794 | 100 | 0 | 1.24 | 0 | 98.76 | 40.8107 | 0
5557 | 704.83 | 196.321 | 31.3 | 38.8534 | 38.8534 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 54.9699 | 665.9766 | 0 | 0.05921 | 4.5752 | 0 | 0 | 193.1021 | 38.8534 | off_peak | 665.9766 |  |  | 5.51 | 0 | 94.49 | 177.7618 | 0
5558 | 703.77 | 201.616 | 31.4 | 39.8866 | 39.8866 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 54.9699 | 663.8834 | 0 | 0.05921 | 4.8034 | 0 | 0 | 193.1021 | 39.8866 | off_peak | 663.8834 |  |  | 5.67 | 0 | 94.33 | 191.59 | 0
5559 | 724.07 | 264.812 | 31.5 | 52.3696 | 52.3696 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 66.5681 | 684.0993 | 0 | 0.05921 | 5.1746 | 0 | 0 | 193.1021 | 52.3696 | off_peak | 671.7004 | 0 | 100 | 7.23 | 0 | 92.77 | 270.9905 | 0
5560 | 733.73 | 573.761 | 31.3 | 113.5515 | 113.5515 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 66.5681 | 620.1785 | 0 | 0.05921 | 5.7609 | 0 | 0 | 193.1021 | 113.5515 | off_peak | 620.1785 |  |  | 15.48 | 0 | 84.52 | 654.1556 | 0
5561 | 708.87 | 192.311 | 31 | 38.1018 | 38.1018 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 66.5681 | 670.7682 | 0 | 0.05921 | 6.2295 | 0 | 0 | 193.1021 | 38.1018 | off_peak | 670.7682 |  |  | 5.38 | 0 | 94.62 | 237.3566 | 0
5562 | 653.22 | 211.854 | 30.4 | 42.0665 | 42.0665 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 66.5681 | 611.1535 | 0 | 0.05921 | 6.4889 | 0 | 0 | 193.1021 | 42.0665 | off_peak | 611.1535 |  |  | 6.44 | 0 | 93.56 | 272.9641 | 0
5563 | 608.26 | 36.1024 | 30 | 7.1791 | 7.1791 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 66.5681 | 601.0809 | 0 | 0.05921 | 6.751 | 0 | 0 | 193.1021 | 7.1791 | off_peak | 601.0809 |  |  | 1.18 | 0 | 98.82 | 48.4664 | 0
5564 | 595.99 | 0 | 29.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 66.5681 | 595.99 | 0 | 0.05921 | 6.97 | 0 | 0 | 193.1021 | 0 | off_peak | 595.99 |  |  | 0 | 0 | 100 | 0 | 0
5565 | 579.25 | 0 | 29.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 66.5681 | 579.25 | 0 | 0.05921 | 7.0431 | 0 | 0 | 193.1021 | 0 | off_peak | 579.25 |  |  | 0 | 0 | 100 | 0 | 0
5566 | 612.23 | 0 | 28.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 66.5681 | 612.23 | 0 | 0.05921 | 7.198 | 0 | 0 | 193.1021 | 0 | off_peak | 612.23 |  |  | 0 | 0 | 100 | 0 | 0
5567 | 600.95 | 0 | 28.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 66.5681 | 600.95 | 0 | 0.05921 | 7.2891 | 0 | 0 | 193.1021 | 0 | off_peak | 600.95 |  |  | 0 | 0 | 100 | 0 | 0
5568 | 611.96 | 0 | 28.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 66.5681 | 611.96 | 0 | 0.05921 | 7.2999 | 0 | 0 | 193.1021 | 0 | off_peak | 611.96 |  |  | 0 | 0 | 100 | 0 | 0
5569 | 608.47 | 0 | 28.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 66.5681 | 608.47 | 0 | 0.05921 | 7.3974 | 0 | 0 | 193.1021 | 0 | off_peak | 608.47 |  |  | 0 | 0 | 100 | 0 | 0
5570 | 598.98 | 0 | 28.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 66.5681 | 598.98 | 0 | 0.05921 | 7.3981 | 0 | 0 | 193.1021 | 0 | off_peak | 598.98 |  |  | 0 | 0 | 100 | 0 | 0
5571 | 633.97 | 0 | 28.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 66.5681 | 633.97 | 0 | 0.05921 | 7.0577 | 0 | 0 | 193.1021 | 0 | off_peak | 633.97 |  |  | 0 | 0 | 100 | 0 | 0
5572 | 583.16 | 0 | 28 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 66.5681 | 583.16 | 0 | 0.05921 | 6.5921 | 0 | 0 | 193.1021 | 0 | off_peak | 583.16 |  |  | 0 | 0 | 100 | 0 | 0
5573 | 631.72 | 0 | 27.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 66.5681 | 631.72 | 0 | 0.05921 | 6.1149 | 0 | 0 | 193.1021 | 0 | off_peak | 631.72 |  |  | 0 | 0 | 100 | 0 | 0
5574 | 753.78 | 0 | 28.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 66.5681 | 753.78 | 0 | 0.05921 | 0 | 0 | 0 | 193.1021 | 0 | off_peak | 753.78 |  |  | 0 | 0 | 100 | 0 | 0
5575 | 771.99 | 39.1664 | 28.7 | 7.8256 | 0 | 0 | 7.8256 | 7.8256 | 0 | 0 | 0 | 0 | 73.8882 | 771.99 | 0 | 0.05921 | 0 | 0 | 0 | 200.4222 | 0 | off_peak | 771.99 | 100 | 0 | 0 | 0 | 100 | 0 | 0
5576 | 825.67 | 174.935 | 29.2 | 34.8887 | 34.8887 | 0 | 0 | 0.50542 | 0.50542 | 0 | 0 | 0 | 74.361 | 791.2867 | 0 | 0.05921 | 0 | 0 | 0 | 200.4222 | 34.8887 | off_peak | 790.7813 | 0 | 100 | 4.23 | 0 | 95.77 | 0 | 0
5577 | 907.7 | 445.804 | 29.6 | 88.7804 | 88.7804 | 0 | 0 | 0.032643 | 0.032643 | 0 | 0 | 0 | 74.3915 | 818.9523 | 0 | 0.05921 | 0 | 0 | 0 | 200.4222 | 88.7804 | off_peak | 818.9196 | 0 | 100 | 9.78 | 0 | 90.22 | 0 | 0
5578 | 937.46 | 637.928 | 30.1 | 126.8087 | 126.8087 | 0 | 0 | 0.0021083 | 0.0021083 | 0 | 0 | 0 | 74.3935 | 810.6534 | 0 | 0.05921 | 0 | 0 | 0 | 200.4222 | 126.8087 | off_peak | 810.6513 | 0 | 100 | 13.53 | 0 | 86.47 | 0 | 0
5579 | 877.2 | 780.808 | 30.4 | 155.0399 | 155.0399 | 0 | 0 | 0.00013616 | 0.00013616 | 0 | 0 | 0 | 74.3936 | 722.1602 | 0 | 0.05921 | 0 | 0 | 0 | 200.4222 | 155.0399 | off_peak | 722.1601 | 0 | 100 | 17.67 | 0 | 82.33 | 0 | 0
5580 | 929.37 | 630.987 | 30.7 | 125.1529 | 125.1529 | 0 | 0 | 8.7942e-06 | 8.7942e-06 | 0 | 0 | 0 | 74.3936 | 804.2171 | 0 | 0.05921 | 0 | 0 | 0 | 200.4222 | 125.1529 | off_peak | 804.2171 | 0 | 100 | 13.47 | 0 | 86.53 | 0 | 0
5581 | 865.59 | 761.977 | 30.9 | 151.023 | 151.023 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 714.567 | 0 | 0.088511 | 0 | 0 | 0 | 200.4222 | 151.023 | on_peak | 714.567 |  |  | 17.45 | 0 | 82.55 | 0 | 0
5582 | 902.12 | 833.828 | 30.9 | 165.2638 | 165.2638 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 736.8562 | 0 | 0.088511 | 0 | 0 | 0 | 200.4222 | 165.2638 | on_peak | 736.8562 |  |  | 18.32 | 0 | 81.68 | 0 | 0
5583 | 946.15 | 730.953 | 30.8 | 144.9274 | 144.9274 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 801.2226 | 0 | 0.088511 | 0 | 0 | 0 | 200.4222 | 144.9274 | on_peak | 801.2226 |  |  | 15.32 | 0 | 84.68 | 0 | 0
5584 | 894.5 | 535.734 | 30.7 | 106.26 | 106.26 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 788.24 | 0 | 0.088511 | 0 | 0 | 0 | 200.4222 | 106.26 | on_peak | 788.24 |  |  | 11.88 | 0 | 88.12 | 0 | 0
5585 | 889.1 | 261.674 | 30.4 | 51.9589 | 51.9589 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 837.1411 | 0 | 0.088511 | 0 | 0 | 0 | 200.4222 | 51.9589 | on_peak | 837.1411 |  |  | 5.84 | 0 | 94.16 | 0 | 0
5586 | 887.99 | 152.44 | 30 | 30.3135 | 30.3135 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 857.6765 | 0 | 0.088511 | 0 | 0 | 0 | 200.4222 | 30.3135 | on_peak | 857.6765 |  |  | 3.41 | 0 | 96.59 | 0 | 0
5587 | 832.15 | 25.0266 | 29.7 | 4.9821 | 4.9821 | 0 | 0 | 0 | 0 | 60.893 | 60.893 | 0 | 9.2962 | 766.2748 | 0 | 0.088511 | 0 | 0 | 0 | 200.4222 | 4.9821 | on_peak | 766.2748 |  |  | 0.6 | 7.32 | 92.08 | 0 | 0
5588 | 899.98 | 0 | 29.4 | 0 | 0 | 0 | 0 | 0 | 0 | 1.7369 | 1.7369 | 0 | 7.4394 | 898.2431 | 0 | 0.088511 | 0 | 0 | 0 | 200.4222 | 0 | on_peak | 898.2431 |  |  | 0 | 0.19 | 99.81 | 0 | 0
5589 | 871.84 | 0 | 29.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 871.84 | 0 | 0.088511 | 0 | 0 | 0 | 200.4222 | 0 | on_peak | 871.84 |  |  | 0 | 0 | 100 | 0 | 0
5590 | 869.1 | 0 | 29.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 869.1 | 0 | 0.05921 | 0 | 0 | 0 | 200.4222 | 0 | off_peak | 869.1 |  |  | 0 | 0 | 100 | 0 | 0
5591 | 847.59 | 0 | 29.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 847.59 | 0 | 0.05921 | 0 | 0 | 0 | 200.4222 | 0 | off_peak | 847.59 |  |  | 0 | 0 | 100 | 0 | 0
5592 | 799.36 | 0 | 29 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 19.0375 | 811.7589 | 0 | 0.05921 | 0 | 0 | 0 | 200.4222 | 0 | off_peak | 799.36 | 0 | 100 | 0 | 0 | 100 | 0 | 0
5593 | 752.98 | 0 | 28.9 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 30.6357 | 765.3789 | 0 | 0.05921 | 0 | 0 | 0 | 200.4222 | 0 | off_peak | 752.98 | 0 | 100 | 0 | 0 | 100 | 0 | 0
5594 | 643.07 | 0 | 28.9 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 42.2338 | 655.4689 | 0 | 0.05921 | 0 | 0 | 0 | 200.4222 | 0 | off_peak | 643.07 | 0 | 100 | 0 | 0 | 100 | 0 | 0
5595 | 611.43 | 0 | 28.8 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 53.832 | 623.8289 | 0 | 0.05921 | 0 | 0 | 0 | 200.4222 | 0 | off_peak | 611.43 | 0 | 100 | 0 | 0 | 100 | 0 | 0
5596 | 624.09 | 0 | 28.8 | 0 | 0 | 0 | 0 | 8.7263 | 8.7263 | 0 | 0 | 0 | 61.9947 | 632.8163 | 0 | 0.05921 | 0 | 0 | 0 | 200.4222 | 0 | off_peak | 624.09 | 0 | 100 | 0 | 0 | 100 | 0 | 0
5597 | 643.72 | 0 | 28.9 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 73.5928 | 656.1189 | 0 | 0.05921 | 0 | 0 | 0 | 200.4222 | 0 | off_peak | 643.72 | 0 | 100 | 0 | 0 | 100 | 0 | 0
5598 | 724.31 | 0 | 29 | 0 | 0 | 0 | 0 | 0.80079 | 0.80079 | 0 | 0 | 0 | 74.3419 | 725.1108 | 0 | 0.05921 | 5.9781 | 0 | 0 | 200.4222 | 0 | off_peak | 724.31 | 0 | 100 | 0 | 0 | 100 | 0 | 0
5599 | 806.95 | 60.2634 | 29.4 | 12.01 | 12.01 | 0 | 0 | 0.05172 | 0.05172 | 0 | 0 | 0 | 74.3903 | 794.9917 | 0 | 0.05921 | 5.4827 | 0 | 0 | 200.4222 | 12.01 | off_peak | 794.94 | 0 | 100 | 1.49 | 0 | 98.51 | 65.8477 | 0
5600 | 844.24 | 239.027 | 29.8 | 47.5666 | 47.5666 | 0 | 0 | 0.0033404 | 0.0033404 | 0 | 0 | 0 | 74.3934 | 796.6768 | 0 | 0.05921 | 5.1795 | 0 | 0 | 200.4222 | 47.5666 | off_peak | 796.6734 | 0 | 100 | 5.63 | 0 | 94.37 | 246.3713 | 0
5601 | 892.61 | 403.3 | 30.1 | 80.1688 | 80.1688 | 0 | 0 | 0.00021574 | 0.00021574 | 0 | 0 | 0 | 74.3936 | 812.4414 | 0 | 0.05921 | 4.9898 | 0 | 0 | 200.4222 | 80.1688 | off_peak | 812.4412 | 0 | 100 | 8.98 | 0 | 91.02 | 400.0284 | 0
5602 | 919 | 527.938 | 30.4 | 104.8292 | 104.8292 | 0 | 0 | 1.3934e-05 | 1.3934e-05 | 0 | 0 | 0 | 74.3936 | 814.1708 | 0 | 0.05921 | 4.8992 | 0 | 0 | 200.4222 | 104.8292 | off_peak | 814.1708 | 0 | 100 | 11.41 | 0 | 88.59 | 513.5806 | 0
5603 | 852.9 | 795.268 | 30.7 | 157.7372 | 157.7372 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 695.1628 | 0 | 0.05921 | 5.0702 | 0 | 0 | 200.4222 | 157.7372 | off_peak | 695.1628 |  |  | 18.49 | 0 | 81.51 | 799.7567 | 0
5604 | 955.43 | 861.407 | 30.9 | 170.7299 | 170.7299 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 784.7001 | 0 | 0.05921 | 5.3666 | 0 | 0 | 200.4222 | 170.7299 | off_peak | 784.7001 |  |  | 17.87 | 0 | 82.13 | 916.2385 | 0
5605 | 893.79 | 816.178 | 30.9 | 161.7656 | 161.7656 | 0 | 0 | 0 | 0 | 18.0148 | 18.0148 | 0 | 55.135 | 714.0096 | 0 | 0.088511 | 5.4776 | 0 | 0 | 200.4222 | 161.7656 | on_peak | 714.0096 |  |  | 18.1 | 2.02 | 79.89 | 886.0837 | 0
5606 | 939.42 | 875.823 | 30.9 | 173.5872 | 173.5872 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 55.135 | 765.8328 | 0 | 0.088511 | 5.5884 | 0 | 0 | 200.4222 | 173.5872 | on_peak | 765.8328 |  |  | 18.48 | 0 | 81.52 | 970.0681 | 0
5607 | 907.83 | 763.941 | 30.7 | 151.5236 | 151.5236 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 55.135 | 756.3064 | 0 | 0.088511 | 5.8602 | 0 | 0 | 200.4222 | 151.5236 | on_peak | 756.3064 |  |  | 16.69 | 0 | 83.31 | 887.9527 | 0
5608 | 874.11 | 619.89 | 30.5 | 123.0423 | 123.0423 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 55.135 | 751.0677 | 0 | 0.088511 | 6.1984 | 0 | 0 | 200.4222 | 123.0423 | on_peak | 751.0677 |  |  | 14.08 | 0 | 85.92 | 762.6683 | 0
5609 | 908.34 | 416.032 | 30.2 | 82.6694 | 82.6694 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 55.135 | 825.6706 | 0 | 0.088511 | 6.6042 | 0 | 0 | 200.4222 | 82.6694 | on_peak | 825.6706 |  |  | 9.1 | 0 | 90.9 | 545.9637 | 0
5610 | 922.14 | 192.042 | 29.9 | 38.2025 | 38.2025 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 55.135 | 883.9375 | 0 | 0.088511 | 7.1484 | 0 | 0 | 200.4222 | 38.2025 | on_peak | 883.9375 |  |  | 4.14 | 0 | 95.86 | 273.0857 | 0
5611 | 929.74 | 27.2295 | 29.8 | 5.4187 | 5.4187 | 0 | 0 | 0 | 0 | 26.0783 | 26.0783 | 0 | 27.2562 | 898.2431 | 0 | 0.088511 | 7.6132 | 0 | 0 | 200.4222 | 5.4187 | on_peak | 898.2431 |  |  | 0.58 | 2.8 | 96.61 | 41.2533 | 0
5612 | 916.78 | 0 | 29.6 | 0 | 0 | 0 | 0 | 0 | 0 | 18.5369 | 18.5369 | 0 | 7.4394 | 898.2431 | 0 | 0.088511 | 8.0291 | 0 | 0 | 200.4222 | 0 | on_peak | 898.2431 |  |  | 0 | 2.02 | 97.98 | 0 | 0
5613 | 881.01 | 0 | 29.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 881.01 | 0 | 0.088511 | 8.2772 | 0 | 0 | 200.4222 | 0 | on_peak | 881.01 |  |  | 0 | 0 | 100 | 0 | 0
5614 | 870.11 | 0 | 29.5 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 19.0375 | 882.5089 | 0 | 0.05921 | 8.6774 | 0 | 0 | 200.4222 | 0 | off_peak | 870.11 | 0 | 100 | 0 | 0 | 100 | 0 | 0
5615 | 895.09 | 0 | 29.4 | 0 | 0 | 0 | 0 | 3.1531 | 3.1531 | 0 | 0 | 0 | 21.9869 | 898.2431 | 0 | 0.05921 | 8.8301 | 0 | 0 | 200.4222 | 0 | off_peak | 895.09 | 0 | 100 | 0 | 0 | 100 | 0 | 0
5616 | 864.43 | 0 | 29.2 | 0 | 0 | 0 | 0 | 5.5733 | 5.5733 | 0 | 0 | 0 | 27.2003 | 870.0033 | 0 | 0.05921 | 9.0041 | 0 | 0 | 200.4222 | 0 | off_peak | 864.43 | 0 | 100 | 0 | 0 | 100 | 0 | 0
5617 | 830.42 | 0 | 29.1 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 38.7984 | 842.8189 | 0 | 0.05921 | 8.9328 | 0 | 0 | 200.4222 | 0 | off_peak | 830.42 | 0 | 100 | 0 | 0 | 100 | 0 | 0
5618 | 745.19 | 0 | 29 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 50.3966 | 757.5889 | 0 | 0.05921 | 8.6465 | 0 | 0 | 200.4222 | 0 | off_peak | 745.19 | 0 | 100 | 0 | 0 | 100 | 0 | 0
5619 | 691.91 | 0 | 28.9 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 61.9947 | 704.3089 | 0 | 0.05921 | 8.1206 | 0 | 0 | 200.4222 | 0 | off_peak | 691.91 | 0 | 100 | 0 | 0 | 100 | 0 | 0
5620 | 686.8 | 0 | 28.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 61.9947 | 686.8 | 0 | 0.05921 | 7.442 | 0 | 0 | 200.4222 | 0 | off_peak | 686.8 |  |  | 0 | 0 | 100 | 0 | 0
5621 | 679.4 | 0 | 28.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 61.9947 | 679.4 | 0 | 0.05921 | 6.6356 | 0 | 0 | 200.4222 | 0 | off_peak | 679.4 |  |  | 0 | 0 | 100 | 0 | 0
5622 | 759.29 | 0 | 28.9 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 73.5928 | 771.6889 | 0 | 0.05921 | 5.9727 | 0 | 0 | 200.4222 | 0 | off_peak | 759.29 | 0 | 100 | 0 | 0 | 100 | 0 | 0
5623 | 844.38 | 44.2166 | 29.2 | 8.8185 | 8.0177 | 0 | 0.80079 | 0.80079 | 0 | 0 | 0 | 0 | 74.3419 | 836.3623 | 0 | 0.05921 | 5.4808 | 0 | 0 | 201.1713 | 8.0177 | off_peak | 836.3623 | 100 | 0 | 0.95 | 0 | 99.05 | 43.9435 | 0
5624 | 896.05 | 235.413 | 29.6 | 46.8817 | 46.8817 | 0 | 0 | 0.05172 | 0.05172 | 0 | 0 | 0 | 74.3903 | 849.22 | 0 | 0.05921 | 5.0947 | 0 | 0 | 201.1713 | 46.8817 | off_peak | 849.1683 | 0 | 100 | 5.23 | 0 | 94.77 | 238.8505 | 0
5625 | 907.22 | 447.019 | 29.9 | 88.9246 | 88.9246 | 0 | 0 | 0.0033404 | 0.0033404 | 0 | 0 | 0 | 74.3934 | 818.2988 | 0 | 0.05921 | 4.8563 | 0 | 0 | 201.1713 | 88.9246 | off_peak | 818.2954 | 0 | 100 | 9.8 | 0 | 90.2 | 431.8439 | 0
5626 | 917.46 | 636.267 | 30.1 | 126.4785 | 126.4785 | 0 | 0 | 0.00021574 | 0.00021574 | 0 | 0 | 0 | 74.3936 | 790.9817 | 0 | 0.05921 | 4.7756 | 0 | 0 | 201.1713 | 126.4785 | off_peak | 790.9815 | 0 | 100 | 13.79 | 0 | 86.21 | 604.0133 | 0
5627 | 935.13 | 785.316 | 30.3 | 155.9923 | 155.9923 | 0 | 0 | 1.3934e-05 | 1.3934e-05 | 0 | 0 | 0 | 74.3936 | 779.1377 | 0 | 0.05921 | 4.9151 | 0 | 0 | 201.1713 | 155.9923 | off_peak | 779.1377 | 0 | 100 | 16.68 | 0 | 83.32 | 766.7145 | 0
5628 | 965.48 | 876.013 | 30.4 | 173.9441 | 173.9441 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 791.5359 | 0 | 0.05921 | 5.2467 | 0 | 0 | 201.1713 | 173.9441 | off_peak | 791.5359 |  |  | 18.02 | 0 | 81.98 | 912.6259 | 0
5629 | 901.57 | 905.315 | 30.5 | 179.6964 | 179.6964 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 721.8736 | 0 | 0.088511 | 5.3312 | 0 | 0 | 201.1713 | 179.6964 | on_peak | 721.8736 |  |  | 19.93 | 0 | 80.07 | 958.0034 | 0
5630 | 928.84 | 868.97 | 30.5 | 172.4823 | 172.4823 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 756.3577 | 0 | 0.088511 | 5.4487 | 0 | 0 | 201.1713 | 172.4823 | on_peak | 756.3577 |  |  | 18.57 | 0 | 81.43 | 939.811 | 0
5631 | 959.62 | 765.787 | 30.4 | 152.0573 | 152.0573 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 807.5627 | 0 | 0.088511 | 5.6731 | 0 | 0 | 201.1713 | 152.0573 | on_peak | 807.5627 |  |  | 15.85 | 0 | 84.15 | 862.6335 | 0
5632 | 919.08 | 607.761 | 30.3 | 120.7234 | 120.7234 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 798.3566 | 0 | 0.088511 | 6.2025 | 0 | 0 | 201.1713 | 120.7234 | on_peak | 798.3566 |  |  | 13.14 | 0 | 86.86 | 748.7921 | 0
5633 | 900.78 | 356.379 | 30.1 | 70.8418 | 70.8418 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 829.9382 | 0 | 0.088511 | 6.6371 | 0 | 0 | 201.1713 | 70.8418 | on_peak | 829.9382 |  |  | 7.86 | 0 | 92.14 | 470.1855 | 0
5634 | 953.64 | 70.0921 | 29.8 | 13.9484 | 13.9484 | 0 | 0 | 0 | 0 | 41.4486 | 41.4486 | 0 | 30.0833 | 898.2431 | 0 | 0.088511 | 7.2607 | 0 | 0 | 201.1713 | 13.9484 | on_peak | 898.2431 |  |  | 1.46 | 4.35 | 94.19 | 101.2744 | 0
5635 | 892.87 | 22.6167 | 29.6 | 4.504 | 0 | 0 | 4.504 | 9.8771 | 5.3731 | 0 | 0 | 0 | 39.3224 | 898.2431 | 0 | 0.088511 | 7.8354 | 0 | 0 | 205.3844 | 0 | on_peak | 892.87 | 45.6 | 54.4 | 0 | 0 | 100 | 0 | 0
5636 | 915.73 | 0 | 29.4 | 0 | 0 | 0 | 0 | 0 | 0 | 17.4869 | 17.4869 | 0 | 20.6281 | 898.2431 | 0 | 0.088511 | 8.2034 | 0 | 0 | 205.3844 | 0 | on_peak | 898.2431 |  |  | 0 | 1.91 | 98.09 | 0 | 0
5637 | 910.58 | 0 | 29.3 | 0 | 0 | 0 | 0 | 0 | 0 | 12.3369 | 12.3369 | 0 | 7.4394 | 898.2431 | 0 | 0.088511 | 8.55 | 0 | 0 | 205.3844 | 0 | on_peak | 898.2431 |  |  | 0 | 1.35 | 98.65 | 0 | 0
5638 | 852.32 | 0 | 29.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 852.32 | 0 | 0.05921 | 8.8436 | 0 | 0 | 205.3844 | 0 | off_peak | 852.32 |  |  | 0 | 0 | 100 | 0 | 0
5639 | 896.5 | 0 | 29.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 896.5 | 0 | 0.05921 | 9.027 | 0 | 0 | 205.3844 | 0 | off_peak | 896.5 |  |  | 0 | 0 | 100 | 0 | 0
5640 | 896.68 | 0 | 29 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 896.68 | 0 | 0.05921 | 9.1829 | 0 | 0 | 205.3844 | 0 | off_peak | 896.68 |  |  | 0 | 0 | 100 | 0 | 0
5641 | 827.32 | 0 | 28.9 | 0 | 0 | 0 | 0 | 8.7263 | 8.7263 | 0 | 0 | 0 | 15.6021 | 836.0463 | 0 | 0.05921 | 9.0509 | 0 | 0 | 205.3844 | 0 | off_peak | 827.32 | 0 | 100 | 0 | 0 | 100 | 0 | 0
5642 | 720.13 | 0 | 28.8 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 27.2003 | 732.5289 | 0 | 0.05921 | 8.7845 | 0 | 0 | 205.3844 | 0 | off_peak | 720.13 | 0 | 100 | 0 | 0 | 100 | 0 | 0
5643 | 719.52 | 0 | 28.7 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 38.7984 | 731.9189 | 0 | 0.05921 | 8.2683 | 0 | 0 | 205.3844 | 0 | off_peak | 719.52 | 0 | 100 | 0 | 0 | 100 | 0 | 0
5644 | 664.53 | 0 | 28.6 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 50.3966 | 676.9289 | 0 | 0.05921 | 7.5326 | 0 | 0 | 205.3844 | 0 | off_peak | 664.53 | 0 | 100 | 0 | 0 | 100 | 0 | 0
5645 | 728.18 | 0 | 28.5 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 61.9947 | 740.5789 | 0 | 0.05921 | 6.8575 | 0 | 0 | 205.3844 | 0 | off_peak | 728.18 | 0 | 100 | 0 | 0 | 100 | 0 | 0
5646 | 777.98 | 0 | 28.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 61.9947 | 777.98 | 0 | 0.05921 | 6.1225 | 0 | 0 | 205.3844 | 0 | off_peak | 777.98 |  |  | 0 | 0 | 100 | 0 | 0
5647 | 817.8 | 46.4938 | 28.8 | 9.2862 | 9.2862 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 73.5928 | 820.9127 | 0 | 0.05921 | 5.6026 | 0 | 0 | 205.3844 | 9.2862 | off_peak | 808.5138 | 0 | 100 | 1.14 | 0 | 98.86 | 52.0271 | 0
5648 | 901.12 | 175.546 | 29.3 | 34.9978 | 34.197 | 0 | 0.80079 | 0.80079 | 0 | 0 | 0 | 0 | 74.3419 | 866.923 | 0 | 0.05921 | 5.2648 | 0 | 0 | 206.1335 | 34.197 | off_peak | 866.923 | 100 | 0 | 3.79 | 0 | 96.21 | 180.0412 | 0
5649 | 863.54 | 427.936 | 29.6 | 85.222 | 85.222 | 0 | 0 | 0.05172 | 0.05172 | 0 | 0 | 0 | 74.3903 | 778.3697 | 0 | 0.05921 | 4.9866 | 0 | 0 | 206.1335 | 85.222 | off_peak | 778.318 | 0 | 100 | 9.87 | 0 | 90.13 | 424.9677 | 0
5650 | 890.75 | 552.112 | 29.9 | 109.8305 | 109.8305 | 0 | 0 | 0.0033404 | 0.0033404 | 0 | 0 | 0 | 74.3934 | 780.9229 | 0 | 0.05921 | 4.8559 | 0 | 0 | 206.1335 | 109.8305 | off_peak | 780.9195 | 0 | 100 | 12.33 | 0 | 87.67 | 533.328 | 0
5651 | 882 | 611.056 | 30.2 | 121.4224 | 121.4224 | 0 | 0 | 0.00021574 | 0.00021574 | 0 | 0 | 0 | 74.3936 | 760.5778 | 0 | 0.05921 | 5.0053 | 0 | 0 | 206.1335 | 121.4224 | off_peak | 760.5776 | 0 | 100 | 13.77 | 0 | 86.23 | 607.7501 | 0
5652 | 893.38 | 526.358 | 30.3 | 104.5538 | 104.5538 | 0 | 1.3934e-05 | 1.3934e-05 | 0 | 0 | 0 | 0 | 74.3936 | 788.8262 | 0 | 0.05921 | 5.3385 | 0 | 0 | 206.1335 | 104.5538 | off_peak | 788.8262 | 100 | 0 | 11.7 | 0 | 88.3 | 558.1603 | 0
5653 | 836.89 | 635.942 | 30.4 | 126.2748 | 126.2748 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 710.6152 | 0 | 0.088511 | 5.508 | 0 | 0 | 206.1335 | 126.2748 | on_peak | 710.6152 |  |  | 15.09 | 0 | 84.91 | 695.5245 | 0
5654 | 941.72 | 343.143 | 30.3 | 68.1607 | 68.1607 | 0 | 0 | 0 | 0 | 62.63 | 62.63 | 0 | 7.4394 | 810.9294 | 0 | 0.088511 | 5.6529 | 0 | 0 | 206.1335 | 68.1607 | on_peak | 810.9294 |  |  | 7.24 | 6.65 | 86.11 | 385.3067 | 0
5655 | 945.41 | 728.527 | 30.1 | 144.8181 | 144.8181 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 800.5919 | 0 | 0.088511 | 5.986 | 0 | 0 | 206.1335 | 144.8181 | on_peak | 800.5919 |  |  | 15.32 | 0 | 84.68 | 866.8831 | 0
5656 | 859.73 | 576.535 | 29.8 | 114.7309 | 114.7309 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 744.9991 | 0 | 0.088511 | 6.5033 | 0 | 0 | 206.1335 | 114.7309 | on_peak | 744.9991 |  |  | 13.34 | 0 | 86.66 | 746.1322 | 0
5657 | 860.68 | 387.607 | 29.6 | 77.1906 | 77.1906 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 783.4894 | 0 | 0.088511 | 6.9928 | 0 | 0 | 206.1335 | 77.1906 | on_peak | 783.4894 |  |  | 8.97 | 0 | 91.03 | 539.7767 | 0
5658 | 850.29 | 181.042 | 29.2 | 36.1067 | 36.1067 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 814.1833 | 0 | 0.088511 | 7.446 | 0 | 0 | 206.1335 | 36.1067 | on_peak | 814.1833 |  |  | 4.25 | 0 | 95.75 | 268.8496 | 0
5659 | 825.96 | 21.412 | 29.1 | 4.2719 | 4.2719 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 821.6881 | 0 | 0.088511 | 7.8643 | 0 | 0 | 206.1335 | 4.2719 | on_peak | 821.6881 |  |  | 0.52 | 0 | 99.48 | 33.5958 | 0
5660 | 858.98 | 0 | 28.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 858.98 | 0 | 0.088511 | 8.1733 | 0 | 0 | 206.1335 | 0 | on_peak | 858.98 |  |  | 0 | 0 | 100 | 0 | 0
5661 | 811.8 | 0 | 28.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 811.8 | 0 | 0.088511 | 8.0295 | 0 | 0 | 206.1335 | 0 | on_peak | 811.8 |  |  | 0 | 0 | 100 | 0 | 0
5662 | 789.61 | 0 | 28.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 789.61 | 0 | 0.05921 | 8.2856 | 0 | 0 | 206.1335 | 0 | off_peak | 789.61 |  |  | 0 | 0 | 100 | 0 | 0
5663 | 818.53 | 0 | 28.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 818.53 | 0 | 0.05921 | 8.1766 | 0 | 0 | 206.1335 | 0 | off_peak | 818.53 |  |  | 0 | 0 | 100 | 0 | 0
5664 | 793.98 | 0 | 28.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 793.98 | 0 | 0.05921 | 8.1495 | 0 | 0 | 206.1335 | 0 | off_peak | 793.98 |  |  | 0 | 0 | 100 | 0 | 0
5665 | 749.14 | 0 | 28.5 | 0 | 0 | 0 | 0 | 8.7263 | 8.7263 | 0 | 0 | 0 | 15.6021 | 757.8663 | 0 | 0.05921 | 8.1725 | 0 | 0 | 206.1335 | 0 | off_peak | 749.14 | 0 | 100 | 0 | 0 | 100 | 0 | 0
5666 | 701.71 | 0 | 28.4 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 27.2003 | 714.1089 | 0 | 0.05921 | 7.9927 | 0 | 0 | 206.1335 | 0 | off_peak | 701.71 | 0 | 100 | 0 | 0 | 100 | 0 | 0
5667 | 659.86 | 0 | 28.2 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 38.7984 | 672.2589 | 0 | 0.05921 | 7.5055 | 0 | 0 | 206.1335 | 0 | off_peak | 659.86 | 0 | 100 | 0 | 0 | 100 | 0 | 0
5668 | 669.31 | 0 | 28.1 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 50.3966 | 681.7089 | 0 | 0.05921 | 6.9448 | 0 | 0 | 206.1335 | 0 | off_peak | 669.31 | 0 | 100 | 0 | 0 | 100 | 0 | 0
5669 | 608.4 | 0 | 28 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 61.9947 | 620.7989 | 0 | 0.05921 | 6.2015 | 0 | 0 | 206.1335 | 0 | off_peak | 608.4 | 0 | 100 | 0 | 0 | 100 | 0 | 0
5670 | 750.78 | 0 | 28 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 61.9947 | 750.78 | 0 | 0.05921 | 5.5475 | 0 | 0 | 206.1335 | 0 | off_peak | 750.78 |  |  | 0 | 0 | 100 | 0 | 0
5671 | 771.68 | 49.6513 | 28.3 | 9.9349 | 9.9349 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 61.9947 | 761.7451 | 0 | 0.05921 | 5.0027 | 0 | 0 | 206.1335 | 9.9349 | off_peak | 761.7451 |  |  | 1.29 | 0 | 98.71 | 49.7017 | 0
5672 | 842.28 | 196.63 | 28.6 | 39.3015 | 39.3015 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 73.5928 | 815.3774 | 0 | 0.05921 | 4.6378 | 0 | 0 | 206.1335 | 39.3015 | off_peak | 802.9785 | 0 | 100 | 4.67 | 0 | 95.33 | 182.2732 | 0
5673 | 860.72 | 421.711 | 28.9 | 84.1975 | 84.1975 | 0 | 0 | 0.80079 | 0.80079 | 0 | 0 | 0 | 74.3419 | 777.3233 | 0 | 0.05921 | 4.3594 | 0 | 0 | 206.1335 | 84.1975 | off_peak | 776.5225 | 0 | 100 | 9.78 | 0 | 90.22 | 367.0465 | 0
5674 | 894.35 | 628.541 | 29.1 | 125.4009 | 125.4009 | 0 | 0 | 0.05172 | 0.05172 | 0 | 0 | 0 | 74.3903 | 769.0008 | 0 | 0.05921 | 4.2762 | 0 | 0 | 206.1335 | 125.4009 | off_peak | 768.9491 | 0 | 100 | 14.02 | 0 | 85.98 | 536.2372 | 0
5675 | 883.94 | 742.778 | 29.3 | 148.0842 | 148.0842 | 0 | 0 | 0.0033404 | 0.0033404 | 0 | 0 | 0 | 74.3934 | 735.8592 | 0 | 0.05921 | 4.4521 | 0 | 0 | 206.1335 | 148.0842 | off_peak | 735.8558 | 0 | 100 | 16.75 | 0 | 83.25 | 659.2825 | 0
5676 | 908.57 | 848.23 | 29.5 | 168.984 | 168.984 | 0 | 0 | 0.00021574 | 0.00021574 | 0 | 0 | 0 | 74.3936 | 739.5863 | 0 | 0.05921 | 4.8221 | 0 | 0 | 206.1335 | 168.984 | off_peak | 739.586 | 0 | 100 | 18.6 | 0 | 81.4 | 814.8598 | 0
5677 | 845.78 | 900.345 | 29.6 | 179.3006 | 179.3006 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 666.4794 | 0 | 0.088511 | 4.9386 | 0 | 0 | 206.1335 | 179.3006 | on_peak | 666.4794 |  |  | 21.2 | 0 | 78.8 | 885.4985 | 0
5678 | 874.02 | 856.117 | 29.6 | 170.4928 | 170.4928 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 703.5272 | 0 | 0.088511 | 5.0824 | 0 | 0 | 206.1335 | 170.4928 | on_peak | 703.5272 |  |  | 19.51 | 0 | 80.49 | 866.5044 | 0
5679 | 886.03 | 765.027 | 29.5 | 152.4083 | 152.4083 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 733.6217 | 0 | 0.088511 | 5.3238 | 0 | 0 | 206.1335 | 152.4083 | on_peak | 733.6217 |  |  | 17.2 | 0 | 82.8 | 811.3913 | 0
5680 | 839 | 560.253 | 29.3 | 111.695 | 111.695 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 727.305 | 0 | 0.088511 | 5.7454 | 0 | 0 | 206.1335 | 111.695 | on_peak | 727.305 |  |  | 13.31 | 0 | 86.69 | 641.728 | 0
5681 | 820.01 | 380.824 | 28.9 | 76.0341 | 76.0341 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 743.9759 | 0 | 0.088511 | 6.2247 | 0 | 0 | 206.1335 | 76.0341 | on_peak | 743.9759 |  |  | 9.27 | 0 | 90.73 | 473.2895 | 0
5682 | 833.79 | 197.354 | 28.5 | 39.4606 | 39.4606 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 794.3294 | 0 | 0.088511 | 6.7434 | 0 | 0 | 206.1335 | 39.4606 | on_peak | 794.3294 |  |  | 4.73 | 0 | 95.27 | 266.1001 | 0
5683 | 775.78 | 26.2455 | 28.2 | 5.2535 | 5.2535 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 770.5265 | 0 | 0.088511 | 7.2767 | 0 | 0 | 206.1335 | 5.2535 | on_peak | 770.5265 |  |  | 0.68 | 0 | 99.32 | 38.2283 | 0
5684 | 829.69 | 0 | 28 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 829.69 | 0 | 0.088511 | 7.7103 | 0 | 0 | 206.1335 | 0 | on_peak | 829.69 |  |  | 0 | 0 | 100 | 0 | 0
5685 | 775.61 | 0 | 28 | 0 | 0 | 0 | 0 | 0 | 0 | 62.63 | 62.63 | 0 | 7.4394 | 712.98 | 0 | 0.088511 | 8.0602 | 0 | 0 | 206.1335 | 0 | on_peak | 712.98 |  |  | 0 | 8.07 | 91.93 | 0 | 0
5686 | 775.05 | 0 | 27.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 775.05 | 0 | 0.05921 | 8.4701 | 0 | 0 | 206.1335 | 0 | off_peak | 775.05 |  |  | 0 | 0 | 100 | 0 | 0
5687 | 774.71 | 0 | 27.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 774.71 | 0 | 0.05921 | 8.717 | 0 | 0 | 206.1335 | 0 | off_peak | 774.71 |  |  | 0 | 0 | 100 | 0 | 0
5688 | 758.11 | 0 | 27.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 758.11 | 0 | 0.05921 | 8.8478 | 0 | 0 | 206.1335 | 0 | off_peak | 758.11 |  |  | 0 | 0 | 100 | 0 | 0
5689 | 715.32 | 0 | 28 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 715.32 | 0 | 0.05921 | 8.7377 | 0 | 0 | 206.1335 | 0 | off_peak | 715.32 |  |  | 0 | 0 | 100 | 0 | 0
5690 | 654.09 | 0 | 28 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 654.09 | 0 | 0.05921 | 8.384 | 0 | 0 | 206.1335 | 0 | off_peak | 654.09 |  |  | 0 | 0 | 100 | 0 | 0
5691 | 609.35 | 0 | 28 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 609.35 | 0 | 0.05921 | 7.8547 | 0 | 0 | 206.1335 | 0 | off_peak | 609.35 |  |  | 0 | 0 | 100 | 0 | 0
5692 | 612.22 | 0 | 27.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 612.22 | 0 | 0.05921 | 7.2709 | 0 | 0 | 206.1335 | 0 | off_peak | 612.22 |  |  | 0 | 0 | 100 | 0 | 0
5693 | 630.25 | 0 | 27.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 630.25 | 0 | 0.05921 | 6.6909 | 0 | 0 | 206.1335 | 0 | off_peak | 630.25 |  |  | 0 | 0 | 100 | 0 | 0
5694 | 723.07 | 0 | 27.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 723.07 | 0 | 0.05921 | 6.0237 | 0 | 0 | 206.1335 | 0 | off_peak | 723.07 |  |  | 0 | 0 | 100 | 0 | 0
5695 | 715.09 | 58.775 | 27.8 | 11.782 | 11.782 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 703.308 | 0 | 0.05921 | 5.4213 | 0 | 0 | 206.1335 | 11.782 | off_peak | 703.308 |  |  | 1.65 | 0 | 98.35 | 63.8734 | 0
5696 | 746.56 | 252.929 | 28.1 | 50.6465 | 50.6465 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 19.0375 | 708.3124 | 0 | 0.05921 | 5.0261 | 0 | 0 | 206.1335 | 50.6465 | off_peak | 695.9135 | 0 | 100 | 6.78 | 0 | 93.22 | 254.5521 | 0
5697 | 792.53 | 465.064 | 28.3 | 93.0567 | 93.0567 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 30.6357 | 711.8723 | 0 | 0.05921 | 4.6893 | 0 | 0 | 206.1335 | 93.0567 | off_peak | 699.4733 | 0 | 100 | 11.74 | 0 | 88.26 | 436.3739 | 0
5698 | 797.18 | 503.666 | 28.6 | 100.6705 | 100.6705 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30.6357 | 696.5095 | 0 | 0.05921 | 4.5019 | 0 | 0 | 206.1335 | 100.6705 | off_peak | 696.5095 |  |  | 12.63 | 0 | 87.37 | 453.2073 | 0
5699 | 749.66 | 762.646 | 29.2 | 152.1007 | 152.1007 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30.6357 | 597.5593 | 0 | 0.05921 | 4.4306 | 0 | 0 | 206.1335 | 152.1007 | off_peak | 597.5593 |  |  | 20.29 | 0 | 79.71 | 673.8995 | 0
5700 | 781.6 | 693.359 | 29.6 | 138.0801 | 138.0801 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30.6357 | 643.5199 | 0 | 0.05921 | 4.4464 | 0 | 0 | 206.1335 | 138.0801 | off_peak | 643.5199 |  |  | 17.67 | 0 | 82.33 | 613.9562 | 0
5701 | 786.02 | 815.8 | 29.9 | 162.2854 | 162.2854 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30.6357 | 623.7346 | 0 | 0.05921 | 4.5706 | 0 | 0 | 206.1335 | 162.2854 | off_peak | 623.7346 |  |  | 20.65 | 0 | 79.35 | 741.7472 | 0
5702 | 772.48 | 875.297 | 30.1 | 173.9934 | 173.9934 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30.6357 | 598.4866 | 0 | 0.05921 | 4.9596 | 0 | 0 | 206.1335 | 173.9934 | off_peak | 598.4866 |  |  | 22.52 | 0 | 77.48 | 862.9455 | 0
5703 | 749.09 | 735.039 | 30.2 | 146.059 | 146.059 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30.6357 | 603.031 | 0 | 0.05921 | 5.3815 | 0 | 0 | 206.1335 | 146.059 | off_peak | 603.031 |  |  | 19.5 | 0 | 80.5 | 786.0159 | 0
5704 | 796.41 | 613.188 | 30 | 121.9355 | 121.9355 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30.6357 | 674.4745 | 0 | 0.05921 | 5.8783 | 0 | 0 | 206.1335 | 121.9355 | off_peak | 674.4745 |  |  | 15.31 | 0 | 84.69 | 716.7709 | 0
5705 | 755.46 | 416.496 | 29.8 | 82.883 | 82.883 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30.6357 | 672.577 | 0 | 0.05921 | 6.4762 | 0 | 0 | 206.1335 | 82.883 | off_peak | 672.577 |  |  | 10.97 | 0 | 89.03 | 536.766 | 0
5706 | 703.7 | 194.511 | 29.4 | 38.7646 | 38.7646 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30.6357 | 664.9354 | 0 | 0.05921 | 7.1335 | 0 | 0 | 206.1335 | 38.7646 | off_peak | 664.9354 |  |  | 5.51 | 0 | 94.49 | 276.5262 | 0
5707 | 619.3 | 23.8401 | 29.2 | 4.7546 | 0 | 0 | 4.7546 | 4.7546 | 0 | 0 | 0 | 0 | 35.0832 | 619.3 | 0 | 0.05921 | 7.5637 | 0 | 0 | 210.5811 | 0 | off_peak | 619.3 | 100 | 0 | 0 | 0 | 100 | 0 | 0
5708 | 619.54 | 0 | 28.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 35.0832 | 619.54 | 0 | 0.05921 | 7.9557 | 0 | 0 | 210.5811 | 0 | off_peak | 619.54 |  |  | 0 | 0 | 100 | 0 | 0
5709 | 591.25 | 0 | 28.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 35.0832 | 591.25 | 0 | 0.05921 | 8.1975 | 0 | 0 | 210.5811 | 0 | off_peak | 591.25 |  |  | 0 | 0 | 100 | 0 | 0
5710 | 595.47 | 0 | 28.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 35.0832 | 595.47 | 0 | 0.05921 | 8.4479 | 0 | 0 | 210.5811 | 0 | off_peak | 595.47 |  |  | 0 | 0 | 100 | 0 | 0
5711 | 600.21 | 0 | 28.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 35.0832 | 600.21 | 0 | 0.05921 | 8.5996 | 0 | 0 | 210.5811 | 0 | off_peak | 600.21 |  |  | 0 | 0 | 100 | 0 | 0
5712 | 594.56 | 0 | 28.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 35.0832 | 594.56 | 0 | 0.05921 | 8.8243 | 0 | 0 | 210.5811 | 0 | off_peak | 594.56 |  |  | 0 | 0 | 100 | 0 | 0
5713 | 594.31 | 0 | 28.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 35.0832 | 594.31 | 0 | 0.05921 | 8.6503 | 0 | 0 | 210.5811 | 0 | off_peak | 594.31 |  |  | 0 | 0 | 100 | 0 | 0
5714 | 583.03 | 0 | 28.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 35.0832 | 583.03 | 0 | 0.05921 | 8.4255 | 0 | 0 | 210.5811 | 0 | off_peak | 583.03 |  |  | 0 | 0 | 100 | 0 | 0
5715 | 604.13 | 0 | 28.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 35.0832 | 604.13 | 0 | 0.05921 | 7.9367 | 0 | 0 | 210.5811 | 0 | off_peak | 604.13 |  |  | 0 | 0 | 100 | 0 | 0
5716 | 604.29 | 0 | 28.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 35.0832 | 604.29 | 0 | 0.05921 | 7.3534 | 0 | 0 | 210.5811 | 0 | off_peak | 604.29 |  |  | 0 | 0 | 100 | 0 | 0
5717 | 592.88 | 0 | 28.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 35.0832 | 592.88 | 0 | 0.05921 | 6.6839 | 0 | 0 | 210.5811 | 0 | off_peak | 592.88 |  |  | 0 | 0 | 100 | 0 | 0
5718 | 714.82 | 0 | 28.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 35.0832 | 714.82 | 0 | 0.05921 | 5.9852 | 0 | 0 | 210.5811 | 0 | off_peak | 714.82 |  |  | 0 | 0 | 100 | 0 | 0
5719 | 749.15 | 59.0142 | 28.8 | 11.7869 | 11.7869 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 35.0832 | 737.3631 | 0 | 0.05921 | 5.495 | 0 | 0 | 210.5811 | 11.7869 | off_peak | 737.3631 |  |  | 1.57 | 0 | 98.43 | 64.7684 | 0
5720 | 803.37 | 254.432 | 29.1 | 50.762 | 50.762 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 35.0832 | 752.608 | 0 | 0.05921 | 5.1132 | 0 | 0 | 210.5811 | 50.762 | off_peak | 752.608 |  |  | 6.32 | 0 | 93.68 | 259.556 | 0
5721 | 767.15 | 466.56 | 29.4 | 92.9819 | 92.9819 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 35.0832 | 674.1681 | 0 | 0.05921 | 4.8043 | 0 | 0 | 210.5811 | 92.9819 | off_peak | 674.1681 |  |  | 12.12 | 0 | 87.88 | 446.7139 | 0
5722 | 780.56 | 655.131 | 29.7 | 130.4194 | 130.4194 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 35.0832 | 650.1406 | 0 | 0.05921 | 4.6419 | 0 | 0 | 210.5811 | 130.4194 | off_peak | 650.1406 |  |  | 16.71 | 0 | 83.29 | 605.3913 | 0
5723 | 759.57 | 759.45 | 30 | 151.0204 | 151.0204 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 35.0832 | 608.5496 | 0 | 0.05921 | 4.5455 | 0 | 0 | 210.5811 | 151.0204 | off_peak | 608.5496 |  |  | 19.88 | 0 | 80.12 | 686.4588 | 0
5724 | 794.9 | 823.94 | 30.2 | 163.7245 | 163.7245 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 35.0832 | 631.1755 | 0 | 0.05921 | 4.5118 | 0 | 0 | 210.5811 | 163.7245 | off_peak | 631.1755 |  |  | 20.6 | 0 | 79.4 | 738.6954 | 0
5725 | 775.3 | 871.492 | 30.3 | 173.1099 | 160.711 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 0 | 46.6814 | 614.589 | 0 | 0.05921 | 4.6024 | 0 | 0 | 222.1792 | 160.711 | off_peak | 614.589 | 100 | 0 | 20.73 | 0 | 79.27 | 739.6512 | 0
5726 | 753.68 | 815.436 | 30.3 | 161.9752 | 161.9752 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 46.6814 | 591.7048 | 0 | 0.05921 | 4.9927 | 0 | 0 | 222.1792 | 161.9752 | off_peak | 591.7048 |  |  | 21.49 | 0 | 78.51 | 808.701 | 0
5727 | 751.05 | 710.631 | 30.3 | 141.1571 | 141.1571 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 46.6814 | 609.8929 | 0 | 0.05921 | 5.4129 | 0 | 0 | 222.1792 | 141.1571 | off_peak | 609.8929 |  |  | 18.79 | 0 | 81.21 | 764.0753 | 0
5728 | 737.32 | 601.03 | 30.1 | 119.474 | 119.474 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 46.6814 | 617.846 | 0 | 0.05921 | 6.0712 | 0 | 0 | 222.1792 | 119.474 | off_peak | 617.846 |  |  | 16.2 | 0 | 83.8 | 725.3502 | 0
5729 | 732.5 | 404.294 | 29.9 | 80.4254 | 80.4254 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 46.6814 | 652.0746 | 0 | 0.05921 | 6.7505 | 0 | 0 | 222.1792 | 80.4254 | off_peak | 652.0746 |  |  | 10.98 | 0 | 89.02 | 542.913 | 0
5730 | 675.44 | 194.541 | 29.5 | 38.7564 | 26.3574 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 0 | 58.2795 | 649.0826 | 0 | 0.05921 | 7.2987 | 0 | 0 | 233.7773 | 26.3574 | off_peak | 649.0826 | 100 | 0 | 3.9 | 0 | 96.1 | 192.3745 | 0
5731 | 605.13 | 21.6076 | 29.3 | 4.3078 | 0 | 0 | 4.3078 | 12.3989 | 8.0911 | 0 | 0 | 0 | 69.8776 | 613.2211 | 0 | 0.05921 | 7.8329 | 0 | 0 | 237.8069 | 0 | off_peak | 605.13 | 34.74 | 65.26 | 0 | 0 | 100 | 0 | 0
5732 | 561.43 | 0 | 29.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 69.8776 | 561.43 | 0 | 0.05921 | 8.1431 | 0 | 0 | 237.8069 | 0 | off_peak | 561.43 |  |  | 0 | 0 | 100 | 0 | 0
5733 | 540.13 | 0 | 29.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 69.8776 | 540.13 | 0 | 0.05921 | 8.4176 | 0 | 0 | 237.8069 | 0 | off_peak | 540.13 |  |  | 0 | 0 | 100 | 0 | 0
5734 | 512.96 | 0 | 29 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 69.8776 | 512.96 | 0 | 0.05921 | 8.5809 | 0 | 0 | 237.8069 | 0 | off_peak | 512.96 |  |  | 0 | 0 | 100 | 0 | 0
5735 | 520.41 | 0 | 28.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 69.8776 | 520.41 | 0 | 0.05921 | 8.639 | 0 | 0 | 237.8069 | 0 | off_peak | 520.41 |  |  | 0 | 0 | 100 | 0 | 0
5736 | 525.34 | 0 | 28.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 69.8776 | 525.34 | 0 | 0.05921 | 8.5035 | 0 | 0 | 237.8069 | 0 | off_peak | 525.34 |  |  | 0 | 0 | 100 | 0 | 0
5737 | 532.39 | 0 | 28.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 69.8776 | 532.39 | 0 | 0.05921 | 8.3768 | 0 | 0 | 237.8069 | 0 | off_peak | 532.39 |  |  | 0 | 0 | 100 | 0 | 0
5738 | 547.05 | 0 | 28.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 69.8776 | 547.05 | 0 | 0.05921 | 8.2428 | 0 | 0 | 237.8069 | 0 | off_peak | 547.05 |  |  | 0 | 0 | 100 | 0 | 0
5739 | 513.44 | 0 | 28.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 69.8776 | 513.44 | 0 | 0.05921 | 7.7652 | 0 | 0 | 237.8069 | 0 | off_peak | 513.44 |  |  | 0 | 0 | 100 | 0 | 0
5740 | 522.12 | 0 | 28.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 69.8776 | 522.12 | 0 | 0.05921 | 7.1642 | 0 | 0 | 237.8069 | 0 | off_peak | 522.12 |  |  | 0 | 0 | 100 | 0 | 0
5741 | 539.43 | 0 | 28.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 69.8776 | 539.43 | 0 | 0.05921 | 6.4991 | 0 | 0 | 237.8069 | 0 | off_peak | 539.43 |  |  | 0 | 0 | 100 | 0 | 0
5742 | 644.58 | 0 | 28.6 | 0 | 0 | 0 | 0 | 4.516 | 4.516 | 0 | 0 | 0 | 74.102 | 649.096 | 0 | 0.05921 | 5.8496 | 0 | 0 | 237.8069 | 0 | off_peak | 644.58 | 0 | 100 | 0 | 0 | 100 | 0 | 0
5743 | 784.33 | 56.8505 | 28.8 | 11.3547 | 11.0631 | 0 | 0.29167 | 0.29167 | 0 | 0 | 0 | 0 | 74.3748 | 773.2669 | 0 | 0.05921 | 5.4058 | 0 | 0 | 238.0798 | 11.0631 | off_peak | 773.2669 | 100 | 0 | 1.41 | 0 | 98.59 | 59.8051 | 0
5744 | 787.58 | 249.666 | 29.2 | 49.7929 | 49.7929 | 0 | 0 | 0.018838 | 0.018838 | 0 | 0 | 0 | 74.3924 | 737.8059 | 0 | 0.05921 | 5.0866 | 0 | 0 | 238.0798 | 49.7929 | off_peak | 737.7871 | 0 | 100 | 6.32 | 0 | 93.68 | 253.2771 | 0
5745 | 816.91 | 355.012 | 29.5 | 70.7253 | 70.7253 | 0 | 0 | 0.0012166 | 0.0012166 | 0 | 0 | 0 | 74.3936 | 746.1859 | 0 | 0.05921 | 4.8938 | 0 | 0 | 238.0798 | 70.7253 | off_peak | 746.1847 | 0 | 100 | 8.66 | 0 | 91.34 | 346.1172 | 0
5746 | 846.35 | 642.394 | 29.7 | 127.8838 | 127.8838 | 0 | 0 | 7.8577e-05 | 7.8577e-05 | 0 | 0 | 0 | 74.3936 | 718.4663 | 0 | 0.05921 | 4.8747 | 0 | 0 | 238.0798 | 127.8838 | off_peak | 718.4662 | 0 | 100 | 15.11 | 0 | 84.89 | 623.3903 | 0
5747 | 828.63 | 778.959 | 29.9 | 154.9567 | 154.9567 | 0 | 0 | 5.075e-06 | 5.075e-06 | 0 | 0 | 0 | 74.3936 | 673.6733 | 0 | 0.05921 | 5.0686 | 0 | 0 | 238.0798 | 154.9567 | off_peak | 673.6733 | 0 | 100 | 18.7 | 0 | 81.3 | 785.4076 | 0
5748 | 891.86 | 819.702 | 30.1 | 162.9421 | 162.9421 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 728.9179 | 0 | 0.05921 | 5.4102 | 0 | 0 | 238.0798 | 162.9421 | off_peak | 728.9179 |  |  | 18.27 | 0 | 81.73 | 881.5546 | 0
5749 | 884.38 | 890.86 | 30.1 | 177.087 | 177.087 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 707.293 | 0 | 0.088511 | 5.597 | 0 | 0 | 238.0798 | 177.087 | on_peak | 707.293 |  |  | 20.02 | 0 | 79.98 | 991.161 | 0
5750 | 897.8 | 765.948 | 30.1 | 152.2568 | 152.2568 | 0 | 0 | 0 | 0 | 62.63 | 62.63 | 0 | 7.4394 | 682.9133 | 0 | 0.088511 | 5.8348 | 0 | 0 | 238.0798 | 152.2568 | on_peak | 682.9133 |  |  | 16.96 | 6.98 | 76.07 | 888.3831 | 0
5751 | 872.59 | 748.805 | 30.1 | 148.849 | 148.849 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 723.741 | 0 | 0.088511 | 6.1498 | 0 | 0 | 238.0798 | 148.849 | on_peak | 723.741 |  |  | 17.06 | 0 | 82.94 | 915.3921 | 0
5752 | 830.03 | 593.281 | 29.9 | 118.0201 | 118.0201 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 712.0099 | 0 | 0.088511 | 6.6184 | 0 | 0 | 238.0798 | 118.0201 | on_peak | 712.0099 |  |  | 14.22 | 0 | 85.78 | 781.1063 | 0
5753 | 831.96 | 400.959 | 29.7 | 79.8204 | 79.8204 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 752.1396 | 0 | 0.088511 | 7.0053 | 0 | 0 | 238.0798 | 79.8204 | on_peak | 752.1396 |  |  | 9.59 | 0 | 90.41 | 559.1638 | 0
5754 | 898.66 | 189.512 | 29.3 | 37.7821 | 37.7821 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 860.8779 | 0 | 0.088511 | 7.4214 | 0 | 0 | 238.0798 | 37.7821 | on_peak | 860.8779 |  |  | 4.2 | 0 | 95.8 | 280.3948 | 0
5755 | 834 | 18.2314 | 29.1 | 3.6374 | 3.6374 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 830.3626 | 0 | 0.088511 | 7.6372 | 0 | 0 | 238.0798 | 3.6374 | on_peak | 830.3626 |  |  | 0.44 | 0 | 99.56 | 27.7793 | 0
5756 | 852.88 | 0 | 28.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 852.88 | 0 | 0.088511 | 7.7476 | 0 | 0 | 238.0798 | 0 | on_peak | 852.88 |  |  | 0 | 0 | 100 | 0 | 0
5757 | 859.19 | 0 | 28.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 859.19 | 0 | 0.088511 | 8.0412 | 0 | 0 | 238.0798 | 0 | on_peak | 859.19 |  |  | 0 | 0 | 100 | 0 | 0
5758 | 793.29 | 0 | 28.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 793.29 | 0 | 0.05921 | 8.3292 | 0 | 0 | 238.0798 | 0 | off_peak | 793.29 |  |  | 0 | 0 | 100 | 0 | 0
5759 | 847.16 | 0 | 28.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 847.16 | 0 | 0.05921 | 8.2813 | 0 | 0 | 238.0798 | 0 | off_peak | 847.16 |  |  | 0 | 0 | 100 | 0 | 0
5760 | 808.66 | 0 | 28.5 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 19.0375 | 821.0589 | 0 | 0.05921 | 8.4038 | 0 | 0 | 238.0798 | 0 | off_peak | 808.66 | 0 | 100 | 0 | 0 | 100 | 0 | 0
5761 | 737.32 | 0 | 28.4 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 30.6357 | 749.7189 | 0 | 0.05921 | 8.293 | 0 | 0 | 238.0798 | 0 | off_peak | 737.32 | 0 | 100 | 0 | 0 | 100 | 0 | 0
5762 | 691.14 | 0 | 28.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30.6357 | 691.14 | 0 | 0.05921 | 8.1632 | 0 | 0 | 238.0798 | 0 | off_peak | 691.14 |  |  | 0 | 0 | 100 | 0 | 0
5763 | 623.19 | 0 | 28.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30.6357 | 623.19 | 0 | 0.05921 | 7.6782 | 0 | 0 | 238.0798 | 0 | off_peak | 623.19 |  |  | 0 | 0 | 100 | 0 | 0
5764 | 639.4 | 0 | 28.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30.6357 | 639.4 | 0 | 0.05921 | 7.0485 | 0 | 0 | 238.0798 | 0 | off_peak | 639.4 |  |  | 0 | 0 | 100 | 0 | 0
5765 | 618.79 | 0 | 28 | 0 | 0 | 0 | 0 | 8.7263 | 8.7263 | 0 | 0 | 0 | 38.7984 | 627.5163 | 0 | 0.05921 | 6.352 | 0 | 0 | 238.0798 | 0 | off_peak | 618.79 | 0 | 100 | 0 | 0 | 100 | 0 | 0
5766 | 709 | 0 | 28.1 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 50.3966 | 721.3989 | 0 | 0.05921 | 5.6528 | 0 | 0 | 238.0798 | 0 | off_peak | 709 | 0 | 100 | 0 | 0 | 100 | 0 | 0
5767 | 798.81 | 56.9235 | 28.4 | 11.3859 | 11.3859 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 61.9947 | 799.823 | 0 | 0.05921 | 5.251 | 0 | 0 | 238.0798 | 11.3859 | off_peak | 787.4241 | 0 | 100 | 1.43 | 0 | 98.57 | 59.787 | 0
5768 | 798.01 | 231.768 | 28.8 | 46.291 | 46.291 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 73.5928 | 764.118 | 0 | 0.05921 | 4.9326 | 0 | 0 | 238.0798 | 46.291 | off_peak | 751.719 | 0 | 100 | 5.8 | 0 | 94.2 | 228.337 | 0
5769 | 816.39 | 461.951 | 29.1 | 92.1644 | 92.1644 | 0 | 0 | 0.80079 | 0.80079 | 0 | 0 | 0 | 74.3419 | 725.0264 | 0 | 0.05921 | 4.7226 | 0 | 0 | 238.0798 | 92.1644 | off_peak | 724.2256 | 0 | 100 | 11.29 | 0 | 88.71 | 435.2524 | 0
5770 | 848.52 | 648.018 | 29.3 | 129.1923 | 129.1923 | 0 | 0 | 0.05172 | 0.05172 | 0 | 0 | 0 | 74.3903 | 719.3794 | 0 | 0.05921 | 4.6967 | 0 | 0 | 238.0798 | 129.1923 | off_peak | 719.3277 | 0 | 100 | 15.23 | 0 | 84.77 | 606.7784 | 0
5771 | 852.44 | 719.461 | 29.5 | 143.3307 | 143.3273 | 0 | 0.0033404 | 0.0033404 | 0 | 0 | 0 | 0 | 74.3934 | 709.1127 | 0 | 0.05921 | 4.9231 | 0 | 0 | 238.0829 | 143.3273 | off_peak | 709.1127 | 100 | 0 | 16.81 | 0 | 83.19 | 705.6179 | 0
5772 | 875.12 | 558.37 | 29.7 | 111.1568 | 111.1568 | 0 | 0 | 0.00021574 | 0.00021574 | 0 | 0 | 0 | 74.3936 | 763.9634 | 0 | 0.05921 | 5.3052 | 0 | 0 | 238.0829 | 111.1568 | off_peak | 763.9632 | 0 | 100 | 12.7 | 0 | 87.3 | 589.7125 | 0
5773 | 856.92 | 727.757 | 29.9 | 144.7712 | 144.7712 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 712.1488 | 0 | 0.088511 | 5.5719 | 0 | 0 | 238.0829 | 144.7712 | on_peak | 712.1488 |  |  | 16.89 | 0 | 83.11 | 806.646 | 0
5774 | 868.95 | 760.691 | 30 | 151.2672 | 151.2672 | 0 | 0 | 0 | 0 | 62.63 | 62.63 | 0 | 7.4394 | 655.0528 | 0 | 0.088511 | 5.8707 | 0 | 0 | 238.0829 | 151.2672 | on_peak | 655.0528 |  |  | 17.41 | 7.21 | 75.38 | 888.0506 | 0
5775 | 840.65 | 702.226 | 30 | 139.6412 | 139.6412 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 701.0088 | 0 | 0.088511 | 6.3016 | 0 | 0 | 238.0829 | 139.6412 | on_peak | 701.0088 |  |  | 16.61 | 0 | 83.39 | 879.967 | 0
5776 | 783.43 | 577.005 | 30 | 114.7403 | 114.7403 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 668.6897 | 0 | 0.088511 | 6.7364 | 0 | 0 | 238.0829 | 114.7403 | on_peak | 668.6897 |  |  | 14.65 | 0 | 85.35 | 772.9376 | 0
5777 | 795.93 | 380.9 | 29.8 | 75.7994 | 75.7994 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 720.1306 | 0 | 0.088511 | 7.0924 | 0 | 0 | 238.0829 | 75.7994 | on_peak | 720.1306 |  |  | 9.52 | 0 | 90.48 | 537.6034 | 0
5778 | 811.49 | 186.826 | 29.5 | 37.2194 | 37.2194 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 774.2706 | 0 | 0.088511 | 7.5878 | 0 | 0 | 238.0829 | 37.2194 | on_peak | 774.2706 |  |  | 4.59 | 0 | 95.41 | 282.4139 | 0
5779 | 767.07 | 19.7973 | 29.3 | 3.9469 | 3.9469 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 763.1231 | 0 | 0.088511 | 8.0145 | 0 | 0 | 238.0829 | 3.9469 | on_peak | 763.1231 |  |  | 0.51 | 0 | 99.49 | 31.6324 | 0
5780 | 783.01 | 0 | 29 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 783.01 | 0 | 0.088511 | 8.089 | 0 | 0 | 238.0829 | 0 | on_peak | 783.01 |  |  | 0 | 0 | 100 | 0 | 0
5781 | 780.16 | 0 | 28.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 780.16 | 0 | 0.088511 | 8.2647 | 0 | 0 | 238.0829 | 0 | on_peak | 780.16 |  |  | 0 | 0 | 100 | 0 | 0
5782 | 746.37 | 0 | 28.7 | 0 | 0 | 0 | 0 | 8.7263 | 8.7263 | 0 | 0 | 0 | 15.6021 | 755.0963 | 0 | 0.05921 | 8.329 | 0 | 0 | 238.0829 | 0 | off_peak | 746.37 | 0 | 100 | 0 | 0 | 100 | 0 | 0
5783 | 773.82 | 0 | 28.5 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 27.2003 | 786.2189 | 0 | 0.05921 | 7.9467 | 0 | 0 | 238.0829 | 0 | off_peak | 773.82 | 0 | 100 | 0 | 0 | 100 | 0 | 0
5784 | 755.99 | 0 | 28.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27.2003 | 755.99 | 0 | 0.05921 | 7.5222 | 0 | 0 | 238.0829 | 0 | off_peak | 755.99 |  |  | 0 | 0 | 100 | 0 | 0
5785 | 719.02 | 0 | 28.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27.2003 | 719.02 | 0 | 0.05921 | 7.3979 | 0 | 0 | 238.0829 | 0 | off_peak | 719.02 |  |  | 0 | 0 | 100 | 0 | 0
5786 | 626.71 | 0 | 28 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 38.7984 | 639.1089 | 0 | 0.05921 | 7.26 | 0 | 0 | 238.0829 | 0 | off_peak | 626.71 | 0 | 100 | 0 | 0 | 100 | 0 | 0
5787 | 622.28 | 0 | 27.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 38.7984 | 622.28 | 0 | 0.05921 | 6.8334 | 0 | 0 | 238.0829 | 0 | off_peak | 622.28 |  |  | 0 | 0 | 100 | 0 | 0
5788 | 618.19 | 0 | 27.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 38.7984 | 618.19 | 0 | 0.05921 | 6.4064 | 0 | 0 | 238.0829 | 0 | off_peak | 618.19 |  |  | 0 | 0 | 100 | 0 | 0
5789 | 627.31 | 0 | 28 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 50.3966 | 639.7089 | 0 | 0.05921 | 6.01 | 0 | 0 | 238.0829 | 0 | off_peak | 627.31 | 0 | 100 | 0 | 0 | 100 | 0 | 0
5790 | 677.44 | 0 | 28.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50.3966 | 677.44 | 0 | 0.05921 | 5.5515 | 0 | 0 | 238.0829 | 0 | off_peak | 677.44 |  |  | 0 | 0 | 100 | 0 | 0
5791 | 746.03 | 49.894 | 28.6 | 9.9726 | 9.9726 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 61.9947 | 748.4563 | 0 | 0.05921 | 5.3089 | 0 | 0 | 238.0829 | 9.9726 | off_peak | 736.0574 | 0 | 100 | 1.34 | 0 | 98.66 | 52.9438 | 0
5792 | 847.17 | 245.857 | 29.1 | 49.0512 | 49.0512 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 73.5928 | 810.5177 | 0 | 0.05921 | 5.1376 | 0 | 0 | 238.0829 | 49.0512 | off_peak | 798.1188 | 0 | 100 | 5.79 | 0 | 94.21 | 252.0064 | 0
5793 | 875.82 | 457.827 | 29.5 | 91.2081 | 91.2081 | 0 | 0 | 0.80079 | 0.80079 | 0 | 0 | 0 | 74.3419 | 785.4127 | 0 | 0.05921 | 5.0714 | 0 | 0 | 238.0829 | 91.2081 | off_peak | 784.6119 | 0 | 100 | 10.41 | 0 | 89.59 | 462.5508 | 0
5794 | 901 | 638.45 | 29.9 | 127.0055 | 127.0055 | 0 | 0 | 0.05172 | 0.05172 | 0 | 0 | 0 | 74.3903 | 774.0462 | 0 | 0.05921 | 5.0897 | 0 | 0 | 238.0829 | 127.0055 | off_peak | 773.9945 | 0 | 100 | 14.1 | 0 | 85.9 | 646.4228 | 0
5795 | 815.68 | 767.972 | 30.2 | 152.6031 | 152.6031 | 0 | 0 | 0.0033404 | 0.0033404 | 0 | 0 | 0 | 74.3934 | 663.0802 | 0 | 0.05921 | 5.3134 | 0 | 0 | 238.0829 | 152.6031 | off_peak | 663.0769 | 0 | 100 | 18.71 | 0 | 81.29 | 810.8435 | 0
5796 | 859.28 | 858.654 | 30.4 | 170.4973 | 170.4973 | 0 | 0 | 0.00021574 | 0.00021574 | 0 | 0 | 0 | 74.3936 | 688.783 | 0 | 0.05921 | 5.6006 | 0 | 0 | 238.0829 | 170.4973 | off_peak | 688.7827 | 0 | 100 | 19.84 | 0 | 80.16 | 954.8938 | 0
5797 | 841.9 | 771.258 | 30.6 | 153.0312 | 153.0312 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 688.8688 | 0 | 0.088511 | 5.7322 | 0 | 0 | 238.0829 | 153.0312 | on_peak | 688.8688 |  |  | 18.18 | 0 | 81.82 | 877.2068 | 0
5798 | 879.89 | 697.458 | 30.6 | 138.3879 | 138.3879 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 741.5021 | 0 | 0.088511 | 6.0982 | 0 | 0 | 238.0829 | 138.3879 | on_peak | 741.5021 |  |  | 15.73 | 0 | 84.27 | 843.9206 | 0
5799 | 907.59 | 625.47 | 30.5 | 124.1499 | 124.1499 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 783.4401 | 0 | 0.088511 | 6.5491 | 0 | 0 | 238.0829 | 124.1499 | on_peak | 783.4401 |  |  | 13.68 | 0 | 86.32 | 813.0659 | 0
5800 | 836.84 | 273.165 | 30.2 | 54.2804 | 54.2804 | 0 | 0 | 0 | 0 | 62.63 | 62.63 | 0 | 7.4394 | 719.9296 | 0 | 0.088511 | 6.9004 | 0 | 0 | 238.0829 | 54.2804 | on_peak | 719.9296 |  |  | 6.49 | 7.48 | 86.03 | 374.5553 | 0
5801 | 853.28 | 342.992 | 29.8 | 68.2557 | 68.2557 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 785.0243 | 0 | 0.088511 | 7.2506 | 0 | 0 | 238.0829 | 68.2557 | on_peak | 785.0243 |  |  | 8 | 0 | 92 | 494.8967 | 0
5802 | 871.33 | 97.904 | 29.3 | 19.5187 | 19.5187 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 851.8113 | 0 | 0.088511 | 7.3499 | 0 | 0 | 238.0829 | 19.5187 | on_peak | 851.8113 |  |  | 2.24 | 0 | 97.76 | 143.4598 | 0
5803 | 834.55 | 7.6 | 29 | 1.5168 | 1.5168 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 833.0332 | 0 | 0.088511 | 7.4936 | 0 | 0 | 238.0829 | 1.5168 | on_peak | 833.0332 |  |  | 0.18 | 0 | 99.82 | 11.3666 | 0
5804 | 841.72 | 0 | 28.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 841.72 | 0 | 0.088511 | 7.6807 | 0 | 0 | 238.0829 | 0 | on_peak | 841.72 |  |  | 0 | 0 | 100 | 0 | 0
5805 | 817.94 | 0 | 28.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 817.94 | 0 | 0.088511 | 7.9036 | 0 | 0 | 238.0829 | 0 | on_peak | 817.94 |  |  | 0 | 0 | 100 | 0 | 0
5806 | 812.63 | 0 | 28.2 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 19.0375 | 825.0289 | 0 | 0.05921 | 8.0878 | 0 | 0 | 238.0829 | 0 | off_peak | 812.63 | 0 | 100 | 0 | 0 | 100 | 0 | 0
5807 | 873.28 | 0 | 28.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19.0375 | 873.28 | 0 | 0.05921 | 8.2537 | 0 | 0 | 238.0829 | 0 | off_peak | 873.28 |  |  | 0 | 0 | 100 | 0 | 0
5808 | 807.49 | 0 | 28 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19.0375 | 807.49 | 0 | 0.05921 | 8.4092 | 0 | 0 | 238.0829 | 0 | off_peak | 807.49 |  |  | 0 | 0 | 100 | 0 | 0
5809 | 687.14 | 0 | 27.9 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 30.6357 | 699.5389 | 0 | 0.05921 | 8.3019 | 0 | 0 | 238.0829 | 0 | off_peak | 687.14 | 0 | 100 | 0 | 0 | 100 | 0 | 0
5810 | 678.78 | 0 | 27.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30.6357 | 678.78 | 0 | 0.05921 | 8.1695 | 0 | 0 | 238.0829 | 0 | off_peak | 678.78 |  |  | 0 | 0 | 100 | 0 | 0
5811 | 663.91 | 0 | 27.7 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 42.2338 | 676.3089 | 0 | 0.05921 | 7.6717 | 0 | 0 | 238.0829 | 0 | off_peak | 663.91 | 0 | 100 | 0 | 0 | 100 | 0 | 0
5812 | 657.17 | 0 | 27.7 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 53.832 | 669.5689 | 0 | 0.05921 | 7.0668 | 0 | 0 | 238.0829 | 0 | off_peak | 657.17 | 0 | 100 | 0 | 0 | 100 | 0 | 0
5813 | 677.52 | 0 | 27.7 | 0 | 0 | 0 | 0 | 8.7263 | 8.7263 | 0 | 0 | 0 | 61.9947 | 686.2463 | 0 | 0.05921 | 6.4523 | 0 | 0 | 238.0829 | 0 | off_peak | 677.52 | 0 | 100 | 0 | 0 | 100 | 0 | 0
5814 | 715.2 | 0 | 27.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 61.9947 | 715.2 | 0 | 0.05921 | 5.8716 | 0 | 0 | 238.0829 | 0 | off_peak | 715.2 |  |  | 0 | 0 | 100 | 0 | 0
5815 | 781.78 | 35.2444 | 28 | 7.0599 | 0 | 0 | 7.0599 | 12.3989 | 5.339 | 0 | 0 | 0 | 73.5928 | 787.119 | 0 | 0.05921 | 5.4535 | 0 | 0 | 244.6868 | 0 | off_peak | 781.78 | 56.94 | 43.06 | 0 | 0 | 100 | 0 | 0
5816 | 821.09 | 228.568 | 28.5 | 45.7018 | 45.7018 | 0 | 0 | 0.80079 | 0.80079 | 0 | 0 | 0 | 74.3419 | 776.189 | 0 | 0.05921 | 5.1695 | 0 | 0 | 244.6868 | 45.7018 | off_peak | 775.3882 | 0 | 100 | 5.57 | 0 | 94.43 | 236.2571 | 0
5817 | 837.36 | 449.065 | 28.9 | 89.6589 | 89.6589 | 0 | 0 | 0.05172 | 0.05172 | 0 | 0 | 0 | 74.3903 | 747.7528 | 0 | 0.05921 | 4.9752 | 0 | 0 | 244.6868 | 89.6589 | off_peak | 747.7011 | 0 | 100 | 10.71 | 0 | 89.29 | 446.0701 | 0
5818 | 841.93 | 629.456 | 29.4 | 125.4458 | 125.4458 | 0 | 0 | 0.0033404 | 0.0033404 | 0 | 0 | 0 | 74.3934 | 716.4875 | 0 | 0.05921 | 4.8916 | 0 | 0 | 244.6868 | 125.4458 | off_peak | 716.4842 | 0 | 100 | 14.9 | 0 | 85.1 | 613.6286 | 0
5819 | 855.99 | 730.757 | 29.9 | 145.368 | 145.3677 | 0 | 0.00021574 | 0.00021574 | 0 | 0 | 0 | 0 | 74.3936 | 710.6223 | 0 | 0.05921 | 5.0489 | 0 | 0 | 244.687 | 145.3677 | off_peak | 710.6223 | 100 | 0 | 16.98 | 0 | 83.02 | 733.9474 | 0
5820 | 894.73 | 864 | 30.3 | 171.6218 | 171.6217 | 0 | 1.3934e-05 | 1.3934e-05 | 0 | 0 | 0 | 0 | 74.3936 | 723.1083 | 0 | 0.05921 | 5.3885 | 0 | 0 | 244.687 | 171.6217 | off_peak | 723.1083 | 100 | 0 | 19.18 | 0 | 80.82 | 924.7834 | 0
5821 | 904.53 | 584.997 | 30.6 | 116.0737 | 116.0737 | 0 | 0 | 0 | 0 | 62.63 | 62.63 | 0 | 7.4394 | 725.8263 | 0 | 0.088511 | 5.5218 | 0 | 0 | 244.687 | 116.0737 | on_peak | 725.8263 |  |  | 12.83 | 6.92 | 80.24 | 640.9351 | 0
5822 | 902.55 | 264.359 | 30.8 | 52.4149 | 52.4149 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 850.1351 | 0 | 0.088511 | 5.637 | 0 | 0 | 244.687 | 52.4149 | on_peak | 850.1351 |  |  | 5.81 | 0 | 94.19 | 295.4651 | 0
5823 | 880.42 | 267.011 | 30.9 | 52.9213 | 52.9213 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 827.4987 | 0 | 0.088511 | 5.9661 | 0 | 0 | 244.687 | 52.9213 | on_peak | 827.4987 |  |  | 6.01 | 0 | 93.99 | 315.7349 | 0
5824 | 833.47 | 198.873 | 30.8 | 39.4309 | 39.4309 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 794.0391 | 0 | 0.088511 | 6.4929 | 0 | 0 | 244.687 | 39.4309 | on_peak | 794.0391 |  |  | 4.73 | 0 | 95.27 | 256.0196 | 0
5825 | 829.49 | 144.195 | 30.5 | 28.6213 | 28.6213 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 800.8687 | 0 | 0.088511 | 7.0586 | 0 | 0 | 244.687 | 28.6213 | on_peak | 800.8687 |  |  | 3.45 | 0 | 96.55 | 202.0262 | 0
5826 | 833.32 | 104.234 | 30 | 20.7275 | 20.7275 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 812.5925 | 0 | 0.088511 | 7.5019 | 0 | 0 | 244.687 | 20.7275 | on_peak | 812.5925 |  |  | 2.49 | 0 | 97.51 | 155.4946 | 0
5827 | 820.4 | 9.5 | 29.7 | 1.8912 | 1.8912 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 818.5088 | 0 | 0.088511 | 7.9436 | 0 | 0 | 244.687 | 1.8912 | on_peak | 818.5088 |  |  | 0.23 | 0 | 99.77 | 15.023 | 0
5828 | 840.44 | 0 | 29.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 840.44 | 0 | 0.088511 | 8.2626 | 0 | 0 | 244.687 | 0 | on_peak | 840.44 |  |  | 0 | 0 | 100 | 0 | 0
5829 | 832.8 | 0 | 29.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 832.8 | 0 | 0.088511 | 8.5905 | 0 | 0 | 244.687 | 0 | on_peak | 832.8 |  |  | 0 | 0 | 100 | 0 | 0
5830 | 782.73 | 0 | 29.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 782.73 | 0 | 0.05921 | 8.6336 | 0 | 0 | 244.687 | 0 | off_peak | 782.73 |  |  | 0 | 0 | 100 | 0 | 0
5831 | 836.68 | 0 | 29 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 19.0375 | 849.0789 | 0 | 0.05921 | 8.4962 | 0 | 0 | 244.687 | 0 | off_peak | 836.68 | 0 | 100 | 0 | 0 | 100 | 0 | 0
5832 | 777.14 | 0 | 28.9 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 30.6357 | 789.5389 | 0 | 0.05921 | 8.0896 | 0 | 0 | 244.687 | 0 | off_peak | 777.14 | 0 | 100 | 0 | 0 | 100 | 0 | 0
5833 | 747.15 | 0 | 28.7 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 42.2338 | 759.5489 | 0 | 0.05921 | 7.8722 | 0 | 0 | 244.687 | 0 | off_peak | 747.15 | 0 | 100 | 0 | 0 | 100 | 0 | 0
5834 | 721 | 0 | 28.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 42.2338 | 721 | 0 | 0.05921 | 7.6008 | 0 | 0 | 244.687 | 0 | off_peak | 721 |  |  | 0 | 0 | 100 | 0 | 0
5835 | 629.13 | 0 | 28.5 | 0 | 0 | 0 | 0 | 8.7263 | 8.7263 | 0 | 0 | 0 | 50.3966 | 637.8563 | 0 | 0.05921 | 7.127 | 0 | 0 | 244.687 | 0 | off_peak | 629.13 | 0 | 100 | 0 | 0 | 100 | 0 | 0
5836 | 657.94 | 0 | 28.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50.3966 | 657.94 | 0 | 0.05921 | 6.6121 | 0 | 0 | 244.687 | 0 | off_peak | 657.94 |  |  | 0 | 0 | 100 | 0 | 0
5837 | 667.3 | 0 | 28.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50.3966 | 667.3 | 0 | 0.05921 | 5.8682 | 0 | 0 | 244.687 | 0 | off_peak | 667.3 |  |  | 0 | 0 | 100 | 0 | 0
5838 | 745.71 | 0 | 28.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50.3966 | 745.71 | 0 | 0.05921 | 5.4292 | 0 | 0 | 244.687 | 0 | off_peak | 745.71 |  |  | 0 | 0 | 100 | 0 | 0
5839 | 756.74 | 38.5604 | 28.7 | 7.7045 | 0 | 0 | 7.7045 | 12.3989 | 4.6945 | 0 | 0 | 0 | 61.9947 | 761.4345 | 0 | 0.05921 | 5.0519 | 0 | 0 | 251.8939 | 0 | off_peak | 756.74 | 62.14 | 37.86 | 0 | 0 | 100 | 0 | 0
5840 | 792.01 | 173.034 | 29.1 | 34.5222 | 34.5222 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 73.5928 | 769.8867 | 0 | 0.05921 | 4.7367 | 0 | 0 | 251.8939 | 34.5222 | off_peak | 757.4878 | 0 | 100 | 4.36 | 0 | 95.64 | 163.5216 | 0
5841 | 840.19 | 362.108 | 29.4 | 72.1654 | 72.1654 | 0 | 0 | 0.80079 | 0.80079 | 0 | 0 | 0 | 74.3419 | 768.8254 | 0 | 0.05921 | 4.5515 | 0 | 0 | 251.8939 | 72.1654 | off_peak | 768.0246 | 0 | 100 | 8.59 | 0 | 91.41 | 328.4605 | 0
5842 | 832.55 | 652.244 | 29.8 | 129.7971 | 129.7971 | 0 | 0 | 0.05172 | 0.05172 | 0 | 0 | 0 | 74.3903 | 702.8046 | 0 | 0.05921 | 4.4891 | 0 | 0 | 251.8939 | 129.7971 | off_peak | 702.7529 | 0 | 100 | 15.59 | 0 | 84.41 | 582.6678 | 0
5843 | 869.47 | 694.141 | 30.1 | 137.9828 | 137.9828 | 0 | 0 | 0.0033404 | 0.0033404 | 0 | 0 | 0 | 74.3934 | 731.4905 | 0 | 0.05921 | 4.6961 | 0 | 0 | 251.8939 | 137.9828 | off_peak | 731.4872 | 0 | 100 | 15.87 | 0 | 84.13 | 647.982 | 0
5844 | 854.92 | 880.814 | 30.4 | 174.8974 | 174.8974 | 0 | 0 | 0.00021574 | 0.00021574 | 0 | 0 | 0 | 74.3936 | 680.0228 | 0 | 0.05921 | 5.0089 | 0 | 0 | 251.8939 | 174.8974 | off_peak | 680.0226 | 0 | 100 | 20.46 | 0 | 79.54 | 876.0465 | 0
5845 | 900.65 | 901.81 | 30.6 | 178.935 | 178.935 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 721.715 | 0 | 0.088511 | 5.1511 | 0 | 0 | 251.8939 | 178.935 | on_peak | 721.715 |  |  | 19.87 | 0 | 80.13 | 921.7046 | 0
5846 | 858.09 | 856.214 | 30.8 | 169.7631 | 169.7631 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 688.3269 | 0 | 0.088511 | 5.4194 | 0 | 0 | 251.8939 | 169.7631 | on_peak | 688.3269 |  |  | 19.78 | 0 | 80.22 | 920.0111 | 0
5847 | 876.25 | 749.089 | 31 | 148.414 | 148.414 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 727.836 | 0 | 0.088511 | 5.8877 | 0 | 0 | 251.8939 | 148.414 | on_peak | 727.836 |  |  | 16.94 | 0 | 83.06 | 873.8099 | 0
5848 | 836.8 | 365.373 | 30.8 | 72.4432 | 72.4432 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 764.3568 | 0 | 0.088511 | 6.4704 | 0 | 0 | 251.8939 | 72.4432 | on_peak | 764.3568 |  |  | 8.66 | 0 | 91.34 | 468.7351 | 0
5849 | 811.57 | 389.859 | 30.3 | 77.4401 | 77.4401 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 734.1299 | 0 | 0.088511 | 7.0874 | 0 | 0 | 251.8939 | 77.4401 | on_peak | 734.1299 |  |  | 9.54 | 0 | 90.46 | 548.8485 | 0
5850 | 887.77 | 84.3656 | 29.7 | 16.795 | 16.795 | 0 | 0 | 0 | 0 | 62.63 | 62.63 | 0 | 7.4394 | 808.345 | 0 | 0.088511 | 7.5637 | 0 | 0 | 251.8939 | 16.795 | on_peak | 808.345 |  |  | 1.89 | 7.05 | 91.05 | 127.032 | 0
5851 | 815.27 | 8.55 | 29.3 | 1.7046 | 1.7046 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 813.5654 | 0 | 0.088511 | 8.1053 | 0 | 0 | 251.8939 | 1.7046 | on_peak | 813.5654 |  |  | 0.21 | 0 | 99.79 | 13.816 | 0
5852 | 839.89 | 0 | 28.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 839.89 | 0 | 0.088511 | 8.5812 | 0 | 0 | 251.8939 | 0 | on_peak | 839.89 |  |  | 0 | 0 | 100 | 0 | 0
5853 | 793.51 | 0 | 28.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 793.51 | 0 | 0.088511 | 8.5942 | 0 | 0 | 251.8939 | 0 | on_peak | 793.51 |  |  | 0 | 0 | 100 | 0 | 0
5854 | 785.52 | 0 | 27.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 785.52 | 0 | 0.05921 | 8.6211 | 0 | 0 | 251.8939 | 0 | off_peak | 785.52 |  |  | 0 | 0 | 100 | 0 | 0
5855 | 774.69 | 0 | 27.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 774.69 | 0 | 0.05921 | 8.7489 | 0 | 0 | 251.8939 | 0 | off_peak | 774.69 |  |  | 0 | 0 | 100 | 0 | 0
5856 | 737.14 | 0 | 27.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 737.14 | 0 | 0.05921 | 8.7101 | 0 | 0 | 251.8939 | 0 | off_peak | 737.14 |  |  | 0 | 0 | 100 | 0 | 0
5857 | 673.19 | 0 | 27.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 673.19 | 0 | 0.05921 | 8.4147 | 0 | 0 | 251.8939 | 0 | off_peak | 673.19 |  |  | 0 | 0 | 100 | 0 | 0
5858 | 645.58 | 0 | 27.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 645.58 | 0 | 0.05921 | 8.1341 | 0 | 0 | 251.8939 | 0 | off_peak | 645.58 |  |  | 0 | 0 | 100 | 0 | 0
5859 | 636.02 | 0 | 27.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 636.02 | 0 | 0.05921 | 7.5963 | 0 | 0 | 251.8939 | 0 | off_peak | 636.02 |  |  | 0 | 0 | 100 | 0 | 0
5860 | 625.84 | 0 | 27.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 625.84 | 0 | 0.05921 | 7.0801 | 0 | 0 | 251.8939 | 0 | off_peak | 625.84 |  |  | 0 | 0 | 100 | 0 | 0
5861 | 637.2 | 0 | 27.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 637.2 | 0 | 0.05921 | 6.2386 | 0 | 0 | 251.8939 | 0 | off_peak | 637.2 |  |  | 0 | 0 | 100 | 0 | 0
5862 | 676.21 | 0 | 27.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 676.21 | 0 | 0.05921 | 5.5205 | 0 | 0 | 251.8939 | 0 | off_peak | 676.21 |  |  | 0 | 0 | 100 | 0 | 0
5863 | 686.43 | 37.5102 | 28.1 | 7.511 | 7.511 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 678.919 | 0 | 0.05921 | 5.0241 | 0 | 0 | 251.8939 | 7.511 | off_peak | 678.919 |  |  | 1.09 | 0 | 98.91 | 37.7366 | 0
5864 | 718.12 | 168.218 | 28.6 | 33.6227 | 33.6227 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 684.4973 | 0 | 0.05921 | 4.6629 | 0 | 0 | 251.8939 | 33.6227 | off_peak | 684.4973 |  |  | 4.68 | 0 | 95.32 | 156.7808 | 0
5865 | 809.38 | 360.51 | 29.1 | 71.9257 | 71.9257 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 737.4543 | 0 | 0.05921 | 4.4417 | 0 | 0 | 251.8939 | 71.9257 | off_peak | 737.4543 |  |  | 8.89 | 0 | 91.11 | 319.4726 | 0
5866 | 769.96 | 165.707 | 29.5 | 33.0121 | 33.0121 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 736.9479 | 0 | 0.05921 | 4.3126 | 0 | 0 | 251.8939 | 33.0121 | off_peak | 736.9479 |  |  | 4.29 | 0 | 95.71 | 142.3688 | 0
5867 | 725.35 | 83.6 | 29.8 | 16.6365 | 16.6365 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 708.7135 | 0 | 0.05921 | 4.2776 | 0 | 0 | 251.8939 | 16.6365 | off_peak | 708.7135 |  |  | 2.29 | 0 | 97.71 | 71.1641 | 0
5868 | 777.14 | 312.141 | 30.1 | 62.048 | 62.048 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 715.092 | 0 | 0.05921 | 4.3326 | 0 | 0 | 251.8939 | 62.048 | off_peak | 715.092 |  |  | 7.98 | 0 | 92.02 | 268.8287 | 0
5869 | 734.2 | 763.753 | 30.3 | 151.7091 | 151.7091 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 582.4909 | 0 | 0.05921 | 4.4988 | 0 | 0 | 251.8939 | 151.7091 | off_peak | 582.4909 |  |  | 20.66 | 0 | 79.34 | 682.5043 | 0
5870 | 717.45 | 805.902 | 30.4 | 160.0226 | 160.0226 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 557.4274 | 0 | 0.05921 | 4.9161 | 0 | 0 | 251.8939 | 160.0226 | off_peak | 557.4274 |  |  | 22.3 | 0 | 77.7 | 786.6884 | 0
5871 | 735.61 | 569.756 | 30.4 | 113.1327 | 113.1327 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 622.4773 | 0 | 0.05921 | 5.4498 | 0 | 0 | 251.8939 | 113.1327 | off_peak | 622.4773 |  |  | 15.38 | 0 | 84.62 | 616.5456 | 0
5872 | 720.41 | 482.553 | 30.4 | 95.8174 | 83.4184 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 0 | 19.0375 | 636.9916 | 0 | 0.05921 | 6.0069 | 0 | 0 | 263.4921 | 83.4184 | off_peak | 636.9916 | 100 | 0 | 11.58 | 0 | 88.42 | 501.0896 | 0
5873 | 713.56 | 231.462 | 30 | 46.0274 | 46.0274 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19.0375 | 667.5326 | 0 | 0.05921 | 6.2004 | 0 | 0 | 263.4921 | 46.0274 | off_peak | 667.5326 |  |  | 6.45 | 0 | 93.55 | 285.3868 | 0
5874 | 632.58 | 174.877 | 29.5 | 34.8389 | 34.8389 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19.0375 | 597.7411 | 0 | 0.05921 | 6.404 | 0 | 0 | 263.4921 | 34.8389 | off_peak | 597.7411 |  |  | 5.51 | 0 | 94.49 | 223.1075 | 0
5875 | 548.3 | 11.3643 | 29.3 | 2.2656 | 2.2656 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19.0375 | 546.0344 | 0 | 0.05921 | 6.6017 | 0 | 0 | 263.4921 | 2.2656 | off_peak | 546.0344 |  |  | 0.41 | 0 | 99.59 | 14.9572 | 0
5876 | 579.45 | 0 | 28.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19.0375 | 579.45 | 0 | 0.05921 | 6.8928 | 0 | 0 | 263.4921 | 0 | off_peak | 579.45 |  |  | 0 | 0 | 100 | 0 | 0
5877 | 549.33 | 0 | 28.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19.0375 | 549.33 | 0 | 0.05921 | 7.1075 | 0 | 0 | 263.4921 | 0 | off_peak | 549.33 |  |  | 0 | 0 | 100 | 0 | 0
5878 | 548.64 | 0 | 28.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19.0375 | 548.64 | 0 | 0.05921 | 7.3633 | 0 | 0 | 263.4921 | 0 | off_peak | 548.64 |  |  | 0 | 0 | 100 | 0 | 0
5879 | 529.68 | 0 | 27.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19.0375 | 529.68 | 0 | 0.05921 | 7.6765 | 0 | 0 | 263.4921 | 0 | off_peak | 529.68 |  |  | 0 | 0 | 100 | 0 | 0
5880 | 557.16 | 0 | 27.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19.0375 | 557.16 | 0 | 0.05921 | 7.7801 | 0 | 0 | 263.4921 | 0 | off_peak | 557.16 |  |  | 0 | 0 | 100 | 0 | 0
5881 | 571.76 | 0 | 27.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19.0375 | 571.76 | 0 | 0.05921 | 7.5503 | 0 | 0 | 263.4921 | 0 | off_peak | 571.76 |  |  | 0 | 0 | 100 | 0 | 0
5882 | 553.44 | 0 | 27.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19.0375 | 553.44 | 0 | 0.05921 | 7.3559 | 0 | 0 | 263.4921 | 0 | off_peak | 553.44 |  |  | 0 | 0 | 100 | 0 | 0
5883 | 552.78 | 0 | 27.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19.0375 | 552.78 | 0 | 0.05921 | 6.8803 | 0 | 0 | 263.4921 | 0 | off_peak | 552.78 |  |  | 0 | 0 | 100 | 0 | 0
5884 | 551.43 | 0 | 27 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19.0375 | 551.43 | 0 | 0.05921 | 6.396 | 0 | 0 | 263.4921 | 0 | off_peak | 551.43 |  |  | 0 | 0 | 100 | 0 | 0
5885 | 556.35 | 0 | 27 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19.0375 | 556.35 | 0 | 0.05921 | 5.7949 | 0 | 0 | 263.4921 | 0 | off_peak | 556.35 |  |  | 0 | 0 | 100 | 0 | 0
5886 | 606.87 | 0 | 27 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19.0375 | 606.87 | 0 | 0.05921 | 5.2226 | 0 | 0 | 263.4921 | 0 | off_peak | 606.87 |  |  | 0 | 0 | 100 | 0 | 0
5887 | 637.82 | 49.2097 | 27.2 | 9.886 | 9.886 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19.0375 | 627.934 | 0 | 0.05921 | 4.8107 | 0 | 0 | 263.4921 | 9.886 | off_peak | 627.934 |  |  | 1.55 | 0 | 98.45 | 47.5587 | 0
5888 | 709.15 | 243.158 | 27.4 | 48.8141 | 48.8141 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19.0375 | 660.3359 | 0 | 0.05921 | 4.5011 | 0 | 0 | 263.4921 | 48.8141 | off_peak | 660.3359 |  |  | 6.88 | 0 | 93.12 | 219.7181 | 0
5889 | 704.74 | 457.077 | 27.6 | 91.6917 | 91.6917 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19.0375 | 613.0483 | 0 | 0.05921 | 4.2528 | 0 | 0 | 263.4921 | 91.6917 | off_peak | 613.0483 |  |  | 13.01 | 0 | 86.99 | 389.9431 | 0
5890 | 716.16 | 646.983 | 28 | 129.5991 | 129.5991 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19.0375 | 586.5609 | 0 | 0.05921 | 4.092 | 0 | 0 | 263.4921 | 129.5991 | off_peak | 586.5609 |  |  | 18.1 | 0 | 81.9 | 530.3199 | 0
5891 | 676.82 | 780.678 | 28.4 | 156.1523 | 156.1523 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19.0375 | 520.6677 | 0 | 0.05921 | 4.0109 | 0 | 0 | 263.4921 | 156.1523 | off_peak | 520.6677 |  |  | 23.07 | 0 | 76.93 | 626.3147 | 0
5892 | 695.64 | 710.426 | 28.7 | 141.945 | 141.945 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19.0375 | 553.695 | 0 | 0.05921 | 4.0227 | 0 | 0 | 263.4921 | 141.945 | off_peak | 553.695 |  |  | 20.4 | 0 | 79.6 | 571.0071 | 0
5893 | 685.1 | 800.216 | 28.9 | 159.7686 | 159.7686 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19.0375 | 525.3314 | 0 | 0.05921 | 4.1297 | 0 | 0 | 263.4921 | 159.7686 | off_peak | 525.3314 |  |  | 23.32 | 0 | 76.68 | 659.8 | 0
5894 | 697.43 | 692.67 | 29 | 138.2458 | 138.2458 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 30.6357 | 571.5831 | 0 | 0.05921 | 4.4735 | 0 | 0 | 263.4921 | 138.2458 | off_peak | 559.1842 | 0 | 100 | 19.82 | 0 | 80.18 | 618.4377 | 0
5895 | 692.51 | 659.074 | 29.1 | 131.4926 | 131.4926 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30.6357 | 561.0174 | 0 | 0.05921 | 4.8859 | 0 | 0 | 263.4921 | 131.4926 | off_peak | 561.0174 |  |  | 18.99 | 0 | 81.01 | 642.4574 | 0
5896 | 704.96 | 367.659 | 29.1 | 73.3521 | 73.3521 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30.6357 | 631.6079 | 0 | 0.05921 | 5.3166 | 0 | 0 | 263.4921 | 73.3521 | off_peak | 631.6079 |  |  | 10.41 | 0 | 89.59 | 389.9809 | 0
5897 | 660.32 | 267.552 | 28.8 | 53.4381 | 53.4381 | 0 | 0 | 8.7263 | 8.7263 | 0 | 0 | 0 | 38.7984 | 615.6082 | 0 | 0.05921 | 5.6996 | 0 | 0 | 263.4921 | 53.4381 | off_peak | 606.8819 | 0 | 100 | 8.09 | 0 | 91.91 | 304.5778 | 0
5898 | 610.81 | 68.1635 | 28.4 | 13.6342 | 13.6342 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 38.7984 | 597.1758 | 0 | 0.05921 | 6.1653 | 0 | 0 | 263.4921 | 13.6342 | off_peak | 597.1758 |  |  | 2.23 | 0 | 97.77 | 84.0593 | 0
5899 | 585.8 | 4.75 | 28.2 | 0.95079 | 0.95079 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 38.7984 | 584.8492 | 0 | 0.05921 | 6.4472 | 0 | 0 | 263.4921 | 0.95079 | off_peak | 584.8492 |  |  | 0.16 | 0 | 99.84 | 6.1299 | 0
5900 | 563.08 | 0 | 27.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 38.7984 | 563.08 | 0 | 0.05921 | 6.8249 | 0 | 0 | 263.4921 | 0 | off_peak | 563.08 |  |  | 0 | 0 | 100 | 0 | 0
5901 | 559.93 | 0 | 27.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 38.7984 | 559.93 | 0 | 0.05921 | 7.1528 | 0 | 0 | 263.4921 | 0 | off_peak | 559.93 |  |  | 0 | 0 | 100 | 0 | 0
5902 | 575.31 | 0 | 27.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 38.7984 | 575.31 | 0 | 0.05921 | 7.3061 | 0 | 0 | 263.4921 | 0 | off_peak | 575.31 |  |  | 0 | 0 | 100 | 0 | 0
5903 | 567.42 | 0 | 27.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 38.7984 | 567.42 | 0 | 0.05921 | 7.5378 | 0 | 0 | 263.4921 | 0 | off_peak | 567.42 |  |  | 0 | 0 | 100 | 0 | 0
5904 | 569.13 | 0 | 27 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 50.3966 | 581.5289 | 0 | 0.05921 | 7.5426 | 0 | 0 | 263.4921 | 0 | off_peak | 569.13 | 0 | 100 | 0 | 0 | 100 | 0 | 0
5905 | 543.93 | 0 | 26.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50.3966 | 543.93 | 0 | 0.05921 | 7.5307 | 0 | 0 | 263.4921 | 0 | off_peak | 543.93 |  |  | 0 | 0 | 100 | 0 | 0
5906 | 568.12 | 0 | 26.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50.3966 | 568.12 | 0 | 0.05921 | 7.2794 | 0 | 0 | 263.4921 | 0 | off_peak | 568.12 |  |  | 0 | 0 | 100 | 0 | 0
5907 | 562.59 | 0 | 26.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50.3966 | 562.59 | 0 | 0.05921 | 6.8266 | 0 | 0 | 263.4921 | 0 | off_peak | 562.59 |  |  | 0 | 0 | 100 | 0 | 0
5908 | 581.66 | 0 | 26.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50.3966 | 581.66 | 0 | 0.05921 | 6.4108 | 0 | 0 | 263.4921 | 0 | off_peak | 581.66 |  |  | 0 | 0 | 100 | 0 | 0
5909 | 572.46 | 0 | 26.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50.3966 | 572.46 | 0 | 0.05921 | 5.8189 | 0 | 0 | 263.4921 | 0 | off_peak | 572.46 |  |  | 0 | 0 | 100 | 0 | 0
5910 | 621.45 | 0 | 26.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50.3966 | 621.45 | 0 | 0.05921 | 5.2934 | 0 | 0 | 263.4921 | 0 | off_peak | 621.45 |  |  | 0 | 0 | 100 | 0 | 0
5911 | 621.5 | 47.6294 | 26.6 | 9.5894 | 9.5894 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50.3966 | 611.9106 | 0 | 0.05921 | 4.8121 | 0 | 0 | 263.4921 | 9.5894 | off_peak | 611.9106 |  |  | 1.54 | 0 | 98.46 | 46.1451 | 0
5912 | 610.58 | 238.885 | 26.9 | 48.0433 | 48.0433 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50.3966 | 562.5367 | 0 | 0.05921 | 4.4796 | 0 | 0 | 263.4921 | 48.0433 | off_peak | 562.5367 |  |  | 7.87 | 0 | 92.13 | 215.2159 | 0
5913 | 633.93 | 341.612 | 27.1 | 68.6535 | 68.6535 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50.3966 | 565.2765 | 0 | 0.05921 | 4.287 | 0 | 0 | 263.4921 | 68.6535 | off_peak | 565.2765 |  |  | 10.83 | 0 | 89.17 | 294.3142 | 0
5914 | 615.91 | 512.578 | 27.4 | 102.9002 | 102.9002 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 61.9947 | 525.4087 | 0 | 0.05921 | 4.177 | 0 | 0 | 263.4921 | 102.9002 | off_peak | 513.0098 | 0 | 100 | 16.71 | 0 | 83.29 | 429.815 | 0
5915 | 651.59 | 713.086 | 27.8 | 142.9444 | 142.9444 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 61.9947 | 508.6456 | 0 | 0.05921 | 4.1953 | 0 | 0 | 263.4921 | 142.9444 | off_peak | 508.6456 |  |  | 21.94 | 0 | 78.06 | 599.6892 | 0
5916 | 669.15 | 875.136 | 28 | 175.3011 | 175.3011 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 61.9947 | 493.8489 | 0 | 0.05921 | 4.2299 | 0 | 0 | 263.4921 | 175.3011 | off_peak | 493.8489 |  |  | 26.2 | 0 | 73.8 | 741.5029 | 0
5917 | 634.46 | 796.136 | 28.1 | 159.4184 | 159.4184 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 61.9947 | 475.0416 | 0 | 0.05921 | 4.3371 | 0 | 0 | 263.4921 | 159.4184 | on_peak | 475.0416 |  |  | 25.13 | 0 | 74.87 | 691.4179 | 0
5918 | 652.43 | 690.948 | 28.1 | 138.3555 | 138.3555 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 61.9947 | 514.0745 | 0 | 0.05921 | 4.5858 | 0 | 0 | 263.4921 | 138.3555 | on_peak | 514.0745 |  |  | 21.21 | 0 | 78.79 | 634.4641 | 0
5919 | 619.54 | 553.657 | 28 | 110.9047 | 110.9047 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 61.9947 | 508.6353 | 0 | 0.05921 | 4.9519 | 0 | 0 | 263.4921 | 110.9047 | on_peak | 508.6353 |  |  | 17.9 | 0 | 82.1 | 549.1851 | 0
5920 | 616.76 | 579.957 | 27.8 | 116.2575 | 116.2575 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 61.9947 | 500.5025 | 0 | 0.05921 | 5.4699 | 0 | 0 | 263.4921 | 116.2575 | on_peak | 500.5025 |  |  | 18.85 | 0 | 81.15 | 635.9156 | 0
5921 | 609.8 | 372.123 | 27.6 | 74.6496 | 74.6496 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 73.5928 | 547.5494 | 0 | 0.05921 | 6.1221 | 0 | 0 | 263.4921 | 74.6496 | on_peak | 535.1504 | 0 | 100 | 12.24 | 0 | 87.76 | 457.012 | 0
5922 | 577.47 | 48.6841 | 27.3 | 9.7769 | 9.7769 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 73.5928 | 567.6931 | 0 | 0.05921 | 6.6152 | 0 | 0 | 263.4921 | 9.7769 | on_peak | 567.6931 |  |  | 1.69 | 0 | 98.31 | 64.6758 | 0
5923 | 593.66 | 1.9 | 27.2 | 0.3817 | 0.3817 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 73.5928 | 593.2783 | 0 | 0.05921 | 7.0427 | 0 | 0 | 263.4921 | 0.3817 | on_peak | 593.2783 |  |  | 0.06 | 0 | 99.94 | 2.6882 | 0
5924 | 585.57 | 0 | 27 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 73.5928 | 585.57 | 0 | 0.05921 | 7.3157 | 0 | 0 | 263.4921 | 0 | on_peak | 585.57 |  |  | 0 | 0 | 100 | 0 | 0
5925 | 609.09 | 0 | 27 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 73.5928 | 609.09 | 0 | 0.05921 | 7.6477 | 0 | 0 | 263.4921 | 0 | on_peak | 609.09 |  |  | 0 | 0 | 100 | 0 | 0
5926 | 566.2 | 0 | 27 | 0 | 0 | 0 | 0 | 0.80079 | 0.80079 | 0 | 0 | 0 | 74.3419 | 567.0008 | 0 | 0.05921 | 7.8743 | 0 | 0 | 263.4921 | 0 | off_peak | 566.2 | 0 | 100 | 0 | 0 | 100 | 0 | 0
5927 | 585.4 | 0 | 26.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3419 | 585.4 | 0 | 0.05921 | 8.0733 | 0 | 0 | 263.4921 | 0 | off_peak | 585.4 |  |  | 0 | 0 | 100 | 0 | 0
5928 | 568.81 | 0 | 26.9 | 0 | 0 | 0 | 0 | 0.05172 | 0.05172 | 0 | 0 | 0 | 74.3903 | 568.8617 | 0 | 0.05921 | 8.3327 | 0 | 0 | 263.4921 | 0 | off_peak | 568.81 | 0 | 100 | 0 | 0 | 100 | 0 | 0
5929 | 587.08 | 0 | 26.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3903 | 587.08 | 0 | 0.05921 | 8.372 | 0 | 0 | 263.4921 | 0 | off_peak | 587.08 |  |  | 0 | 0 | 100 | 0 | 0
5930 | 584.8 | 0 | 26.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3903 | 584.8 | 0 | 0.05921 | 8.124 | 0 | 0 | 263.4921 | 0 | off_peak | 584.8 |  |  | 0 | 0 | 100 | 0 | 0
5931 | 568.15 | 0 | 26.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3903 | 568.15 | 0 | 0.05921 | 7.5193 | 0 | 0 | 263.4921 | 0 | off_peak | 568.15 |  |  | 0 | 0 | 100 | 0 | 0
5932 | 604.26 | 0 | 26.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3903 | 604.26 | 0 | 0.05921 | 6.8646 | 0 | 0 | 263.4921 | 0 | off_peak | 604.26 |  |  | 0 | 0 | 100 | 0 | 0
5933 | 569.48 | 0 | 26.6 | 0 | 0 | 0 | 0 | 0.0033404 | 0.0033404 | 0 | 0 | 0 | 74.3934 | 569.4833 | 0 | 0.05921 | 5.9837 | 0 | 0 | 263.4921 | 0 | off_peak | 569.48 | 0 | 100 | 0 | 0 | 100 | 0 | 0
5934 | 690.76 | 0 | 26.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3934 | 690.76 | 0 | 0.05921 | 5.3109 | 0 | 0 | 263.4921 | 0 | off_peak | 690.76 |  |  | 0 | 0 | 100 | 0 | 0
5935 | 776.82 | 47.8141 | 26.7 | 9.6231 | 9.6231 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3934 | 767.1969 | 0 | 0.05921 | 4.7938 | 0 | 0 | 263.4921 | 9.6231 | off_peak | 767.1969 |  |  | 1.24 | 0 | 98.76 | 46.1308 | 0
5936 | 872.59 | 241.789 | 26.9 | 48.6274 | 48.6274 | 0 | 0 | 0.00021574 | 0.00021574 | 0 | 0 | 0 | 74.3936 | 823.9628 | 0 | 0.05921 | 4.461 | 0 | 0 | 263.4921 | 48.6274 | off_peak | 823.9626 | 0 | 100 | 5.57 | 0 | 94.43 | 216.9272 | 0
5937 | 873.49 | 454.608 | 27.1 | 91.3622 | 91.3622 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 782.1278 | 0 | 0.05921 | 4.258 | 0 | 0 | 263.4921 | 91.3622 | off_peak | 782.1278 |  |  | 10.46 | 0 | 89.54 | 389.0194 | 0
5938 | 822.46 | 643.615 | 27.4 | 129.206 | 129.206 | 0 | 0 | 1.4896e-05 | 1.4896e-05 | 0 | 0 | 0 | 74.3936 | 693.254 | 0 | 0.05921 | 4.1767 | 0 | 0 | 263.4921 | 129.206 | off_peak | 693.254 | 0 | 100 | 15.71 | 0 | 84.29 | 539.661 | 0
5939 | 798.71 | 789.656 | 27.6 | 158.4086 | 158.4086 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 640.3014 | 0 | 0.05921 | 4.342 | 0 | 0 | 263.4921 | 158.4086 | off_peak | 640.3014 |  |  | 19.83 | 0 | 80.17 | 687.8061 | 0
5940 | 865.98 | 877.734 | 27.8 | 175.9495 | 175.9495 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 690.0305 | 0 | 0.05921 | 4.6983 | 0 | 0 | 263.4921 | 175.9495 | off_peak | 690.0305 |  |  | 20.32 | 0 | 79.68 | 826.6599 | 0
5941 | 833.65 | 897.909 | 27.8 | 179.9938 | 179.9938 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 653.6562 | 0 | 0.088511 | 4.8843 | 0 | 0 | 263.4921 | 179.9938 | on_peak | 653.6562 |  |  | 21.59 | 0 | 78.41 | 879.1376 | 0
5942 | 863.82 | 791.084 | 27.8 | 158.5797 | 158.5797 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 705.2403 | 0 | 0.088511 | 5.0414 | 0 | 0 | 263.4921 | 158.5797 | on_peak | 705.2403 |  |  | 18.36 | 0 | 81.64 | 799.463 | 0
5943 | 853.42 | 739.611 | 27.7 | 148.3155 | 148.3155 | 0 | 0 | 0 | 0 | 62.63 | 62.63 | 0 | 7.4394 | 642.4746 | 0 | 0.088511 | 5.2763 | 0 | 0 | 263.4921 | 148.3155 | on_peak | 642.4746 |  |  | 17.38 | 7.34 | 75.28 | 782.5577 | 0
5944 | 790.04 | 512.896 | 27.6 | 102.8893 | 102.8893 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 687.1507 | 0 | 0.088511 | 5.7105 | 0 | 0 | 263.4921 | 102.8893 | on_peak | 687.1507 |  |  | 13.02 | 0 | 86.98 | 587.5543 | 0
5945 | 809.94 | 14.25 | 27.4 | 2.8607 | 2.8607 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 807.0793 | 0 | 0.088511 | 6.2476 | 0 | 0 | 263.4921 | 2.8607 | on_peak | 807.0793 |  |  | 0.35 | 0 | 99.65 | 17.8724 | 0
5946 | 836.07 | 7.6 | 27.1 | 1.5274 | 1.5274 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 834.5426 | 0 | 0.088511 | 6.7724 | 0 | 0 | 263.4921 | 1.5274 | on_peak | 834.5426 |  |  | 0.18 | 0 | 99.82 | 10.3439 | 0
5947 | 829.21 | 0 | 27 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 829.21 | 0 | 0.088511 | 7.4141 | 0 | 0 | 263.4921 | 0 | on_peak | 829.21 |  |  | 0 | 0 | 100 | 0 | 0
5948 | 839.2 | 0 | 26.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 839.2 | 0 | 0.088511 | 7.8512 | 0 | 0 | 263.4921 | 0 | on_peak | 839.2 |  |  | 0 | 0 | 100 | 0 | 0
5949 | 791.38 | 0 | 26.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 791.38 | 0 | 0.088511 | 8.1302 | 0 | 0 | 263.4921 | 0 | on_peak | 791.38 |  |  | 0 | 0 | 100 | 0 | 0
5950 | 811.62 | 0 | 26.8 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 19.0375 | 824.0189 | 0 | 0.05921 | 8.4208 | 0 | 0 | 263.4921 | 0 | off_peak | 811.62 | 0 | 100 | 0 | 0 | 100 | 0 | 0
5951 | 809.67 | 0 | 26.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19.0375 | 809.67 | 0 | 0.05921 | 8.5598 | 0 | 0 | 263.4921 | 0 | off_peak | 809.67 |  |  | 0 | 0 | 100 | 0 | 0
5952 | 816.09 | 0 | 26.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19.0375 | 816.09 | 0 | 0.05921 | 8.74 | 0 | 0 | 263.4921 | 0 | off_peak | 816.09 |  |  | 0 | 0 | 100 | 0 | 0
5953 | 733.51 | 0 | 26.6 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 30.6357 | 745.9089 | 0 | 0.05921 | 8.7825 | 0 | 0 | 263.4921 | 0 | off_peak | 733.51 | 0 | 100 | 0 | 0 | 100 | 0 | 0
5954 | 658.85 | 0 | 26.5 | 0 | 0 | 0 | 0 | 8.7263 | 8.7263 | 0 | 0 | 0 | 38.7984 | 667.5763 | 0 | 0.05921 | 8.4932 | 0 | 0 | 263.4921 | 0 | off_peak | 658.85 | 0 | 100 | 0 | 0 | 100 | 0 | 0
5955 | 621.08 | 0 | 26.4 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 50.3966 | 633.4789 | 0 | 0.05921 | 7.8251 | 0 | 0 | 263.4921 | 0 | off_peak | 621.08 | 0 | 100 | 0 | 0 | 100 | 0 | 0
5956 | 662.76 | 0 | 26.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50.3966 | 662.76 | 0 | 0.05921 | 7.0342 | 0 | 0 | 263.4921 | 0 | off_peak | 662.76 |  |  | 0 | 0 | 100 | 0 | 0
5957 | 646.64 | 0 | 26.2 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 61.9947 | 659.0389 | 0 | 0.05921 | 6.1821 | 0 | 0 | 263.4921 | 0 | off_peak | 646.64 | 0 | 100 | 0 | 0 | 100 | 0 | 0
5958 | 704.19 | 0 | 26.2 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 73.5928 | 716.5889 | 0 | 0.05921 | 5.5043 | 0 | 0 | 263.4921 | 0 | off_peak | 704.19 | 0 | 100 | 0 | 0 | 100 | 0 | 0
5959 | 770.15 | 47.6356 | 26.2 | 9.6045 | 9.6045 | 0 | 0 | 0.80079 | 0.80079 | 0 | 0 | 0 | 74.3419 | 761.3463 | 0 | 0.05921 | 5.0076 | 0 | 0 | 263.4921 | 9.6045 | off_peak | 760.5455 | 0 | 100 | 1.25 | 0 | 98.75 | 48.0959 | 0
5960 | 840.7 | 242.69 | 26.5 | 48.8793 | 48.8793 | 0 | 0 | 0.05172 | 0.05172 | 0 | 0 | 0 | 74.3903 | 791.8724 | 0 | 0.05921 | 4.6231 | 0 | 0 | 263.4921 | 48.8793 | off_peak | 791.8207 | 0 | 100 | 5.81 | 0 | 94.19 | 225.9748 | 0
5961 | 862.35 | 364.504 | 26.8 | 73.3338 | 73.3338 | 0 | 0 | 0.0033404 | 0.0033404 | 0 | 0 | 0 | 74.3934 | 789.0196 | 0 | 0.05921 | 4.3503 | 0 | 0 | 263.4921 | 73.3338 | off_peak | 789.0162 | 0 | 100 | 8.5 | 0 | 91.5 | 319.022 | 0
5962 | 851.33 | 643.157 | 27.3 | 129.1609 | 129.1609 | 0 | 0 | 0.00021574 | 0.00021574 | 0 | 0 | 0 | 74.3936 | 722.1693 | 0 | 0.05921 | 4.2493 | 0 | 0 | 263.4921 | 129.1609 | off_peak | 722.1691 | 0 | 100 | 15.17 | 0 | 84.83 | 548.8472 | 0
5963 | 826.45 | 676.438 | 27.8 | 135.5979 | 135.5979 | 0 | 1.3934e-05 | 1.3934e-05 | 0 | 0 | 0 | 0 | 74.3936 | 690.8521 | 0 | 0.05921 | 4.3993 | 0 | 0 | 263.4921 | 135.5979 | off_peak | 690.8521 | 100 | 0 | 16.41 | 0 | 83.59 | 596.5313 | 0
5964 | 903.98 | 773.725 | 28.3 | 154.818 | 154.818 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 749.162 | 0 | 0.05921 | 4.7206 | 0 | 0 | 263.4921 | 154.818 | off_peak | 749.162 |  |  | 17.13 | 0 | 82.87 | 730.8337 | 0
5965 | 818.86 | 581.387 | 28.7 | 116.1627 | 116.1627 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 702.6973 | 0 | 0.088511 | 4.9345 | 0 | 0 | 263.4921 | 116.1627 | on_peak | 702.6973 |  |  | 14.19 | 0 | 85.81 | 573.2021 | 0
5966 | 866.14 | 723.037 | 28.9 | 144.3593 | 144.3593 | 0 | 0 | 0 | 0 | 62.63 | 62.63 | 0 | 7.4394 | 659.1507 | 0 | 0.088511 | 5.064 | 0 | 0 | 263.4921 | 144.3593 | on_peak | 659.1507 |  |  | 16.67 | 7.23 | 76.1 | 731.032 | 0
5967 | 848.3 | 302.103 | 28.9 | 60.3169 | 60.3169 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 787.9831 | 0 | 0.088511 | 5.2417 | 0 | 0 | 263.4921 | 60.3169 | on_peak | 787.9831 |  |  | 7.11 | 0 | 92.89 | 316.1661 | 0
5968 | 827.34 | 229.038 | 28.8 | 45.7457 | 45.7457 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 781.5943 | 0 | 0.088511 | 5.6593 | 0 | 0 | 263.4921 | 45.7457 | on_peak | 781.5943 |  |  | 5.53 | 0 | 94.47 | 258.8908 | 0
5969 | 829.12 | 188.364 | 28.6 | 37.6494 | 37.6494 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 791.4706 | 0 | 0.088511 | 6.308 | 0 | 0 | 263.4921 | 37.6494 | on_peak | 791.4706 |  |  | 4.54 | 0 | 95.46 | 237.4918 | 0
5970 | 814.92 | 16.15 | 28.3 | 3.2315 | 3.2315 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 811.6885 | 0 | 0.088511 | 6.8711 | 0 | 0 | 263.4921 | 3.2315 | on_peak | 811.6885 |  |  | 0.4 | 0 | 99.6 | 22.2041 | 0
5971 | 828.95 | 0 | 28.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 828.95 | 0 | 0.088511 | 7.4862 | 0 | 0 | 263.4921 | 0 | on_peak | 828.95 |  |  | 0 | 0 | 100 | 0 | 0
5972 | 823.47 | 0 | 27.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 823.47 | 0 | 0.088511 | 7.9118 | 0 | 0 | 263.4921 | 0 | on_peak | 823.47 |  |  | 0 | 0 | 100 | 0 | 0
5973 | 784.55 | 0 | 27.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 784.55 | 0 | 0.088511 | 8.178 | 0 | 0 | 263.4921 | 0 | on_peak | 784.55 |  |  | 0 | 0 | 100 | 0 | 0
5974 | 780.24 | 0 | 27.4 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 19.0375 | 792.6389 | 0 | 0.05921 | 8.3895 | 0 | 0 | 263.4921 | 0 | off_peak | 780.24 | 0 | 100 | 0 | 0 | 100 | 0 | 0
5975 | 818.07 | 0 | 27.2 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 30.6357 | 830.4689 | 0 | 0.05921 | 8.6329 | 0 | 0 | 263.4921 | 0 | off_peak | 818.07 | 0 | 100 | 0 | 0 | 100 | 0 | 0
5976 | 804.37 | 0 | 26.9 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 42.2338 | 816.7689 | 0 | 0.05921 | 8.8568 | 0 | 0 | 263.4921 | 0 | off_peak | 804.37 | 0 | 100 | 0 | 0 | 100 | 0 | 0
5977 | 736.86 | 0 | 26.6 | 0 | 0 | 0 | 0 | 8.7263 | 8.7263 | 0 | 0 | 0 | 50.3966 | 745.5863 | 0 | 0.05921 | 8.7756 | 0 | 0 | 263.4921 | 0 | off_peak | 736.86 | 0 | 100 | 0 | 0 | 100 | 0 | 0
5978 | 654.95 | 0 | 26.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50.3966 | 654.95 | 0 | 0.05921 | 8.5091 | 0 | 0 | 263.4921 | 0 | off_peak | 654.95 |  |  | 0 | 0 | 100 | 0 | 0
5979 | 620.01 | 0 | 26.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50.3966 | 620.01 | 0 | 0.05921 | 7.8924 | 0 | 0 | 263.4921 | 0 | off_peak | 620.01 |  |  | 0 | 0 | 100 | 0 | 0
5980 | 652.22 | 0 | 26.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50.3966 | 652.22 | 0 | 0.05921 | 7.0602 | 0 | 0 | 263.4921 | 0 | off_peak | 652.22 |  |  | 0 | 0 | 100 | 0 | 0
5981 | 641.36 | 0 | 26.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50.3966 | 641.36 | 0 | 0.05921 | 6.1186 | 0 | 0 | 263.4921 | 0 | off_peak | 641.36 |  |  | 0 | 0 | 100 | 0 | 0
5982 | 694.33 | 0 | 26.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50.3966 | 694.33 | 0 | 0.05921 | 5.4526 | 0 | 0 | 263.4921 | 0 | off_peak | 694.33 |  |  | 0 | 0 | 100 | 0 | 0
5983 | 725.73 | 48.5023 | 26.6 | 9.7651 | 9.7651 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 61.9947 | 728.3638 | 0 | 0.05921 | 4.9838 | 0 | 0 | 263.4921 | 9.7651 | off_peak | 715.9649 | 0 | 100 | 1.35 | 0 | 98.65 | 48.6672 | 0
5984 | 810.86 | 244.347 | 27 | 49.124 | 49.124 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 73.5928 | 774.1349 | 0 | 0.05921 | 4.6566 | 0 | 0 | 263.4921 | 49.124 | off_peak | 761.736 | 0 | 100 | 6.06 | 0 | 93.94 | 228.7509 | 0
5985 | 806.3 | 458.603 | 27.4 | 92.0647 | 92.0647 | 0 | 0 | 0.80079 | 0.80079 | 0 | 0 | 0 | 74.3419 | 715.0361 | 0 | 0.05921 | 4.4449 | 0 | 0 | 263.4921 | 92.0647 | off_peak | 714.2353 | 0 | 100 | 11.42 | 0 | 88.58 | 409.217 | 0
5986 | 840.26 | 441.891 | 27.9 | 88.5487 | 88.497 | 0 | 0.05172 | 0.05172 | 0 | 0 | 0 | 0 | 74.3903 | 751.763 | 0 | 0.05921 | 4.3455 | 0 | 0 | 263.5405 | 88.497 | off_peak | 751.763 | 100 | 0 | 10.53 | 0 | 89.47 | 384.5653 | 0
5987 | 830.31 | 716.699 | 28.4 | 143.3551 | 143.3551 | 0 | 0 | 0.0033404 | 0.0033404 | 0 | 0 | 0 | 74.3934 | 686.9582 | 0 | 0.05921 | 4.5146 | 0 | 0 | 263.5405 | 143.3551 | off_peak | 686.9549 | 0 | 100 | 17.27 | 0 | 82.73 | 647.194 | 0
5988 | 879.55 | 875.277 | 29 | 174.6913 | 174.6913 | 0 | 0 | 0.00021574 | 0.00021574 | 0 | 0 | 0 | 74.3936 | 704.8589 | 0 | 0.05921 | 4.8657 | 0 | 0 | 263.5405 | 174.6913 | off_peak | 704.8587 | 0 | 100 | 19.86 | 0 | 80.14 | 849.9945 | 0
5989 | 836.98 | 895.892 | 29.4 | 178.5445 | 178.5445 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 658.4355 | 0 | 0.088511 | 4.9896 | 0 | 0 | 263.5405 | 178.5445 | on_peak | 658.4355 |  |  | 21.33 | 0 | 78.67 | 890.8689 | 0
5990 | 879.95 | 837.999 | 29.7 | 166.8236 | 166.8236 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 713.1264 | 0 | 0.088511 | 5.1018 | 0 | 0 | 263.5405 | 166.8236 | on_peak | 713.1264 |  |  | 18.96 | 0 | 81.04 | 851.0946 | 0
5991 | 848.66 | 728.594 | 29.8 | 144.9908 | 144.9908 | 0 | 0 | 0 | 0 | 62.63 | 62.63 | 0 | 7.4394 | 641.0392 | 0 | 0.088511 | 5.2283 | 0 | 0 | 263.5405 | 144.9908 | on_peak | 641.0392 |  |  | 17.08 | 7.38 | 75.54 | 758.0483 | 0
5992 | 863.16 | 565.207 | 29.6 | 112.5591 | 112.5591 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 750.6009 | 0 | 0.088511 | 5.6014 | 0 | 0 | 263.5405 | 112.5591 | on_peak | 750.6009 |  |  | 13.04 | 0 | 86.96 | 630.4844 | 0
5993 | 866.45 | 366.027 | 29.3 | 72.9731 | 72.9731 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 793.4769 | 0 | 0.088511 | 6.3288 | 0 | 0 | 263.5405 | 72.9731 | on_peak | 793.4769 |  |  | 8.42 | 0 | 91.58 | 461.8319 | 0
5994 | 876.38 | 155.586 | 28.8 | 31.0752 | 31.0752 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 845.3048 | 0 | 0.088511 | 7.0703 | 0 | 0 | 263.5405 | 31.0752 | on_peak | 845.3048 |  |  | 3.55 | 0 | 96.45 | 219.7112 | 0
5995 | 843.11 | 0 | 28.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 843.11 | 0 | 0.088511 | 7.7 | 0 | 0 | 263.5405 | 0 | on_peak | 843.11 |  |  | 0 | 0 | 100 | 0 | 0
5996 | 813.83 | 0 | 28 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 813.83 | 0 | 0.088511 | 8.042 | 0 | 0 | 263.5405 | 0 | on_peak | 813.83 |  |  | 0 | 0 | 100 | 0 | 0
5997 | 842.43 | 0 | 27.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 842.43 | 0 | 0.088511 | 8.4138 | 0 | 0 | 263.5405 | 0 | on_peak | 842.43 |  |  | 0 | 0 | 100 | 0 | 0
5998 | 808.37 | 0 | 27.6 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 19.0375 | 820.7689 | 0 | 0.05921 | 8.6588 | 0 | 0 | 263.5405 | 0 | off_peak | 808.37 | 0 | 100 | 0 | 0 | 100 | 0 | 0
5999 | 832.81 | 0 | 27.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19.0375 | 832.81 | 0 | 0.05921 | 8.8352 | 0 | 0 | 263.5405 | 0 | off_peak | 832.81 |  |  | 0 | 0 | 100 | 0 | 0
6000 | 770.88 | 0 | 27.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19.0375 | 770.88 | 0 | 0.05921 | 8.9071 | 0 | 0 | 263.5405 | 0 | off_peak | 770.88 |  |  | 0 | 0 | 100 | 0 | 0
6001 | 752.49 | 0 | 27.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19.0375 | 752.49 | 0 | 0.05921 | 8.7321 | 0 | 0 | 263.5405 | 0 | off_peak | 752.49 |  |  | 0 | 0 | 100 | 0 | 0
6002 | 683.57 | 0 | 27 | 0 | 0 | 0 | 0 | 8.7263 | 8.7263 | 0 | 0 | 0 | 27.2003 | 692.2963 | 0 | 0.05921 | 8.4392 | 0 | 0 | 263.5405 | 0 | off_peak | 683.57 | 0 | 100 | 0 | 0 | 100 | 0 | 0
6003 | 636.03 | 0 | 26.8 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 38.7984 | 648.4289 | 0 | 0.05921 | 7.8676 | 0 | 0 | 263.5405 | 0 | off_peak | 636.03 | 0 | 100 | 0 | 0 | 100 | 0 | 0
6004 | 663.98 | 0 | 26.6 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 50.3966 | 676.3789 | 0 | 0.05921 | 7.1435 | 0 | 0 | 263.5405 | 0 | off_peak | 663.98 | 0 | 100 | 0 | 0 | 100 | 0 | 0
6005 | 652.33 | 0 | 26.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50.3966 | 652.33 | 0 | 0.05921 | 6.1863 | 0 | 0 | 263.5405 | 0 | off_peak | 652.33 |  |  | 0 | 0 | 100 | 0 | 0
6006 | 734.85 | 0 | 26.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50.3966 | 734.85 | 0 | 0.05921 | 5.5553 | 0 | 0 | 263.5405 | 0 | off_peak | 734.85 |  |  | 0 | 0 | 100 | 0 | 0
6007 | 780.12 | 33.5016 | 26.8 | 6.7401 | 0 | 0 | 6.7401 | 12.3989 | 5.6588 | 0 | 0 | 0 | 61.9947 | 785.7788 | 0 | 0.05921 | 5.0413 | 0 | 0 | 269.8453 | 0 | off_peak | 780.12 | 54.36 | 45.64 | 0 | 0 | 100 | 0 | 0
6008 | 800.77 | 172.966 | 27.2 | 34.7482 | 34.7482 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 73.5928 | 778.4207 | 0 | 0.05921 | 4.6882 | 0 | 0 | 269.8453 | 34.7482 | off_peak | 766.0218 | 0 | 100 | 4.34 | 0 | 95.66 | 162.9056 | 0
6009 | 795.68 | 446.992 | 27.7 | 89.6361 | 89.6361 | 0 | 0 | 0.80079 | 0.80079 | 0 | 0 | 0 | 74.3419 | 706.8447 | 0 | 0.05921 | 4.4346 | 0 | 0 | 269.8453 | 89.6361 | off_peak | 706.0439 | 0 | 100 | 11.27 | 0 | 88.73 | 397.4977 | 0
6010 | 825.37 | 511.611 | 28.4 | 102.3331 | 102.3331 | 0 | 0 | 0.05172 | 0.05172 | 0 | 0 | 0 | 74.3903 | 723.0886 | 0 | 0.05921 | 4.3292 | 0 | 0 | 269.8453 | 102.3331 | off_peak | 723.0369 | 0 | 100 | 12.4 | 0 | 87.6 | 443.0218 | 0
6011 | 849.12 | 766.034 | 29 | 152.8881 | 152.8881 | 0 | 0 | 0.0033404 | 0.0033404 | 0 | 0 | 0 | 74.3934 | 696.2352 | 0 | 0.05921 | 4.4651 | 0 | 0 | 269.8453 | 152.8881 | off_peak | 696.2319 | 0 | 100 | 18.01 | 0 | 81.99 | 682.6611 | 0
6012 | 898.96 | 850.472 | 29.6 | 169.3686 | 169.3686 | 0 | 0 | 0.00021574 | 0.00021574 | 0 | 0 | 0 | 74.3936 | 729.5916 | 0 | 0.05921 | 4.7919 | 0 | 0 | 269.8453 | 169.3686 | off_peak | 729.5914 | 0 | 100 | 18.84 | 0 | 81.16 | 811.5942 | 0
6013 | 900.61 | 807.399 | 30.1 | 160.4965 | 160.4965 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 740.1135 | 0 | 0.088511 | 4.9253 | 0 | 0 | 269.8453 | 160.4965 | on_peak | 740.1135 |  |  | 17.82 | 0 | 82.18 | 790.496 | 0
6014 | 863.7 | 831.412 | 30.3 | 165.1486 | 165.1486 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 698.5514 | 0 | 0.088511 | 5.0917 | 0 | 0 | 269.8453 | 165.1486 | on_peak | 698.5514 |  |  | 19.12 | 0 | 80.88 | 840.8936 | 0
6015 | 896.27 | 718.844 | 30.4 | 142.7361 | 142.7361 | 0 | 0 | 0 | 0 | 37.3982 | 37.3982 | 0 | 34.4133 | 716.1357 | 0 | 0.088511 | 5.3438 | 0 | 0 | 269.8453 | 142.7361 | on_peak | 716.1357 |  |  | 15.93 | 4.17 | 79.9 | 762.7553 | 0
6016 | 872.55 | 492.011 | 30.3 | 97.7312 | 97.7312 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 34.4133 | 774.8188 | 0 | 0.088511 | 5.8503 | 0 | 0 | 269.8453 | 97.7312 | on_peak | 774.8188 |  |  | 11.2 | 0 | 88.8 | 571.7585 | 0
6017 | 832.68 | 320.209 | 30 | 63.6752 | 63.6752 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 34.4133 | 769.0048 | 0 | 0.088511 | 6.4385 | 0 | 0 | 269.8453 | 63.6752 | on_peak | 769.0048 |  |  | 7.65 | 0 | 92.35 | 409.9724 | 0
6018 | 896.44 | 129.765 | 29.5 | 25.8517 | 25.8517 | 0 | 0 | 0 | 0 | 22.075 | 22.075 | 0 | 10.8141 | 848.5132 | 0 | 0.088511 | 6.964 | 0 | 0 | 269.8453 | 25.8517 | on_peak | 848.5132 |  |  | 2.88 | 2.46 | 94.65 | 180.0305 | 0
6019 | 851.67 | 0 | 29.2 | 0 | 0 | 0 | 0 | 0 | 0 | 3.1568 | 3.1568 | 0 | 7.4394 | 848.5132 | 0 | 0.088511 | 7.2002 | 0 | 0 | 269.8453 | 0 | on_peak | 848.5132 |  |  | 0 | 0.37 | 99.63 | 0 | 0
6020 | 798.56 | 0 | 28.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 798.56 | 0 | 0.088511 | 7.5383 | 0 | 0 | 269.8453 | 0 | on_peak | 798.56 |  |  | 0 | 0 | 100 | 0 | 0
6021 | 801.87 | 0 | 28.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 801.87 | 0 | 0.088511 | 7.7794 | 0 | 0 | 269.8453 | 0 | on_peak | 801.87 |  |  | 0 | 0 | 100 | 0 | 0
6022 | 795.68 | 0 | 28.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 795.68 | 0 | 0.05921 | 7.8028 | 0 | 0 | 269.8453 | 0 | off_peak | 795.68 |  |  | 0 | 0 | 100 | 0 | 0
6023 | 794.88 | 0 | 27.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 794.88 | 0 | 0.05921 | 7.8228 | 0 | 0 | 269.8453 | 0 | off_peak | 794.88 |  |  | 0 | 0 | 100 | 0 | 0
6024 | 784.47 | 0 | 27.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 784.47 | 0 | 0.05921 | 7.6583 | 0 | 0 | 269.8453 | 0 | off_peak | 784.47 |  |  | 0 | 0 | 100 | 0 | 0
6025 | 696.78 | 0 | 27 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 696.78 | 0 | 0.05921 | 7.4173 | 0 | 0 | 269.8453 | 0 | off_peak | 696.78 |  |  | 0 | 0 | 100 | 0 | 0
6026 | 639.43 | 0 | 26.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 639.43 | 0 | 0.05921 | 7.1571 | 0 | 0 | 269.8453 | 0 | off_peak | 639.43 |  |  | 0 | 0 | 100 | 0 | 0
6027 | 627.91 | 0 | 26.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 627.91 | 0 | 0.05921 | 6.6478 | 0 | 0 | 269.8453 | 0 | off_peak | 627.91 |  |  | 0 | 0 | 100 | 0 | 0
6028 | 629.9 | 0 | 26.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 629.9 | 0 | 0.05921 | 6.1479 | 0 | 0 | 269.8453 | 0 | off_peak | 629.9 |  |  | 0 | 0 | 100 | 0 | 0
6029 | 643.58 | 0 | 25.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 643.58 | 0 | 0.05921 | 5.6465 | 0 | 0 | 269.8453 | 0 | off_peak | 643.58 |  |  | 0 | 0 | 100 | 0 | 0
6030 | 704.76 | 0 | 25.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 704.76 | 0 | 0.05921 | 4.9269 | 0 | 0 | 269.8453 | 0 | off_peak | 704.76 |  |  | 0 | 0 | 100 | 0 | 0
6031 | 744.25 | 13.3 | 26.1 | 2.6826 | 0 | 0 | 2.6826 | 2.6826 | 0 | 0 | 0 | 0 | 9.9487 | 744.25 | 0 | 0.05921 | 4.5025 | 0 | 0 | 272.3546 | 0 | off_peak | 744.25 | 100 | 0 | 0 | 0 | 100 | 0 | 0
6032 | 782.92 | 23.75 | 26.6 | 4.7817 | 0 | 0 | 4.7817 | 12.3989 | 7.6173 | 0 | 0 | 0 | 21.5468 | 790.5373 | 0 | 0.05921 | 4.2092 | 0 | 0 | 276.8274 | 0 | off_peak | 782.92 | 38.57 | 61.43 | 0 | 0 | 100 | 0 | 0
6033 | 757.33 | 57.95 | 27.3 | 11.6377 | 11.6377 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21.5468 | 745.6923 | 0 | 0.05921 | 4.0026 | 0 | 0 | 276.8274 | 11.6377 | off_peak | 745.6923 |  |  | 1.54 | 0 | 98.46 | 46.5816 | 0
6034 | 792.35 | 128.919 | 28 | 25.8242 | 25.8242 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21.5468 | 766.5258 | 0 | 0.05921 | 3.8922 | 0 | 0 | 276.8274 | 25.8242 | off_peak | 766.5258 |  |  | 3.26 | 0 | 96.74 | 100.5136 | 0
6035 | 799.18 | 498.254 | 28.7 | 99.5525 | 99.5525 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21.5468 | 699.6275 | 0 | 0.05921 | 3.8593 | 0 | 0 | 276.8274 | 99.5525 | off_peak | 699.6275 |  |  | 12.46 | 0 | 87.54 | 384.2045 | 0
6036 | 798.61 | 228.789 | 29.4 | 45.5959 | 45.5959 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21.5468 | 753.0141 | 0 | 0.05921 | 3.9556 | 0 | 0 | 276.8274 | 45.5959 | off_peak | 753.0141 |  |  | 5.71 | 0 | 94.29 | 180.3588 | 0
6037 | 752.08 | 38.95 | 29.9 | 7.7482 | 0 | 0 | 7.7482 | 7.7482 | 0 | 0 | 0 | 0 | 28.7947 | 752.08 | 0 | 0.05921 | 4.0625 | 0 | 0 | 284.0752 | 0 | off_peak | 752.08 | 100 | 0 | 0 | 0 | 100 | 0 | 0
6038 | 750.5 | 191.797 | 30.3 | 38.0978 | 38.0978 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 28.7947 | 712.4022 | 0 | 0.05921 | 4.3311 | 0 | 0 | 284.0752 | 38.0978 | off_peak | 712.4022 |  |  | 5.08 | 0 | 94.92 | 165.0049 | 0
6039 | 756.24 | 190.553 | 30.6 | 37.8091 | 37.8091 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 28.7947 | 718.4309 | 0 | 0.05921 | 4.6058 | 0 | 0 | 284.0752 | 37.8091 | off_peak | 718.4309 |  |  | 5 | 0 | 95 | 174.1408 | 0
6040 | 727.28 | 102.6 | 30.6 | 20.3576 | 20.3576 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 28.7947 | 706.9224 | 0 | 0.05921 | 5.1025 | 0 | 0 | 284.0752 | 20.3576 | off_peak | 706.9224 |  |  | 2.8 | 0 | 97.2 | 103.8758 | 0
6041 | 749.04 | 65.55 | 30.5 | 13.0111 | 13.0111 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 28.7947 | 736.0289 | 0 | 0.05921 | 5.7759 | 0 | 0 | 284.0752 | 13.0111 | off_peak | 736.0289 |  |  | 1.74 | 0 | 98.26 | 75.1507 | 0
6042 | 690.72 | 21.85 | 30.2 | 4.3418 | 0 | 0 | 4.3418 | 12.3989 | 8.0571 | 0 | 0 | 0 | 40.3928 | 698.7771 | 0 | 0.05921 | 6.2644 | 0 | 0 | 288.1366 | 0 | off_peak | 690.72 | 35.02 | 64.98 | 0 | 0 | 100 | 0 | 0
6043 | 661.11 | 0 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40.3928 | 661.11 | 0 | 0.05921 | 6.8276 | 0 | 0 | 288.1366 | 0 | off_peak | 661.11 |  |  | 0 | 0 | 100 | 0 | 0
6044 | 675.79 | 0 | 29.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40.3928 | 675.79 | 0 | 0.05921 | 6.9964 | 0 | 0 | 288.1366 | 0 | off_peak | 675.79 |  |  | 0 | 0 | 100 | 0 | 0
6045 | 608.33 | 0 | 29.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40.3928 | 608.33 | 0 | 0.05921 | 7.1354 | 0 | 0 | 288.1366 | 0 | off_peak | 608.33 |  |  | 0 | 0 | 100 | 0 | 0
6046 | 615.44 | 0 | 28.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40.3928 | 615.44 | 0 | 0.05921 | 6.9826 | 0 | 0 | 288.1366 | 0 | off_peak | 615.44 |  |  | 0 | 0 | 100 | 0 | 0
6047 | 641.36 | 0 | 28.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40.3928 | 641.36 | 0 | 0.05921 | 7.2158 | 0 | 0 | 288.1366 | 0 | off_peak | 641.36 |  |  | 0 | 0 | 100 | 0 | 0
6048 | 648.01 | 0 | 28 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40.3928 | 648.01 | 0 | 0.05921 | 7.4864 | 0 | 0 | 288.1366 | 0 | off_peak | 648.01 |  |  | 0 | 0 | 100 | 0 | 0
6049 | 639.63 | 0 | 27.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40.3928 | 639.63 | 0 | 0.05921 | 7.4054 | 0 | 0 | 288.1366 | 0 | off_peak | 639.63 |  |  | 0 | 0 | 100 | 0 | 0
6050 | 625.91 | 0 | 27.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40.3928 | 625.91 | 0 | 0.05921 | 7.1845 | 0 | 0 | 288.1366 | 0 | off_peak | 625.91 |  |  | 0 | 0 | 100 | 0 | 0
6051 | 623.46 | 0 | 26.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40.3928 | 623.46 | 0 | 0.05921 | 6.7257 | 0 | 0 | 288.1366 | 0 | off_peak | 623.46 |  |  | 0 | 0 | 100 | 0 | 0
6052 | 652.09 | 0 | 26.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40.3928 | 652.09 | 0 | 0.05921 | 6.2321 | 0 | 0 | 288.1366 | 0 | off_peak | 652.09 |  |  | 0 | 0 | 100 | 0 | 0
6053 | 644.76 | 0 | 26.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40.3928 | 644.76 | 0 | 0.05921 | 5.6137 | 0 | 0 | 288.1366 | 0 | off_peak | 644.76 |  |  | 0 | 0 | 100 | 0 | 0
6054 | 687.49 | 0 | 26.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40.3928 | 687.49 | 0 | 0.05921 | 5.129 | 0 | 0 | 288.1366 | 0 | off_peak | 687.49 |  |  | 0 | 0 | 100 | 0 | 0
6055 | 700.12 | 13.3 | 26.5 | 2.6787 | 0 | 0 | 2.6787 | 2.6787 | 0 | 0 | 0 | 0 | 42.8985 | 700.12 | 0 | 0.05921 | 4.688 | 0 | 0 | 290.6423 | 0 | off_peak | 700.12 | 100 | 0 | 0 | 0 | 100 | 0 | 0
6056 | 752.5 | 19 | 27 | 3.8198 | 0 | 0 | 3.8198 | 3.8198 | 0 | 0 | 0 | 0 | 46.4716 | 752.5 | 0 | 0.05921 | 4.3517 | 0 | 0 | 294.2154 | 0 | off_peak | 752.5 | 100 | 0 | 0 | 0 | 100 | 0 | 0
6057 | 712.66 | 42.75 | 27.6 | 8.5758 | 8.5758 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 46.4716 | 704.0842 | 0 | 0.05921 | 4.1528 | 0 | 0 | 294.2154 | 8.5758 | off_peak | 704.0842 |  |  | 1.2 | 0 | 98.8 | 35.6141 | 0
6058 | 748.34 | 93.1 | 28.2 | 18.6356 | 18.6356 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 46.4716 | 729.7044 | 0 | 0.05921 | 4.0126 | 0 | 0 | 294.2154 | 18.6356 | off_peak | 729.7044 |  |  | 2.49 | 0 | 97.51 | 74.7767 | 0
6059 | 736.85 | 89.3 | 28.9 | 17.8294 | 17.8294 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 46.4716 | 719.0206 | 0 | 0.05921 | 3.975 | 0 | 0 | 294.2154 | 17.8294 | off_peak | 719.0206 |  |  | 2.42 | 0 | 97.58 | 70.8725 | 0
6060 | 743.32 | 78.85 | 29.5 | 15.7085 | 15.7085 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 46.4716 | 727.6115 | 0 | 0.05921 | 4.0141 | 0 | 0 | 294.2154 | 15.7085 | off_peak | 727.6115 |  |  | 2.11 | 0 | 97.89 | 63.056 | 0
6061 | 745.81 | 87.4 | 30 | 17.3799 | 17.3799 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 46.4716 | 728.4301 | 0 | 0.05921 | 4.1309 | 0 | 0 | 294.2154 | 17.3799 | off_peak | 728.4301 |  |  | 2.33 | 0 | 97.67 | 71.7949 | 0
6062 | 723.59 | 56.05 | 30.3 | 11.1336 | 11.1336 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 46.4716 | 712.4564 | 0 | 0.05921 | 4.4152 | 0 | 0 | 294.2154 | 11.1336 | off_peak | 712.4564 |  |  | 1.54 | 0 | 98.46 | 49.1566 | 0
6063 | 743.05 | 78.85 | 30.4 | 15.6567 | 15.6567 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 46.4716 | 727.3933 | 0 | 0.05921 | 4.7567 | 0 | 0 | 294.2154 | 15.6567 | off_peak | 727.3933 |  |  | 2.11 | 0 | 97.89 | 74.4749 | 0
6064 | 752.8 | 57.95 | 30.4 | 11.5067 | 11.5067 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 58.0697 | 753.6922 | 0 | 0.05921 | 5.3695 | 0 | 0 | 294.2154 | 11.5067 | off_peak | 741.2933 | 0 | 100 | 1.53 | 0 | 98.47 | 61.7859 | 0
6065 | 710.22 | 38.95 | 30.3 | 7.7369 | 7.7369 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 58.0697 | 702.4831 | 0 | 0.05921 | 6.095 | 0 | 0 | 294.2154 | 7.7369 | off_peak | 702.4831 |  |  | 1.09 | 0 | 98.91 | 47.1566 | 0
6066 | 704.31 | 10.45 | 29.8 | 2.0796 | 2.0796 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 58.0697 | 702.2304 | 0 | 0.05921 | 6.8304 | 0 | 0 | 294.2154 | 2.0796 | off_peak | 702.2304 |  |  | 0.3 | 0 | 99.7 | 14.2042 | 0
6067 | 616.43 | 0 | 29.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 58.0697 | 616.43 | 0 | 0.05921 | 7.354 | 0 | 0 | 294.2154 | 0 | off_peak | 616.43 |  |  | 0 | 0 | 100 | 0 | 0
6068 | 645 | 0 | 29 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 58.0697 | 645 | 0 | 0.05921 | 7.4975 | 0 | 0 | 294.2154 | 0 | off_peak | 645 |  |  | 0 | 0 | 100 | 0 | 0
6069 | 594.71 | 0 | 28.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 58.0697 | 594.71 | 0 | 0.05921 | 7.5925 | 0 | 0 | 294.2154 | 0 | off_peak | 594.71 |  |  | 0 | 0 | 100 | 0 | 0
6070 | 634.01 | 0 | 28.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 58.0697 | 634.01 | 0 | 0.05921 | 8.0175 | 0 | 0 | 294.2154 | 0 | off_peak | 634.01 |  |  | 0 | 0 | 100 | 0 | 0
6071 | 597.17 | 0 | 28 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 58.0697 | 597.17 | 0 | 0.05921 | 8.1386 | 0 | 0 | 294.2154 | 0 | off_peak | 597.17 |  |  | 0 | 0 | 100 | 0 | 0
6072 | 621.12 | 0 | 27.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 58.0697 | 621.12 | 0 | 0.05921 | 8.3795 | 0 | 0 | 294.2154 | 0 | off_peak | 621.12 |  |  | 0 | 0 | 100 | 0 | 0
6073 | 627.21 | 0 | 27.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 58.0697 | 627.21 | 0 | 0.05921 | 8.3081 | 0 | 0 | 294.2154 | 0 | off_peak | 627.21 |  |  | 0 | 0 | 100 | 0 | 0
6074 | 617.51 | 0 | 27 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 58.0697 | 617.51 | 0 | 0.05921 | 8.0232 | 0 | 0 | 294.2154 | 0 | off_peak | 617.51 |  |  | 0 | 0 | 100 | 0 | 0
6075 | 625.1 | 0 | 26.7 | 0 | 0 | 0 | 0 | 4.196 | 4.196 | 0 | 0 | 0 | 61.9947 | 629.296 | 0 | 0.05921 | 7.452 | 0 | 0 | 294.2154 | 0 | off_peak | 625.1 | 0 | 100 | 0 | 0 | 100 | 0 | 0
6076 | 611.32 | 0 | 26.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 61.9947 | 611.32 | 0 | 0.05921 | 6.8293 | 0 | 0 | 294.2154 | 0 | off_peak | 611.32 |  |  | 0 | 0 | 100 | 0 | 0
6077 | 613.7 | 0 | 26.4 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 73.5928 | 626.0989 | 0 | 0.05921 | 6.0642 | 0 | 0 | 294.2154 | 0 | off_peak | 613.7 | 0 | 100 | 0 | 0 | 100 | 0 | 0
6078 | 741.16 | 0 | 26.5 | 0 | 0 | 0 | 0 | 0.80079 | 0.80079 | 0 | 0 | 0 | 74.3419 | 741.9608 | 0 | 0.05921 | 5.4696 | 0 | 0 | 294.2154 | 0 | off_peak | 741.16 | 0 | 100 | 0 | 0 | 100 | 0 | 0
6079 | 830.46 | 28.4613 | 26.8 | 5.7261 | 5.7261 | 0 | 0 | 0.05172 | 0.05172 | 0 | 0 | 0 | 74.3903 | 824.7857 | 0 | 0.05921 | 4.954 | 0 | 0 | 294.2154 | 5.7261 | off_peak | 824.7339 | 0 | 100 | 0.69 | 0 | 99.31 | 28.3672 | 0
6080 | 795.93 | 217.558 | 27.2 | 43.7066 | 43.7066 | 0 | 0 | 0.0033404 | 0.0033404 | 0 | 0 | 0 | 74.3934 | 752.2268 | 0 | 0.05921 | 4.6129 | 0 | 0 | 294.2154 | 43.7066 | off_peak | 752.2234 | 0 | 100 | 5.49 | 0 | 94.51 | 201.6137 | 0
6081 | 793.13 | 428.748 | 27.6 | 86.0088 | 86.0088 | 0 | 0 | 0.00021574 | 0.00021574 | 0 | 0 | 0 | 74.3936 | 707.1214 | 0 | 0.05921 | 4.4028 | 0 | 0 | 294.2154 | 86.0088 | off_peak | 707.1212 | 0 | 100 | 10.84 | 0 | 89.16 | 378.6825 | 0
6082 | 787.65 | 580.433 | 28.1 | 116.226 | 116.226 | 0 | 0 | 1.4896e-05 | 1.4896e-05 | 0 | 0 | 0 | 74.3936 | 671.4241 | 0 | 0.05921 | 4.3541 | 0 | 0 | 294.2154 | 116.226 | off_peak | 671.424 | 0 | 100 | 14.76 | 0 | 85.24 | 506.0652 | 0
6083 | 838.67 | 737.019 | 28.6 | 147.3121 | 147.3121 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 691.3579 | 0 | 0.05921 | 4.5278 | 0 | 0 | 294.2154 | 147.3121 | off_peak | 691.3579 |  |  | 17.56 | 0 | 82.44 | 666.9942 | 0
6084 | 853.39 | 844.475 | 29.1 | 168.4821 | 168.4821 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 684.9079 | 0 | 0.05921 | 4.8727 | 0 | 0 | 294.2154 | 168.4821 | off_peak | 684.9079 |  |  | 19.74 | 0 | 80.26 | 820.9636 | 0
6085 | 813.49 | 864.63 | 29.4 | 172.3142 | 172.3142 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 641.1758 | 0 | 0.088511 | 4.9998 | 0 | 0 | 294.2154 | 172.3142 | on_peak | 641.1758 |  |  | 21.18 | 0 | 78.82 | 861.5305 | 0
6086 | 844.5 | 834.426 | 29.6 | 166.1731 | 166.1731 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 678.3269 | 0 | 0.088511 | 5.186 | 0 | 0 | 294.2154 | 166.1731 | on_peak | 678.3269 |  |  | 19.68 | 0 | 80.32 | 861.7669 | 0
6087 | 897.97 | 722.927 | 29.8 | 143.8631 | 143.8631 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 754.1069 | 0 | 0.088511 | 5.4776 | 0 | 0 | 294.2154 | 143.8631 | on_peak | 754.1069 |  |  | 16.02 | 0 | 83.98 | 788.0194 | 0
6088 | 809.34 | 557.256 | 29.9 | 110.8538 | 110.8538 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 698.4862 | 0 | 0.088511 | 5.9417 | 0 | 0 | 294.2154 | 110.8538 | on_peak | 698.4862 |  |  | 13.7 | 0 | 86.3 | 658.6629 | 0
6089 | 825.05 | 225.721 | 29.8 | 44.9187 | 44.9187 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 780.1313 | 0 | 0.088511 | 6.5925 | 0 | 0 | 294.2154 | 44.9187 | on_peak | 780.1313 |  |  | 5.44 | 0 | 94.56 | 296.1278 | 0
6090 | 830.53 | 140.947 | 29.4 | 28.0897 | 28.0897 | 0 | 0 | 0 | 0 | 62.63 | 62.63 | 0 | 7.4394 | 739.8103 | 0 | 0.088511 | 7.2292 | 0 | 0 | 294.2154 | 28.0897 | on_peak | 739.8103 |  |  | 3.38 | 7.54 | 89.08 | 203.0657 | 0
6091 | 831.76 | 0 | 29.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 831.76 | 0 | 0.088511 | 7.9094 | 0 | 0 | 294.2154 | 0 | on_peak | 831.76 |  |  | 0 | 0 | 100 | 0 | 0
6092 | 833.41 | 0 | 28.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 833.41 | 0 | 0.088511 | 8.1985 | 0 | 0 | 294.2154 | 0 | on_peak | 833.41 |  |  | 0 | 0 | 100 | 0 | 0
6093 | 799.98 | 0 | 28.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 799.98 | 0 | 0.088511 | 8.498 | 0 | 0 | 294.2154 | 0 | on_peak | 799.98 |  |  | 0 | 0 | 100 | 0 | 0
6094 | 814.06 | 0 | 28.3 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 19.0375 | 826.4589 | 0 | 0.05921 | 8.742 | 0 | 0 | 294.2154 | 0 | off_peak | 814.06 | 0 | 100 | 0 | 0 | 100 | 0 | 0
6095 | 790.17 | 0 | 27.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19.0375 | 790.17 | 0 | 0.05921 | 8.8497 | 0 | 0 | 294.2154 | 0 | off_peak | 790.17 |  |  | 0 | 0 | 100 | 0 | 0
6096 | 796.37 | 0 | 27.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19.0375 | 796.37 | 0 | 0.05921 | 8.9631 | 0 | 0 | 294.2154 | 0 | off_peak | 796.37 |  |  | 0 | 0 | 100 | 0 | 0
6097 | 730.77 | 0 | 27.2 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 30.6357 | 743.1689 | 0 | 0.05921 | 8.7831 | 0 | 0 | 294.2154 | 0 | off_peak | 730.77 | 0 | 100 | 0 | 0 | 100 | 0 | 0
6098 | 644.23 | 0 | 26.9 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 42.2338 | 656.6289 | 0 | 0.05921 | 8.4624 | 0 | 0 | 294.2154 | 0 | off_peak | 644.23 | 0 | 100 | 0 | 0 | 100 | 0 | 0
6099 | 639.62 | 0 | 26.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 42.2338 | 639.62 | 0 | 0.05921 | 7.9368 | 0 | 0 | 294.2154 | 0 | off_peak | 639.62 |  |  | 0 | 0 | 100 | 0 | 0
6100 | 634.55 | 0 | 26.3 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 53.832 | 646.9489 | 0 | 0.05921 | 7.3116 | 0 | 0 | 294.2154 | 0 | off_peak | 634.55 | 0 | 100 | 0 | 0 | 100 | 0 | 0
6101 | 656.25 | 0 | 26.2 | 0 | 0 | 0 | 0 | 8.7263 | 8.7263 | 0 | 0 | 0 | 61.9947 | 664.9763 | 0 | 0.05921 | 6.5632 | 0 | 0 | 294.2154 | 0 | off_peak | 656.25 | 0 | 100 | 0 | 0 | 100 | 0 | 0
6102 | 712.05 | 0 | 26.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 61.9947 | 712.05 | 0 | 0.05921 | 5.8704 | 0 | 0 | 294.2154 | 0 | off_peak | 712.05 |  |  | 0 | 0 | 100 | 0 | 0
6103 | 738.98 | 41.6967 | 26.5 | 8.398 | 8.398 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 61.9947 | 730.582 | 0 | 0.05921 | 5.3313 | 0 | 0 | 294.2154 | 8.398 | off_peak | 730.582 |  |  | 1.14 | 0 | 98.86 | 44.7718 | 0
6104 | 805.61 | 235.939 | 27 | 47.4336 | 47.4336 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 73.5928 | 770.5753 | 0 | 0.05921 | 4.9682 | 0 | 0 | 294.2154 | 47.4336 | off_peak | 758.1764 | 0 | 100 | 5.89 | 0 | 94.11 | 235.6596 | 0
6105 | 824.07 | 450.662 | 27.5 | 90.4377 | 90.4377 | 0 | 0 | 0.80079 | 0.80079 | 0 | 0 | 0 | 74.3419 | 734.4331 | 0 | 0.05921 | 4.7509 | 0 | 0 | 294.2154 | 90.4377 | off_peak | 733.6323 | 0 | 100 | 10.97 | 0 | 89.03 | 429.6641 | 0
6106 | 847.65 | 640.184 | 28.2 | 128.1438 | 128.0921 | 0 | 0.05172 | 0.05172 | 0 | 0 | 0 | 0 | 74.3903 | 719.5579 | 0 | 0.05921 | 4.6705 | 0 | 0 | 294.2638 | 128.0921 | off_peak | 719.5579 | 100 | 0 | 15.11 | 0 | 84.89 | 598.2479 | 0
6107 | 802.89 | 790.497 | 28.9 | 157.8282 | 157.8282 | 0 | 0 | 0.0033404 | 0.0033404 | 0 | 0 | 0 | 74.3934 | 645.0652 | 0 | 0.05921 | 4.8085 | 0 | 0 | 294.2638 | 157.8282 | off_peak | 645.0618 | 0 | 100 | 19.66 | 0 | 80.34 | 758.9173 | 0
6108 | 830.62 | 839.662 | 29.6 | 167.2158 | 167.2158 | 0 | 0 | 0.00021574 | 0.00021574 | 0 | 0 | 0 | 74.3936 | 663.4044 | 0 | 0.05921 | 5.1333 | 0 | 0 | 294.2638 | 167.2158 | off_peak | 663.4042 | 0 | 100 | 20.13 | 0 | 79.87 | 858.3644 | 0
6109 | 865.83 | 894.191 | 30.1 | 177.7492 | 177.7492 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 688.0808 | 0 | 0.088511 | 5.2591 | 0 | 0 | 294.2638 | 177.7492 | on_peak | 688.0808 |  |  | 20.53 | 0 | 79.47 | 934.7923 | 0
6110 | 871.85 | 811.868 | 30.5 | 161.1481 | 161.1481 | 0 | 0 | 0 | 0 | 62.63 | 62.63 | 0 | 7.4394 | 648.0719 | 0 | 0.088511 | 5.3787 | 62.63 | 0 | 227.3095 | 223.7781 | on_peak | 648.0719 |  |  | 18.48 | 7.18 | 74.33 | 1203.6282 | 0
6111 | 852.2 | 730.261 | 30.7 | 144.8434 | 144.8434 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 707.3566 | 0 | 0.088511 | 5.6102 | 0 | 0 | 227.3095 | 144.8434 | on_peak | 707.3566 |  |  | 17 | 0 | 83 | 812.6037 | 0
6112 | 793.8 | 563.918 | 30.7 | 111.8501 | 111.8501 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 681.9499 | 0 | 0.088511 | 6.0504 | 0 | 0 | 227.3095 | 111.8501 | on_peak | 681.9499 |  |  | 14.09 | 0 | 85.91 | 676.741 | 0
6113 | 814.61 | 361.22 | 30.4 | 71.7251 | 71.7251 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 742.8849 | 0 | 0.088511 | 6.7485 | 0 | 0 | 227.3095 | 71.7251 | on_peak | 742.8849 |  |  | 8.8 | 0 | 91.2 | 484.0378 | 0
6114 | 816.54 | 147.371 | 29.9 | 29.3162 | 29.3162 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 787.2238 | 0 | 0.088511 | 7.4205 | 0 | 0 | 227.3095 | 29.3162 | on_peak | 787.2238 |  |  | 3.59 | 0 | 96.41 | 217.5416 | 0
6115 | 834.23 | 0 | 29.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 834.23 | 0 | 0.088511 | 7.9497 | 0 | 0 | 227.3095 | 0 | on_peak | 834.23 |  |  | 0 | 0 | 100 | 0 | 0
6116 | 810.02 | 0 | 29 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 810.02 | 0 | 0.088511 | 8.1351 | 0 | 0 | 227.3095 | 0 | on_peak | 810.02 |  |  | 0 | 0 | 100 | 0 | 0
6117 | 775.29 | 0 | 28.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 775.29 | 0 | 0.088511 | 8.3241 | 0 | 0 | 227.3095 | 0 | on_peak | 775.29 |  |  | 0 | 0 | 100 | 0 | 0
6118 | 780.94 | 0 | 28.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 780.94 | 0 | 0.05921 | 8.4413 | 0 | 0 | 227.3095 | 0 | off_peak | 780.94 |  |  | 0 | 0 | 100 | 0 | 0
6119 | 800.14 | 0 | 28 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 19.0375 | 812.5389 | 0 | 0.05921 | 8.6896 | 0 | 0 | 227.3095 | 0 | off_peak | 800.14 | 0 | 100 | 0 | 0 | 100 | 0 | 0
6120 | 770.1 | 0 | 27.8 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 30.6357 | 782.4989 | 0 | 0.05921 | 8.6082 | 0 | 0 | 227.3095 | 0 | off_peak | 770.1 | 0 | 100 | 0 | 0 | 100 | 0 | 0
6121 | 714.38 | 0 | 27.5 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 42.2338 | 726.7789 | 0 | 0.05921 | 8.526 | 0 | 0 | 227.3095 | 0 | off_peak | 714.38 | 0 | 100 | 0 | 0 | 100 | 0 | 0
6122 | 650.11 | 0 | 27.2 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 53.832 | 662.5089 | 0 | 0.05921 | 8.2895 | 0 | 0 | 227.3095 | 0 | off_peak | 650.11 | 0 | 100 | 0 | 0 | 100 | 0 | 0
6123 | 602.05 | 0 | 27 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 53.832 | 602.05 | 0 | 0.05921 | 7.8156 | 0 | 0 | 227.3095 | 0 | off_peak | 602.05 |  |  | 0 | 0 | 100 | 0 | 0
6124 | 613.48 | 0 | 26.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 53.832 | 613.48 | 0 | 0.05921 | 7.1729 | 0 | 0 | 227.3095 | 0 | off_peak | 613.48 |  |  | 0 | 0 | 100 | 0 | 0
6125 | 639.41 | 0 | 26.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 53.832 | 639.41 | 0 | 0.05921 | 6.4147 | 0 | 0 | 227.3095 | 0 | off_peak | 639.41 |  |  | 0 | 0 | 100 | 0 | 0
6126 | 674.7 | 0 | 26.5 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 65.4301 | 687.0989 | 0 | 0.05921 | 5.8268 | 0 | 0 | 227.3095 | 0 | off_peak | 674.7 | 0 | 100 | 0 | 0 | 100 | 0 | 0
6127 | 708.12 | 41.0823 | 26.6 | 8.2712 | 0 | 0 | 8.2712 | 8.2712 | 0 | 0 | 0 | 0 | 73.1671 | 708.12 | 0 | 0.05921 | 5.2917 | 0 | 0 | 235.0466 | 0 | off_peak | 708.12 | 100 | 0 | 0 | 0 | 100 | 0 | 0
6128 | 781.76 | 233.373 | 27.1 | 46.9008 | 46.9008 | 0 | 0 | 1.2265 | 1.2265 | 0 | 0 | 0 | 74.3144 | 736.0857 | 0 | 0.05921 | 4.9634 | 0 | 0 | 235.0466 | 46.9008 | off_peak | 734.8592 | 0 | 100 | 6 | 0 | 94 | 232.7866 | 0
6129 | 800.94 | 444.841 | 27.8 | 89.1723 | 89.1723 | 0 | 0 | 0.079214 | 0.079214 | 0 | 0 | 0 | 74.3885 | 711.8469 | 0 | 0.05921 | 4.7435 | 0 | 0 | 235.0466 | 89.1723 | off_peak | 711.7677 | 0 | 100 | 11.13 | 0 | 88.87 | 422.9915 | 0
6130 | 823.1 | 632.658 | 28.5 | 126.499 | 126.4939 | 0 | 0.0051161 | 0.0051161 | 0 | 0 | 0 | 0 | 74.3933 | 696.6061 | 0 | 0.05921 | 4.6903 | 0 | 0 | 235.0514 | 126.4939 | off_peak | 696.6061 | 100 | 0 | 15.37 | 0 | 84.63 | 593.2895 | 0
6131 | 807.27 | 773.23 | 29.2 | 154.2116 | 154.2116 | 0 | 0 | 0.00033043 | 0.00033043 | 0 | 0 | 0 | 74.3936 | 653.0587 | 0 | 0.05921 | 4.8474 | 0 | 0 | 235.0514 | 154.2116 | off_peak | 653.0584 | 0 | 100 | 19.1 | 0 | 80.9 | 747.5266 | 0
6132 | 894.96 | 183.35 | 29.8 | 36.4868 | 36.4868 | 0 | 0 | 2.1341e-05 | 2.1341e-05 | 0 | 0 | 0 | 74.3936 | 858.4732 | 0 | 0.05921 | 5.2122 | 0 | 0 | 235.0514 | 36.4868 | off_peak | 858.4732 | 0 | 100 | 4.08 | 0 | 95.92 | 190.1771 | 0
6133 | 852.75 | 471.451 | 30.3 | 93.6473 | 93.6473 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 759.1027 | 0 | 0.088511 | 5.3189 | 0 | 0 | 235.0514 | 93.6473 | on_peak | 759.1027 |  |  | 10.98 | 0 | 89.02 | 498.0995 | 0
6134 | 838.52 | 566.448 | 30.7 | 112.352 | 112.352 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 726.168 | 0 | 0.088511 | 5.4575 | 0 | 0 | 235.0514 | 112.352 | on_peak | 726.168 |  |  | 13.4 | 0 | 86.6 | 613.1628 | 0
6135 | 858.83 | 26.6 | 30.9 | 5.2721 | 5.2721 | 0 | 0 | 0 | 0 | 40.0132 | 40.0132 | 0 | 31.6177 | 813.5447 | 0 | 0.088511 | 5.6947 | 40.0132 | 0 | 192.2754 | 45.2853 | on_peak | 813.5447 |  |  | 0.61 | 4.66 | 94.73 | 257.8846 | 0
6136 | 843.91 | 405.1 | 30.9 | 80.2904 | 80.2904 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 31.6177 | 763.6196 | 0 | 0.088511 | 6.1011 | 0 | 0 | 192.2754 | 80.2904 | on_peak | 763.6196 |  |  | 9.51 | 0 | 90.49 | 489.8581 | 0
6137 | 818.71 | 77.3593 | 30.7 | 15.3438 | 15.3438 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 31.6177 | 803.3662 | 0 | 0.088511 | 6.6326 | 0 | 0 | 192.2754 | 15.3438 | on_peak | 803.3662 |  |  | 1.87 | 0 | 98.13 | 101.7688 | 0
6138 | 826.85 | 39.9 | 30.3 | 7.9256 | 7.9256 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 31.6177 | 818.9244 | 0 | 0.088511 | 7.254 | 0 | 0 | 192.2754 | 7.9256 | on_peak | 818.9244 |  |  | 0.96 | 0 | 99.04 | 57.4925 | 0
6139 | 796.17 | 0 | 29.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 31.6177 | 796.17 | 0 | 0.088511 | 7.7656 | 0 | 0 | 192.2754 | 0 | on_peak | 796.17 |  |  | 0 | 0 | 100 | 0 | 0
6140 | 871.13 | 0 | 29.4 | 0 | 0 | 0 | 0 | 0 | 0 | 22.6168 | 22.6168 | 0 | 7.4394 | 848.5132 | 0 | 0.088511 | 8.2757 | 0 | 0 | 192.2754 | 0 | on_peak | 848.5132 |  |  | 0 | 2.6 | 97.4 | 0 | 0
6141 | 805.11 | 0 | 29 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 805.11 | 0 | 0.088511 | 8.4298 | 0 | 0 | 192.2754 | 0 | on_peak | 805.11 |  |  | 0 | 0 | 100 | 0 | 0
6142 | 804.61 | 0 | 28.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 804.61 | 0 | 0.05921 | 8.7309 | 0 | 0 | 192.2754 | 0 | off_peak | 804.61 |  |  | 0 | 0 | 100 | 0 | 0
6143 | 822.29 | 0 | 28.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 822.29 | 0 | 0.05921 | 8.7082 | 0 | 0 | 192.2754 | 0 | off_peak | 822.29 |  |  | 0 | 0 | 100 | 0 | 0
6144 | 776.54 | 0 | 27.6 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 19.0375 | 788.9389 | 0 | 0.05921 | 8.6463 | 0 | 0 | 192.2754 | 0 | off_peak | 776.54 | 0 | 100 | 0 | 0 | 100 | 0 | 0
6145 | 702.12 | 0 | 27.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19.0375 | 702.12 | 0 | 0.05921 | 8.4986 | 0 | 0 | 192.2754 | 0 | off_peak | 702.12 |  |  | 0 | 0 | 100 | 0 | 0
6146 | 687.63 | 0 | 26.8 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 30.6357 | 700.0289 | 0 | 0.05921 | 8.2569 | 0 | 0 | 192.2754 | 0 | off_peak | 687.63 | 0 | 100 | 0 | 0 | 100 | 0 | 0
6147 | 630.36 | 0 | 26.5 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 42.2338 | 642.7589 | 0 | 0.05921 | 7.9308 | 0 | 0 | 192.2754 | 0 | off_peak | 630.36 | 0 | 100 | 0 | 0 | 100 | 0 | 0
6148 | 647.31 | 0 | 26.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 42.2338 | 647.31 | 0 | 0.05921 | 7.2144 | 0 | 0 | 192.2754 | 0 | off_peak | 647.31 |  |  | 0 | 0 | 100 | 0 | 0
6149 | 642.26 | 0 | 26.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 42.2338 | 642.26 | 0 | 0.05921 | 6.4771 | 0 | 0 | 192.2754 | 0 | off_peak | 642.26 |  |  | 0 | 0 | 100 | 0 | 0
6150 | 702.53 | 0 | 26.2 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 53.832 | 714.9289 | 0 | 0.05921 | 5.8154 | 0 | 0 | 192.2754 | 0 | off_peak | 702.53 | 0 | 100 | 0 | 0 | 100 | 0 | 0
6151 | 789.64 | 38.5882 | 26.6 | 7.7691 | 7.7691 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 65.4301 | 794.2698 | 0 | 0.05921 | 5.3034 | 0 | 0 | 192.2754 | 7.7691 | off_peak | 781.8709 | 0 | 100 | 0.98 | 0 | 99.02 | 41.2027 | 0
6152 | 825.19 | 228.427 | 27.2 | 45.8901 | 36.9266 | 0 | 8.9635 | 8.9635 | 0 | 0 | 0 | 0 | 73.8147 | 788.2634 | 0 | 0.05921 | 4.9574 | 0 | 0 | 200.66 | 36.9266 | off_peak | 788.2634 | 100 | 0 | 4.47 | 0 | 95.53 | 183.0581 | 0
6153 | 863.42 | 439.182 | 27.8 | 88.0379 | 88.0379 | 0 | 0 | 0.57892 | 0.57892 | 0 | 0 | 0 | 74.3563 | 775.961 | 0 | 0.05921 | 4.7528 | 0 | 0 | 200.66 | 88.0379 | off_peak | 775.3821 | 0 | 100 | 10.2 | 0 | 89.8 | 418.4298 | 0
6154 | 819.34 | 625.83 | 28.4 | 125.1794 | 125.1794 | 0 | 0 | 0.03739 | 0.03739 | 0 | 0 | 0 | 74.3912 | 694.198 | 0 | 0.05921 | 4.6588 | 0 | 0 | 200.66 | 125.1794 | off_peak | 694.1606 | 0 | 100 | 15.28 | 0 | 84.72 | 583.1808 | 0
6155 | 814.01 | 768.375 | 29 | 153.3554 | 153.3554 | 0 | 0 | 0.0024148 | 0.0024148 | 0 | 0 | 0 | 74.3935 | 660.6571 | 0 | 0.05921 | 4.82 | 0 | 0 | 200.66 | 153.3554 | off_peak | 660.6546 | 0 | 100 | 18.84 | 0 | 81.16 | 739.1724 | 0
6156 | 838.84 | 689.367 | 29.6 | 137.2851 | 137.2851 | 0 | 0 | 0.00015596 | 0.00015596 | 0 | 0 | 0 | 74.3936 | 701.5551 | 0 | 0.05921 | 5.1397 | 0 | 0 | 200.66 | 137.2851 | off_peak | 701.5549 | 0 | 100 | 16.37 | 0 | 83.63 | 705.6008 | 0
6157 | 843.87 | 871.284 | 30 | 173.2592 | 173.2592 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 670.6108 | 0 | 0.088511 | 5.2327 | 0 | 0 | 200.66 | 173.2592 | on_peak | 670.6108 |  |  | 20.53 | 0 | 79.47 | 906.6207 | 0
6158 | 875.74 | 824.198 | 30.4 | 163.6556 | 163.6556 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 712.0844 | 0 | 0.088511 | 5.4182 | 0 | 0 | 200.66 | 163.6556 | on_peak | 712.0844 |  |  | 18.69 | 0 | 81.31 | 886.7215 | 0
6159 | 883.78 | 709.699 | 30.6 | 140.8168 | 140.8168 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 742.9632 | 0 | 0.088511 | 5.6516 | 0 | 0 | 200.66 | 140.8168 | on_peak | 742.9632 |  |  | 15.93 | 0 | 84.07 | 795.838 | 0
6160 | 845.87 | 544.566 | 30.7 | 108.0118 | 108.0118 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 737.8582 | 0 | 0.088511 | 6.0815 | 0 | 0 | 200.66 | 108.0118 | on_peak | 737.8582 |  |  | 12.77 | 0 | 87.23 | 656.8787 | 0
6161 | 858.56 | 343.288 | 30.5 | 68.1394 | 68.1394 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 790.4206 | 0 | 0.088511 | 6.6052 | 0 | 0 | 200.66 | 68.1394 | on_peak | 790.4206 |  |  | 7.94 | 0 | 92.06 | 450.074 | 0
6162 | 897.3 | 133.342 | 30.1 | 26.506 | 26.506 | 0 | 0 | 0 | 0 | 22.2808 | 22.2808 | 0 | 50.5745 | 848.5132 | 0 | 0.088511 | 7.1944 | 0 | 0 | 200.66 | 26.506 | on_peak | 848.5132 |  |  | 2.95 | 2.48 | 94.56 | 190.696 | 0
6163 | 832.42 | 0 | 29.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50.5745 | 832.42 | 0 | 0.088511 | 7.688 | 0 | 0 | 200.66 | 0 | on_peak | 832.42 |  |  | 0 | 0 | 100 | 0 | 0
6164 | 869.1 | 0 | 29.3 | 0 | 0 | 0 | 0 | 0 | 0 | 20.5868 | 20.5868 | 0 | 28.5663 | 848.5132 | 0 | 0.088511 | 8.0735 | 0 | 0 | 200.66 | 0 | on_peak | 848.5132 |  |  | 0 | 2.37 | 97.63 | 0 | 0
6165 | 842.65 | 0 | 29 | 0 | 0 | 0 | 0 | 0 | 0 | 19.7625 | 19.7625 | 0 | 7.4394 | 822.8875 | 0 | 0.088511 | 8.3711 | 0 | 0 | 200.66 | 0 | on_peak | 822.8875 |  |  | 0 | 2.35 | 97.65 | 0 | 0
6166 | 795.98 | 0 | 28.8 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 19.0375 | 808.3789 | 0 | 0.05921 | 8.5781 | 0 | 0 | 200.66 | 0 | off_peak | 795.98 | 0 | 100 | 0 | 0 | 100 | 0 | 0
6167 | 846.49 | 0 | 28.6 | 0 | 0 | 0 | 0 | 8.7263 | 8.7263 | 0 | 0 | 0 | 27.2003 | 855.2163 | 0 | 0.05921 | 8.66 | 0 | 0 | 200.66 | 0 | off_peak | 846.49 | 0 | 100 | 0 | 0 | 100 | 0 | 0
6168 | 820.52 | 0 | 28.4 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 38.7984 | 832.9189 | 0 | 0.05921 | 8.712 | 0 | 0 | 200.66 | 0 | off_peak | 820.52 | 0 | 100 | 0 | 0 | 100 | 0 | 0
6169 | 751.74 | 0 | 28.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 38.7984 | 751.74 | 0 | 0.05921 | 8.494 | 0 | 0 | 200.66 | 0 | off_peak | 751.74 |  |  | 0 | 0 | 100 | 0 | 0
6170 | 674.24 | 0 | 27.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 38.7984 | 674.24 | 0 | 0.05921 | 8.2251 | 0 | 0 | 200.66 | 0 | off_peak | 674.24 |  |  | 0 | 0 | 100 | 0 | 0
6171 | 642.92 | 0 | 27.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 38.7984 | 642.92 | 0 | 0.05921 | 7.7216 | 0 | 0 | 200.66 | 0 | off_peak | 642.92 |  |  | 0 | 0 | 100 | 0 | 0
6172 | 645.39 | 0 | 27.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 38.7984 | 645.39 | 0 | 0.05921 | 7.0895 | 0 | 0 | 200.66 | 0 | off_peak | 645.39 |  |  | 0 | 0 | 100 | 0 | 0
6173 | 665.55 | 0 | 27.1 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 50.3966 | 677.9489 | 0 | 0.05921 | 6.3656 | 0 | 0 | 200.66 | 0 | off_peak | 665.55 | 0 | 100 | 0 | 0 | 100 | 0 | 0
6174 | 737.96 | 0 | 26.9 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 61.9947 | 750.3589 | 0 | 0.05921 | 5.73 | 0 | 0 | 200.66 | 0 | off_peak | 737.96 | 0 | 100 | 0 | 0 | 100 | 0 | 0
6175 | 805.81 | 39.3217 | 27.1 | 7.9024 | 0 | 0 | 7.9024 | 12.3989 | 4.4965 | 0 | 0 | 0 | 73.5928 | 810.3065 | 0 | 0.05921 | 5.2236 | 0 | 0 | 208.0521 | 0 | off_peak | 805.81 | 63.73 | 36.27 | 0 | 0 | 100 | 0 | 0
6176 | 818.1 | 231.072 | 27.5 | 46.371 | 46.371 | 0 | 0 | 0.80079 | 0.80079 | 0 | 0 | 0 | 74.3419 | 772.5298 | 0 | 0.05921 | 4.8871 | 0 | 0 | 208.0521 | 46.371 | off_peak | 771.729 | 0 | 100 | 5.67 | 0 | 94.33 | 226.6175 | 0
6177 | 895.77 | 442.85 | 28.1 | 88.6763 | 88.6763 | 0 | 0 | 0.05172 | 0.05172 | 0 | 0 | 0 | 74.3903 | 807.1454 | 0 | 0.05921 | 4.6459 | 0 | 0 | 208.0521 | 88.6763 | off_peak | 807.0937 | 0 | 100 | 9.9 | 0 | 90.1 | 411.9804 | 0
6178 | 898.5 | 631.966 | 28.7 | 126.2685 | 126.2685 | 0 | 0 | 0.0033404 | 0.0033404 | 0 | 0 | 0 | 74.3934 | 772.2348 | 0 | 0.05921 | 4.5644 | 0 | 0 | 208.0521 | 126.2685 | off_peak | 772.2315 | 0 | 100 | 14.05 | 0 | 85.95 | 576.3433 | 0
6179 | 869.06 | 776.685 | 29.4 | 154.7874 | 154.7874 | 0 | 0 | 0.00021574 | 0.00021574 | 0 | 0 | 0 | 74.3936 | 714.2728 | 0 | 0.05921 | 4.7084 | 0 | 0 | 208.0521 | 154.7874 | off_peak | 714.2726 | 0 | 100 | 17.81 | 0 | 82.19 | 728.8005 | 0
6180 | 977.68 | 861.585 | 30 | 171.3305 | 171.3305 | 0 | 0 | 1.3934e-05 | 1.3934e-05 | 0 | 0 | 0 | 74.3936 | 806.3495 | 0 | 0.05921 | 5.0604 | 0 | 0 | 208.0521 | 171.3305 | off_peak | 806.3495 | 0 | 100 | 17.52 | 0 | 82.48 | 866.9973 | 0
6181 | 870.61 | 880.65 | 30.5 | 174.8007 | 174.8007 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 695.8093 | 0 | 0.088511 | 5.2252 | 0 | 0 | 208.0521 | 174.8007 | on_peak | 695.8093 |  |  | 20.08 | 0 | 79.92 | 913.3769 | 0
6182 | 946.99 | 832.87 | 30.8 | 165.1346 | 165.1346 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 781.8554 | 0 | 0.088511 | 5.4299 | 0 | 0 | 208.0521 | 165.1346 | on_peak | 781.8554 |  |  | 17.44 | 0 | 82.56 | 896.6611 | 0
6183 | 891.67 | 719.277 | 31 | 142.5075 | 142.5075 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 749.1625 | 0 | 0.088511 | 5.8054 | 0 | 0 | 208.0521 | 142.5075 | on_peak | 749.1625 |  |  | 15.98 | 0 | 84.02 | 827.3168 | 0
6184 | 862.67 | 553.332 | 31 | 109.6295 | 109.6295 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 753.0405 | 0 | 0.088511 | 6.1973 | 0 | 0 | 208.0521 | 109.6295 | on_peak | 753.0405 |  |  | 12.71 | 0 | 87.29 | 679.4017 | 0
6185 | 854.01 | 349.532 | 30.8 | 69.3023 | 69.3023 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 784.7077 | 0 | 0.088511 | 6.5901 | 0 | 0 | 208.0521 | 69.3023 | on_peak | 784.7077 |  |  | 8.11 | 0 | 91.89 | 456.7095 | 0
6186 | 857.44 | 137.664 | 30.4 | 27.335 | 27.335 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 830.105 | 0 | 0.088511 | 6.9811 | 0 | 0 | 208.0521 | 27.335 | on_peak | 830.105 |  |  | 3.19 | 0 | 96.81 | 190.8288 | 0
6187 | 858.19 | 0 | 30.2 | 0 | 0 | 0 | 0 | 0 | 0 | 62.63 | 62.63 | 0 | 7.4394 | 795.56 | 0 | 0.088511 | 7.2953 | 0 | 0 | 208.0521 | 0 | on_peak | 795.56 |  |  | 0 | 7.3 | 92.7 | 0 | 0
6188 | 802.22 | 0 | 29.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 802.22 | 0 | 0.088511 | 7.5313 | 0 | 0 | 208.0521 | 0 | on_peak | 802.22 |  |  | 0 | 0 | 100 | 0 | 0
6189 | 804.62 | 0 | 29.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 804.62 | 0 | 0.088511 | 7.8177 | 0 | 0 | 208.0521 | 0 | on_peak | 804.62 |  |  | 0 | 0 | 100 | 0 | 0
6190 | 808.65 | 0 | 29.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 808.65 | 0 | 0.05921 | 7.986 | 0 | 0 | 208.0521 | 0 | off_peak | 808.65 |  |  | 0 | 0 | 100 | 0 | 0
6191 | 771.64 | 0 | 29.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 771.64 | 0 | 0.05921 | 8.2002 | 0 | 0 | 208.0521 | 0 | off_peak | 771.64 |  |  | 0 | 0 | 100 | 0 | 0
6192 | 780.36 | 0 | 28.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 780.36 | 0 | 0.05921 | 8.2955 | 0 | 0 | 208.0521 | 0 | off_peak | 780.36 |  |  | 0 | 0 | 100 | 0 | 0
6193 | 727.78 | 0 | 28.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 727.78 | 0 | 0.05921 | 8.0107 | 0 | 0 | 208.0521 | 0 | off_peak | 727.78 |  |  | 0 | 0 | 100 | 0 | 0
6194 | 640.29 | 0 | 28.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 640.29 | 0 | 0.05921 | 7.7217 | 0 | 0 | 208.0521 | 0 | off_peak | 640.29 |  |  | 0 | 0 | 100 | 0 | 0
6195 | 627.19 | 0 | 28.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 627.19 | 0 | 0.05921 | 7.1397 | 0 | 0 | 208.0521 | 0 | off_peak | 627.19 |  |  | 0 | 0 | 100 | 0 | 0
6196 | 646.02 | 0 | 28 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 646.02 | 0 | 0.05921 | 6.664 | 0 | 0 | 208.0521 | 0 | off_peak | 646.02 |  |  | 0 | 0 | 100 | 0 | 0
6197 | 620.32 | 0 | 28 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 620.32 | 0 | 0.05921 | 6.041 | 0 | 0 | 208.0521 | 0 | off_peak | 620.32 |  |  | 0 | 0 | 100 | 0 | 0
6198 | 702.21 | 0 | 28 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 702.21 | 0 | 0.05921 | 5.5254 | 0 | 0 | 208.0521 | 0 | off_peak | 702.21 |  |  | 0 | 0 | 100 | 0 | 0
6199 | 772.25 | 38.5866 | 28.4 | 7.7181 | 0 | 0 | 7.7181 | 7.7181 | 0 | 0 | 0 | 0 | 14.659 | 772.25 | 0 | 0.05921 | 5.1164 | 0 | 0 | 215.2718 | 0 | off_peak | 772.25 | 100 | 0 | 0 | 0 | 100 | 0 | 0
6200 | 751.02 | 230.767 | 29 | 46.0574 | 46.0574 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14.659 | 704.9626 | 0 | 0.05921 | 4.7419 | 0 | 0 | 215.2718 | 46.0574 | off_peak | 704.9626 |  |  | 6.13 | 0 | 93.87 | 218.4015 | 0
6201 | 856.5 | 443.706 | 29.5 | 88.3949 | 88.3949 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14.659 | 768.1051 | 0 | 0.05921 | 4.5142 | 0 | 0 | 215.2718 | 88.3949 | off_peak | 768.1051 |  |  | 10.32 | 0 | 89.68 | 399.0315 | 0
6202 | 772.19 | 374.872 | 30 | 74.5452 | 74.5452 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14.659 | 697.6448 | 0 | 0.05921 | 4.4008 | 0 | 0 | 215.2718 | 74.5452 | off_peak | 697.6448 |  |  | 9.65 | 0 | 90.35 | 328.0585 | 0
6203 | 753.39 | 358.48 | 30.5 | 71.1549 | 71.1549 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14.659 | 682.2351 | 0 | 0.05921 | 4.3664 | 0 | 0 | 215.2718 | 71.1549 | off_peak | 682.2351 |  |  | 9.44 | 0 | 90.56 | 310.6933 | 0
6204 | 818.24 | 863.209 | 30.8 | 171.15 | 171.15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14.659 | 647.09 | 0 | 0.05921 | 4.4501 | 0 | 0 | 215.2718 | 171.15 | off_peak | 647.09 |  |  | 20.92 | 0 | 79.08 | 761.643 | 0
6205 | 745.64 | 879.623 | 31.1 | 174.2121 | 174.2121 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14.659 | 571.4279 | 0 | 0.05921 | 4.6338 | 0 | 0 | 215.2718 | 174.2121 | off_peak | 571.4279 |  |  | 23.36 | 0 | 76.64 | 807.2673 | 0
6206 | 733.91 | 744.421 | 31.2 | 147.3806 | 147.3806 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14.659 | 586.5294 | 0 | 0.05921 | 4.8755 | 0 | 0 | 215.2718 | 147.3806 | off_peak | 586.5294 |  |  | 20.08 | 0 | 79.92 | 718.5515 | 0
6207 | 740.72 | 713.313 | 31.2 | 141.2219 | 141.2219 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14.659 | 599.4981 | 0 | 0.05921 | 5.2888 | 0 | 0 | 215.2718 | 141.2219 | off_peak | 599.4981 |  |  | 19.07 | 0 | 80.93 | 746.8977 | 0
6208 | 704.65 | 544.786 | 31 | 107.9363 | 107.9363 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 26.2572 | 609.1127 | 0 | 0.05921 | 5.8363 | 0 | 0 | 215.2718 | 107.9363 | off_peak | 596.7137 | 0 | 100 | 15.32 | 0 | 84.68 | 629.9472 | 0
6209 | 709.66 | 340.315 | 30.7 | 67.4997 | 55.1007 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 0 | 37.8553 | 654.5593 | 0 | 0.05921 | 6.5141 | 0 | 0 | 226.8699 | 55.1007 | off_peak | 654.5593 | 100 | 0 | 7.76 | 0 | 92.24 | 358.929 | 0
6210 | 686.33 | 128.418 | 30 | 25.5366 | 25.5366 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 37.8553 | 660.7934 | 0 | 0.05921 | 7.0777 | 0 | 0 | 226.8699 | 25.5366 | off_peak | 660.7934 |  |  | 3.72 | 0 | 96.28 | 180.7406 | 0
6211 | 635.06 | 0 | 29.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 37.8553 | 635.06 | 0 | 0.05921 | 7.373 | 0 | 0 | 226.8699 | 0 | off_peak | 635.06 |  |  | 0 | 0 | 100 | 0 | 0
6212 | 610.34 | 0 | 29 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 37.8553 | 610.34 | 0 | 0.05921 | 7.3652 | 0 | 0 | 226.8699 | 0 | off_peak | 610.34 |  |  | 0 | 0 | 100 | 0 | 0
6213 | 624.77 | 0 | 28.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 37.8553 | 624.77 | 0 | 0.05921 | 7.5527 | 0 | 0 | 226.8699 | 0 | off_peak | 624.77 |  |  | 0 | 0 | 100 | 0 | 0
6214 | 639.78 | 0 | 28.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 37.8553 | 639.78 | 0 | 0.05921 | 7.6327 | 0 | 0 | 226.8699 | 0 | off_peak | 639.78 |  |  | 0 | 0 | 100 | 0 | 0
6215 | 611.55 | 0 | 28.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 37.8553 | 611.55 | 0 | 0.05921 | 7.655 | 0 | 0 | 226.8699 | 0 | off_peak | 611.55 |  |  | 0 | 0 | 100 | 0 | 0
6216 | 656.74 | 0 | 28.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 37.8553 | 656.74 | 0 | 0.05921 | 7.4815 | 0 | 0 | 226.8699 | 0 | off_peak | 656.74 |  |  | 0 | 0 | 100 | 0 | 0
6217 | 630.37 | 0 | 28.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 37.8553 | 630.37 | 0 | 0.05921 | 7.3633 | 0 | 0 | 226.8699 | 0 | off_peak | 630.37 |  |  | 0 | 0 | 100 | 0 | 0
6218 | 635.78 | 0 | 28.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 37.8553 | 635.78 | 0 | 0.05921 | 7.1671 | 0 | 0 | 226.8699 | 0 | off_peak | 635.78 |  |  | 0 | 0 | 100 | 0 | 0
6219 | 647.87 | 0 | 28.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 37.8553 | 647.87 | 0 | 0.05921 | 6.7053 | 0 | 0 | 226.8699 | 0 | off_peak | 647.87 |  |  | 0 | 0 | 100 | 0 | 0
6220 | 645.01 | 0 | 28.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 37.8553 | 645.01 | 0 | 0.05921 | 6.2789 | 0 | 0 | 226.8699 | 0 | off_peak | 645.01 |  |  | 0 | 0 | 100 | 0 | 0
6221 | 627.42 | 0 | 28.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 37.8553 | 627.42 | 0 | 0.05921 | 5.7318 | 0 | 0 | 226.8699 | 0 | off_peak | 627.42 |  |  | 0 | 0 | 100 | 0 | 0
6222 | 672.84 | 0 | 28.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 37.8553 | 672.84 | 0 | 0.05921 | 5.2919 | 0 | 0 | 226.8699 | 0 | off_peak | 672.84 |  |  | 0 | 0 | 100 | 0 | 0
6223 | 703.42 | 35.0116 | 28.6 | 6.998 | 6.998 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 37.8553 | 696.422 | 0 | 0.05921 | 4.9062 | 0 | 0 | 226.8699 | 6.998 | off_peak | 696.422 |  |  | 0.99 | 0 | 99.01 | 34.3336 | 0
6224 | 738.35 | 223.078 | 29.1 | 44.5065 | 44.5065 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 37.8553 | 693.8435 | 0 | 0.05921 | 4.5965 | 0 | 0 | 226.8699 | 44.5065 | off_peak | 693.8435 |  |  | 6.03 | 0 | 93.97 | 204.5739 | 0
6225 | 715.86 | 432.274 | 29.5 | 86.1174 | 86.1174 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 37.8553 | 629.7426 | 0 | 0.05921 | 4.3644 | 0 | 0 | 226.8699 | 86.1174 | off_peak | 629.7426 |  |  | 12.03 | 0 | 87.97 | 375.8474 | 0
6226 | 754.53 | 619.499 | 29.9 | 123.2356 | 123.2356 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 37.8553 | 631.2944 | 0 | 0.05921 | 4.2445 | 0 | 0 | 226.8699 | 123.2356 | off_peak | 631.2944 |  |  | 16.33 | 0 | 83.67 | 523.0676 | 0
6227 | 741.58 | 769.61 | 30.2 | 152.9286 | 152.9286 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 37.8553 | 588.6514 | 0 | 0.05921 | 4.1871 | 0 | 0 | 226.8699 | 152.9286 | off_peak | 588.6514 |  |  | 20.62 | 0 | 79.38 | 640.3296 | 0
6228 | 730.14 | 853.079 | 30.5 | 169.3281 | 169.3281 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 37.8553 | 560.8119 | 0 | 0.05921 | 4.2204 | 0 | 0 | 226.8699 | 169.3281 | off_peak | 560.8119 |  |  | 23.19 | 0 | 76.81 | 714.639 | 0
6229 | 728.08 | 870.403 | 30.6 | 172.7033 | 172.7033 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 37.8553 | 555.3767 | 0 | 0.05921 | 4.3627 | 0 | 0 | 226.8699 | 172.7033 | off_peak | 555.3767 |  |  | 23.72 | 0 | 76.28 | 753.4523 | 0
6230 | 741.91 | 818.516 | 30.7 | 162.3483 | 162.3483 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 37.8553 | 579.5617 | 0 | 0.05921 | 4.6759 | 0 | 0 | 226.8699 | 162.3483 | off_peak | 579.5617 |  |  | 21.88 | 0 | 78.12 | 759.1194 | 0
6231 | 702.25 | 476.92 | 30.6 | 94.6293 | 94.6293 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 49.4535 | 620.0196 | 0 | 0.05921 | 5.2386 | 0 | 0 | 226.8699 | 94.6293 | off_peak | 607.6207 | 0 | 100 | 13.48 | 0 | 86.52 | 495.7241 | 0
6232 | 717.11 | 350.693 | 30.4 | 69.6348 | 69.6348 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 49.4535 | 647.4752 | 0 | 0.05921 | 5.8149 | 0 | 0 | 226.8699 | 69.6348 | off_peak | 647.4752 |  |  | 9.71 | 0 | 90.29 | 404.9194 | 0
6233 | 724.78 | 240.838 | 30 | 47.8918 | 47.8918 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 49.4535 | 676.8882 | 0 | 0.05921 | 6.4472 | 0 | 0 | 226.8699 | 47.8918 | off_peak | 676.8882 |  |  | 6.61 | 0 | 93.39 | 308.7689 | 0
6234 | 664.56 | 44.65 | 29.5 | 8.8952 | 8.8952 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 49.4535 | 655.6648 | 0 | 0.05921 | 6.9775 | 0 | 0 | 226.8699 | 8.8952 | off_peak | 655.6648 |  |  | 1.34 | 0 | 98.66 | 62.0664 | 0
6235 | 639.82 | 0 | 29.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 49.4535 | 639.82 | 0 | 0.05921 | 7.2691 | 0 | 0 | 226.8699 | 0 | off_peak | 639.82 |  |  | 0 | 0 | 100 | 0 | 0
6236 | 596.3 | 0 | 28.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 49.4535 | 596.3 | 0 | 0.05921 | 7.6361 | 0 | 0 | 226.8699 | 0 | off_peak | 596.3 |  |  | 0 | 0 | 100 | 0 | 0
6237 | 620.91 | 0 | 28.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 49.4535 | 620.91 | 0 | 0.05921 | 7.6773 | 0 | 0 | 226.8699 | 0 | off_peak | 620.91 |  |  | 0 | 0 | 100 | 0 | 0
6238 | 623.05 | 0 | 28.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 49.4535 | 623.05 | 0 | 0.05921 | 7.8579 | 0 | 0 | 226.8699 | 0 | off_peak | 623.05 |  |  | 0 | 0 | 100 | 0 | 0
6239 | 639.87 | 0 | 28.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 49.4535 | 639.87 | 0 | 0.05921 | 7.9091 | 0 | 0 | 226.8699 | 0 | off_peak | 639.87 |  |  | 0 | 0 | 100 | 0 | 0
6240 | 620.11 | 0 | 28.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 49.4535 | 620.11 | 0 | 0.05921 | 7.9088 | 0 | 0 | 226.8699 | 0 | off_peak | 620.11 |  |  | 0 | 0 | 100 | 0 | 0
6241 | 629.61 | 0 | 28.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 49.4535 | 629.61 | 0 | 0.05921 | 8.004 | 0 | 0 | 226.8699 | 0 | off_peak | 629.61 |  |  | 0 | 0 | 100 | 0 | 0
6242 | 615.81 | 0 | 28.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 49.4535 | 615.81 | 0 | 0.05921 | 7.6972 | 0 | 0 | 226.8699 | 0 | off_peak | 615.81 |  |  | 0 | 0 | 100 | 0 | 0
6243 | 602.54 | 0 | 28.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 49.4535 | 602.54 | 0 | 0.05921 | 7.2821 | 0 | 0 | 226.8699 | 0 | off_peak | 602.54 |  |  | 0 | 0 | 100 | 0 | 0
6244 | 609.98 | 0 | 28.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 49.4535 | 609.98 | 0 | 0.05921 | 6.644 | 0 | 0 | 226.8699 | 0 | off_peak | 609.98 |  |  | 0 | 0 | 100 | 0 | 0
6245 | 615.66 | 0 | 28.3 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 61.0516 | 628.0589 | 0 | 0.05921 | 5.84 | 0 | 0 | 226.8699 | 0 | off_peak | 615.66 | 0 | 100 | 0 | 0 | 100 | 0 | 0
6246 | 724.24 | 0 | 28.3 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 72.6498 | 736.6389 | 0 | 0.05921 | 5.2554 | 0 | 0 | 226.8699 | 0 | off_peak | 724.24 | 0 | 100 | 0 | 0 | 100 | 0 | 0
6247 | 778.28 | 35.7786 | 28.6 | 7.1513 | 7.1513 | 0 | 0 | 1.7439 | 1.7439 | 0 | 0 | 0 | 74.281 | 772.8726 | 0 | 0.05921 | 4.7813 | 0 | 0 | 226.8699 | 7.1513 | off_peak | 771.1287 | 0 | 100 | 0.92 | 0 | 99.08 | 34.1927 | 0
6248 | 816.86 | 230.318 | 29.2 | 45.9342 | 45.9342 | 0 | 0 | 0.11263 | 0.11263 | 0 | 0 | 0 | 74.3864 | 771.0384 | 0 | 0.05921 | 4.5092 | 0 | 0 | 226.8699 | 45.9342 | off_peak | 770.9258 | 0 | 100 | 5.62 | 0 | 94.38 | 207.1279 | 0
6249 | 789.98 | 447.128 | 29.5 | 89.0766 | 89.0693 | 0 | 0.0072743 | 0.0072743 | 0 | 0 | 0 | 0 | 74.3932 | 700.9107 | 0 | 0.05921 | 4.3269 | 0 | 0 | 226.8767 | 89.0693 | off_peak | 700.9107 | 100 | 0 | 11.27 | 0 | 88.73 | 385.3905 | 0
6250 | 856.38 | 640.065 | 29.9 | 127.3268 | 127.3268 | 0 | 0 | 0.00046981 | 0.00046981 | 0 | 0 | 0 | 74.3936 | 729.0537 | 0 | 0.05921 | 4.2752 | 0 | 0 | 226.8767 | 127.3268 | off_peak | 729.0532 | 0 | 100 | 14.87 | 0 | 85.13 | 544.3515 | 0
6251 | 814.39 | 785.81 | 30.2 | 156.1477 | 156.1477 | 0 | 0 | 3.0343e-05 | 3.0343e-05 | 0 | 0 | 0 | 74.3936 | 658.2424 | 0 | 0.05921 | 4.4517 | 0 | 0 | 226.8767 | 156.1477 | off_peak | 658.2423 | 0 | 100 | 19.17 | 0 | 80.83 | 695.1225 | 0
6252 | 834.32 | 871.206 | 30.4 | 172.9896 | 172.9896 | 0 | 0 | 1.9597e-06 | 1.9597e-06 | 0 | 0 | 0 | 74.3936 | 661.3304 | 0 | 0.05921 | 4.8255 | 0 | 0 | 226.8767 | 172.9896 | off_peak | 661.3304 | 0 | 100 | 20.73 | 0 | 79.27 | 834.7627 | 0
6253 | 827.76 | 889.363 | 30.5 | 176.5301 | 176.5301 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 651.2299 | 0 | 0.088511 | 5.0279 | 0 | 0 | 226.8767 | 176.5301 | on_peak | 651.2299 |  |  | 21.33 | 0 | 78.67 | 887.5683 | 0
6254 | 844.74 | 813.541 | 30.5 | 161.4802 | 161.4802 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 683.2598 | 0 | 0.088511 | 5.1279 | 0 | 0 | 226.8767 | 161.4802 | on_peak | 683.2598 |  |  | 19.12 | 0 | 80.88 | 828.0537 | 0
6255 | 875.7 | 718.469 | 30.4 | 142.6616 | 142.6616 | 0 | 0 | 0 | 0 | 62.63 | 62.63 | 0 | 7.4394 | 670.4084 | 0 | 0.088511 | 5.2794 | 0 | 0 | 226.8767 | 142.6616 | on_peak | 670.4084 |  |  | 16.29 | 7.15 | 76.56 | 753.1608 | 0
6256 | 838.54 | 548.353 | 30.2 | 108.9628 | 108.9628 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 729.5772 | 0 | 0.088511 | 5.7063 | 0 | 0 | 226.8767 | 108.9628 | on_peak | 729.5772 |  |  | 12.99 | 0 | 87.01 | 621.7737 | 0
6257 | 837.88 | 340.894 | 29.8 | 67.8382 | 67.8382 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 770.0418 | 0 | 0.088511 | 6.2382 | 0 | 0 | 226.8767 | 67.8382 | on_peak | 770.0418 |  |  | 8.1 | 0 | 91.9 | 423.187 | 0
6258 | 828.98 | 126.407 | 29.3 | 25.2012 | 25.2012 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 803.7788 | 0 | 0.088511 | 6.7455 | 0 | 0 | 226.8767 | 25.2012 | on_peak | 803.7788 |  |  | 3.04 | 0 | 96.96 | 169.9948 | 0
6259 | 843.34 | 0 | 29.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 843.34 | 0 | 0.088511 | 7.2523 | 0 | 0 | 226.8767 | 0 | on_peak | 843.34 |  |  | 0 | 0 | 100 | 0 | 0
6260 | 806.08 | 0 | 28.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 806.08 | 0 | 0.088511 | 7.6687 | 0 | 0 | 226.8767 | 0 | on_peak | 806.08 |  |  | 0 | 0 | 100 | 0 | 0
6261 | 789.97 | 0 | 28.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 789.97 | 0 | 0.088511 | 7.9265 | 0 | 0 | 226.8767 | 0 | on_peak | 789.97 |  |  | 0 | 0 | 100 | 0 | 0
6262 | 787.55 | 0 | 28.5 | 0 | 0 | 0 | 0 | 1.3799 | 1.3799 | 0 | 0 | 0 | 8.7302 | 788.9299 | 0 | 0.05921 | 8.2984 | 0 | 0 | 226.8767 | 0 | off_peak | 787.55 | 0 | 100 | 0 | 0 | 100 | 0 | 0
6263 | 755.11 | 0 | 28.3 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 20.3283 | 767.5089 | 0 | 0.05921 | 8.229 | 0 | 0 | 226.8767 | 0 | off_peak | 755.11 | 0 | 100 | 0 | 0 | 100 | 0 | 0
6264 | 749.68 | 0 | 28.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20.3283 | 749.68 | 0 | 0.05921 | 8.2141 | 0 | 0 | 226.8767 | 0 | off_peak | 749.68 |  |  | 0 | 0 | 100 | 0 | 0
6265 | 682.37 | 0 | 28 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 31.9265 | 694.7689 | 0 | 0.05921 | 8.0707 | 0 | 0 | 226.8767 | 0 | off_peak | 682.37 | 0 | 100 | 0 | 0 | 100 | 0 | 0
6266 | 613.61 | 0 | 27.8 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 43.5246 | 626.0089 | 0 | 0.05921 | 7.6165 | 0 | 0 | 226.8767 | 0 | off_peak | 613.61 | 0 | 100 | 0 | 0 | 100 | 0 | 0
6267 | 592.13 | 0 | 27.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 43.5246 | 592.13 | 0 | 0.05921 | 6.9729 | 0 | 0 | 226.8767 | 0 | off_peak | 592.13 |  |  | 0 | 0 | 100 | 0 | 0
6268 | 583.69 | 0 | 27.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 43.5246 | 583.69 | 0 | 0.05921 | 6.3699 | 0 | 0 | 226.8767 | 0 | off_peak | 583.69 |  |  | 0 | 0 | 100 | 0 | 0
6269 | 604.93 | 0 | 27.5 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 55.1228 | 617.3289 | 0 | 0.05921 | 5.598 | 0 | 0 | 226.8767 | 0 | off_peak | 604.93 | 0 | 100 | 0 | 0 | 100 | 0 | 0
6270 | 653.02 | 0 | 27.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 55.1228 | 653.02 | 0 | 0.05921 | 4.9918 | 0 | 0 | 226.8767 | 0 | off_peak | 653.02 |  |  | 0 | 0 | 100 | 0 | 0
6271 | 770.37 | 36.6746 | 28 | 7.3464 | 0 | 0 | 7.3464 | 7.3464 | 0 | 0 | 0 | 0 | 61.9947 | 770.37 | 0 | 0.05921 | 4.6101 | 0 | 0 | 233.7486 | 0 | off_peak | 770.37 | 100 | 0 | 0 | 0 | 100 | 0 | 0
6272 | 797.27 | 230.456 | 28.6 | 46.0625 | 46.0625 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 73.5928 | 763.6064 | 0 | 0.05921 | 4.3446 | 0 | 0 | 233.7486 | 46.0625 | off_peak | 751.2075 | 0 | 100 | 5.78 | 0 | 94.22 | 200.125 | 0
6273 | 837.93 | 445.22 | 29.1 | 88.8263 | 88.8263 | 0 | 0 | 0.80079 | 0.80079 | 0 | 0 | 0 | 74.3419 | 749.9045 | 0 | 0.05921 | 4.1907 | 0 | 0 | 233.7486 | 88.8263 | off_peak | 749.1037 | 0 | 100 | 10.6 | 0 | 89.4 | 372.2487 | 0
6274 | 838.06 | 636.609 | 29.4 | 126.8713 | 126.8713 | 0 | 0 | 0.05172 | 0.05172 | 0 | 0 | 0 | 74.3903 | 711.2404 | 0 | 0.05921 | 4.1475 | 0 | 0 | 233.7486 | 126.8713 | off_peak | 711.1887 | 0 | 100 | 15.14 | 0 | 84.86 | 526.1958 | 0
6275 | 808.82 | 776.418 | 29.6 | 154.621 | 154.621 | 0 | 0 | 0.0033404 | 0.0033404 | 0 | 0 | 0 | 74.3934 | 654.2023 | 0 | 0.05921 | 4.3381 | 0 | 0 | 233.7486 | 154.621 | off_peak | 654.199 | 0 | 100 | 19.12 | 0 | 80.88 | 670.7555 | 0
6276 | 856.36 | 861.646 | 29.8 | 171.4682 | 171.4682 | 0 | 0 | 0.00021574 | 0.00021574 | 0 | 0 | 0 | 74.3936 | 684.892 | 0 | 0.05921 | 4.7983 | 0 | 0 | 233.7486 | 171.4682 | off_peak | 684.8918 | 0 | 100 | 20.02 | 0 | 79.98 | 822.761 | 0
6277 | 809.6 | 879.586 | 29.8 | 175.0383 | 175.0383 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 634.5617 | 0 | 0.088511 | 5.0281 | 0 | 0 | 233.7486 | 175.0383 | on_peak | 634.5617 |  |  | 21.62 | 0 | 78.38 | 880.1119 | 0
6278 | 840.93 | 826.885 | 29.8 | 164.5508 | 164.5508 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 676.3792 | 0 | 0.088511 | 5.104 | 0 | 0 | 233.7486 | 164.5508 | on_peak | 676.3792 |  |  | 19.57 | 0 | 80.43 | 839.8633 | 0
6279 | 912.57 | 705.864 | 29.7 | 140.519 | 140.519 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 772.051 | 0 | 0.088511 | 5.2293 | 0 | 0 | 233.7486 | 140.519 | on_peak | 772.051 |  |  | 15.4 | 0 | 84.6 | 734.8164 | 0
6280 | 811.28 | 157.7 | 29.5 | 31.4169 | 31.4169 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 779.8631 | 0 | 0.088511 | 5.6721 | 0 | 0 | 233.7486 | 31.4169 | on_peak | 779.8631 |  |  | 3.87 | 0 | 96.13 | 178.2006 | 0
6281 | 816.41 | 213.171 | 29.2 | 42.5144 | 42.5144 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 773.8956 | 0 | 0.088511 | 6.139 | 0 | 0 | 233.7486 | 42.5144 | on_peak | 773.8956 |  |  | 5.21 | 0 | 94.79 | 260.9977 | 0
6282 | 806.52 | 59.0753 | 28.8 | 11.7991 | 11.7991 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 794.7209 | 0 | 0.088511 | 6.58 | 0 | 0 | 233.7486 | 11.7991 | on_peak | 794.7209 |  |  | 1.46 | 0 | 98.54 | 77.6378 | 0
6283 | 779.93 | 0 | 28.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 779.93 | 0 | 0.088511 | 7.0973 | 0 | 0 | 233.7486 | 0 | on_peak | 779.93 |  |  | 0 | 0 | 100 | 0 | 0
6284 | 804.03 | 0 | 28.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 804.03 | 0 | 0.088511 | 7.2677 | 0 | 0 | 233.7486 | 0 | on_peak | 804.03 |  |  | 0 | 0 | 100 | 0 | 0
6285 | 791.25 | 0 | 28.2 | 0 | 0 | 0 | 0 | 0 | 0 | 62.63 | 62.63 | 0 | 7.4394 | 728.62 | 0 | 0.088511 | 7.3351 | 62.63 | 0 | 166.7944 | 62.63 | on_peak | 728.62 |  |  | 0 | 7.92 | 92.08 | 459.3955 | 0
6286 | 744.75 | 0 | 28.2 | 0 | 0 | 0 | 0 | 8.7263 | 8.7263 | 0 | 0 | 0 | 15.6021 | 753.4763 | 0 | 0.05921 | 7.5419 | 0 | 0 | 166.7944 | 0 | off_peak | 744.75 | 0 | 100 | 0 | 0 | 100 | 0 | 0
6287 | 771.21 | 0 | 28.2 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 27.2003 | 783.6089 | 0 | 0.05921 | 7.5632 | 0 | 0 | 166.7944 | 0 | off_peak | 771.21 | 0 | 100 | 0 | 0 | 100 | 0 | 0
6288 | 763.54 | 0 | 28.2 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 38.7984 | 775.9389 | 0 | 0.05921 | 7.5492 | 0 | 0 | 166.7944 | 0 | off_peak | 763.54 | 0 | 100 | 0 | 0 | 100 | 0 | 0
6289 | 724.63 | 0 | 28.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 38.7984 | 724.63 | 0 | 0.05921 | 7.522 | 0 | 0 | 166.7944 | 0 | off_peak | 724.63 |  |  | 0 | 0 | 100 | 0 | 0
6290 | 632.92 | 0 | 28.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 38.7984 | 632.92 | 0 | 0.05921 | 7.0974 | 0 | 0 | 166.7944 | 0 | off_peak | 632.92 |  |  | 0 | 0 | 100 | 0 | 0
6291 | 647.07 | 0 | 28.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 38.7984 | 647.07 | 0 | 0.05921 | 6.4627 | 0 | 0 | 166.7944 | 0 | off_peak | 647.07 |  |  | 0 | 0 | 100 | 0 | 0
6292 | 626.32 | 0 | 28.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 38.7984 | 626.32 | 0 | 0.05921 | 5.9478 | 0 | 0 | 166.7944 | 0 | off_peak | 626.32 |  |  | 0 | 0 | 100 | 0 | 0
6293 | 651 | 0 | 28.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 38.7984 | 651 | 0 | 0.05921 | 5.186 | 0 | 0 | 166.7944 | 0 | off_peak | 651 |  |  | 0 | 0 | 100 | 0 | 0
6294 | 701.57 | 0 | 28.3 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 50.3966 | 713.9689 | 0 | 0.05921 | 4.6621 | 0 | 0 | 166.7944 | 0 | off_peak | 701.57 | 0 | 100 | 0 | 0 | 100 | 0 | 0
6295 | 796.04 | 34.607 | 28.3 | 6.9247 | 0 | 0 | 6.9247 | 12.3989 | 5.4743 | 0 | 0 | 0 | 61.9947 | 801.5143 | 0 | 0.05921 | 4.3062 | 0 | 0 | 173.2718 | 0 | off_peak | 796.04 | 55.85 | 44.15 | 0 | 0 | 100 | 0 | 0
6296 | 890.26 | 226.477 | 28.3 | 45.3168 | 45.3168 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 73.5928 | 857.3422 | 0 | 0.05921 | 4.1128 | 0 | 0 | 173.2718 | 45.3168 | off_peak | 844.9432 | 0 | 100 | 5.09 | 0 | 94.91 | 186.3775 | 0
6297 | 872.26 | 439.98 | 28.3 | 88.0375 | 87.2367 | 0 | 0.80079 | 0.80079 | 0 | 0 | 0 | 0 | 74.3419 | 785.0233 | 0 | 0.05921 | 3.9811 | 0 | 0 | 174.0209 | 87.2367 | off_peak | 785.0233 | 100 | 0 | 10 | 0 | 90 | 347.2952 | 0
6298 | 889.18 | 629.562 | 28.5 | 125.88 | 125.88 | 0 | 0 | 0.05172 | 0.05172 | 0 | 0 | 0 | 74.3903 | 763.3517 | 0 | 0.05921 | 3.9164 | 0 | 0 | 174.0209 | 125.88 | off_peak | 763.3 | 0 | 100 | 14.16 | 0 | 85.84 | 492.9977 | 0
6299 | 824.33 | 504.199 | 28.7 | 100.7403 | 100.7403 | 0 | 0 | 0.0033404 | 0.0033404 | 0 | 0 | 0 | 74.3934 | 723.593 | 0 | 0.05921 | 3.6804 | 0 | 0 | 174.0209 | 100.7403 | off_peak | 723.5897 | 0 | 100 | 12.22 | 0 | 87.78 | 370.768 | 0
6300 | 857.6 | 848.18 | 28.8 | 169.4068 | 169.4066 | 0 | 0.00021574 | 0.00021574 | 0 | 0 | 0 | 0 | 74.3936 | 688.1934 | 0 | 0.05921 | 4.4638 | 0 | 0 | 174.0211 | 169.4066 | off_peak | 688.1934 | 100 | 0 | 19.75 | 0 | 80.25 | 756.2002 | 0
6301 | 832.15 | 579.493 | 28.9 | 115.6998 | 115.6998 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 716.4502 | 0 | 0.088511 | 4.7012 | 0 | 0 | 174.0211 | 115.6998 | on_peak | 716.4502 |  |  | 13.9 | 0 | 86.1 | 543.9239 | 0
6302 | 858.77 | 504.09 | 28.9 | 100.645 | 100.645 | 0 | 0 | 0 | 0 | 62.63 | 62.63 | 0 | 7.4394 | 695.495 | 0 | 0.088511 | 4.7882 | 0 | 0 | 174.0211 | 100.645 | on_peak | 695.495 |  |  | 11.72 | 7.29 | 80.99 | 481.9038 | 0
6303 | 887.27 | 383.709 | 28.9 | 76.6101 | 76.6101 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 810.6599 | 0 | 0.088511 | 4.9344 | 0 | 0 | 174.0211 | 76.6101 | on_peak | 810.6599 |  |  | 8.63 | 0 | 91.37 | 378.0216 | 0
6304 | 847.46 | 517.872 | 28.9 | 103.3967 | 103.3967 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 744.0633 | 0 | 0.088511 | 5.3278 | 0 | 0 | 174.0211 | 103.3967 | on_peak | 744.0633 |  |  | 12.2 | 0 | 87.8 | 550.8812 | 0
6305 | 828.21 | 155.057 | 28.8 | 30.9695 | 30.9695 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 797.2405 | 0 | 0.088511 | 5.8306 | 0 | 0 | 174.0211 | 30.9695 | on_peak | 797.2405 |  |  | 3.74 | 0 | 96.26 | 180.5706 | 0
6306 | 825.12 | 108.698 | 28.7 | 21.7182 | 21.7182 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 803.4018 | 0 | 0.088511 | 6.395 | 0 | 0 | 174.0211 | 21.7182 | on_peak | 803.4018 |  |  | 2.63 | 0 | 97.37 | 138.8887 | 0
6307 | 811.28 | 0 | 28.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 811.28 | 0 | 0.088511 | 7.0465 | 0 | 0 | 174.0211 | 0 | on_peak | 811.28 |  |  | 0 | 0 | 100 | 0 | 0
6308 | 820.9 | 0 | 28.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 820.9 | 0 | 0.088511 | 7.6023 | 0 | 0 | 174.0211 | 0 | on_peak | 820.9 |  |  | 0 | 0 | 100 | 0 | 0
6309 | 780.46 | 0 | 28.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 780.46 | 0 | 0.088511 | 7.639 | 0 | 0 | 174.0211 | 0 | on_peak | 780.46 |  |  | 0 | 0 | 100 | 0 | 0
6310 | 763.6 | 0 | 28.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 763.6 | 0 | 0.05921 | 7.708 | 0 | 0 | 174.0211 | 0 | off_peak | 763.6 |  |  | 0 | 0 | 100 | 0 | 0
6311 | 805.1 | 0 | 28.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 805.1 | 0 | 0.05921 | 7.6044 | 0 | 0 | 174.0211 | 0 | off_peak | 805.1 |  |  | 0 | 0 | 100 | 0 | 0
6312 | 768.19 | 0 | 28.2 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 19.0375 | 780.5889 | 0 | 0.05921 | 7.3403 | 0 | 0 | 174.0211 | 0 | off_peak | 768.19 | 0 | 100 | 0 | 0 | 100 | 0 | 0
6313 | 720.29 | 0 | 28.1 | 0 | 0 | 0 | 0 | 8.7263 | 8.7263 | 0 | 0 | 0 | 27.2003 | 729.0163 | 0 | 0.05921 | 7.2851 | 0 | 0 | 174.0211 | 0 | off_peak | 720.29 | 0 | 100 | 0 | 0 | 100 | 0 | 0
6314 | 660.36 | 0 | 28 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 38.7984 | 672.7589 | 0 | 0.05921 | 7.0619 | 0 | 0 | 174.0211 | 0 | off_peak | 660.36 | 0 | 100 | 0 | 0 | 100 | 0 | 0
6315 | 625.04 | 0 | 27.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 38.7984 | 625.04 | 0 | 0.05921 | 6.5923 | 0 | 0 | 174.0211 | 0 | off_peak | 625.04 |  |  | 0 | 0 | 100 | 0 | 0
6316 | 658.67 | 0 | 27.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 38.7984 | 658.67 | 0 | 0.05921 | 5.9521 | 0 | 0 | 174.0211 | 0 | off_peak | 658.67 |  |  | 0 | 0 | 100 | 0 | 0
6317 | 623.85 | 0 | 27.9 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 50.3966 | 636.2489 | 0 | 0.05921 | 5.1606 | 0 | 0 | 174.0211 | 0 | off_peak | 623.85 | 0 | 100 | 0 | 0 | 100 | 0 | 0
6318 | 720.18 | 0 | 28 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 61.9947 | 732.5789 | 0 | 0.05921 | 4.5627 | 0 | 0 | 174.0211 | 0 | off_peak | 720.18 | 0 | 100 | 0 | 0 | 100 | 0 | 0
6319 | 770.76 | 31.5657 | 28.1 | 6.3207 | 0 | 0 | 6.3207 | 12.3989 | 6.0782 | 0 | 0 | 0 | 73.5928 | 776.8382 | 0 | 0.05921 | 4.1041 | 0 | 0 | 179.9336 | 0 | off_peak | 770.76 | 50.98 | 49.02 | 0 | 0 | 100 | 0 | 0
6320 | 828.21 | 218.867 | 28.4 | 43.7781 | 43.7781 | 0 | 0 | 0.80079 | 0.80079 | 0 | 0 | 0 | 74.3419 | 785.2327 | 0 | 0.05921 | 3.9092 | 0 | 0 | 179.9336 | 43.7781 | off_peak | 784.4319 | 0 | 100 | 5.29 | 0 | 94.71 | 171.1367 | 0
6321 | 842.43 | 428.913 | 28.7 | 85.698 | 85.698 | 0 | 0 | 0.05172 | 0.05172 | 0 | 0 | 0 | 74.3903 | 756.7837 | 0 | 0.05921 | 3.7881 | 0 | 0 | 179.9336 | 85.698 | off_peak | 756.732 | 0 | 100 | 10.17 | 0 | 89.83 | 324.6321 | 0
6322 | 825.5 | 615.223 | 28.9 | 122.8335 | 122.8302 | 0 | 0.0033404 | 0.0033404 | 0 | 0 | 0 | 0 | 74.3934 | 702.6698 | 0 | 0.05921 | 3.7754 | 0 | 0 | 179.9367 | 122.8302 | off_peak | 702.6698 | 100 | 0 | 14.88 | 0 | 85.12 | 463.7308 | 0
6323 | 851.07 | 753.052 | 29.1 | 150.2422 | 150.242 | 0 | 0.00021574 | 0.00021574 | 0 | 0 | 0 | 0 | 74.3936 | 700.828 | 0 | 0.05921 | 4.0199 | 0 | 0 | 179.9369 | 150.242 | off_peak | 700.828 | 100 | 0 | 17.65 | 0 | 82.35 | 603.9559 | 0
6324 | 899.03 | 423.214 | 29.2 | 84.405 | 84.405 | 0 | 1.3934e-05 | 1.3934e-05 | 0 | 0 | 0 | 0 | 74.3936 | 814.625 | 0 | 0.05921 | 4.4544 | 0 | 0 | 179.9369 | 84.405 | off_peak | 814.625 | 100 | 0 | 9.39 | 0 | 90.61 | 375.9742 | 0
6325 | 806.42 | 198.55 | 29.3 | 39.584 | 39.584 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 766.836 | 0 | 0.088511 | 4.6802 | 0 | 0 | 179.9369 | 39.584 | on_peak | 766.836 |  |  | 4.91 | 0 | 95.09 | 185.2628 | 0
6326 | 829.28 | 105.45 | 29.3 | 21.0231 | 21.0231 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 808.2569 | 0 | 0.088511 | 4.807 | 0 | 0 | 179.9369 | 21.0231 | on_peak | 808.2569 |  |  | 2.54 | 0 | 97.46 | 101.0572 | 0
6327 | 823.18 | 263.618 | 29.2 | 52.5755 | 52.5755 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 770.6045 | 0 | 0.088511 | 4.9221 | 0 | 0 | 179.9369 | 52.5755 | on_peak | 770.6045 |  |  | 6.39 | 0 | 93.61 | 258.7798 | 0
6328 | 881.28 | 302.317 | 29 | 60.3376 | 60.3376 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 820.9424 | 0 | 0.088511 | 5.301 | 0 | 0 | 179.9369 | 60.3376 | on_peak | 820.9424 |  |  | 6.85 | 0 | 93.15 | 319.8494 | 0
6329 | 892.94 | 315.868 | 28.8 | 63.0883 | 63.0883 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 829.8517 | 0 | 0.088511 | 5.7752 | 0 | 0 | 179.9369 | 63.0883 | on_peak | 829.8517 |  |  | 7.07 | 0 | 92.93 | 364.347 | 0
6330 | 863.15 | 110.005 | 28.6 | 21.9873 | 21.9873 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 841.1627 | 0 | 0.088511 | 6.3456 | 0 | 0 | 179.9369 | 21.9873 | on_peak | 841.1627 |  |  | 2.55 | 0 | 97.45 | 139.5227 | 0
6331 | 821.43 | 0 | 28.4 | 0 | 0 | 0 | 0 | 0 | 0 | 62.63 | 62.63 | 0 | 7.4394 | 758.8 | 0 | 0.088511 | 6.7608 | 62.63 | 0 | 112.9826 | 62.63 | on_peak | 758.8 |  |  | 0 | 7.62 | 92.38 | 423.4261 | 0
6332 | 798.21 | 0 | 28.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 798.21 | 0 | 0.088511 | 7.0008 | 0 | 0 | 112.9826 | 0 | on_peak | 798.21 |  |  | 0 | 0 | 100 | 0 | 0
6333 | 818.99 | 0 | 28.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 818.99 | 0 | 0.088511 | 7.1828 | 0 | 0 | 112.9826 | 0 | on_peak | 818.99 |  |  | 0 | 0 | 100 | 0 | 0
6334 | 768.88 | 0 | 28.4 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 19.0375 | 781.2789 | 0 | 0.05921 | 7.3375 | 0 | 0 | 112.9826 | 0 | off_peak | 768.88 | 0 | 100 | 0 | 0 | 100 | 0 | 0
6335 | 806.56 | 0 | 28.4 | 0 | 0 | 0 | 0 | 8.7263 | 8.7263 | 0 | 0 | 0 | 27.2003 | 815.2863 | 0 | 0.05921 | 7.3761 | 0 | 0 | 112.9826 | 0 | off_peak | 806.56 | 0 | 100 | 0 | 0 | 100 | 0 | 0
6336 | 784.32 | 0 | 28.3 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 38.7984 | 796.7189 | 0 | 0.05921 | 7.1634 | 0 | 0 | 112.9826 | 0 | off_peak | 784.32 | 0 | 100 | 0 | 0 | 100 | 0 | 0
6337 | 721.74 | 0 | 28.2 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 50.3966 | 734.1389 | 0 | 0.05921 | 7.0162 | 0 | 0 | 112.9826 | 0 | off_peak | 721.74 | 0 | 100 | 0 | 0 | 100 | 0 | 0
6338 | 655.1 | 0 | 28.2 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 61.9947 | 667.4989 | 0 | 0.05921 | 6.6885 | 0 | 0 | 112.9826 | 0 | off_peak | 655.1 | 0 | 100 | 0 | 0 | 100 | 0 | 0
6339 | 666.2 | 0 | 28.1 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 73.5928 | 678.5989 | 0 | 0.05921 | 6.1935 | 0 | 0 | 112.9826 | 0 | off_peak | 666.2 | 0 | 100 | 0 | 0 | 100 | 0 | 0
6340 | 650.47 | 0 | 28 | 0 | 0 | 0 | 0 | 0.80079 | 0.80079 | 0 | 0 | 0 | 74.3419 | 651.2708 | 0 | 0.05921 | 5.6515 | 0 | 0 | 112.9826 | 0 | off_peak | 650.47 | 0 | 100 | 0 | 0 | 100 | 0 | 0
6341 | 673.23 | 0 | 28 | 0 | 0 | 0 | 0 | 0.05172 | 0.05172 | 0 | 0 | 0 | 74.3903 | 673.2817 | 0 | 0.05921 | 5.0215 | 0 | 0 | 112.9826 | 0 | off_peak | 673.23 | 0 | 100 | 0 | 0 | 100 | 0 | 0
6342 | 728.59 | 0 | 28 | 0 | 0 | 0 | 0 | 0.0033404 | 0.0033404 | 0 | 0 | 0 | 74.3934 | 728.5933 | 0 | 0.05921 | 4.3886 | 0 | 0 | 112.9826 | 0 | off_peak | 728.59 | 0 | 100 | 0 | 0 | 100 | 0 | 0
6343 | 790.17 | 32.3497 | 28.1 | 6.4777 | 6.4775 | 0 | 0.00021574 | 0.00021574 | 0 | 0 | 0 | 0 | 74.3936 | 783.6925 | 0 | 0.05921 | 3.9561 | 0 | 0 | 112.9828 | 6.4775 | off_peak | 783.6925 | 100 | 0 | 0.82 | 0 | 99.18 | 25.6253 | 0
6344 | 804.89 | 221.566 | 28.4 | 44.3179 | 44.3179 | 0 | 0 | 1.4896e-05 | 1.4896e-05 | 0 | 0 | 0 | 74.3936 | 760.5721 | 0 | 0.05921 | 3.723 | 0 | 0 | 112.9828 | 44.3179 | off_peak | 760.5721 | 0 | 100 | 5.51 | 0 | 94.49 | 164.9954 | 0
6345 | 875.69 | 431.795 | 28.6 | 86.3053 | 86.3053 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 789.3847 | 0 | 0.05921 | 3.5885 | 0 | 0 | 112.9828 | 86.3053 | off_peak | 789.3847 |  |  | 9.86 | 0 | 90.14 | 309.7101 | 0
6346 | 886.52 | 279.55 | 28.8 | 55.8345 | 55.8345 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 830.6855 | 0 | 0.05921 | 3.5507 | 0 | 0 | 112.9828 | 55.8345 | off_peak | 830.6855 |  |  | 6.3 | 0 | 93.7 | 198.2499 | 0
6347 | 915.87 | 128.069 | 28.9 | 25.5699 | 25.5699 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 890.3001 | 0 | 0.05921 | 3.7544 | 0 | 0 | 112.9828 | 25.5699 | off_peak | 890.3001 |  |  | 2.79 | 0 | 97.21 | 95.9984 | 0
6348 | 950.81 | 288.979 | 29 | 57.6756 | 57.6756 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 893.1344 | 0 | 0.05921 | 4.1932 | 0 | 0 | 112.9828 | 57.6756 | off_peak | 893.1344 |  |  | 6.07 | 0 | 93.93 | 241.8481 | 0
6349 | 892.98 | 45.6 | 29 | 9.101 | 9.101 | 0 | 0 | 0 | 0 | 35.3657 | 35.3657 | 0 | 36.5861 | 848.5132 | 0 | 0.088511 | 4.4307 | 0 | 0 | 112.9828 | 9.101 | on_peak | 848.5132 |  |  | 1.02 | 3.96 | 95.02 | 40.3242 | 0
6350 | 880.86 | 194.608 | 29 | 38.8406 | 32.3468 | 0 | 6.4939 | 6.4939 | 0 | 0 | 0 | 0 | 42.6606 | 848.5132 | 0 | 0.088511 | 4.5285 | 0 | 0 | 119.0573 | 32.3468 | on_peak | 848.5132 | 100 | 0 | 3.67 | 0 | 96.33 | 146.4836 | 0
6351 | 898.72 | 86.45 | 28.9 | 17.2603 | 17.2603 | 0 | 0 | 0 | 0 | 32.9464 | 32.9464 | 0 | 7.4394 | 848.5132 | 0 | 0.088511 | 4.5819 | 0 | 0 | 119.0573 | 17.2603 | on_peak | 848.5132 |  |  | 1.92 | 3.67 | 94.41 | 79.0851 | 0
6352 | 808.36 | 108.86 | 28.7 | 21.7505 | 21.7505 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 786.6095 | 0 | 0.088511 | 4.7421 | 0 | 0 | 119.0573 | 21.7505 | on_peak | 786.6095 |  |  | 2.69 | 0 | 97.31 | 103.1438 | 0
6353 | 821.1 | 84.3484 | 28.5 | 16.8653 | 16.8653 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 804.2347 | 0 | 0.088511 | 5.1328 | 0 | 0 | 119.0573 | 16.8653 | on_peak | 804.2347 |  |  | 2.05 | 0 | 97.95 | 86.5656 | 0
6354 | 793.76 | 39.1132 | 28.3 | 7.8263 | 7.8263 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 785.9337 | 0 | 0.088511 | 5.6346 | 0 | 0 | 119.0573 | 7.8263 | on_peak | 785.9337 |  |  | 0.99 | 0 | 99.01 | 44.0985 | 0
6355 | 790.47 | 0 | 28.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 790.47 | 0 | 0.088511 | 6.1354 | 0 | 0 | 119.0573 | 0 | on_peak | 790.47 |  |  | 0 | 0 | 100 | 0 | 0
6356 | 819.75 | 0 | 28.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 819.75 | 0 | 0.088511 | 6.4941 | 0 | 0 | 119.0573 | 0 | on_peak | 819.75 |  |  | 0 | 0 | 100 | 0 | 0
6357 | 778.65 | 0 | 28.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 778.65 | 0 | 0.088511 | 6.8184 | 0 | 0 | 119.0573 | 0 | on_peak | 778.65 |  |  | 0 | 0 | 100 | 0 | 0
6358 | 781.01 | 0 | 28.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 781.01 | 0 | 0.05921 | 7.1965 | 0 | 0 | 119.0573 | 0 | off_peak | 781.01 |  |  | 0 | 0 | 100 | 0 | 0
6359 | 769.88 | 0 | 28 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 769.88 | 0 | 0.05921 | 7.3273 | 0 | 0 | 119.0573 | 0 | off_peak | 769.88 |  |  | 0 | 0 | 100 | 0 | 0
6360 | 753.8 | 0 | 27.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 753.8 | 0 | 0.05921 | 7.7786 | 0 | 0 | 119.0573 | 0 | off_peak | 753.8 |  |  | 0 | 0 | 100 | 0 | 0
6361 | 702.98 | 0 | 27.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 702.98 | 0 | 0.05921 | 7.849 | 0 | 0 | 119.0573 | 0 | off_peak | 702.98 |  |  | 0 | 0 | 100 | 0 | 0
6362 | 649.45 | 0 | 27.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 649.45 | 0 | 0.05921 | 7.4537 | 0 | 0 | 119.0573 | 0 | off_peak | 649.45 |  |  | 0 | 0 | 100 | 0 | 0
6363 | 659.22 | 0 | 27.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 659.22 | 0 | 0.05921 | 6.8538 | 0 | 0 | 119.0573 | 0 | off_peak | 659.22 |  |  | 0 | 0 | 100 | 0 | 0
6364 | 660.05 | 0 | 27.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 660.05 | 0 | 0.05921 | 6.2871 | 0 | 0 | 119.0573 | 0 | off_peak | 660.05 |  |  | 0 | 0 | 100 | 0 | 0
6365 | 680.25 | 0 | 27.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 680.25 | 0 | 0.05921 | 5.5364 | 0 | 0 | 119.0573 | 0 | off_peak | 680.25 |  |  | 0 | 0 | 100 | 0 | 0
6366 | 677.15 | 0 | 27.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 677.15 | 0 | 0.05921 | 5.0524 | 0 | 0 | 119.0573 | 0 | off_peak | 677.15 |  |  | 0 | 0 | 100 | 0 | 0
6367 | 736.98 | 29.3105 | 28 | 5.8713 | 0 | 0 | 5.8713 | 5.8713 | 0 | 0 | 0 | 0 | 12.9314 | 736.98 | 0 | 0.05921 | 4.6054 | 0 | 0 | 124.5494 | 0 | off_peak | 736.98 | 100 | 0 | 0 | 0 | 100 | 0 | 0
6368 | 732.56 | 213.519 | 28.3 | 42.7239 | 42.7239 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 24.5296 | 702.235 | 0 | 0.05921 | 4.2691 | 0 | 0 | 124.5494 | 42.7239 | off_peak | 689.8361 | 0 | 100 | 5.83 | 0 | 94.17 | 182.3929 | 0
6369 | 766.53 | 421.396 | 28.6 | 84.2268 | 84.2268 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 24.5296 | 682.3032 | 0 | 0.05921 | 4.0621 | 0 | 0 | 124.5494 | 84.2268 | off_peak | 682.3032 |  |  | 10.99 | 0 | 89.01 | 342.1347 | 0
6370 | 770.11 | 605.612 | 28.7 | 121.0029 | 121.0029 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 24.5296 | 649.1071 | 0 | 0.05921 | 3.913 | 0 | 0 | 124.5494 | 121.0029 | off_peak | 649.1071 |  |  | 15.71 | 0 | 84.29 | 473.4872 | 0
6371 | 757.49 | 329.497 | 28.9 | 65.7863 | 65.7863 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 24.5296 | 691.7037 | 0 | 0.05921 | 3.8786 | 0 | 0 | 124.5494 | 65.7863 | off_peak | 691.7037 |  |  | 8.68 | 0 | 91.32 | 255.1564 | 0
6372 | 786.25 | 699.525 | 29 | 139.614 | 139.614 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 24.5296 | 646.636 | 0 | 0.05921 | 3.9684 | 0 | 0 | 124.5494 | 139.614 | off_peak | 646.636 |  |  | 17.76 | 0 | 82.24 | 554.0474 | 0
6373 | 724.94 | 454.763 | 29.1 | 90.7303 | 90.7303 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 24.5296 | 634.2097 | 0 | 0.05921 | 4.1675 | 0 | 0 | 124.5494 | 90.7303 | off_peak | 634.2097 |  |  | 12.52 | 0 | 87.48 | 378.1207 | 0
6374 | 744.79 | 714.345 | 29.1 | 142.5198 | 142.5198 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 24.5296 | 602.2702 | 0 | 0.05921 | 4.2819 | 0 | 0 | 124.5494 | 142.5198 | off_peak | 602.2702 |  |  | 19.14 | 0 | 80.86 | 610.2561 | 0
6375 | 725.59 | 403.208 | 29.1 | 80.4445 | 80.4445 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 24.5296 | 645.1455 | 0 | 0.05921 | 4.3047 | 0 | 0 | 124.5494 | 80.4445 | off_peak | 645.1455 |  |  | 11.09 | 0 | 88.91 | 346.289 | 0
6376 | 724.57 | 405.515 | 28.9 | 80.9639 | 80.9639 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 24.5296 | 643.6061 | 0 | 0.05921 | 4.4767 | 0 | 0 | 124.5494 | 80.9639 | off_peak | 643.6061 |  |  | 11.17 | 0 | 88.83 | 362.4541 | 0
6377 | 724.43 | 206.913 | 28.7 | 41.3418 | 41.3418 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 24.5296 | 683.0882 | 0 | 0.05921 | 4.7605 | 0 | 0 | 124.5494 | 41.3418 | off_peak | 683.0882 |  |  | 5.71 | 0 | 94.29 | 196.8076 | 0
6378 | 658.68 | 69.2001 | 28.2 | 13.8516 | 13.8516 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 24.5296 | 644.8284 | 0 | 0.05921 | 5.2466 | 0 | 0 | 124.5494 | 13.8516 | off_peak | 644.8284 |  |  | 2.1 | 0 | 97.9 | 72.6738 | 0
6379 | 626.34 | 0 | 28 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 24.5296 | 626.34 | 0 | 0.05921 | 5.7282 | 0 | 0 | 124.5494 | 0 | off_peak | 626.34 |  |  | 0 | 0 | 100 | 0 | 0
6380 | 626.63 | 0 | 27.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 24.5296 | 626.63 | 0 | 0.05921 | 6.1698 | 0 | 0 | 124.5494 | 0 | off_peak | 626.63 |  |  | 0 | 0 | 100 | 0 | 0
6381 | 608.47 | 0 | 27.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 24.5296 | 608.47 | 0 | 0.05921 | 6.4444 | 0 | 0 | 124.5494 | 0 | off_peak | 608.47 |  |  | 0 | 0 | 100 | 0 | 0
6382 | 615.7 | 0 | 27.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 24.5296 | 615.7 | 0 | 0.05921 | 6.7023 | 0 | 0 | 124.5494 | 0 | off_peak | 615.7 |  |  | 0 | 0 | 100 | 0 | 0
6383 | 592.34 | 0 | 27.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 24.5296 | 592.34 | 0 | 0.05921 | 6.8226 | 0 | 0 | 124.5494 | 0 | off_peak | 592.34 |  |  | 0 | 0 | 100 | 0 | 0
6384 | 621.64 | 0 | 27.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 24.5296 | 621.64 | 0 | 0.05921 | 7.0322 | 0 | 0 | 124.5494 | 0 | off_peak | 621.64 |  |  | 0 | 0 | 100 | 0 | 0
6385 | 602.26 | 0 | 27.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 24.5296 | 602.26 | 0 | 0.05921 | 7.0536 | 0 | 0 | 124.5494 | 0 | off_peak | 602.26 |  |  | 0 | 0 | 100 | 0 | 0
6386 | 598.94 | 0 | 27.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 24.5296 | 598.94 | 0 | 0.05921 | 6.8208 | 0 | 0 | 124.5494 | 0 | off_peak | 598.94 |  |  | 0 | 0 | 100 | 0 | 0
6387 | 626.06 | 0 | 27.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 24.5296 | 626.06 | 0 | 0.05921 | 6.3944 | 0 | 0 | 124.5494 | 0 | off_peak | 626.06 |  |  | 0 | 0 | 100 | 0 | 0
6388 | 625.53 | 0 | 27.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 24.5296 | 625.53 | 0 | 0.05921 | 5.9223 | 0 | 0 | 124.5494 | 0 | off_peak | 625.53 |  |  | 0 | 0 | 100 | 0 | 0
6389 | 638.2 | 0 | 27.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 24.5296 | 638.2 | 0 | 0.05921 | 5.3155 | 0 | 0 | 124.5494 | 0 | off_peak | 638.2 |  |  | 0 | 0 | 100 | 0 | 0
6390 | 690.11 | 0 | 27.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 24.5296 | 690.11 | 0 | 0.05921 | 4.7991 | 0 | 0 | 124.5494 | 0 | off_peak | 690.11 |  |  | 0 | 0 | 100 | 0 | 0
6391 | 671.39 | 28.6557 | 27.5 | 5.7506 | 0 | 0 | 5.7506 | 12.3989 | 6.6484 | 0 | 0 | 0 | 36.1277 | 678.0384 | 0 | 0.05921 | 4.328 | 0 | 0 | 129.9285 | 0 | off_peak | 671.39 | 46.38 | 53.62 | 0 | 0 | 100 | 0 | 0
6392 | 733.06 | 212.73 | 28 | 42.6126 | 42.6126 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 36.1277 | 690.4474 | 0 | 0.05921 | 4.0122 | 0 | 0 | 129.9285 | 42.6126 | off_peak | 690.4474 |  |  | 5.81 | 0 | 94.19 | 170.9714 | 0
6393 | 743.93 | 422.136 | 28.4 | 84.4362 | 84.4362 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 36.1277 | 659.4938 | 0 | 0.05921 | 3.7863 | 0 | 0 | 129.9285 | 84.4362 | off_peak | 659.4938 |  |  | 11.35 | 0 | 88.65 | 319.7037 | 0
6394 | 722.06 | 609.028 | 28.8 | 121.641 | 121.641 | 0 | 0 | 9.9966 | 9.9966 | 0 | 0 | 0 | 45.4787 | 610.4156 | 0 | 0.05921 | 3.6511 | 0 | 0 | 129.9285 | 121.641 | off_peak | 600.419 | 0 | 100 | 16.85 | 0 | 83.15 | 444.1208 | 0
6395 | 719.04 | 755.694 | 29.1 | 150.7693 | 150.7693 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 45.4787 | 568.2707 | 0 | 0.05921 | 3.5738 | 0 | 0 | 129.9285 | 150.7693 | off_peak | 568.2707 |  |  | 20.97 | 0 | 79.03 | 538.8142 | 0
6396 | 746.68 | 837.144 | 29.3 | 166.8975 | 166.8975 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 45.4787 | 579.7825 | 0 | 0.05921 | 3.6312 | 0 | 0 | 129.9285 | 166.8975 | off_peak | 579.7825 |  |  | 22.35 | 0 | 77.65 | 606.037 | 0
6397 | 724.74 | 428.346 | 29.4 | 85.3661 | 85.3661 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 45.4787 | 639.3739 | 0 | 0.05921 | 3.7998 | 0 | 0 | 129.9285 | 85.3661 | off_peak | 639.3739 |  |  | 11.78 | 0 | 88.22 | 324.3783 | 0
6398 | 697.96 | 548.926 | 29.4 | 109.3968 | 109.3968 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 45.4787 | 588.5632 | 0 | 0.05921 | 3.9576 | 0 | 0 | 129.9285 | 109.3968 | off_peak | 588.5632 |  |  | 15.67 | 0 | 84.33 | 432.9505 | 0
6399 | 708.86 | 242.001 | 29.2 | 48.2642 | 48.2642 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 45.4787 | 660.5958 | 0 | 0.05921 | 4.1992 | 0 | 0 | 129.9285 | 48.2642 | off_peak | 660.5958 |  |  | 6.81 | 0 | 93.19 | 202.6711 | 0
6400 | 704.38 | 65.55 | 29 | 13.0827 | 13.0827 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 45.4787 | 691.2973 | 0 | 0.05921 | 4.5873 | 0 | 0 | 129.9285 | 13.0827 | off_peak | 691.2973 |  |  | 1.86 | 0 | 98.14 | 60.0147 | 0
6401 | 696.78 | 269.138 | 28.6 | 53.7941 | 53.7941 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 45.4787 | 642.9859 | 0 | 0.05921 | 4.9715 | 0 | 0 | 129.9285 | 53.7941 | off_peak | 642.9859 |  |  | 7.72 | 0 | 92.28 | 267.4395 | 0
6402 | 664.78 | 71.8306 | 28 | 14.3886 | 1.9897 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 0 | 57.0769 | 662.7903 | 0 | 0.05921 | 5.4755 | 0 | 0 | 141.5267 | 1.9897 | off_peak | 662.7903 | 100 | 0 | 0.3 | 0 | 99.7 | 10.8943 | 0
6403 | 578.58 | 0 | 27.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 57.0769 | 578.58 | 0 | 0.05921 | 6.1642 | 0 | 0 | 141.5267 | 0 | off_peak | 578.58 |  |  | 0 | 0 | 100 | 0 | 0
6404 | 600.9 | 0 | 27.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 57.0769 | 600.9 | 0 | 0.05921 | 6.6987 | 0 | 0 | 141.5267 | 0 | off_peak | 600.9 |  |  | 0 | 0 | 100 | 0 | 0
6405 | 585.45 | 0 | 27.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 57.0769 | 585.45 | 0 | 0.05921 | 6.9964 | 0 | 0 | 141.5267 | 0 | off_peak | 585.45 |  |  | 0 | 0 | 100 | 0 | 0
6406 | 601.63 | 0 | 27.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 57.0769 | 601.63 | 0 | 0.05921 | 7.2637 | 0 | 0 | 141.5267 | 0 | off_peak | 601.63 |  |  | 0 | 0 | 100 | 0 | 0
6407 | 604.71 | 0 | 27.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 57.0769 | 604.71 | 0 | 0.05921 | 7.5184 | 0 | 0 | 141.5267 | 0 | off_peak | 604.71 |  |  | 0 | 0 | 100 | 0 | 0
6408 | 572.94 | 0 | 27 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 57.0769 | 572.94 | 0 | 0.05921 | 7.4949 | 0 | 0 | 141.5267 | 0 | off_peak | 572.94 |  |  | 0 | 0 | 100 | 0 | 0
6409 | 619.56 | 0 | 26.9 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 68.675 | 631.9589 | 0 | 0.05921 | 7.3741 | 0 | 0 | 141.5267 | 0 | off_peak | 619.56 | 0 | 100 | 0 | 0 | 100 | 0 | 0
6410 | 610.13 | 0 | 26.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 68.675 | 610.13 | 0 | 0.05921 | 7.1586 | 0 | 0 | 141.5267 | 0 | off_peak | 610.13 |  |  | 0 | 0 | 100 | 0 | 0
6411 | 553.13 | 0 | 26.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 68.675 | 553.13 | 0 | 0.05921 | 6.6908 | 0 | 0 | 141.5267 | 0 | off_peak | 553.13 |  |  | 0 | 0 | 100 | 0 | 0
6412 | 596.96 | 0 | 26.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 68.675 | 596.96 | 0 | 0.05921 | 6.07 | 0 | 0 | 141.5267 | 0 | off_peak | 596.96 |  |  | 0 | 0 | 100 | 0 | 0
6413 | 599.94 | 0 | 26.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 68.675 | 599.94 | 0 | 0.05921 | 5.4576 | 0 | 0 | 141.5267 | 0 | off_peak | 599.94 |  |  | 0 | 0 | 100 | 0 | 0
6414 | 683.44 | 0 | 26.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 68.675 | 683.44 | 0 | 0.05921 | 4.8138 | 0 | 0 | 141.5267 | 0 | off_peak | 683.44 |  |  | 0 | 0 | 100 | 0 | 0
6415 | 721.35 | 28.4243 | 26.8 | 5.7186 | 0 | 0 | 5.7186 | 5.7186 | 0 | 0 | 0 | 0 | 74.0243 | 721.35 | 0 | 0.05921 | 4.1503 | 0 | 0 | 146.876 | 0 | off_peak | 721.35 | 100 | 0 | 0 | 0 | 100 | 0 | 0
6416 | 803.02 | 212.939 | 27.4 | 42.7476 | 42.7476 | 0 | 0 | 0.36934 | 0.36934 | 0 | 0 | 0 | 74.3698 | 760.6418 | 0 | 0.05921 | 3.7821 | 0 | 0 | 146.876 | 42.7476 | off_peak | 760.2724 | 0 | 100 | 5.32 | 0 | 94.68 | 161.6738 | 0
6417 | 788.5 | 422.344 | 27.8 | 84.6626 | 84.6626 | 0 | 0 | 0.023854 | 0.023854 | 0 | 0 | 0 | 74.3921 | 703.8613 | 0 | 0.05921 | 3.5913 | 0 | 0 | 146.876 | 84.6626 | off_peak | 703.8374 | 0 | 100 | 10.74 | 0 | 89.26 | 304.0471 | 0
6418 | 800.32 | 608.434 | 28.2 | 121.7885 | 121.7885 | 0 | 0 | 0.0015406 | 0.0015406 | 0 | 0 | 0 | 74.3935 | 678.533 | 0 | 0.05921 | 3.5528 | 0 | 0 | 146.876 | 121.7885 | off_peak | 678.5315 | 0 | 100 | 15.22 | 0 | 84.78 | 432.6915 | 0
6419 | 809.85 | 748.334 | 28.6 | 149.5737 | 149.5737 | 0 | 0 | 9.9503e-05 | 9.9503e-05 | 0 | 0 | 0 | 74.3936 | 660.2764 | 0 | 0.05921 | 3.7344 | 0 | 0 | 146.876 | 149.5737 | off_peak | 660.2763 | 0 | 100 | 18.47 | 0 | 81.53 | 558.5697 | 0
6420 | 835.2 | 629.776 | 28.9 | 125.7391 | 125.7391 | 0 | 0 | 6.4265e-06 | 6.4265e-06 | 0 | 0 | 0 | 74.3936 | 709.4609 | 0 | 0.05921 | 4.0928 | 0 | 0 | 146.876 | 125.7391 | off_peak | 709.4609 | 0 | 100 | 15.05 | 0 | 84.95 | 514.6277 | 0
6421 | 819.74 | 782.907 | 29.1 | 156.1986 | 156.1986 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 663.5414 | 0 | 0.088511 | 4.3832 | 0 | 0 | 146.876 | 156.1986 | on_peak | 663.5414 |  |  | 19.05 | 0 | 80.95 | 684.6467 | 0
6422 | 847.14 | 525.027 | 29.2 | 104.7104 | 104.7104 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 742.4296 | 0 | 0.088511 | 4.5507 | 0 | 0 | 146.876 | 104.7104 | on_peak | 742.4296 |  |  | 12.36 | 0 | 87.64 | 476.5014 | 0
6423 | 831.02 | 349.603 | 29.1 | 69.7497 | 69.7497 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 761.2703 | 0 | 0.088511 | 4.7625 | 0 | 0 | 146.876 | 69.7497 | on_peak | 761.2703 |  |  | 8.39 | 0 | 91.61 | 332.1833 | 0
6424 | 857.7 | 412.489 | 28.9 | 82.3563 | 82.3563 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 775.3437 | 0 | 0.088511 | 5.1765 | 0 | 0 | 146.876 | 82.3563 | on_peak | 775.3437 |  |  | 9.6 | 0 | 90.4 | 426.3189 | 0
6425 | 816.17 | 217.126 | 28.5 | 43.414 | 43.414 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 772.756 | 0 | 0.088511 | 5.6337 | 0 | 0 | 146.876 | 43.414 | on_peak | 772.756 |  |  | 5.32 | 0 | 94.68 | 244.5812 | 0
6426 | 829.11 | 63.952 | 27.9 | 12.8151 | 12.8151 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 816.2949 | 0 | 0.088511 | 6.3077 | 0 | 0 | 146.876 | 12.8151 | on_peak | 816.2949 |  |  | 1.55 | 0 | 98.45 | 80.8332 | 0
6427 | 781.91 | 0 | 27.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 781.91 | 0 | 0.088511 | 6.9536 | 0 | 0 | 146.876 | 0 | on_peak | 781.91 |  |  | 0 | 0 | 100 | 0 | 0
6428 | 803.42 | 0 | 27.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 803.42 | 0 | 0.088511 | 7.3444 | 0 | 0 | 146.876 | 0 | on_peak | 803.42 |  |  | 0 | 0 | 100 | 0 | 0
6429 | 843.28 | 0 | 27.2 | 0 | 0 | 0 | 0 | 0 | 0 | 62.63 | 62.63 | 0 | 7.4394 | 780.65 | 0 | 0.088511 | 7.8135 | 0 | 0 | 146.876 | 0 | on_peak | 780.65 |  |  | 0 | 7.43 | 92.57 | 0 | 0
6430 | 770.12 | 0 | 27.1 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 19.0375 | 782.5189 | 0 | 0.05921 | 7.9483 | 0 | 0 | 146.876 | 0 | off_peak | 770.12 | 0 | 100 | 0 | 0 | 100 | 0 | 0
6431 | 787.95 | 0 | 27 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 30.6357 | 800.3489 | 0 | 0.05921 | 7.7509 | 0 | 0 | 146.876 | 0 | off_peak | 787.95 | 0 | 100 | 0 | 0 | 100 | 0 | 0
6432 | 786.53 | 0 | 27 | 0 | 0 | 0 | 0 | 8.7263 | 8.7263 | 0 | 0 | 0 | 38.7984 | 795.2563 | 0 | 0.05921 | 7.5939 | 0 | 0 | 146.876 | 0 | off_peak | 786.53 | 0 | 100 | 0 | 0 | 100 | 0 | 0
6433 | 727.84 | 0 | 26.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 38.7984 | 727.84 | 0 | 0.05921 | 7.5105 | 0 | 0 | 146.876 | 0 | off_peak | 727.84 |  |  | 0 | 0 | 100 | 0 | 0
6434 | 684.15 | 0 | 26.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 38.7984 | 684.15 | 0 | 0.05921 | 7.2218 | 0 | 0 | 146.876 | 0 | off_peak | 684.15 |  |  | 0 | 0 | 100 | 0 | 0
6435 | 636.03 | 0 | 26.9 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 50.3966 | 648.4289 | 0 | 0.05921 | 6.7156 | 0 | 0 | 146.876 | 0 | off_peak | 636.03 | 0 | 100 | 0 | 0 | 100 | 0 | 0
6436 | 642.2 | 0 | 26.9 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 61.9947 | 654.5989 | 0 | 0.05921 | 6.1128 | 0 | 0 | 146.876 | 0 | off_peak | 642.2 | 0 | 100 | 0 | 0 | 100 | 0 | 0
6437 | 666.73 | 0 | 26.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 61.9947 | 666.73 | 0 | 0.05921 | 5.4288 | 0 | 0 | 146.876 | 0 | off_peak | 666.73 |  |  | 0 | 0 | 100 | 0 | 0
6438 | 711.62 | 0 | 27 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 61.9947 | 711.62 | 0 | 0.05921 | 4.9045 | 0 | 0 | 146.876 | 0 | off_peak | 711.62 |  |  | 0 | 0 | 100 | 0 | 0
6439 | 794.09 | 12.35 | 27.4 | 2.4793 | 0 | 0 | 2.4793 | 12.3989 | 9.9197 | 0 | 0 | 0 | 73.5928 | 804.0097 | 0 | 0.05921 | 4.5066 | 0 | 0 | 149.1951 | 0 | off_peak | 794.09 | 20 | 80 | 0 | 0 | 100 | 0 | 0
6440 | 852.98 | 58.4982 | 28 | 11.7179 | 10.9172 | 0 | 0.80079 | 0.80079 | 0 | 0 | 0 | 0 | 74.3419 | 842.0628 | 0 | 0.05921 | 4.2446 | 0 | 0 | 149.9442 | 10.9172 | off_peak | 842.0628 | 100 | 0 | 1.28 | 0 | 98.72 | 46.3387 | 0
6441 | 906.27 | 58.9 | 28.4 | 11.7813 | 11.7813 | 0 | 0 | 0 | 0 | 1.3543 | 1.3543 | 0 | 72.8941 | 893.1344 | 0 | 0.05921 | 4.0762 | 0 | 0 | 149.9442 | 11.7813 | off_peak | 893.1344 |  |  | 1.3 | 0.15 | 98.55 | 48.0232 | 0
6442 | 892.3 | 611.084 | 28.8 | 122.0517 | 122.0517 | 0 | 0 | 1.4996 | 1.4996 | 0 | 0 | 0 | 74.2968 | 771.7479 | 0 | 0.05921 | 4.0456 | 0 | 0 | 149.9442 | 122.0517 | off_peak | 770.2483 | 0 | 100 | 13.68 | 0 | 86.32 | 493.7724 | 0
6443 | 842.39 | 623.244 | 29.1 | 124.3441 | 124.3441 | 0 | 0 | 0.09685 | 0.09685 | 0 | 0 | 0 | 74.3874 | 718.1428 | 0 | 0.05921 | 4.3061 | 0 | 0 | 149.9442 | 124.3441 | off_peak | 718.0459 | 0 | 100 | 14.76 | 0 | 85.24 | 535.4398 | 0
6444 | 971.02 | 725.366 | 29.3 | 144.6128 | 144.6128 | 0 | 0 | 0.0062551 | 0.0062551 | 0 | 0 | 0 | 74.3932 | 826.4134 | 0 | 0.05921 | 4.7811 | 0 | 0 | 149.9442 | 144.6128 | off_peak | 826.4072 | 0 | 100 | 14.89 | 0 | 85.11 | 691.4154 | 0
6445 | 873.71 | 669.729 | 29.5 | 133.4231 | 133.4231 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3932 | 740.2869 | 0 | 0.088511 | 5.0421 | 0 | 0 | 149.9442 | 133.4231 | on_peak | 740.2869 |  |  | 15.27 | 0 | 84.73 | 672.7268 | 0
6446 | 895.8 | 599.733 | 29.5 | 119.4785 | 119.4785 | 0 | 0 | 0 | 0 | 62.6296 | 62.6296 | 0 | 7.4394 | 713.6919 | 0 | 0.088511 | 5.2312 | 0 | 0 | 149.9442 | 119.4785 | on_peak | 713.6919 |  |  | 13.34 | 6.99 | 79.67 | 625.0169 | 0
6447 | 863.35 | 636.302 | 29.5 | 126.7638 | 126.7638 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 736.5862 | 0 | 0.088511 | 5.4895 | 0 | 0 | 149.9442 | 126.7638 | on_peak | 736.5862 |  |  | 14.68 | 0 | 85.32 | 695.8739 | 0
6448 | 806.76 | 461.775 | 29.3 | 92.0619 | 92.0619 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 714.6981 | 0 | 0.088511 | 5.9823 | 0 | 0 | 149.9442 | 92.0619 | on_peak | 714.6981 |  |  | 11.41 | 0 | 88.59 | 550.7459 | 0
6449 | 808.72 | 300.82 | 29 | 60.0389 | 60.0389 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 748.6811 | 0 | 0.088511 | 6.3898 | 0 | 0 | 149.9442 | 60.0389 | on_peak | 748.6811 |  |  | 7.42 | 0 | 92.58 | 383.6369 | 0
6450 | 815.83 | 95.5688 | 28.5 | 19.1088 | 19.1088 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 796.7212 | 0 | 0.088511 | 6.6151 | 0 | 0 | 149.9442 | 19.1088 | on_peak | 796.7212 |  |  | 2.34 | 0 | 97.66 | 126.4067 | 0
6451 | 828.97 | 0 | 28.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 828.97 | 0 | 0.088511 | 6.7528 | 0 | 0 | 149.9442 | 0 | on_peak | 828.97 |  |  | 0 | 0 | 100 | 0 | 0
6452 | 811.55 | 0 | 28 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 811.55 | 0 | 0.088511 | 6.8424 | 0 | 0 | 149.9442 | 0 | on_peak | 811.55 |  |  | 0 | 0 | 100 | 0 | 0
6453 | 791.59 | 0 | 27.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 791.59 | 0 | 0.088511 | 7.1487 | 0 | 0 | 149.9442 | 0 | on_peak | 791.59 |  |  | 0 | 0 | 100 | 0 | 0
6454 | 777.27 | 0 | 27.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 777.27 | 0 | 0.05921 | 7.563 | 0 | 0 | 149.9442 | 0 | off_peak | 777.27 |  |  | 0 | 0 | 100 | 0 | 0
6455 | 772.52 | 0 | 27.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 772.52 | 0 | 0.05921 | 7.6305 | 0 | 0 | 149.9442 | 0 | off_peak | 772.52 |  |  | 0 | 0 | 100 | 0 | 0
6456 | 780.54 | 0 | 27.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 780.54 | 0 | 0.05921 | 7.5293 | 0 | 0 | 149.9442 | 0 | off_peak | 780.54 |  |  | 0 | 0 | 100 | 0 | 0
6457 | 711.66 | 0 | 27.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 711.66 | 0 | 0.05921 | 7.5065 | 0 | 0 | 149.9442 | 0 | off_peak | 711.66 |  |  | 0 | 0 | 100 | 0 | 0
6458 | 654.33 | 0 | 27.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 654.33 | 0 | 0.05921 | 7.153 | 0 | 0 | 149.9442 | 0 | off_peak | 654.33 |  |  | 0 | 0 | 100 | 0 | 0
6459 | 633.33 | 0 | 27 | 0 | 0 | 0 | 0 | 8.7263 | 8.7263 | 0 | 0 | 0 | 15.6021 | 642.0563 | 0 | 0.05921 | 6.6863 | 0 | 0 | 149.9442 | 0 | off_peak | 633.33 | 0 | 100 | 0 | 0 | 100 | 0 | 0
6460 | 621.8 | 0 | 26.9 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 27.2003 | 634.1989 | 0 | 0.05921 | 5.9267 | 0 | 0 | 149.9442 | 0 | off_peak | 621.8 | 0 | 100 | 0 | 0 | 100 | 0 | 0
6461 | 675.46 | 0 | 27 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 38.7984 | 687.8589 | 0 | 0.05921 | 14.316 | 0 | 0 | 149.9442 | 0 | off_peak | 675.46 | 0 | 100 | 0 | 0 | 100 | 0 | 0
6462 | 706.27 | 0 | 27.1 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 50.3966 | 718.6689 | 0 | 0.05921 | 4.7305 | 0 | 0 | 149.9442 | 0 | off_peak | 706.27 | 0 | 100 | 0 | 0 | 100 | 0 | 0
6463 | 796.25 | 20.7669 | 27.4 | 4.169 | 0 | 0 | 4.169 | 12.3989 | 8.23 | 0 | 0 | 0 | 61.9947 | 804.48 | 0 | 0.05921 | 4.382 | 0 | 0 | 153.8439 | 0 | off_peak | 796.25 | 33.62 | 66.38 | 0 | 0 | 100 | 0 | 0
6464 | 817.18 | 94.1964 | 27.9 | 18.8756 | 6.4767 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 0 | 73.5928 | 810.7033 | 0 | 0.05921 | 4.1442 | 0 | 0 | 165.442 | 6.4767 | off_peak | 810.7033 | 100 | 0 | 0.79 | 0 | 99.21 | 26.8408 | 0
6465 | 798.22 | 201.263 | 28.3 | 40.2716 | 40.2716 | 0 | 0 | 0.80079 | 0.80079 | 0 | 0 | 0 | 74.3419 | 758.7492 | 0 | 0.05921 | 4.0219 | 0 | 0 | 165.442 | 40.2716 | off_peak | 757.9484 | 0 | 100 | 5.05 | 0 | 94.95 | 161.9694 | 0
6466 | 831.18 | 457.926 | 28.6 | 91.5282 | 91.5282 | 0 | 0 | 0.05172 | 0.05172 | 0 | 0 | 0 | 74.3903 | 739.7035 | 0 | 0.05921 | 4.0332 | 0 | 0 | 165.442 | 91.5282 | off_peak | 739.6518 | 0 | 100 | 11.01 | 0 | 88.99 | 369.1529 | 0
6467 | 832.63 | 190.373 | 28.9 | 38.0093 | 38.0093 | 0 | 0 | 0.0033404 | 0.0033404 | 0 | 0 | 0 | 74.3934 | 794.6241 | 0 | 0.05921 | 4.3183 | 0 | 0 | 165.442 | 38.0093 | off_peak | 794.6207 | 0 | 100 | 4.56 | 0 | 95.44 | 164.1372 | 0
6468 | 880.67 | 303.345 | 29.2 | 60.4986 | 60.4986 | 0 | 0 | 0.00021574 | 0.00021574 | 0 | 0 | 0 | 74.3936 | 820.1716 | 0 | 0.05921 | 4.763 | 0 | 0 | 165.442 | 60.4986 | off_peak | 820.1714 | 0 | 100 | 6.87 | 0 | 93.13 | 288.1565 | 0
6469 | 848.79 | 53.2 | 29.5 | 10.5985 | 10.5985 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 838.1915 | 0 | 0.088511 | 5.1457 | 0 | 0 | 165.442 | 10.5985 | on_peak | 838.1915 |  |  | 1.25 | 0 | 98.75 | 54.5366 | 0
6470 | 875.3 | 486.563 | 29.6 | 96.8974 | 96.8974 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 778.4026 | 0 | 0.088511 | 5.3121 | 0 | 0 | 165.442 | 96.8974 | on_peak | 778.4026 |  |  | 11.07 | 0 | 88.93 | 514.7291 | 0
6471 | 928.27 | 228.083 | 29.7 | 45.4053 | 45.4053 | 0 | 0 | 0 | 0 | 34.3514 | 34.3514 | 0 | 37.6704 | 848.5132 | 0 | 0.088511 | 5.4675 | 0 | 0 | 165.442 | 45.4053 | on_peak | 848.5132 |  |  | 4.89 | 3.7 | 91.41 | 248.2557 | 0
6472 | 836.62 | 413.092 | 29.6 | 82.2659 | 82.2659 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 37.6704 | 754.3541 | 0 | 0.088511 | 5.6428 | 0 | 0 | 165.442 | 82.2659 | on_peak | 754.3541 |  |  | 9.83 | 0 | 90.17 | 464.2086 | 0
6473 | 840.53 | 5.7 | 29.3 | 1.1364 | 1.1364 | 0 | 0 | 0 | 0 | 25.7618 | 25.7618 | 0 | 10.1299 | 813.6318 | 0 | 0.088511 | 5.8594 | 0 | 0 | 165.442 | 1.1364 | on_peak | 813.6318 |  |  | 0.14 | 3.06 | 96.8 | 6.6585 | 0
6474 | 840.13 | 45.8858 | 28.7 | 9.1681 | 9.1681 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1299 | 830.9619 | 0 | 0.088511 | 6.0921 | 0 | 0 | 165.442 | 9.1681 | on_peak | 830.9619 |  |  | 1.09 | 0 | 98.91 | 55.853 | 0
6475 | 812.39 | 0 | 28.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1299 | 812.39 | 0 | 0.088511 | 6.2664 | 0 | 0 | 165.442 | 0 | on_peak | 812.39 |  |  | 0 | 0 | 100 | 0 | 0
6476 | 851.03 | 0 | 27.7 | 0 | 0 | 0 | 0 | 0 | 0 | 2.5168 | 2.5168 | 0 | 7.4394 | 848.5132 | 0 | 0.088511 | 6.5455 | 0 | 0 | 165.442 | 0 | on_peak | 848.5132 |  |  | 0 | 0.3 | 99.7 | 0 | 0
6477 | 808.35 | 0 | 27.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 808.35 | 0 | 0.088511 | 6.8197 | 0 | 0 | 165.442 | 0 | on_peak | 808.35 |  |  | 0 | 0 | 100 | 0 | 0
6478 | 784.28 | 0 | 27.2 | 0 | 0 | 0 | 0 | 8.7263 | 8.7263 | 0 | 0 | 0 | 15.6021 | 793.0063 | 0 | 0.05921 | 7.0504 | 0 | 0 | 165.442 | 0 | off_peak | 784.28 | 0 | 100 | 0 | 0 | 100 | 0 | 0
6479 | 806.33 | 0 | 27.1 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 27.2003 | 818.7289 | 0 | 0.05921 | 7.1789 | 0 | 0 | 165.442 | 0 | off_peak | 806.33 | 0 | 100 | 0 | 0 | 100 | 0 | 0
6480 | 784.74 | 0 | 27.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27.2003 | 784.74 | 0 | 0.05921 | 7.2032 | 0 | 0 | 165.442 | 0 | off_peak | 784.74 |  |  | 0 | 0 | 100 | 0 | 0
6481 | 750.53 | 0 | 27.1 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 38.7984 | 762.9289 | 0 | 0.05921 | 7.2427 | 0 | 0 | 165.442 | 0 | off_peak | 750.53 | 0 | 100 | 0 | 0 | 100 | 0 | 0
6482 | 683.56 | 0 | 27.1 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 50.3966 | 695.9589 | 0 | 0.05921 | 6.9787 | 0 | 0 | 165.442 | 0 | off_peak | 683.56 | 0 | 100 | 0 | 0 | 100 | 0 | 0
6483 | 655.03 | 0 | 27.1 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 61.9947 | 667.4289 | 0 | 0.05921 | 6.4099 | 0 | 0 | 165.442 | 0 | off_peak | 655.03 | 0 | 100 | 0 | 0 | 100 | 0 | 0
6484 | 658.58 | 0 | 27.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 61.9947 | 658.58 | 0 | 0.05921 | 5.889 | 0 | 0 | 165.442 | 0 | off_peak | 658.58 |  |  | 0 | 0 | 100 | 0 | 0
6485 | 675.2 | 0 | 27.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 61.9947 | 675.2 | 0 | 0.05921 | 5.2228 | 0 | 0 | 165.442 | 0 | off_peak | 675.2 |  |  | 0 | 0 | 100 | 0 | 0
6486 | 722.25 | 0 | 27.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 61.9947 | 722.25 | 0 | 0.05921 | 4.688 | 0 | 0 | 165.442 | 0 | off_peak | 722.25 |  |  | 0 | 0 | 100 | 0 | 0
6487 | 795.98 | 25.6724 | 27.5 | 5.1519 | 0 | 0 | 5.1519 | 12.3989 | 7.2471 | 0 | 0 | 0 | 73.5928 | 803.2271 | 0 | 0.05921 | 4.2898 | 0 | 0 | 170.2612 | 0 | off_peak | 795.98 | 41.55 | 58.45 | 0 | 0 | 100 | 0 | 0
6488 | 842.47 | 209.313 | 27.9 | 41.9434 | 41.9434 | 0 | 0 | 0.80079 | 0.80079 | 0 | 0 | 0 | 74.3419 | 801.3274 | 0 | 0.05921 | 4.0431 | 0 | 0 | 170.2612 | 41.9434 | off_peak | 800.5266 | 0 | 100 | 4.98 | 0 | 95.02 | 169.5794 | 0
6489 | 842.16 | 417.104 | 28.2 | 83.4905 | 83.4388 | 0 | 0.05172 | 0.05172 | 0 | 0 | 0 | 0 | 74.3903 | 758.7212 | 0 | 0.05921 | 3.8913 | 0 | 0 | 170.3096 | 83.4388 | off_peak | 758.7212 | 100 | 0 | 9.91 | 0 | 90.09 | 324.6879 | 0
6490 | 878.87 | 601.653 | 28.6 | 120.2558 | 120.2558 | 0 | 0 | 0.0033404 | 0.0033404 | 0 | 0 | 0 | 74.3934 | 758.6176 | 0 | 0.05921 | 3.8739 | 0 | 0 | 170.3096 | 120.2558 | off_peak | 758.6142 | 0 | 100 | 13.68 | 0 | 86.32 | 465.8598 | 0
6491 | 831.83 | 732.122 | 28.8 | 146.2266 | 146.2266 | 0 | 0 | 0.00021574 | 0.00021574 | 0 | 0 | 0 | 74.3936 | 685.6036 | 0 | 0.05921 | 4.1676 | 0 | 0 | 170.3096 | 146.2266 | off_peak | 685.6034 | 0 | 100 | 17.58 | 0 | 82.42 | 609.4081 | 0
6492 | 878.3 | 167.2 | 29 | 33.3704 | 33.3704 | 0 | 0 | 1.3934e-05 | 1.3934e-05 | 0 | 0 | 0 | 74.3936 | 844.9296 | 0 | 0.05921 | 4.6323 | 0 | 0 | 170.3096 | 33.3704 | off_peak | 844.9296 | 0 | 100 | 3.8 | 0 | 96.2 | 154.5836 | 0
6493 | 831.28 | 760.278 | 29.1 | 151.6839 | 151.6839 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 679.5961 | 0 | 0.088511 | 4.9056 | 0 | 0 | 170.3096 | 151.6839 | on_peak | 679.5961 |  |  | 18.25 | 0 | 81.75 | 744.0951 | 0
6494 | 867.41 | 714.219 | 29.2 | 142.4426 | 142.4426 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 724.9674 | 0 | 0.088511 | 4.9959 | 0 | 0 | 170.3096 | 142.4426 | on_peak | 724.9674 |  |  | 16.42 | 0 | 83.58 | 711.6338 | 0
6495 | 842.67 | 657.909 | 29.2 | 131.2122 | 131.2122 | 0 | 0 | 0 | 0 | 62.63 | 62.63 | 0 | 7.4394 | 648.8278 | 0 | 0.088511 | 5.1748 | 62.63 | 0 | 103.3553 | 193.8422 | on_peak | 648.8278 |  |  | 15.57 | 7.43 | 77 | 1003.0953 | 0
6496 | 837.19 | 490.113 | 29.1 | 97.783 | 97.783 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 739.407 | 0 | 0.088511 | 5.3749 | 0 | 0 | 103.3553 | 97.783 | on_peak | 739.407 |  |  | 11.68 | 0 | 88.32 | 525.5699 | 0
6497 | 828.1 | 222.374 | 28.8 | 44.4147 | 44.4147 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 783.6853 | 0 | 0.088511 | 5.7908 | 0 | 0 | 103.3553 | 44.4147 | on_peak | 783.6853 |  |  | 5.36 | 0 | 94.64 | 257.1973 | 0
6498 | 853.83 | 31.4889 | 28.3 | 6.3007 | 6.3007 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 847.5293 | 0 | 0.088511 | 6.161 | 0 | 0 | 103.3553 | 6.3007 | on_peak | 847.5293 |  |  | 0.74 | 0 | 99.26 | 38.8187 | 0
6499 | 839.84 | 0 | 28.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 839.84 | 0 | 0.088511 | 6.5571 | 0 | 0 | 103.3553 | 0 | on_peak | 839.84 |  |  | 0 | 0 | 100 | 0 | 0
6500 | 824.51 | 0 | 27.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 824.51 | 0 | 0.088511 | 6.9346 | 0 | 0 | 103.3553 | 0 | on_peak | 824.51 |  |  | 0 | 0 | 100 | 0 | 0
6501 | 821.68 | 0 | 27.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 821.68 | 0 | 0.088511 | 7.2601 | 0 | 0 | 103.3553 | 0 | on_peak | 821.68 |  |  | 0 | 0 | 100 | 0 | 0
6502 | 804.52 | 0 | 27.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 804.52 | 0 | 0.05921 | 7.5411 | 0 | 0 | 103.3553 | 0 | off_peak | 804.52 |  |  | 0 | 0 | 100 | 0 | 0
6503 | 810.15 | 0 | 27.5 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 19.0375 | 822.5489 | 0 | 0.05921 | 7.6651 | 0 | 0 | 103.3553 | 0 | off_peak | 810.15 | 0 | 100 | 0 | 0 | 100 | 0 | 0
6504 | 805.8 | 0 | 27.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19.0375 | 805.8 | 0 | 0.05921 | 7.7164 | 0 | 0 | 103.3553 | 0 | off_peak | 805.8 |  |  | 0 | 0 | 100 | 0 | 0
6505 | 727.49 | 0 | 27.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19.0375 | 727.49 | 0 | 0.05921 | 7.73 | 0 | 0 | 103.3553 | 0 | off_peak | 727.49 |  |  | 0 | 0 | 100 | 0 | 0
6506 | 698.04 | 0 | 27.1 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 30.6357 | 710.4389 | 0 | 0.05921 | 7.2872 | 0 | 0 | 103.3553 | 0 | off_peak | 698.04 | 0 | 100 | 0 | 0 | 100 | 0 | 0
6507 | 679.21 | 0 | 27 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 42.2338 | 691.6089 | 0 | 0.05921 | 6.8351 | 0 | 0 | 103.3553 | 0 | off_peak | 679.21 | 0 | 100 | 0 | 0 | 100 | 0 | 0
6508 | 658.14 | 0 | 27 | 0 | 0 | 0 | 0 | 5.8657 | 5.8657 | 0 | 0 | 0 | 47.7206 | 664.0057 | 0 | 0.05921 | 6.2653 | 0 | 0 | 103.3553 | 0 | off_peak | 658.14 | 0 | 100 | 0 | 0 | 100 | 0 | 0
6509 | 707.21 | 0 | 27 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 59.3188 | 719.6089 | 0 | 0.05921 | 5.6284 | 0 | 0 | 103.3553 | 0 | off_peak | 707.21 | 0 | 100 | 0 | 0 | 100 | 0 | 0
6510 | 705.45 | 0 | 27 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 59.3188 | 705.45 | 0 | 0.05921 | 5.0972 | 0 | 0 | 103.3553 | 0 | off_peak | 705.45 |  |  | 0 | 0 | 100 | 0 | 0
6511 | 814.35 | 14.25 | 27.4 | 2.8607 | 0 | 0 | 2.8607 | 2.8607 | 0 | 0 | 0 | 0 | 61.9947 | 814.35 | 0 | 0.05921 | 4.7392 | 0 | 0 | 106.0312 | 0 | off_peak | 814.35 | 100 | 0 | 0 | 0 | 100 | 0 | 0
6512 | 842.21 | 65.138 | 27.9 | 13.0527 | 13.0527 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 73.5928 | 841.5562 | 0 | 0.05921 | 4.5199 | 0 | 0 | 106.0312 | 13.0527 | off_peak | 829.1573 | 0 | 100 | 1.55 | 0 | 98.45 | 58.9969 | 0
6513 | 880.9 | 300.739 | 28.2 | 60.1981 | 60.1981 | 0 | 0 | 0.80079 | 0.80079 | 0 | 0 | 0 | 74.3419 | 821.5027 | 0 | 0.05921 | 4.3677 | 0 | 0 | 106.0312 | 60.1981 | off_peak | 820.7019 | 0 | 100 | 6.83 | 0 | 93.17 | 262.9243 | 0
6514 | 888.51 | 476.107 | 28.5 | 95.1969 | 95.1969 | 0 | 0 | 0.05172 | 0.05172 | 0 | 0 | 0 | 74.3903 | 793.3648 | 0 | 0.05921 | 4.357 | 0 | 0 | 106.0312 | 95.1969 | off_peak | 793.3131 | 0 | 100 | 10.71 | 0 | 89.29 | 414.7757 | 0
6515 | 849.66 | 726.44 | 28.8 | 145.0917 | 145.0884 | 0 | 0.0033404 | 0.0033404 | 0 | 0 | 0 | 0 | 74.3934 | 704.5716 | 0 | 0.05921 | 4.6063 | 0 | 0 | 106.0343 | 145.0884 | off_peak | 704.5716 | 100 | 0 | 17.08 | 0 | 82.92 | 668.3198 | 0
6516 | 872.33 | 702.785 | 29 | 140.2646 | 140.2646 | 0 | 0 | 0.00021574 | 0.00021574 | 0 | 0 | 0 | 74.3936 | 732.0656 | 0 | 0.05921 | 5.025 | 0 | 0 | 106.0343 | 140.2646 | off_peak | 732.0654 | 0 | 100 | 16.08 | 0 | 83.92 | 704.8269 | 0
6517 | 857.97 | 346.764 | 29.1 | 69.1833 | 69.1833 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 788.7867 | 0 | 0.088511 | 5.3346 | 0 | 0 | 106.0343 | 69.1833 | on_peak | 788.7867 |  |  | 8.06 | 0 | 91.94 | 369.0644 | 0
6518 | 855.48 | 77.9 | 29.1 | 15.5419 | 15.5419 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 839.9381 | 0 | 0.088511 | 5.4931 | 0 | 0 | 106.0343 | 15.5419 | on_peak | 839.9381 |  |  | 1.82 | 0 | 98.18 | 85.373 | 0
6519 | 867.81 | 323.57 | 29 | 64.5794 | 64.5794 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 803.2306 | 0 | 0.088511 | 5.6973 | 0 | 0 | 106.0343 | 64.5794 | on_peak | 803.2306 |  |  | 7.44 | 0 | 92.56 | 367.9279 | 0
6520 | 773.79 | 60.8 | 28.8 | 12.1436 | 12.1436 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 761.6464 | 0 | 0.088511 | 5.9231 | 0 | 0 | 106.0343 | 12.1436 | on_peak | 761.6464 |  |  | 1.57 | 0 | 98.43 | 71.927 | 0
6521 | 842.9 | 55.1 | 28.5 | 11.0172 | 11.0172 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 831.8828 | 0 | 0.088511 | 6.3358 | 0 | 0 | 106.0343 | 11.0172 | on_peak | 831.8828 |  |  | 1.31 | 0 | 98.69 | 69.8029 | 0
6522 | 813.57 | 38.95 | 28.1 | 7.7994 | 7.7994 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 805.7706 | 0 | 0.088511 | 6.6961 | 0 | 0 | 106.0343 | 7.7994 | on_peak | 805.7706 |  |  | 0.96 | 0 | 99.04 | 52.2252 | 0
6523 | 804.8 | 0 | 27.9 | 0 | 0 | 0 | 0 | 0 | 0 | 62.63 | 62.63 | 0 | 7.4394 | 742.17 | 0 | 0.088511 | 6.9954 | 0 | 0 | 106.0343 | 0 | on_peak | 742.17 |  |  | 0 | 7.78 | 92.22 | 0 | 0
6524 | 805.84 | 0 | 27.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 805.84 | 0 | 0.088511 | 7.2775 | 0 | 0 | 106.0343 | 0 | on_peak | 805.84 |  |  | 0 | 0 | 100 | 0 | 0
6525 | 811.45 | 0 | 27.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 811.45 | 0 | 0.088511 | 7.3151 | 0 | 0 | 106.0343 | 0 | on_peak | 811.45 |  |  | 0 | 0 | 100 | 0 | 0
6526 | 771.69 | 0 | 27.7 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 19.0375 | 784.0889 | 0 | 0.05921 | 7.3897 | 0 | 0 | 106.0343 | 0 | off_peak | 771.69 | 0 | 100 | 0 | 0 | 100 | 0 | 0
6527 | 792.26 | 0 | 27.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19.0375 | 792.26 | 0 | 0.05921 | 7.4766 | 0 | 0 | 106.0343 | 0 | off_peak | 792.26 |  |  | 0 | 0 | 100 | 0 | 0
6528 | 762.21 | 0 | 27.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19.0375 | 762.21 | 0 | 0.05921 | 7.5376 | 0 | 0 | 106.0343 | 0 | off_peak | 762.21 |  |  | 0 | 0 | 100 | 0 | 0
6529 | 714.9 | 0 | 27.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19.0375 | 714.9 | 0 | 0.05921 | 7.4128 | 0 | 0 | 106.0343 | 0 | off_peak | 714.9 |  |  | 0 | 0 | 100 | 0 | 0
6530 | 643.32 | 0 | 27.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19.0375 | 643.32 | 0 | 0.05921 | 7.1949 | 0 | 0 | 106.0343 | 0 | off_peak | 643.32 |  |  | 0 | 0 | 100 | 0 | 0
6531 | 650.51 | 0 | 27.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19.0375 | 650.51 | 0 | 0.05921 | 6.7472 | 0 | 0 | 106.0343 | 0 | off_peak | 650.51 |  |  | 0 | 0 | 100 | 0 | 0
6532 | 645.62 | 0 | 27.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19.0375 | 645.62 | 0 | 0.05921 | 6.2844 | 0 | 0 | 106.0343 | 0 | off_peak | 645.62 |  |  | 0 | 0 | 100 | 0 | 0
6533 | 656.21 | 0 | 27.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19.0375 | 656.21 | 0 | 0.05921 | 5.6717 | 0 | 0 | 106.0343 | 0 | off_peak | 656.21 |  |  | 0 | 0 | 100 | 0 | 0
6534 | 693.34 | 0 | 27.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19.0375 | 693.34 | 0 | 0.05921 | 5.2328 | 0 | 0 | 106.0343 | 0 | off_peak | 693.34 |  |  | 0 | 0 | 100 | 0 | 0
6535 | 753.28 | 10.45 | 27.4 | 2.0978 | 0 | 0 | 2.0978 | 2.0978 | 0 | 0 | 0 | 0 | 20.9999 | 753.28 | 0 | 0.05921 | 4.8806 | 0 | 0 | 107.9967 | 0 | off_peak | 753.28 | 100 | 0 | 0 | 0 | 100 | 0 | 0
6536 | 749.39 | 188.687 | 27.8 | 37.824 | 37.824 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20.9999 | 711.566 | 0 | 0.05921 | 4.6534 | 0 | 0 | 107.9967 | 37.824 | off_peak | 711.566 |  |  | 5.05 | 0 | 94.95 | 176.0094 | 0
6537 | 732.23 | 388.29 | 28 | 77.7795 | 77.7795 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20.9999 | 654.4505 | 0 | 0.05921 | 4.5008 | 0 | 0 | 107.9967 | 77.7795 | off_peak | 654.4505 |  |  | 10.62 | 0 | 89.38 | 350.0684 | 0
6538 | 730.21 | 567.222 | 28.3 | 113.4979 | 113.4979 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20.9999 | 616.7121 | 0 | 0.05921 | 4.4423 | 0 | 0 | 107.9967 | 113.4979 | off_peak | 616.7121 |  |  | 15.54 | 0 | 84.46 | 504.1889 | 0
6539 | 712.06 | 694.752 | 28.5 | 138.9146 | 138.9146 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20.9999 | 573.1454 | 0 | 0.05921 | 4.4569 | 0 | 0 | 107.9967 | 138.9146 | off_peak | 573.1454 |  |  | 19.51 | 0 | 80.49 | 619.1241 | 0
6540 | 751.96 | 671.328 | 28.7 | 134.1331 | 134.1331 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20.9999 | 617.8269 | 0 | 0.05921 | 4.558 | 0 | 0 | 107.9967 | 134.1331 | off_peak | 617.8269 |  |  | 17.84 | 0 | 82.16 | 611.3835 | 0
6541 | 764.36 | 558.31 | 28.7 | 111.5518 | 111.5518 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20.9999 | 652.8082 | 0 | 0.05921 | 4.7911 | 0 | 0 | 107.9967 | 111.5518 | off_peak | 652.8082 |  |  | 14.59 | 0 | 85.41 | 534.4527 | 0
6542 | 728.6 | 736.259 | 28.6 | 147.1602 | 147.1602 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20.9999 | 581.4398 | 0 | 0.05921 | 5.1429 | 0 | 0 | 107.9967 | 147.1602 | off_peak | 581.4398 |  |  | 20.2 | 0 | 79.8 | 756.8255 | 0
6543 | 744.05 | 614.9 | 28.5 | 122.9483 | 122.9483 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20.9999 | 621.1017 | 0 | 0.05921 | 5.5038 | 0 | 0 | 107.9967 | 122.9483 | off_peak | 621.1017 |  |  | 16.52 | 0 | 83.48 | 676.6803 | 0
6544 | 742.86 | 125.4 | 28.3 | 25.0918 | 25.0918 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20.9999 | 717.7682 | 0 | 0.05921 | 6.0005 | 0 | 0 | 107.9967 | 25.0918 | off_peak | 717.7682 |  |  | 3.38 | 0 | 96.62 | 150.5646 | 0
6545 | 701.63 | 257.42 | 28.1 | 51.5458 | 51.5458 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20.9999 | 650.0842 | 0 | 0.05921 | 6.4777 | 0 | 0 | 107.9967 | 51.5458 | off_peak | 650.0842 |  |  | 7.35 | 0 | 92.65 | 333.8988 | 0
6546 | 644.59 | 59.4233 | 27.8 | 11.9119 | 11.9119 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20.9999 | 632.6781 | 0 | 0.05921 | 6.9232 | 0 | 0 | 107.9967 | 11.9119 | off_peak | 632.6781 |  |  | 1.85 | 0 | 98.15 | 82.4689 | 0
6547 | 602.62 | 0 | 27.6 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 32.598 | 615.0189 | 0 | 0.05921 | 7.4815 | 0 | 0 | 107.9967 | 0 | off_peak | 602.62 | 0 | 100 | 0 | 0 | 100 | 0 | 0
6548 | 593.78 | 0 | 26.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 32.598 | 593.78 | 0 | 0.05921 | 7.7573 | 0 | 0 | 107.9967 | 0 | off_peak | 593.78 |  |  | 0 | 0 | 100 | 0 | 0
6549 | 596.46 | 0 | 26 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 32.598 | 596.46 | 0 | 0.05921 | 7.8276 | 0 | 0 | 107.9967 | 0 | off_peak | 596.46 |  |  | 0 | 0 | 100 | 0 | 0
6550 | 585.18 | 0 | 25.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 32.598 | 585.18 | 0 | 0.05921 | 7.7437 | 0 | 0 | 107.9967 | 0 | off_peak | 585.18 |  |  | 0 | 0 | 100 | 0 | 0
6551 | 592.45 | 0 | 25.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 32.598 | 592.45 | 0 | 0.05921 | 7.5387 | 0 | 0 | 107.9967 | 0 | off_peak | 592.45 |  |  | 0 | 0 | 100 | 0 | 0
6552 | 580.87 | 0 | 25.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 32.598 | 580.87 | 0 | 0.05921 | 7.3885 | 0 | 0 | 107.9967 | 0 | off_peak | 580.87 |  |  | 0 | 0 | 100 | 0 | 0
6553 | 582.23 | 0 | 25.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 32.598 | 582.23 | 0 | 0.05921 | 7.2346 | 0 | 0 | 107.9967 | 0 | off_peak | 582.23 |  |  | 0 | 0 | 100 | 0 | 0
6554 | 587.05 | 0 | 25.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 32.598 | 587.05 | 0 | 0.05921 | 6.9864 | 0 | 0 | 107.9967 | 0 | off_peak | 587.05 |  |  | 0 | 0 | 100 | 0 | 0
6555 | 602.79 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 32.598 | 602.79 | 0 | 0.05921 | 6.4805 | 0 | 0 | 107.9967 | 0 | off_peak | 602.79 |  |  | 0 | 0 | 100 | 0 | 0
6556 | 610.6 | 0 | 24.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 32.598 | 610.6 | 0 | 0.05921 | 6.0567 | 0 | 0 | 107.9967 | 0 | off_peak | 610.6 |  |  | 0 | 0 | 100 | 0 | 0
6557 | 584.51 | 0 | 24.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 32.598 | 584.51 | 0 | 0.05921 | 5.5891 | 0 | 0 | 107.9967 | 0 | off_peak | 584.51 |  |  | 0 | 0 | 100 | 0 | 0
6558 | 671.3 | 0 | 24.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 32.598 | 671.3 | 0 | 0.05921 | 5.1242 | 0 | 0 | 107.9967 | 0 | off_peak | 671.3 |  |  | 0 | 0 | 100 | 0 | 0
6559 | 703.02 | 26.211 | 25.2 | 5.3039 | 0 | 0 | 5.3039 | 12.3989 | 7.095 | 0 | 0 | 0 | 44.1962 | 710.115 | 0 | 0.05921 | 4.7945 | 0 | 0 | 112.958 | 0 | off_peak | 703.02 | 42.78 | 57.22 | 0 | 0 | 100 | 0 | 0
6560 | 731.5 | 205.997 | 25.7 | 41.6093 | 41.6093 | 0 | 0 | 0.82089 | 0.82089 | 0 | 0 | 0 | 44.964 | 690.7116 | 0 | 0.05921 | 4.5467 | 0 | 0 | 112.958 | 41.6093 | off_peak | 689.8907 | 0 | 100 | 5.69 | 0 | 94.31 | 189.1842 | 0
6561 | 741.89 | 420.382 | 26.2 | 84.7596 | 84.7596 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 44.964 | 657.1304 | 0 | 0.05921 | 4.3755 | 0 | 0 | 112.958 | 84.7596 | off_peak | 657.1304 |  |  | 11.42 | 0 | 88.58 | 370.8666 | 0
6562 | 732.7 | 538.278 | 26.7 | 108.3342 | 108.3342 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 44.964 | 624.3658 | 0 | 0.05921 | 4.2672 | 0 | 0 | 112.958 | 108.3342 | off_peak | 624.3658 |  |  | 14.79 | 0 | 85.21 | 462.2859 | 0
6563 | 700.4 | 563.276 | 27.2 | 113.16 | 100.7611 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 0 | 56.5622 | 599.6389 | 0 | 0.05921 | 4.2438 | 0 | 0 | 124.5562 | 100.7611 | off_peak | 599.6389 | 100 | 0 | 14.39 | 0 | 85.61 | 427.6097 | 0
6564 | 704.13 | 262.613 | 27.6 | 52.6814 | 52.6814 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 56.5622 | 651.4486 | 0 | 0.05921 | 4.3362 | 0 | 0 | 124.5562 | 52.6814 | off_peak | 651.4486 |  |  | 7.48 | 0 | 92.52 | 228.4373 | 0
6565 | 726.86 | 257.904 | 28 | 51.6615 | 51.6615 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 56.5622 | 675.1985 | 0 | 0.05921 | 4.5237 | 0 | 0 | 124.5562 | 51.6615 | off_peak | 675.1985 |  |  | 7.11 | 0 | 92.89 | 233.701 | 0
6566 | 720.25 | 167.2 | 28.1 | 33.4801 | 33.4801 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 56.5622 | 686.7699 | 0 | 0.05921 | 4.7879 | 0 | 0 | 124.5562 | 33.4801 | off_peak | 686.7699 |  |  | 4.65 | 0 | 95.35 | 160.3003 | 0
6567 | 728.14 | 216.584 | 28.1 | 43.3688 | 43.3688 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 56.5622 | 684.7712 | 0 | 0.05921 | 5.0157 | 0 | 0 | 124.5562 | 43.3688 | off_peak | 684.7712 |  |  | 5.96 | 0 | 94.04 | 217.5256 | 0
6568 | 742.17 | 64.6 | 27.9 | 12.9449 | 12.9449 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 68.1603 | 741.624 | 0 | 0.05921 | 5.333 | 0 | 0 | 124.5562 | 12.9449 | off_peak | 729.2251 | 0 | 100 | 1.74 | 0 | 98.26 | 69.0359 | 0
6569 | 702.73 | 37.05 | 27.5 | 7.4351 | 7.4351 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 68.1603 | 695.2949 | 0 | 0.05921 | 5.9567 | 0 | 0 | 124.5562 | 7.4351 | off_peak | 695.2949 |  |  | 1.06 | 0 | 98.94 | 44.2886 | 0
6570 | 649.63 | 20.9 | 27.1 | 4.2003 | 0 | 0 | 4.2003 | 4.2003 | 0 | 0 | 0 | 0 | 72.0893 | 649.63 | 0 | 0.05921 | 6.5631 | 0 | 0 | 128.4852 | 0 | off_peak | 649.63 | 100 | 0 | 0 | 0 | 100 | 0 | 0
6571 | 584.23 | 0 | 26.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 72.0893 | 584.23 | 0 | 0.05921 | 6.9352 | 0 | 0 | 128.4852 | 0 | off_peak | 584.23 |  |  | 0 | 0 | 100 | 0 | 0
6572 | 589.44 | 0 | 26.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 72.0893 | 589.44 | 0 | 0.05921 | 7.2477 | 0 | 0 | 128.4852 | 0 | off_peak | 589.44 |  |  | 0 | 0 | 100 | 0 | 0
6573 | 555.6 | 0 | 26.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 72.0893 | 555.6 | 0 | 0.05921 | 7.4256 | 0 | 0 | 128.4852 | 0 | off_peak | 555.6 |  |  | 0 | 0 | 100 | 0 | 0
6574 | 564.09 | 0 | 26.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 72.0893 | 564.09 | 0 | 0.05921 | 7.3044 | 0 | 0 | 128.4852 | 0 | off_peak | 564.09 |  |  | 0 | 0 | 100 | 0 | 0
6575 | 593.09 | 0 | 26.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 72.0893 | 593.09 | 0 | 0.05921 | 7.335 | 0 | 0 | 128.4852 | 0 | off_peak | 593.09 |  |  | 0 | 0 | 100 | 0 | 0
6576 | 575.13 | 0 | 26.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 72.0893 | 575.13 | 0 | 0.05921 | 7.3517 | 0 | 0 | 128.4852 | 0 | off_peak | 575.13 |  |  | 0 | 0 | 100 | 0 | 0
6577 | 569.69 | 0 | 26.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 72.0893 | 569.69 | 0 | 0.05921 | 7.3751 | 0 | 0 | 128.4852 | 0 | off_peak | 569.69 |  |  | 0 | 0 | 100 | 0 | 0
6578 | 591.15 | 0 | 25.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 72.0893 | 591.15 | 0 | 0.05921 | 7.1487 | 0 | 0 | 128.4852 | 0 | off_peak | 591.15 |  |  | 0 | 0 | 100 | 0 | 0
6579 | 570.36 | 0 | 25.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 72.0893 | 570.36 | 0 | 0.05921 | 6.6151 | 0 | 0 | 128.4852 | 0 | off_peak | 570.36 |  |  | 0 | 0 | 100 | 0 | 0
6580 | 591.13 | 0 | 25.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 72.0893 | 591.13 | 0 | 0.05921 | 6.0827 | 0 | 0 | 128.4852 | 0 | off_peak | 591.13 |  |  | 0 | 0 | 100 | 0 | 0
6581 | 572.72 | 0 | 25.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 72.0893 | 572.72 | 0 | 0.05921 | 5.4123 | 0 | 0 | 128.4852 | 0 | off_peak | 572.72 |  |  | 0 | 0 | 100 | 0 | 0
6582 | 676.88 | 0 | 25.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 72.0893 | 676.88 | 0 | 0.05921 | 4.9375 | 0 | 0 | 128.4852 | 0 | off_peak | 676.88 |  |  | 0 | 0 | 100 | 0 | 0
6583 | 728.51 | 11.4 | 25.5 | 2.3043 | 0 | 0 | 2.3043 | 2.3043 | 0 | 0 | 0 | 0 | 74.2448 | 728.51 | 0 | 0.05921 | 4.5492 | 0 | 0 | 130.6407 | 0 | off_peak | 728.51 | 100 | 0 | 0 | 0 | 100 | 0 | 0
6584 | 770.11 | 62.964 | 25.8 | 12.7135 | 12.7135 | 0 | 0 | 0.14883 | 0.14883 | 0 | 0 | 0 | 74.384 | 757.5453 | 0 | 0.05921 | 4.31 | 0 | 0 | 130.6407 | 12.7135 | off_peak | 757.3965 | 0 | 100 | 1.65 | 0 | 98.35 | 54.7949 | 0
6585 | 806.45 | 90.25 | 26.2 | 18.1967 | 18.1967 | 0 | 0 | 0.0096121 | 0.0096121 | 0 | 0 | 0 | 74.393 | 788.2629 | 0 | 0.05921 | 4.1512 | 0 | 0 | 130.6407 | 18.1967 | off_peak | 788.2533 | 0 | 100 | 2.26 | 0 | 97.74 | 75.5383 | 0
6586 | 810.36 | 288.221 | 26.7 | 58.0076 | 58.0076 | 0 | 0 | 0.00062081 | 0.00062081 | 0 | 0 | 0 | 74.3936 | 752.3531 | 0 | 0.05921 | 4.1619 | 0 | 0 | 130.6407 | 58.0076 | off_peak | 752.3524 | 0 | 100 | 7.16 | 0 | 92.84 | 241.4194 | 0
6587 | 805.27 | 553.659 | 27.2 | 111.228 | 111.228 | 0 | 0 | 4.0095e-05 | 4.0095e-05 | 0 | 0 | 0 | 74.3936 | 694.0421 | 0 | 0.05921 | 4.4257 | 0 | 0 | 130.6407 | 111.228 | off_peak | 694.042 | 0 | 100 | 13.81 | 0 | 86.19 | 492.2671 | 0
6588 | 844.79 | 441.392 | 27.7 | 88.5131 | 88.5131 | 0 | 0 | 2.5896e-06 | 2.5896e-06 | 0 | 0 | 0 | 74.3936 | 756.2769 | 0 | 0.05921 | 4.8515 | 0 | 0 | 130.6407 | 88.5131 | off_peak | 756.2769 | 0 | 100 | 10.48 | 0 | 89.52 | 429.4174 | 0
6589 | 804.51 | 379.484 | 28 | 76.0156 | 76.0156 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 728.4944 | 0 | 0.088511 | 5.0935 | 0 | 0 | 130.6407 | 76.0156 | on_peak | 728.4944 |  |  | 9.45 | 0 | 90.55 | 387.1835 | 0
6590 | 824.37 | 673.784 | 28.2 | 134.8695 | 134.8695 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 689.5005 | 0 | 0.088511 | 5.1237 | 0 | 0 | 130.6407 | 134.8695 | on_peak | 689.5005 |  |  | 16.36 | 0 | 83.64 | 691.035 | 0
6591 | 819.2 | 587.388 | 28.2 | 117.5758 | 117.5758 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 701.6242 | 0 | 0.088511 | 5.1078 | 0 | 0 | 130.6407 | 117.5758 | on_peak | 701.6242 |  |  | 14.35 | 0 | 85.65 | 600.5529 | 0
6592 | 817.94 | 286.081 | 28.2 | 57.264 | 57.264 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 760.676 | 0 | 0.088511 | 5.2326 | 0 | 0 | 130.6407 | 57.264 | on_peak | 760.676 |  |  | 7 | 0 | 93 | 299.6384 | 0
6593 | 827.27 | 273.155 | 28 | 54.7165 | 54.7165 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 772.5535 | 0 | 0.088511 | 5.5333 | 0 | 0 | 130.6407 | 54.7165 | on_peak | 772.5535 |  |  | 6.61 | 0 | 93.39 | 302.7634 | 0
6594 | 800.25 | 74.8898 | 27.6 | 15.0232 | 15.0232 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 785.2268 | 0 | 0.088511 | 5.8372 | 0 | 0 | 130.6407 | 15.0232 | on_peak | 785.2268 |  |  | 1.88 | 0 | 98.12 | 87.6934 | 0
6595 | 806.45 | 0 | 27.4 | 0 | 0 | 0 | 0 | 0 | 0 | 62.63 | 62.63 | 0 | 7.4394 | 743.82 | 0 | 0.088511 | 6.0902 | 0 | 0 | 130.6407 | 0 | on_peak | 743.82 |  |  | 0 | 7.77 | 92.23 | 0 | 0
6596 | 810.27 | 0 | 27.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 810.27 | 0 | 0.088511 | 6.3274 | 0 | 0 | 130.6407 | 0 | on_peak | 810.27 |  |  | 0 | 0 | 100 | 0 | 0
6597 | 810.17 | 0 | 27.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 810.17 | 0 | 0.088511 | 6.6961 | 0 | 0 | 130.6407 | 0 | on_peak | 810.17 |  |  | 0 | 0 | 100 | 0 | 0
6598 | 785.83 | 0 | 27.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 785.83 | 0 | 0.05921 | 7.0542 | 0 | 0 | 130.6407 | 0 | off_peak | 785.83 |  |  | 0 | 0 | 100 | 0 | 0
6599 | 769.23 | 0 | 26.9 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 19.0375 | 781.6289 | 0 | 0.05921 | 7.4208 | 0 | 0 | 130.6407 | 0 | off_peak | 769.23 | 0 | 100 | 0 | 0 | 100 | 0 | 0
6600 | 741.02 | 0 | 26.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19.0375 | 741.02 | 0 | 0.05921 | 7.7275 | 0 | 0 | 130.6407 | 0 | off_peak | 741.02 |  |  | 0 | 0 | 100 | 0 | 0
6601 | 711.37 | 0 | 26.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19.0375 | 711.37 | 0 | 0.05921 | 7.657 | 0 | 0 | 130.6407 | 0 | off_peak | 711.37 |  |  | 0 | 0 | 100 | 0 | 0
6602 | 613.65 | 0 | 25.8 | 0 | 0 | 0 | 0 | 8.7263 | 8.7263 | 0 | 0 | 0 | 27.2003 | 622.3763 | 0 | 0.05921 | 7.3557 | 0 | 0 | 130.6407 | 0 | off_peak | 613.65 | 0 | 100 | 0 | 0 | 100 | 0 | 0
6603 | 610.03 | 0 | 25.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27.2003 | 610.03 | 0 | 0.05921 | 6.8097 | 0 | 0 | 130.6407 | 0 | off_peak | 610.03 |  |  | 0 | 0 | 100 | 0 | 0
6604 | 595.38 | 0 | 24.7 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 38.7984 | 607.7789 | 0 | 0.05921 | 6.1801 | 0 | 0 | 130.6407 | 0 | off_peak | 595.38 | 0 | 100 | 0 | 0 | 100 | 0 | 0
6605 | 634.86 | 0 | 24.3 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 50.3966 | 647.2589 | 0 | 0.05921 | 5.3291 | 0 | 0 | 130.6407 | 0 | off_peak | 634.86 | 0 | 100 | 0 | 0 | 100 | 0 | 0
6606 | 702.38 | 0 | 24.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50.3966 | 702.38 | 0 | 0.05921 | 4.8461 | 0 | 0 | 130.6407 | 0 | off_peak | 702.38 |  |  | 0 | 0 | 100 | 0 | 0
6607 | 784.4 | 24.5246 | 24.2 | 4.9805 | 4.9805 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 61.9947 | 791.8184 | 0 | 0.05921 | 4.4635 | 0 | 0 | 130.6407 | 4.9805 | off_peak | 779.4195 | 0 | 100 | 0.63 | 0 | 99.37 | 22.2308 | 0
6608 | 845.46 | 212.398 | 24.8 | 43.0416 | 43.0416 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 73.5928 | 814.8174 | 0 | 0.05921 | 4.206 | 0 | 0 | 130.6407 | 43.0416 | off_peak | 802.4184 | 0 | 100 | 5.09 | 0 | 94.91 | 181.0343 | 0
6609 | 825.28 | 426.723 | 25.7 | 86.1937 | 86.1937 | 0 | 0 | 0.80079 | 0.80079 | 0 | 0 | 0 | 74.3419 | 739.8871 | 0 | 0.05921 | 4.0464 | 0 | 0 | 130.6407 | 86.1937 | off_peak | 739.0863 | 0 | 100 | 10.44 | 0 | 89.56 | 348.777 | 0
6610 | 809.06 | 616.625 | 26.7 | 124.1024 | 124.1024 | 0 | 0 | 0.05172 | 0.05172 | 0 | 0 | 0 | 74.3903 | 685.0093 | 0 | 0.05921 | 4.0311 | 0 | 0 | 130.6407 | 124.1024 | off_peak | 684.9576 | 0 | 100 | 15.34 | 0 | 84.66 | 500.2679 | 0
6611 | 830.88 | 757.9 | 27.6 | 152.0382 | 152.0382 | 0 | 0 | 0.0033404 | 0.0033404 | 0 | 0 | 0 | 74.3934 | 678.8451 | 0 | 0.05921 | 4.3121 | 0 | 0 | 130.6407 | 152.0382 | off_peak | 678.8418 | 0 | 100 | 18.3 | 0 | 81.7 | 655.6048 | 0
6612 | 839.91 | 835.613 | 28.2 | 167.2623 | 167.2623 | 0 | 0 | 0.00021574 | 0.00021574 | 0 | 0 | 0 | 74.3936 | 672.6479 | 0 | 0.05921 | 4.7538 | 0 | 0 | 130.6407 | 167.2623 | off_peak | 672.6477 | 0 | 100 | 19.91 | 0 | 80.09 | 795.1288 | 0
6613 | 850.02 | 844.227 | 28.7 | 168.6788 | 168.6788 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 681.3412 | 0 | 0.088511 | 4.9643 | 0 | 0 | 130.6407 | 168.6788 | on_peak | 681.3412 |  |  | 19.84 | 0 | 80.16 | 837.3724 | 0
6614 | 861.25 | 495.309 | 29 | 98.8558 | 98.8558 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 762.3942 | 0 | 0.088511 | 5.0114 | 0 | 0 | 130.6407 | 98.8558 | on_peak | 762.3942 |  |  | 11.48 | 0 | 88.52 | 495.4049 | 0
6615 | 816.24 | 226.356 | 29.1 | 45.1605 | 45.1605 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 771.0795 | 0 | 0.088511 | 5.0996 | 0 | 0 | 130.6407 | 45.1605 | on_peak | 771.0795 |  |  | 5.53 | 0 | 94.47 | 230.3019 | 0
6616 | 794.37 | 165.825 | 29 | 33.096 | 33.096 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 761.274 | 0 | 0.088511 | 5.2894 | 0 | 0 | 130.6407 | 33.096 | on_peak | 761.274 |  |  | 4.17 | 0 | 95.83 | 175.0568 | 0
6617 | 819.29 | 170.369 | 28.8 | 34.0278 | 34.0278 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 785.2622 | 0 | 0.088511 | 5.5536 | 0 | 0 | 130.6407 | 34.0278 | on_peak | 785.2622 |  |  | 4.15 | 0 | 95.85 | 188.9775 | 0
6618 | 820.17 | 51.1267 | 28.2 | 10.2339 | 10.2339 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 809.9361 | 0 | 0.088511 | 5.8734 | 0 | 0 | 130.6407 | 10.2339 | on_peak | 809.9361 |  |  | 1.25 | 0 | 98.75 | 60.1082 | 0
6619 | 824.45 | 0 | 27.6 | 0 | 0 | 0 | 0 | 0 | 0 | 62.63 | 62.63 | 0 | 7.4394 | 761.82 | 0 | 0.088511 | 6.2833 | 0 | 0 | 130.6407 | 0 | on_peak | 761.82 |  |  | 0 | 7.6 | 92.4 | 0 | 0
6620 | 817.45 | 0 | 27.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 817.45 | 0 | 0.088511 | 6.6361 | 0 | 0 | 130.6407 | 0 | on_peak | 817.45 |  |  | 0 | 0 | 100 | 0 | 0
6621 | 827.8 | 0 | 26.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 827.8 | 0 | 0.088511 | 7.1727 | 0 | 0 | 130.6407 | 0 | on_peak | 827.8 |  |  | 0 | 0 | 100 | 0 | 0
6622 | 749.94 | 0 | 26.7 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 19.0375 | 762.3389 | 0 | 0.05921 | 7.5872 | 0 | 0 | 130.6407 | 0 | off_peak | 749.94 | 0 | 100 | 0 | 0 | 100 | 0 | 0
6623 | 791.66 | 0 | 26.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19.0375 | 791.66 | 0 | 0.05921 | 7.846 | 0 | 0 | 130.6407 | 0 | off_peak | 791.66 |  |  | 0 | 0 | 100 | 0 | 0
6624 | 774.79 | 0 | 26.1 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 30.6357 | 787.1889 | 0 | 0.05921 | 8.0403 | 0 | 0 | 130.6407 | 0 | off_peak | 774.79 | 0 | 100 | 0 | 0 | 100 | 0 | 0
6625 | 678.48 | 0 | 25.9 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 42.2338 | 690.8789 | 0 | 0.05921 | 7.9516 | 0 | 0 | 130.6407 | 0 | off_peak | 678.48 | 0 | 100 | 0 | 0 | 100 | 0 | 0
6626 | 643.82 | 0 | 25.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 42.2338 | 643.82 | 0 | 0.05921 | 7.5053 | 0 | 0 | 130.6407 | 0 | off_peak | 643.82 |  |  | 0 | 0 | 100 | 0 | 0
6627 | 580.45 | 0 | 25.4 | 0 | 0 | 0 | 0 | 8.7263 | 8.7263 | 0 | 0 | 0 | 50.3966 | 589.1763 | 0 | 0.05921 | 6.9849 | 0 | 0 | 130.6407 | 0 | off_peak | 580.45 | 0 | 100 | 0 | 0 | 100 | 0 | 0
6628 | 605.09 | 0 | 25.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50.3966 | 605.09 | 0 | 0.05921 | 6.3677 | 0 | 0 | 130.6407 | 0 | off_peak | 605.09 |  |  | 0 | 0 | 100 | 0 | 0
6629 | 603.76 | 0 | 24.9 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 61.9947 | 616.1589 | 0 | 0.05921 | 5.5565 | 0 | 0 | 130.6407 | 0 | off_peak | 603.76 | 0 | 100 | 0 | 0 | 100 | 0 | 0
6630 | 696.36 | 0 | 24.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 61.9947 | 696.36 | 0 | 0.05921 | 5.0097 | 0 | 0 | 130.6407 | 0 | off_peak | 696.36 |  |  | 0 | 0 | 100 | 0 | 0
6631 | 745.27 | 22.4966 | 24.9 | 4.5572 | 0 | 0 | 4.5572 | 12.3989 | 7.8417 | 0 | 0 | 0 | 73.5928 | 753.1117 | 0 | 0.05921 | 4.5772 | 0 | 0 | 134.9035 | 0 | off_peak | 745.27 | 36.75 | 63.25 | 0 | 0 | 100 | 0 | 0
6632 | 774.16 | 206.136 | 25.4 | 41.6824 | 41.6824 | 0 | 0 | 0.80079 | 0.80079 | 0 | 0 | 0 | 74.3419 | 733.2784 | 0 | 0.05921 | 4.2795 | 0 | 0 | 134.9035 | 41.6824 | off_peak | 732.4776 | 0 | 100 | 5.38 | 0 | 94.62 | 178.3789 | 0
6633 | 801.98 | 417.602 | 25.9 | 84.2904 | 84.2904 | 0 | 0 | 0.05172 | 0.05172 | 0 | 0 | 0 | 74.3903 | 717.7413 | 0 | 0.05921 | 4.0721 | 0 | 0 | 134.9035 | 84.2904 | off_peak | 717.6896 | 0 | 100 | 10.51 | 0 | 89.49 | 343.2354 | 0
6634 | 801.37 | 604 | 26.5 | 121.6495 | 121.6495 | 0 | 0 | 0.0033404 | 0.0033404 | 0 | 0 | 0 | 74.3934 | 679.7238 | 0 | 0.05921 | 4.0761 | 0 | 0 | 134.9035 | 121.6495 | off_peak | 679.7205 | 0 | 100 | 15.18 | 0 | 84.82 | 495.8563 | 0
6635 | 796.58 | 694.611 | 27.1 | 139.5953 | 139.5953 | 0 | 0 | 0.00021574 | 0.00021574 | 0 | 0 | 0 | 74.3936 | 656.9849 | 0 | 0.05921 | 4.3391 | 0 | 0 | 134.9035 | 139.5953 | off_peak | 656.9847 | 0 | 100 | 17.52 | 0 | 82.48 | 605.716 | 0
6636 | 861.49 | 655.499 | 27.6 | 131.4961 | 131.4961 | 0 | 0 | 1.3934e-05 | 1.3934e-05 | 0 | 0 | 0 | 74.3936 | 729.9939 | 0 | 0.05921 | 4.7512 | 0 | 0 | 134.9035 | 131.4961 | off_peak | 729.9939 | 0 | 100 | 15.26 | 0 | 84.74 | 624.7704 | 0
6637 | 802.45 | 585.644 | 27.9 | 117.3548 | 117.3548 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 685.0952 | 0 | 0.088511 | 5.042 | 0 | 0 | 134.9035 | 117.3548 | on_peak | 685.0952 |  |  | 14.62 | 0 | 85.38 | 591.7028 | 0
6638 | 886.38 | 473.313 | 28.1 | 94.7762 | 94.7762 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 791.6038 | 0 | 0.088511 | 5.1859 | 0 | 0 | 134.9035 | 94.7762 | on_peak | 791.6038 |  |  | 10.69 | 0 | 89.31 | 491.5046 | 0
6639 | 868.33 | 606.638 | 28.1 | 121.4733 | 121.4733 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 746.8567 | 0 | 0.088511 | 5.2728 | 0 | 0 | 134.9035 | 121.4733 | on_peak | 746.8567 |  |  | 13.99 | 0 | 86.01 | 640.5054 | 0
6640 | 828.51 | 311.548 | 27.9 | 62.4298 | 62.4298 | 0 | 0 | 0 | 0 | 62.4511 | 62.4511 | 0 | 7.6306 | 703.6291 | 0 | 0.088511 | 5.5883 | 0 | 0 | 134.9035 | 62.4298 | on_peak | 703.6291 |  |  | 7.54 | 7.54 | 84.93 | 348.8764 | 0
6641 | 853.38 | 221.386 | 27.6 | 44.411 | 44.411 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.6306 | 808.969 | 0 | 0.088511 | 6.1094 | 0 | 0 | 134.9035 | 44.411 | on_peak | 808.969 |  |  | 5.2 | 0 | 94.8 | 271.3239 | 0
6642 | 843.18 | 66.3877 | 27 | 13.3467 | 13.3467 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.6306 | 829.8333 | 0 | 0.088511 | 6.5377 | 0 | 0 | 134.9035 | 13.3467 | on_peak | 829.8333 |  |  | 1.58 | 0 | 98.42 | 87.2566 | 0
6643 | 831.8 | 0 | 26.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0.17891 | 0.17891 | 0 | 7.4394 | 831.6211 | 0 | 0.088511 | 6.8178 | 0 | 0 | 134.9035 | 0 | on_peak | 831.6211 |  |  | 0 | 0.02 | 99.98 | 0 | 0
6644 | 825.58 | 0 | 26.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 825.58 | 0 | 0.088511 | 7.252 | 0 | 0 | 134.9035 | 0 | on_peak | 825.58 |  |  | 0 | 0 | 100 | 0 | 0
6645 | 804.61 | 0 | 25.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 804.61 | 0 | 0.088511 | 7.7258 | 0 | 0 | 134.9035 | 0 | on_peak | 804.61 |  |  | 0 | 0 | 100 | 0 | 0
6646 | 762.47 | 0 | 25.7 | 0 | 0 | 0 | 0 | 8.7263 | 8.7263 | 0 | 0 | 0 | 15.6021 | 771.1963 | 0 | 0.05921 | 8.0553 | 0 | 0 | 134.9035 | 0 | off_peak | 762.47 | 0 | 100 | 0 | 0 | 100 | 0 | 0
6647 | 795.65 | 0 | 25.4 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 27.2003 | 808.0489 | 0 | 0.05921 | 8.2865 | 0 | 0 | 134.9035 | 0 | off_peak | 795.65 | 0 | 100 | 0 | 0 | 100 | 0 | 0
6648 | 750.34 | 0 | 25.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27.2003 | 750.34 | 0 | 0.05921 | 8.4707 | 0 | 0 | 134.9035 | 0 | off_peak | 750.34 |  |  | 0 | 0 | 100 | 0 | 0
6649 | 689.37 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27.2003 | 689.37 | 0 | 0.05921 | 8.3023 | 0 | 0 | 134.9035 | 0 | off_peak | 689.37 |  |  | 0 | 0 | 100 | 0 | 0
6650 | 641.84 | 0 | 24.9 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 38.7984 | 654.2389 | 0 | 0.05921 | 7.9966 | 0 | 0 | 134.9035 | 0 | off_peak | 641.84 | 0 | 100 | 0 | 0 | 100 | 0 | 0
6651 | 638.37 | 0 | 24.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 38.7984 | 638.37 | 0 | 0.05921 | 7.4083 | 0 | 0 | 134.9035 | 0 | off_peak | 638.37 |  |  | 0 | 0 | 100 | 0 | 0
6652 | 641.09 | 0 | 24.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 38.7984 | 641.09 | 0 | 0.05921 | 6.7319 | 0 | 0 | 134.9035 | 0 | off_peak | 641.09 |  |  | 0 | 0 | 100 | 0 | 0
6653 | 649.61 | 0 | 24.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 38.7984 | 649.61 | 0 | 0.05921 | 5.8306 | 0 | 0 | 134.9035 | 0 | off_peak | 649.61 |  |  | 0 | 0 | 100 | 0 | 0
6654 | 705.18 | 0 | 24.7 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 50.3966 | 717.5789 | 0 | 0.05921 | 5.2668 | 0 | 0 | 134.9035 | 0 | off_peak | 705.18 | 0 | 100 | 0 | 0 | 100 | 0 | 0
6655 | 773.93 | 23.5305 | 25.1 | 4.7632 | 0 | 0 | 4.7632 | 12.3989 | 7.6357 | 0 | 0 | 0 | 61.9947 | 781.5657 | 0 | 0.05921 | 4.8205 | 0 | 0 | 139.3591 | 0 | off_peak | 773.93 | 38.42 | 61.58 | 0 | 0 | 100 | 0 | 0
6656 | 807.68 | 208.17 | 25.8 | 42.033 | 42.033 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 73.5928 | 778.0459 | 0 | 0.05921 | 4.5461 | 0 | 0 | 139.3591 | 42.033 | off_peak | 765.647 | 0 | 100 | 5.2 | 0 | 94.8 | 191.0859 | 0
6657 | 803.67 | 419.49 | 26.4 | 84.5186 | 83.7178 | 0 | 0.80079 | 0.80079 | 0 | 0 | 0 | 0 | 74.3419 | 719.9522 | 0 | 0.05921 | 4.3716 | 0 | 0 | 140.1082 | 83.7178 | off_peak | 719.9522 | 100 | 0 | 10.42 | 0 | 89.58 | 365.9776 | 0
6658 | 855.86 | 604.204 | 27 | 121.4704 | 121.4704 | 0 | 0 | 0.05172 | 0.05172 | 0 | 0 | 0 | 74.3903 | 734.4413 | 0 | 0.05921 | 4.3443 | 0 | 0 | 140.1082 | 121.4704 | off_peak | 734.3896 | 0 | 100 | 14.19 | 0 | 85.81 | 527.701 | 0
6659 | 824.18 | 740.734 | 27.5 | 148.6486 | 148.6486 | 0 | 0 | 0.0033404 | 0.0033404 | 0 | 0 | 0 | 74.3934 | 675.5347 | 0 | 0.05921 | 4.569 | 0 | 0 | 140.1082 | 148.6486 | off_peak | 675.5314 | 0 | 100 | 18.04 | 0 | 81.96 | 679.1815 | 0
6660 | 829.84 | 597.52 | 27.8 | 119.7781 | 119.7781 | 0 | 0 | 0.00021574 | 0.00021574 | 0 | 0 | 0 | 74.3936 | 710.0621 | 0 | 0.05921 | 4.9546 | 0 | 0 | 140.1082 | 119.7781 | off_peak | 710.0619 | 0 | 100 | 14.43 | 0 | 85.57 | 593.4516 | 0
6661 | 829.54 | 648.232 | 28 | 129.8493 | 129.8493 | 0 | 0 | 0 | 0 | 62.63 | 62.63 | 0 | 7.4394 | 637.0607 | 0 | 0.088511 | 5.259 | 0 | 0 | 140.1082 | 129.8493 | on_peak | 637.0607 |  |  | 15.65 | 7.55 | 76.8 | 682.8713 | 0
6662 | 815.05 | 379.921 | 28.1 | 76.0754 | 76.0754 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 738.9746 | 0 | 0.088511 | 5.3604 | 0 | 0 | 140.1082 | 76.0754 | on_peak | 738.9746 |  |  | 9.33 | 0 | 90.67 | 407.7957 | 0
6663 | 812.75 | 171.956 | 28.1 | 34.4325 | 34.4325 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 778.3175 | 0 | 0.088511 | 5.606 | 0 | 0 | 140.1082 | 34.4325 | on_peak | 778.3175 |  |  | 4.24 | 0 | 95.76 | 193.0292 | 0
6664 | 801.78 | 90.3924 | 27.9 | 18.1134 | 18.1134 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 783.6666 | 0 | 0.088511 | 5.9971 | 0 | 0 | 140.1082 | 18.1134 | on_peak | 783.6666 |  |  | 2.26 | 0 | 97.74 | 108.627 | 0
6665 | 829.3 | 42.769 | 27.5 | 8.5828 | 8.5828 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 820.7172 | 0 | 0.088511 | 6.5652 | 0 | 0 | 140.1082 | 8.5828 | on_peak | 820.7172 |  |  | 1.03 | 0 | 98.97 | 56.3472 | 0
6666 | 816.12 | 38.4589 | 26.9 | 7.7347 | 7.7347 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 808.3853 | 0 | 0.088511 | 6.9353 | 0 | 0 | 140.1082 | 7.7347 | on_peak | 808.3853 |  |  | 0.95 | 0 | 99.05 | 53.6419 | 0
6667 | 800.14 | 0 | 26.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 800.14 | 0 | 0.088511 | 7.4065 | 0 | 0 | 140.1082 | 0 | on_peak | 800.14 |  |  | 0 | 0 | 100 | 0 | 0
6668 | 770.3 | 0 | 26.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 770.3 | 0 | 0.088511 | 7.8031 | 0 | 0 | 140.1082 | 0 | on_peak | 770.3 |  |  | 0 | 0 | 100 | 0 | 0
6669 | 792.92 | 0 | 26.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 792.92 | 0 | 0.088511 | 7.9639 | 0 | 0 | 140.1082 | 0 | on_peak | 792.92 |  |  | 0 | 0 | 100 | 0 | 0
6670 | 731.27 | 0 | 25.9 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 19.0375 | 743.6689 | 0 | 0.05921 | 8.1491 | 0 | 0 | 140.1082 | 0 | off_peak | 731.27 | 0 | 100 | 0 | 0 | 100 | 0 | 0
6671 | 745.93 | 0 | 25.8 | 0 | 0 | 0 | 0 | 8.7263 | 8.7263 | 0 | 0 | 0 | 27.2003 | 754.6563 | 0 | 0.05921 | 8.4079 | 0 | 0 | 140.1082 | 0 | off_peak | 745.93 | 0 | 100 | 0 | 0 | 100 | 0 | 0
6672 | 730.54 | 0 | 25.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27.2003 | 730.54 | 0 | 0.05921 | 8.5504 | 0 | 0 | 140.1082 | 0 | off_peak | 730.54 |  |  | 0 | 0 | 100 | 0 | 0
6673 | 670.89 | 0 | 25.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27.2003 | 670.89 | 0 | 0.05921 | 8.4486 | 0 | 0 | 140.1082 | 0 | off_peak | 670.89 |  |  | 0 | 0 | 100 | 0 | 0
6674 | 588.15 | 0 | 25.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27.2003 | 588.15 | 0 | 0.05921 | 8.0942 | 0 | 0 | 140.1082 | 0 | off_peak | 588.15 |  |  | 0 | 0 | 100 | 0 | 0
6675 | 573.88 | 0 | 25.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27.2003 | 573.88 | 0 | 0.05921 | 7.57 | 0 | 0 | 140.1082 | 0 | off_peak | 573.88 |  |  | 0 | 0 | 100 | 0 | 0
6676 | 557.04 | 0 | 25.3 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 38.7984 | 569.4389 | 0 | 0.05921 | 6.9091 | 0 | 0 | 140.1082 | 0 | off_peak | 557.04 | 0 | 100 | 0 | 0 | 100 | 0 | 0
6677 | 601.03 | 0 | 25.3 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 50.3966 | 613.4289 | 0 | 0.05921 | 6.0275 | 0 | 0 | 140.1082 | 0 | off_peak | 601.03 | 0 | 100 | 0 | 0 | 100 | 0 | 0
6678 | 673.13 | 0 | 25.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50.3966 | 673.13 | 0 | 0.05921 | 5.3886 | 0 | 0 | 140.1082 | 0 | off_peak | 673.13 |  |  | 0 | 0 | 100 | 0 | 0
6679 | 756.14 | 22.4185 | 25.7 | 4.5283 | 0 | 0 | 4.5283 | 12.3989 | 7.8706 | 0 | 0 | 0 | 61.9947 | 764.0106 | 0 | 0.05921 | 4.9124 | 0 | 0 | 144.344 | 0 | off_peak | 756.14 | 36.52 | 63.48 | 0 | 0 | 100 | 0 | 0
6680 | 812.23 | 205.317 | 26.3 | 41.3821 | 28.9832 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 0 | 73.5928 | 783.2468 | 0 | 0.05921 | 4.5887 | 0 | 0 | 155.9422 | 28.9832 | off_peak | 783.2468 | 100 | 0 | 3.57 | 0 | 96.43 | 132.9958 | 0
6681 | 796.96 | 418.143 | 26.9 | 84.0948 | 84.0948 | 0 | 0 | 0.80079 | 0.80079 | 0 | 0 | 0 | 74.3419 | 713.666 | 0 | 0.05921 | 4.3803 | 0 | 0 | 155.9422 | 84.0948 | off_peak | 712.8652 | 0 | 100 | 10.55 | 0 | 89.45 | 368.3634 | 0
6682 | 820.33 | 573.12 | 27.3 | 115.0958 | 115.0958 | 0 | 0 | 0.05172 | 0.05172 | 0 | 0 | 0 | 74.3903 | 705.2859 | 0 | 0.05921 | 4.3093 | 0 | 0 | 155.9422 | 115.0958 | off_peak | 705.2342 | 0 | 100 | 14.03 | 0 | 85.97 | 495.9789 | 0
6683 | 780.46 | 432.814 | 27.7 | 86.7929 | 86.7929 | 0 | 0 | 0.0033404 | 0.0033404 | 0 | 0 | 0 | 74.3934 | 693.6704 | 0 | 0.05921 | 4.4935 | 0 | 0 | 155.9422 | 86.7929 | off_peak | 693.6671 | 0 | 100 | 11.12 | 0 | 88.88 | 390.0053 | 0
6684 | 835.31 | 505.017 | 28 | 101.1615 | 101.1613 | 0 | 0.00021574 | 0.00021574 | 0 | 0 | 0 | 0 | 74.3936 | 734.1487 | 0 | 0.05921 | 4.8612 | 0 | 0 | 155.9424 | 101.1613 | off_peak | 734.1487 | 100 | 0 | 12.11 | 0 | 87.89 | 491.7641 | 0
6685 | 813.14 | 521.169 | 28.1 | 104.3589 | 104.3589 | 0 | 0 | 0 | 0 | 62.63 | 62.63 | 0 | 7.4394 | 646.1511 | 0 | 0.088511 | 5.1896 | 0 | 0 | 155.9424 | 104.3589 | on_peak | 646.1511 |  |  | 12.83 | 7.7 | 79.46 | 541.5811 | 0
6686 | 847.05 | 643.73 | 28.2 | 128.8536 | 128.8536 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 718.1964 | 0 | 0.088511 | 5.348 | 0 | 0 | 155.9424 | 128.8536 | on_peak | 718.1964 |  |  | 15.21 | 0 | 84.79 | 689.1121 | 0
6687 | 865.45 | 477.33 | 28.1 | 95.5806 | 95.5806 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 769.8694 | 0 | 0.088511 | 5.6738 | 0 | 0 | 155.9424 | 95.5806 | on_peak | 769.8694 |  |  | 11.04 | 0 | 88.96 | 542.306 | 0
6688 | 814.9 | 467.784 | 27.8 | 93.7714 | 93.7714 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 721.1286 | 0 | 0.088511 | 6.1058 | 0 | 0 | 155.9424 | 93.7714 | on_peak | 721.1286 |  |  | 11.51 | 0 | 88.49 | 572.55 | 0
6689 | 828.39 | 262.567 | 27.4 | 52.7104 | 52.7104 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 775.6796 | 0 | 0.088511 | 6.5454 | 0 | 0 | 155.9424 | 52.7104 | on_peak | 775.6796 |  |  | 6.36 | 0 | 93.64 | 345.0129 | 0
6690 | 827.76 | 58.6273 | 26.8 | 11.7951 | 11.7951 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 815.9649 | 0 | 0.088511 | 6.9055 | 0 | 0 | 155.9424 | 11.7951 | on_peak | 815.9649 |  |  | 1.42 | 0 | 98.58 | 81.4515 | 0
6691 | 801.04 | 0 | 26.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 801.04 | 0 | 0.088511 | 7.3186 | 0 | 0 | 155.9424 | 0 | on_peak | 801.04 |  |  | 0 | 0 | 100 | 0 | 0
6692 | 807.89 | 0 | 26.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 807.89 | 0 | 0.088511 | 7.7322 | 0 | 0 | 155.9424 | 0 | on_peak | 807.89 |  |  | 0 | 0 | 100 | 0 | 0
6693 | 794.22 | 0 | 26.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 794.22 | 0 | 0.088511 | 7.9898 | 0 | 0 | 155.9424 | 0 | on_peak | 794.22 |  |  | 0 | 0 | 100 | 0 | 0
6694 | 774.59 | 0 | 26 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 774.59 | 0 | 0.05921 | 8.1991 | 0 | 0 | 155.9424 | 0 | off_peak | 774.59 |  |  | 0 | 0 | 100 | 0 | 0
6695 | 764.72 | 0 | 25.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 764.72 | 0 | 0.05921 | 8.317 | 0 | 0 | 155.9424 | 0 | off_peak | 764.72 |  |  | 0 | 0 | 100 | 0 | 0
6696 | 742.9 | 0 | 25.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 742.9 | 0 | 0.05921 | 8.3296 | 0 | 0 | 155.9424 | 0 | off_peak | 742.9 |  |  | 0 | 0 | 100 | 0 | 0
6697 | 673.73 | 0 | 25.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 673.73 | 0 | 0.05921 | 8.0681 | 0 | 0 | 155.9424 | 0 | off_peak | 673.73 |  |  | 0 | 0 | 100 | 0 | 0
6698 | 617.53 | 0 | 25.6 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 19.0375 | 629.9289 | 0 | 0.05921 | 7.7562 | 0 | 0 | 155.9424 | 0 | off_peak | 617.53 | 0 | 100 | 0 | 0 | 100 | 0 | 0
6699 | 593.83 | 0 | 25.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19.0375 | 593.83 | 0 | 0.05921 | 7.2152 | 0 | 0 | 155.9424 | 0 | off_peak | 593.83 |  |  | 0 | 0 | 100 | 0 | 0
6700 | 604.95 | 0 | 25.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19.0375 | 604.95 | 0 | 0.05921 | 6.6788 | 0 | 0 | 155.9424 | 0 | off_peak | 604.95 |  |  | 0 | 0 | 100 | 0 | 0
6701 | 613.6 | 0 | 25.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19.0375 | 613.6 | 0 | 0.05921 | 5.9842 | 0 | 0 | 155.9424 | 0 | off_peak | 613.6 |  |  | 0 | 0 | 100 | 0 | 0
6702 | 704.29 | 0 | 25.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19.0375 | 704.29 | 0 | 0.05921 | 5.4123 | 0 | 0 | 155.9424 | 0 | off_peak | 704.29 |  |  | 0 | 0 | 100 | 0 | 0
6703 | 789.7 | 21.7429 | 25.5 | 4.395 | 0 | 0 | 4.395 | 4.395 | 0 | 0 | 0 | 0 | 23.1487 | 789.7 | 0 | 0.05921 | 5.0368 | 0 | 0 | 160.0535 | 0 | off_peak | 789.7 | 100 | 0 | 0 | 0 | 100 | 0 | 0
6704 | 755.99 | 203.496 | 26.1 | 41.0448 | 41.0448 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 23.1487 | 714.9452 | 0 | 0.05921 | 4.7089 | 0 | 0 | 160.0535 | 41.0448 | off_peak | 714.9452 |  |  | 5.43 | 0 | 94.57 | 193.2769 | 0
6705 | 723.77 | 414.956 | 26.5 | 83.5748 | 83.5748 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 23.1487 | 640.1952 | 0 | 0.05921 | 4.4665 | 0 | 0 | 160.0535 | 83.5748 | off_peak | 640.1952 |  |  | 11.55 | 0 | 88.45 | 373.2875 | 0
6706 | 783.42 | 603.384 | 27 | 121.3055 | 121.3055 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 23.1487 | 662.1145 | 0 | 0.05921 | 4.3171 | 0 | 0 | 160.0535 | 121.3055 | off_peak | 662.1145 |  |  | 15.48 | 0 | 84.52 | 523.6862 | 0
6707 | 737.38 | 744.262 | 27.4 | 149.4109 | 149.4109 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 23.1487 | 587.9691 | 0 | 0.05921 | 4.3179 | 0 | 0 | 160.0535 | 149.4109 | off_peak | 587.9691 |  |  | 20.26 | 0 | 79.74 | 645.1464 | 0
6708 | 763.02 | 823.934 | 27.7 | 165.2249 | 165.2249 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 23.1487 | 597.7951 | 0 | 0.05921 | 4.4002 | 0 | 0 | 160.0535 | 165.2249 | off_peak | 597.7951 |  |  | 21.65 | 0 | 78.35 | 727.0218 | 0
6709 | 758.61 | 700.302 | 27.9 | 140.3306 | 140.3306 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 23.1487 | 618.2794 | 0 | 0.05921 | 4.5597 | 0 | 0 | 160.0535 | 140.3306 | off_peak | 618.2794 |  |  | 18.5 | 0 | 81.5 | 639.8716 | 0
6710 | 734.26 | 763.558 | 28 | 152.9506 | 152.9506 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 23.1487 | 581.3094 | 0 | 0.05921 | 4.8664 | 0 | 0 | 160.0535 | 152.9506 | off_peak | 581.3094 |  |  | 20.83 | 0 | 79.17 | 744.313 | 0
6711 | 737.12 | 650.847 | 28 | 130.3731 | 130.3731 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 23.1487 | 606.7469 | 0 | 0.05921 | 5.2115 | 0 | 0 | 160.0535 | 130.3731 | off_peak | 606.7469 |  |  | 17.69 | 0 | 82.31 | 679.4446 | 0
6712 | 745.06 | 439.556 | 27.8 | 88.1129 | 88.1129 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 23.1487 | 656.9471 | 0 | 0.05921 | 5.5576 | 0 | 0 | 160.0535 | 88.1129 | off_peak | 656.9471 |  |  | 11.83 | 0 | 88.17 | 489.6928 | 0
6713 | 739.05 | 268.823 | 27.3 | 53.9859 | 53.9859 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 23.1487 | 685.0641 | 0 | 0.05921 | 6.0465 | 0 | 0 | 160.0535 | 53.9859 | off_peak | 685.0641 |  |  | 7.3 | 0 | 92.7 | 326.425 | 0
6714 | 672.69 | 67.9294 | 26.6 | 13.6765 | 13.6765 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 23.1487 | 659.0135 | 0 | 0.05921 | 6.6525 | 0 | 0 | 160.0535 | 13.6765 | off_peak | 659.0135 |  |  | 2.03 | 0 | 97.97 | 90.9822 | 0
6715 | 644.79 | 0 | 26.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 23.1487 | 644.79 | 0 | 0.05921 | 7.2651 | 0 | 0 | 160.0535 | 0 | off_peak | 644.79 |  |  | 0 | 0 | 100 | 0 | 0
6716 | 646.07 | 0 | 25.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 23.1487 | 646.07 | 0 | 0.05921 | 7.6726 | 0 | 0 | 160.0535 | 0 | off_peak | 646.07 |  |  | 0 | 0 | 100 | 0 | 0
6717 | 593.07 | 0 | 25.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 23.1487 | 593.07 | 0 | 0.05921 | 7.9281 | 0 | 0 | 160.0535 | 0 | off_peak | 593.07 |  |  | 0 | 0 | 100 | 0 | 0
6718 | 622.69 | 0 | 25.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 23.1487 | 622.69 | 0 | 0.05921 | 8.1634 | 0 | 0 | 160.0535 | 0 | off_peak | 622.69 |  |  | 0 | 0 | 100 | 0 | 0
6719 | 605.98 | 0 | 25.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 23.1487 | 605.98 | 0 | 0.05921 | 8.2269 | 0 | 0 | 160.0535 | 0 | off_peak | 605.98 |  |  | 0 | 0 | 100 | 0 | 0
6720 | 620.6 | 0 | 25.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 23.1487 | 620.6 | 0 | 0.05921 | 8.0435 | 0 | 0 | 160.0535 | 0 | off_peak | 620.6 |  |  | 0 | 0 | 100 | 0 | 0
6721 | 601.83 | 0 | 25.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 23.1487 | 601.83 | 0 | 0.05921 | 7.7637 | 0 | 0 | 160.0535 | 0 | off_peak | 601.83 |  |  | 0 | 0 | 100 | 0 | 0
6722 | 591.87 | 0 | 25.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 23.1487 | 591.87 | 0 | 0.05921 | 7.2691 | 0 | 0 | 160.0535 | 0 | off_peak | 591.87 |  |  | 0 | 0 | 100 | 0 | 0
6723 | 618.99 | 0 | 25.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 23.1487 | 618.99 | 0 | 0.05921 | 6.7729 | 0 | 0 | 160.0535 | 0 | off_peak | 618.99 |  |  | 0 | 0 | 100 | 0 | 0
6724 | 630.14 | 0 | 25.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 23.1487 | 630.14 | 0 | 0.05921 | 6.2367 | 0 | 0 | 160.0535 | 0 | off_peak | 630.14 |  |  | 0 | 0 | 100 | 0 | 0
6725 | 620.78 | 0 | 25.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 23.1487 | 620.78 | 0 | 0.05921 | 5.6819 | 0 | 0 | 160.0535 | 0 | off_peak | 620.78 |  |  | 0 | 0 | 100 | 0 | 0
6726 | 687.8 | 0 | 25.7 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 34.7468 | 700.1989 | 0 | 0.05921 | 5.0726 | 0 | 0 | 160.0535 | 0 | off_peak | 687.8 | 0 | 100 | 0 | 0 | 100 | 0 | 0
6727 | 710.49 | 21.9065 | 25.9 | 4.4217 | 3.7301 | 0 | 0.69158 | 0.69158 | 0 | 0 | 0 | 0 | 35.3937 | 706.7599 | 0 | 0.05921 | 4.6405 | 0 | 0 | 160.7005 | 3.7301 | off_peak | 706.7599 | 100 | 0 | 0.53 | 0 | 99.47 | 17.3096 | 0
6728 | 719.99 | 175.519 | 26.4 | 35.3635 | 35.3635 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 35.3937 | 684.6265 | 0 | 0.05921 | 4.3224 | 0 | 0 | 160.7005 | 35.3635 | off_peak | 684.6265 |  |  | 4.91 | 0 | 95.09 | 152.8555 | 0
6729 | 726.98 | 92.9666 | 26.9 | 18.697 | 18.697 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 35.3937 | 708.283 | 0 | 0.05921 | 4.0911 | 0 | 0 | 160.7005 | 18.697 | off_peak | 708.283 |  |  | 2.57 | 0 | 97.43 | 76.4915 | 0
6730 | 733.34 | 526.793 | 27.5 | 105.7155 | 105.7155 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 35.3937 | 627.6245 | 0 | 0.05921 | 3.9286 | 0 | 0 | 160.7005 | 105.7155 | off_peak | 627.6245 |  |  | 14.42 | 0 | 85.58 | 415.3147 | 0
6731 | 706.55 | 406.249 | 28 | 81.377 | 81.377 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 46.9919 | 637.572 | 0 | 0.05921 | 3.8773 | 0 | 0 | 160.7005 | 81.377 | off_peak | 625.173 | 0 | 100 | 11.52 | 0 | 88.48 | 315.5193 | 0
6732 | 738.75 | 401.063 | 28.4 | 80.2212 | 80.2212 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 58.59 | 670.9278 | 0 | 0.05921 | 3.9185 | 0 | 0 | 160.7005 | 80.2212 | off_peak | 658.5288 | 0 | 100 | 10.86 | 0 | 89.14 | 314.347 | 0
6733 | 736.84 | 344.579 | 28.7 | 68.8478 | 68.8478 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 58.59 | 667.9922 | 0 | 0.05921 | 4.0261 | 0 | 0 | 160.7005 | 68.8478 | off_peak | 667.9922 |  |  | 9.34 | 0 | 90.66 | 277.189 | 0
6734 | 753.04 | 342.844 | 28.7 | 68.5012 | 68.5012 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 58.59 | 684.5388 | 0 | 0.05921 | 4.3417 | 0 | 0 | 160.7005 | 68.5012 | off_peak | 684.5388 |  |  | 9.1 | 0 | 90.9 | 297.41 | 0
6735 | 749.31 | 569.851 | 28.6 | 113.8993 | 113.8993 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 58.59 | 635.4107 | 0 | 0.05921 | 4.6486 | 0 | 0 | 160.7005 | 113.8993 | off_peak | 635.4107 |  |  | 15.2 | 0 | 84.8 | 529.4731 | 0
6736 | 736.32 | 368.407 | 28.4 | 73.6893 | 73.6893 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 70.1882 | 675.0297 | 0 | 0.05921 | 5.0153 | 0 | 0 | 160.7005 | 73.6893 | off_peak | 662.6307 | 0 | 100 | 10.01 | 0 | 89.99 | 369.5737 | 0
6737 | 722.57 | 172.525 | 28.1 | 34.5464 | 34.5464 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 70.1882 | 688.0236 | 0 | 0.05921 | 5.3292 | 0 | 0 | 160.7005 | 34.5464 | off_peak | 688.0236 |  |  | 4.78 | 0 | 95.22 | 184.1049 | 0
6738 | 648.97 | 44.1011 | 27.6 | 8.8469 | 8.8469 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 70.1882 | 640.1231 | 0 | 0.05921 | 5.758 | 0 | 0 | 160.7005 | 8.8469 | off_peak | 640.1231 |  |  | 1.36 | 0 | 98.64 | 50.9407 | 0
6739 | 617.03 | 0 | 27.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 70.1882 | 617.03 | 0 | 0.05921 | 6.2196 | 0 | 0 | 160.7005 | 0 | off_peak | 617.03 |  |  | 0 | 0 | 100 | 0 | 0
6740 | 620.46 | 0 | 27.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 70.1882 | 620.46 | 0 | 0.05921 | 6.4317 | 0 | 0 | 160.7005 | 0 | off_peak | 620.46 |  |  | 0 | 0 | 100 | 0 | 0
6741 | 613.25 | 0 | 27 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 70.1882 | 613.25 | 0 | 0.05921 | 6.5074 | 0 | 0 | 160.7005 | 0 | off_peak | 613.25 |  |  | 0 | 0 | 100 | 0 | 0
6742 | 599.76 | 0 | 27 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 70.1882 | 599.76 | 0 | 0.05921 | 6.5817 | 0 | 0 | 160.7005 | 0 | off_peak | 599.76 |  |  | 0 | 0 | 100 | 0 | 0
6743 | 612.72 | 0 | 26.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 70.1882 | 612.72 | 0 | 0.05921 | 6.6769 | 0 | 0 | 160.7005 | 0 | off_peak | 612.72 |  |  | 0 | 0 | 100 | 0 | 0
6744 | 610.91 | 0 | 26.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 70.1882 | 610.91 | 0 | 0.05921 | 6.8442 | 0 | 0 | 160.7005 | 0 | off_peak | 610.91 |  |  | 0 | 0 | 100 | 0 | 0
6745 | 582.95 | 0 | 26.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 70.1882 | 582.95 | 0 | 0.05921 | 6.9482 | 0 | 0 | 160.7005 | 0 | off_peak | 582.95 |  |  | 0 | 0 | 100 | 0 | 0
6746 | 602.19 | 0 | 26.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 70.1882 | 602.19 | 0 | 0.05921 | 6.6225 | 0 | 0 | 160.7005 | 0 | off_peak | 602.19 |  |  | 0 | 0 | 100 | 0 | 0
6747 | 588.63 | 0 | 26.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 70.1882 | 588.63 | 0 | 0.05921 | 6.1179 | 0 | 0 | 160.7005 | 0 | off_peak | 588.63 |  |  | 0 | 0 | 100 | 0 | 0
6748 | 597.37 | 0 | 26.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 70.1882 | 597.37 | 0 | 0.05921 | 5.5232 | 0 | 0 | 160.7005 | 0 | off_peak | 597.37 |  |  | 0 | 0 | 100 | 0 | 0
6749 | 624.27 | 0 | 26.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 70.1882 | 624.27 | 0 | 0.05921 | 4.9292 | 0 | 0 | 160.7005 | 0 | off_peak | 624.27 |  |  | 0 | 0 | 100 | 0 | 0
6750 | 674.35 | 0 | 26.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 70.1882 | 674.35 | 0 | 0.05921 | 4.431 | 0 | 0 | 160.7005 | 0 | off_peak | 674.35 |  |  | 0 | 0 | 100 | 0 | 0
6751 | 798.56 | 20.9108 | 26.9 | 4.2055 | 0 | 0 | 4.2055 | 4.2055 | 0 | 0 | 0 | 0 | 74.122 | 798.56 | 0 | 0.05921 | 4.0509 | 0 | 0 | 164.6343 | 0 | off_peak | 798.56 | 100 | 0 | 0 | 0 | 100 | 0 | 0
6752 | 788.15 | 189.989 | 27.3 | 38.1542 | 38.1542 | 0 | 0 | 0.27161 | 0.27161 | 0 | 0 | 0 | 74.3761 | 750.2674 | 0 | 0.05921 | 3.7925 | 0 | 0 | 164.6343 | 38.1542 | off_peak | 749.9958 | 0 | 100 | 4.84 | 0 | 95.16 | 144.7016 | 0
6753 | 841.21 | 172.823 | 27.7 | 34.6565 | 34.6565 | 0 | 0 | 0.017542 | 0.017542 | 0 | 0 | 0 | 74.3925 | 806.5711 | 0 | 0.05921 | 3.6344 | 0 | 0 | 164.6343 | 34.6565 | off_peak | 806.5535 | 0 | 100 | 4.12 | 0 | 95.88 | 125.9546 | 0
6754 | 843.57 | 542.433 | 28.1 | 108.6168 | 108.6168 | 0 | 0 | 0.001133 | 0.001133 | 0 | 0 | 0 | 74.3936 | 734.9543 | 0 | 0.05921 | 3.6323 | 0 | 0 | 164.6343 | 108.6168 | off_peak | 734.9532 | 0 | 100 | 12.88 | 0 | 87.12 | 394.53 | 0
6755 | 837.41 | 448.914 | 28.4 | 89.7924 | 89.7924 | 0 | 0 | 7.3174e-05 | 7.3174e-05 | 0 | 0 | 0 | 74.3936 | 747.6177 | 0 | 0.05921 | 3.8622 | 0 | 0 | 164.6343 | 89.7924 | off_peak | 747.6176 | 0 | 100 | 10.72 | 0 | 89.28 | 346.7937 | 0
6756 | 867.69 | 119.539 | 28.5 | 23.9016 | 23.9016 | 0 | 0 | 0 | 0 | 1.6266 | 1.6266 | 0 | 72.6547 | 842.1617 | 0 | 0.05921 | 4.2868 | 0 | 0 | 164.6343 | 23.9016 | off_peak | 842.1617 |  |  | 2.75 | 0.19 | 97.06 | 102.4626 | 0
6757 | 774.11 | 33.25 | 28.5 | 6.6483 | 6.6483 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 72.6547 | 767.4617 | 0 | 0.088511 | 4.6556 | 0 | 0 | 164.6343 | 6.6483 | on_peak | 767.4617 |  |  | 0.86 | 0 | 99.14 | 30.9516 | 0
6758 | 859.37 | 43.7 | 28.5 | 8.7377 | 8.7377 | 0 | 0 | 0 | 0 | 54.4002 | 54.4002 | 0 | 14.4985 | 796.232 | 0 | 0.088511 | 4.5038 | 0 | 0 | 164.6343 | 8.7377 | on_peak | 796.232 |  |  | 1.02 | 6.33 | 92.65 | 39.3528 | 0
6759 | 850.39 | 60.8 | 28.3 | 12.1657 | 12.1657 | 0 | 0 | 0 | 0 | 6.6032 | 6.6032 | 0 | 7.4394 | 831.6211 | 0 | 0.088511 | 4.4526 | 0 | 0 | 164.6343 | 12.1657 | on_peak | 831.6211 |  |  | 1.43 | 0.78 | 97.79 | 54.1687 | 0
6760 | 796.79 | 302.461 | 28.1 | 60.5648 | 60.5648 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 736.2252 | 0 | 0.088511 | 4.7647 | 0 | 0 | 164.6343 | 60.5648 | on_peak | 736.2252 |  |  | 7.6 | 0 | 92.4 | 288.5758 | 0
6761 | 828.73 | 155.628 | 27.8 | 31.197 | 31.197 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 797.533 | 0 | 0.088511 | 5.0289 | 0 | 0 | 164.6343 | 31.197 | on_peak | 797.533 |  |  | 3.76 | 0 | 96.24 | 156.8868 | 0
6762 | 807.3 | 27.6467 | 27.4 | 5.5501 | 5.5501 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 801.7499 | 0 | 0.088511 | 5.2603 | 0 | 0 | 164.6343 | 5.5501 | on_peak | 801.7499 |  |  | 0.69 | 0 | 99.31 | 29.1951 | 0
6763 | 772.79 | 0 | 27.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 772.79 | 0 | 0.088511 | 5.4639 | 0 | 0 | 164.6343 | 0 | on_peak | 772.79 |  |  | 0 | 0 | 100 | 0 | 0
6764 | 800.02 | 0 | 27 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 800.02 | 0 | 0.088511 | 5.5595 | 0 | 0 | 164.6343 | 0 | on_peak | 800.02 |  |  | 0 | 0 | 100 | 0 | 0
6765 | 762.71 | 0 | 27 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 762.71 | 0 | 0.088511 | 5.6242 | 0 | 0 | 164.6343 | 0 | on_peak | 762.71 |  |  | 0 | 0 | 100 | 0 | 0
6766 | 777.89 | 0 | 26.9 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 19.0375 | 790.2889 | 0 | 0.05921 | 5.7884 | 0 | 0 | 164.6343 | 0 | off_peak | 777.89 | 0 | 100 | 0 | 0 | 100 | 0 | 0
6767 | 768.61 | 0 | 26.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19.0375 | 768.61 | 0 | 0.05921 | 6.111 | 0 | 0 | 164.6343 | 0 | off_peak | 768.61 |  |  | 0 | 0 | 100 | 0 | 0
6768 | 696.77 | 0 | 26.9 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 30.6357 | 709.1689 | 0 | 0.05921 | 6.4245 | 0 | 0 | 164.6343 | 0 | off_peak | 696.77 | 0 | 100 | 0 | 0 | 100 | 0 | 0
6769 | 660.18 | 0 | 26.9 | 0 | 0 | 0 | 0 | 5.1769 | 5.1769 | 0 | 0 | 0 | 35.4782 | 665.3569 | 0 | 0.05921 | 6.6319 | 0 | 0 | 164.6343 | 0 | off_peak | 660.18 | 0 | 100 | 0 | 0 | 100 | 0 | 0
6770 | 595.52 | 0 | 26.9 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 47.0764 | 607.9189 | 0 | 0.05921 | 6.3665 | 0 | 0 | 164.6343 | 0 | off_peak | 595.52 | 0 | 100 | 0 | 0 | 100 | 0 | 0
6771 | 601.43 | 0 | 27 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 58.6745 | 613.8289 | 0 | 0.05921 | 5.9109 | 0 | 0 | 164.6343 | 0 | off_peak | 601.43 | 0 | 100 | 0 | 0 | 100 | 0 | 0
6772 | 612.06 | 0 | 27 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 70.2727 | 624.4589 | 0 | 0.05921 | 5.3245 | 0 | 0 | 164.6343 | 0 | off_peak | 612.06 | 0 | 100 | 0 | 0 | 100 | 0 | 0
6773 | 589.52 | 0 | 27.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 70.2727 | 589.52 | 0 | 0.05921 | 4.6979 | 0 | 0 | 164.6343 | 0 | off_peak | 589.52 |  |  | 0 | 0 | 100 | 0 | 0
6774 | 673.84 | 0 | 27.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 70.2727 | 673.84 | 0 | 0.05921 | 4.2281 | 0 | 0 | 164.6343 | 0 | off_peak | 673.84 |  |  | 0 | 0 | 100 | 0 | 0
6775 | 740.11 | 20.5278 | 27.4 | 4.121 | 0 | 0 | 4.121 | 4.121 | 0 | 0 | 0 | 0 | 74.1275 | 740.11 | 0 | 0.05921 | 3.8723 | 0 | 0 | 168.4891 | 0 | off_peak | 740.11 | 100 | 0 | 0 | 0 | 100 | 0 | 0
6776 | 762.13 | 192.262 | 27.9 | 38.5266 | 38.5266 | 0 | 0 | 0.26616 | 0.26616 | 0 | 0 | 0 | 74.3765 | 723.8696 | 0 | 0.05921 | 3.6465 | 0 | 0 | 168.4891 | 38.5266 | off_peak | 723.6034 | 0 | 100 | 5.06 | 0 | 94.94 | 140.4854 | 0
6777 | 783.53 | 340.794 | 28.3 | 68.1909 | 68.1909 | 0 | 0 | 0.01719 | 0.01719 | 0 | 0 | 0 | 74.3925 | 715.3563 | 0 | 0.05921 | 3.5388 | 0 | 0 | 168.4891 | 68.1909 | off_peak | 715.3391 | 0 | 100 | 8.7 | 0 | 91.3 | 241.3167 | 0
6778 | 804.18 | 569.441 | 28.7 | 113.7758 | 113.7758 | 0 | 0 | 0.0011102 | 0.0011102 | 0 | 0 | 0 | 74.3936 | 690.4053 | 0 | 0.05921 | 3.5365 | 0 | 0 | 168.4891 | 113.7758 | off_peak | 690.4042 | 0 | 100 | 14.15 | 0 | 85.85 | 402.3669 | 0
6779 | 810.67 | 720.957 | 29.1 | 143.8389 | 143.8389 | 0 | 0 | 7.1704e-05 | 7.1704e-05 | 0 | 0 | 0 | 74.3936 | 666.8311 | 0 | 0.05921 | 3.7987 | 0 | 0 | 168.4891 | 143.8389 | off_peak | 666.8311 | 0 | 100 | 17.74 | 0 | 82.26 | 546.4057 | 0
6780 | 868.78 | 713.043 | 29.5 | 142.0521 | 142.0521 | 0 | 0 | 4.631e-06 | 4.631e-06 | 0 | 0 | 0 | 74.3936 | 726.7279 | 0 | 0.05921 | 4.2763 | 0 | 0 | 168.4891 | 142.0521 | off_peak | 726.7279 | 0 | 100 | 16.35 | 0 | 83.65 | 607.4536 | 0
6781 | 816.76 | 787.527 | 29.6 | 156.8333 | 156.8333 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 659.9267 | 0 | 0.088511 | 4.4577 | 0 | 0 | 168.4891 | 156.8333 | on_peak | 659.9267 |  |  | 19.2 | 0 | 80.8 | 699.1119 | 0
6782 | 867.36 | 687.253 | 29.7 | 136.814 | 136.814 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 730.546 | 0 | 0.088511 | 4.4858 | 0 | 0 | 168.4891 | 136.814 | on_peak | 730.546 |  |  | 15.77 | 0 | 84.23 | 613.7183 | 0
6783 | 838.85 | 628.162 | 29.7 | 125.0505 | 125.0505 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 713.7995 | 0 | 0.088511 | 4.5179 | 0 | 0 | 168.4891 | 125.0505 | on_peak | 713.7995 |  |  | 14.91 | 0 | 85.09 | 564.9635 | 0
6784 | 804.62 | 455.64 | 29.6 | 90.7392 | 90.7392 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 713.8808 | 0 | 0.088511 | 4.8728 | 0 | 0 | 168.4891 | 90.7392 | on_peak | 713.8808 |  |  | 11.28 | 0 | 88.72 | 442.1504 | 0
6785 | 868.76 | 250.812 | 29.2 | 50.0215 | 50.0215 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 818.7385 | 0 | 0.088511 | 5.2121 | 0 | 0 | 168.4891 | 50.0215 | on_peak | 818.7385 |  |  | 5.76 | 0 | 94.24 | 260.7161 | 0
6786 | 839.51 | 55.658 | 28.7 | 11.1206 | 11.1206 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 828.3894 | 0 | 0.088511 | 5.5121 | 0 | 0 | 168.4891 | 11.1206 | on_peak | 828.3894 |  |  | 1.32 | 0 | 98.68 | 61.2979 | 0
6787 | 839.7 | 0 | 28.2 | 0 | 0 | 0 | 0 | 0 | 0 | 51.3011 | 51.3011 | 0 | 19.5505 | 788.3989 | 0 | 0.088511 | 6.0333 | 51.3011 | 0 | 113.646 | 51.3011 | on_peak | 788.3989 |  |  | 0 | 6.11 | 93.89 | 309.5125 | 0
6788 | 842.95 | 0 | 28 | 0 | 0 | 0 | 0 | 0 | 0 | 11.3289 | 11.3289 | 0 | 7.4394 | 831.6211 | 0 | 0.088511 | 6.4557 | 0 | 0 | 113.646 | 0 | on_peak | 831.6211 |  |  | 0 | 1.34 | 98.66 | 0 | 0
6789 | 825.9 | 0 | 27.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 825.9 | 0 | 0.088511 | 6.8415 | 0 | 0 | 113.646 | 0 | on_peak | 825.9 |  |  | 0 | 0 | 100 | 0 | 0
6790 | 778.66 | 0 | 27.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 778.66 | 0 | 0.05921 | 7.2547 | 0 | 0 | 113.646 | 0 | off_peak | 778.66 |  |  | 0 | 0 | 100 | 0 | 0
6791 | 792.66 | 0 | 27.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 792.66 | 0 | 0.05921 | 7.6124 | 0 | 0 | 113.646 | 0 | off_peak | 792.66 |  |  | 0 | 0 | 100 | 0 | 0
6792 | 751.3 | 0 | 27.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 751.3 | 0 | 0.05921 | 7.7636 | 0 | 0 | 113.646 | 0 | off_peak | 751.3 |  |  | 0 | 0 | 100 | 0 | 0
6793 | 666.08 | 0 | 27.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 666.08 | 0 | 0.05921 | 7.8072 | 0 | 0 | 113.646 | 0 | off_peak | 666.08 |  |  | 0 | 0 | 100 | 0 | 0
6794 | 620.27 | 0 | 27.3 | 0 | 0 | 0 | 0 | 8.7263 | 8.7263 | 0 | 0 | 0 | 15.6021 | 628.9963 | 0 | 0.05921 | 7.3915 | 0 | 0 | 113.646 | 0 | off_peak | 620.27 | 0 | 100 | 0 | 0 | 100 | 0 | 0
6795 | 616.58 | 0 | 27.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15.6021 | 616.58 | 0 | 0.05921 | 6.9186 | 0 | 0 | 113.646 | 0 | off_peak | 616.58 |  |  | 0 | 0 | 100 | 0 | 0
6796 | 612.55 | 0 | 27.4 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 27.2003 | 624.9489 | 0 | 0.05921 | 6.3172 | 0 | 0 | 113.646 | 0 | off_peak | 612.55 | 0 | 100 | 0 | 0 | 100 | 0 | 0
6797 | 628.55 | 0 | 27.4 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 38.7984 | 640.9489 | 0 | 0.05921 | 5.6306 | 0 | 0 | 113.646 | 0 | off_peak | 628.55 | 0 | 100 | 0 | 0 | 100 | 0 | 0
6798 | 697.56 | 0 | 27.4 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 50.3966 | 709.9589 | 0 | 0.05921 | 5.0871 | 0 | 0 | 113.646 | 0 | off_peak | 697.56 | 0 | 100 | 0 | 0 | 100 | 0 | 0
6799 | 715.45 | 19.8476 | 27.7 | 3.9801 | 0 | 0 | 3.9801 | 12.3989 | 8.4189 | 0 | 0 | 0 | 61.9947 | 723.8689 | 0 | 0.05921 | 4.6804 | 0 | 0 | 117.369 | 0 | off_peak | 715.45 | 32.1 | 67.9 | 0 | 0 | 100 | 0 | 0
6800 | 794.29 | 190.669 | 28.3 | 38.1518 | 38.1518 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 73.5928 | 768.5372 | 0 | 0.05921 | 4.3996 | 0 | 0 | 117.369 | 38.1518 | off_peak | 756.1382 | 0 | 100 | 4.8 | 0 | 95.2 | 167.8518 | 0
6801 | 748.11 | 399.053 | 28.7 | 79.7319 | 79.7319 | 0 | 0 | 0.80079 | 0.80079 | 0 | 0 | 0 | 74.3419 | 669.1789 | 0 | 0.05921 | 4.2424 | 0 | 0 | 117.369 | 79.7319 | off_peak | 668.3781 | 0 | 100 | 10.66 | 0 | 89.34 | 338.2571 | 0
6802 | 793.25 | 517.76 | 29.1 | 103.2989 | 103.2989 | 0 | 0 | 0.05172 | 0.05172 | 0 | 0 | 0 | 74.3903 | 690.0029 | 0 | 0.05921 | 4.2261 | 0 | 0 | 117.369 | 103.2989 | off_peak | 689.9511 | 0 | 100 | 13.02 | 0 | 86.98 | 436.5548 | 0
6803 | 774.9 | 613.731 | 29.4 | 122.3119 | 122.3119 | 0 | 0 | 0.0033404 | 0.0033404 | 0 | 0 | 0 | 74.3934 | 652.5914 | 0 | 0.05921 | 4.4451 | 0 | 0 | 117.369 | 122.3119 | off_peak | 652.5881 | 0 | 100 | 15.78 | 0 | 84.22 | 543.6879 | 0
6804 | 826.74 | 728.682 | 29.6 | 145.1145 | 145.1145 | 0 | 0 | 0.00021574 | 0.00021574 | 0 | 0 | 0 | 74.3936 | 681.6257 | 0 | 0.05921 | 4.8841 | 0 | 0 | 117.369 | 145.1145 | off_peak | 681.6255 | 0 | 100 | 17.55 | 0 | 82.45 | 708.7549 | 0
6805 | 792.39 | 747.408 | 29.6 | 148.8438 | 148.8438 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 643.5462 | 0 | 0.088511 | 5.0767 | 0 | 0 | 117.369 | 148.8438 | on_peak | 643.5462 |  |  | 18.78 | 0 | 81.22 | 755.6379 | 0
6806 | 802.13 | 644.165 | 29.6 | 128.2833 | 128.2833 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 673.8467 | 0 | 0.088511 | 5.3015 | 0 | 0 | 117.369 | 128.2833 | on_peak | 673.8467 |  |  | 15.99 | 0 | 84.01 | 680.0893 | 0
6807 | 806.22 | 616.677 | 29.5 | 122.8541 | 122.8541 | 0 | 0 | 0 | 0 | 62.63 | 62.63 | 0 | 7.4394 | 620.7359 | 0 | 0.088511 | 5.6372 | 62.63 | 0 | 50.4147 | 185.4841 | on_peak | 620.7359 |  |  | 15.24 | 7.77 | 76.99 | 1045.6138 | 0
6808 | 748.29 | 441.536 | 29.2 | 88.0591 | 88.0591 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 660.2309 | 0 | 0.088511 | 5.9807 | 0 | 0 | 50.4147 | 88.0591 | on_peak | 660.2309 |  |  | 11.77 | 0 | 88.23 | 526.6561 | 0
6809 | 778.02 | 244.132 | 28.8 | 48.7604 | 48.7604 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 729.2596 | 0 | 0.088511 | 6.1936 | 0 | 0 | 50.4147 | 48.7604 | on_peak | 729.2596 |  |  | 6.27 | 0 | 93.73 | 302.0049 | 0
6810 | 793.82 | 50.0312 | 28.3 | 10.011 | 10.011 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 783.809 | 0 | 0.088511 | 6.5253 | 0 | 0 | 50.4147 | 10.011 | on_peak | 783.809 |  |  | 1.26 | 0 | 98.74 | 65.324 | 0
6811 | 773.99 | 0 | 28 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 773.99 | 0 | 0.088511 | 7.0167 | 0 | 0 | 50.4147 | 0 | on_peak | 773.99 |  |  | 0 | 0 | 100 | 0 | 0
6812 | 783.46 | 0 | 27.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 783.46 | 0 | 0.088511 | 7.2446 | 0 | 0 | 50.4147 | 0 | on_peak | 783.46 |  |  | 0 | 0 | 100 | 0 | 0
6813 | 781.1 | 0 | 27.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 781.1 | 0 | 0.088511 | 7.5018 | 0 | 0 | 50.4147 | 0 | on_peak | 781.1 |  |  | 0 | 0 | 100 | 0 | 0
6814 | 725.72 | 0 | 27.7 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 19.0375 | 738.1189 | 0 | 0.05921 | 7.6857 | 0 | 0 | 50.4147 | 0 | off_peak | 725.72 | 0 | 100 | 0 | 0 | 100 | 0 | 0
6815 | 769.93 | 0 | 27.6 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 30.6357 | 782.3289 | 0 | 0.05921 | 7.5865 | 0 | 0 | 50.4147 | 0 | off_peak | 769.93 | 0 | 100 | 0 | 0 | 100 | 0 | 0
6816 | 718.73 | 0 | 27.6 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 42.2338 | 731.1289 | 0 | 0.05921 | 7.5395 | 0 | 0 | 50.4147 | 0 | off_peak | 718.73 | 0 | 100 | 0 | 0 | 100 | 0 | 0
6817 | 697.41 | 0 | 27.5 | 0 | 0 | 0 | 0 | 8.7263 | 8.7263 | 0 | 0 | 0 | 50.3966 | 706.1363 | 0 | 0.05921 | 7.6042 | 0 | 0 | 50.4147 | 0 | off_peak | 697.41 | 0 | 100 | 0 | 0 | 100 | 0 | 0
6818 | 597.59 | 0 | 27.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50.3966 | 597.59 | 0 | 0.05921 | 7.2627 | 0 | 0 | 50.4147 | 0 | off_peak | 597.59 |  |  | 0 | 0 | 100 | 0 | 0
6819 | 615.41 | 0 | 27.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50.3966 | 615.41 | 0 | 0.05921 | 6.9649 | 0 | 0 | 50.4147 | 0 | off_peak | 615.41 |  |  | 0 | 0 | 100 | 0 | 0
6820 | 599.27 | 0 | 27.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50.3966 | 599.27 | 0 | 0.05921 | 6.5033 | 0 | 0 | 50.4147 | 0 | off_peak | 599.27 |  |  | 0 | 0 | 100 | 0 | 0
6821 | 605.35 | 0 | 27.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50.3966 | 605.35 | 0 | 0.05921 | 5.9497 | 0 | 0 | 50.4147 | 0 | off_peak | 605.35 |  |  | 0 | 0 | 100 | 0 | 0
6822 | 656.42 | 0 | 27.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50.3966 | 656.42 | 0 | 0.05921 | 5.5123 | 0 | 0 | 50.4147 | 0 | off_peak | 656.42 |  |  | 0 | 0 | 100 | 0 | 0
6823 | 677.65 | 12.3831 | 27.7 | 2.4832 | 0 | 0 | 2.4832 | 12.3989 | 9.9157 | 0 | 0 | 0 | 61.9947 | 687.5657 | 0 | 0.05921 | 5.2042 | 0 | 0 | 52.7375 | 0 | off_peak | 677.65 | 20.03 | 79.97 | 0 | 0 | 100 | 0 | 0
6824 | 808.29 | 134.428 | 28.2 | 26.9081 | 14.5091 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 0 | 73.5928 | 793.7809 | 0 | 0.05921 | 5.0447 | 0 | 0 | 64.3357 | 14.5091 | off_peak | 793.7809 | 100 | 0 | 1.8 | 0 | 98.2 | 73.1945 | 0
6825 | 800.8 | 283.67 | 28.5 | 56.7194 | 56.7194 | 0 | 0 | 0.80079 | 0.80079 | 0 | 0 | 0 | 74.3419 | 744.8814 | 0 | 0.05921 | 4.9947 | 0 | 0 | 64.3357 | 56.7194 | off_peak | 744.0806 | 0 | 100 | 7.08 | 0 | 92.92 | 283.2968 | 0
6826 | 792.57 | 504.087 | 28.8 | 100.6812 | 100.6812 | 0 | 0 | 0.05172 | 0.05172 | 0 | 0 | 0 | 74.3903 | 691.9405 | 0 | 0.05921 | 5.0597 | 0 | 0 | 64.3357 | 100.6812 | off_peak | 691.8888 | 0 | 100 | 12.7 | 0 | 87.3 | 509.4189 | 0
6827 | 823.4 | 571.211 | 29 | 114.0046 | 114.0046 | 0 | 0 | 0.0033404 | 0.0033404 | 0 | 0 | 0 | 74.3934 | 709.3988 | 0 | 0.05921 | 5.3681 | 0 | 0 | 64.3357 | 114.0046 | off_peak | 709.3954 | 0 | 100 | 13.85 | 0 | 86.15 | 611.9869 | 0
6828 | 829.86 | 790.278 | 29.2 | 157.6116 | 157.6116 | 0 | 0 | 0.00021574 | 0.00021574 | 0 | 0 | 0 | 74.3936 | 672.2486 | 0 | 0.05921 | 5.8516 | 0 | 0 | 64.3357 | 157.6116 | off_peak | 672.2484 | 0 | 100 | 18.99 | 0 | 81.01 | 922.2761 | 0
6829 | 847.19 | 780.256 | 29.3 | 155.556 | 155.556 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 691.634 | 0 | 0.088511 | 6.0286 | 0 | 0 | 64.3357 | 155.556 | on_peak | 691.634 |  |  | 18.36 | 0 | 81.64 | 937.7835 | 0
6830 | 898.99 | 668.439 | 29.4 | 133.2148 | 133.2148 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 765.7752 | 0 | 0.088511 | 6.1546 | 0 | 0 | 64.3357 | 133.2148 | on_peak | 765.7752 |  |  | 14.82 | 0 | 85.18 | 819.8791 | 0
6831 | 868.84 | 389.4 | 29.3 | 77.6328 | 77.6328 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 791.2072 | 0 | 0.088511 | 6.5222 | 0 | 0 | 64.3357 | 77.6328 | on_peak | 791.2072 |  |  | 8.94 | 0 | 91.06 | 506.3348 | 0
6832 | 821.47 | 391.979 | 29.1 | 78.2042 | 78.2042 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 743.2658 | 0 | 0.088511 | 6.9809 | 0 | 0 | 64.3357 | 78.2042 | on_peak | 743.2658 |  |  | 9.52 | 0 | 90.48 | 545.9377 | 0
6833 | 837.35 | 209.337 | 28.8 | 41.8108 | 41.8108 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 795.5392 | 0 | 0.088511 | 7.3223 | 0 | 0 | 64.3357 | 41.8108 | on_peak | 795.5392 |  |  | 4.99 | 0 | 95.01 | 306.1516 | 0
6834 | 860.67 | 21.85 | 28.3 | 4.3721 | 4.3721 | 0 | 0 | 0 | 0 | 62.3611 | 62.3611 | 0 | 7.7268 | 793.9369 | 0 | 0.088511 | 7.4873 | 0 | 0 | 64.3357 | 4.3721 | on_peak | 793.9369 |  |  | 0.51 | 7.25 | 92.25 | 32.7348 | 0
6835 | 812.46 | 0 | 28 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.7268 | 812.46 | 0 | 0.088511 | 7.6433 | 0 | 0 | 64.3357 | 0 | on_peak | 812.46 |  |  | 0 | 0 | 100 | 0 | 0
6836 | 827.9 | 0 | 27.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.7268 | 827.9 | 0 | 0.088511 | 7.9658 | 0 | 0 | 64.3357 | 0 | on_peak | 827.9 |  |  | 0 | 0 | 100 | 0 | 0
6837 | 831.89 | 0 | 27.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0.26891 | 0.26891 | 0 | 7.4394 | 831.6211 | 0 | 0.088511 | 8.1389 | 0 | 0 | 64.3357 | 0 | on_peak | 831.6211 |  |  | 0 | 0.03 | 99.97 | 0 | 0
6838 | 787.58 | 0 | 27.7 | 0 | 0 | 0 | 0 | 8.7263 | 8.7263 | 0 | 0 | 0 | 15.6021 | 796.3063 | 0 | 0.05921 | 8.3388 | 0 | 0 | 64.3357 | 0 | off_peak | 787.58 | 0 | 100 | 0 | 0 | 100 | 0 | 0
6839 | 824.6 | 0 | 27.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15.6021 | 824.6 | 0 | 0.05921 | 8.4149 | 0 | 0 | 64.3357 | 0 | off_peak | 824.6 |  |  | 0 | 0 | 100 | 0 | 0
6840 | 777.62 | 0 | 27.6 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 27.2003 | 790.0189 | 0 | 0.05921 | 8.2733 | 0 | 0 | 64.3357 | 0 | off_peak | 777.62 | 0 | 100 | 0 | 0 | 100 | 0 | 0
6841 | 698.89 | 0 | 27.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27.2003 | 698.89 | 0 | 0.05921 | 8.2347 | 0 | 0 | 64.3357 | 0 | off_peak | 698.89 |  |  | 0 | 0 | 100 | 0 | 0
6842 | 636.34 | 0 | 27.5 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 38.7984 | 648.7389 | 0 | 0.05921 | 7.9874 | 0 | 0 | 64.3357 | 0 | off_peak | 636.34 | 0 | 100 | 0 | 0 | 100 | 0 | 0
6843 | 609.58 | 0 | 27.5 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 50.3966 | 621.9789 | 0 | 0.05921 | 7.5787 | 0 | 0 | 64.3357 | 0 | off_peak | 609.58 | 0 | 100 | 0 | 0 | 100 | 0 | 0
6844 | 663.46 | 0 | 27.4 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 61.9947 | 675.8589 | 0 | 0.05921 | 7.0214 | 0 | 0 | 64.3357 | 0 | off_peak | 663.46 | 0 | 100 | 0 | 0 | 100 | 0 | 0
6845 | 618.89 | 0 | 27.5 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 73.5928 | 631.2889 | 0 | 0.05921 | 6.3716 | 0 | 0 | 64.3357 | 0 | off_peak | 618.89 | 0 | 100 | 0 | 0 | 100 | 0 | 0
6846 | 666.06 | 0 | 27.5 | 0 | 0 | 0 | 0 | 0.80079 | 0.80079 | 0 | 0 | 0 | 74.3419 | 666.8608 | 0 | 0.05921 | 5.9058 | 0 | 0 | 64.3357 | 0 | off_peak | 666.06 | 0 | 100 | 0 | 0 | 100 | 0 | 0
6847 | 710.96 | 15.9109 | 27.7 | 3.1906 | 3.1906 | 0 | 0 | 0.05172 | 0.05172 | 0 | 0 | 0 | 74.3903 | 707.8211 | 0 | 0.05921 | 5.5402 | 0 | 0 | 64.3357 | 3.1906 | off_peak | 707.7694 | 0 | 100 | 0.45 | 0 | 99.55 | 17.6768 | 0
6848 | 866.72 | 188.935 | 28.1 | 37.8324 | 37.829 | 0 | 0.0033404 | 0.0033404 | 0 | 0 | 0 | 0 | 74.3934 | 828.891 | 0 | 0.05921 | 5.275 | 0 | 0 | 64.3388 | 37.829 | off_peak | 828.891 | 100 | 0 | 4.36 | 0 | 95.64 | 199.5478 | 0
6849 | 899.1 | 392.408 | 28.4 | 78.49 | 78.49 | 0 | 0 | 0.00021574 | 0.00021574 | 0 | 0 | 0 | 74.3936 | 820.6102 | 0 | 0.05921 | 5.1205 | 0 | 0 | 64.3388 | 78.49 | off_peak | 820.61 | 0 | 100 | 8.73 | 0 | 91.27 | 401.9084 | 0
6850 | 870.22 | 520.935 | 28.6 | 104.1222 | 104.1222 | 0 | 0 | 1.3934e-05 | 1.3934e-05 | 0 | 0 | 0 | 74.3936 | 766.0978 | 0 | 0.05921 | 5.1247 | 0 | 0 | 64.3388 | 104.1222 | off_peak | 766.0978 | 0 | 100 | 11.97 | 0 | 88.03 | 533.5945 | 0
6851 | 853.34 | 407.549 | 28.5 | 81.4888 | 81.4888 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 771.8512 | 0 | 0.05921 | 5.3918 | 0 | 0 | 64.3388 | 81.4888 | off_peak | 771.8512 |  |  | 9.55 | 0 | 90.45 | 439.3684 | 0
6852 | 923.72 | 270.18 | 28.4 | 54.0418 | 54.0418 | 0 | 0 | 0 | 0 | 27.5165 | 27.5165 | 0 | 44.9773 | 842.1617 | 0 | 0.05921 | 5.7229 | 0 | 0 | 64.3388 | 54.0418 | off_peak | 842.1617 |  |  | 5.85 | 2.98 | 91.17 | 309.2767 | 0
6853 | 825.01 | 83.6 | 28.2 | 16.734 | 4.335 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 0 | 56.5754 | 820.675 | 0 | 0.088511 | 5.8573 | 0 | 0 | 75.937 | 4.335 | on_peak | 820.675 | 100 | 0 | 0.53 | 0 | 99.47 | 25.3917 | 0
6854 | 874.06 | 81.7 | 28 | 16.3656 | 16.3656 | 0 | 0 | 0 | 0 | 26.0733 | 26.0733 | 0 | 28.7019 | 831.6211 | 0 | 0.088511 | 6.1461 | 0 | 0 | 75.937 | 16.3656 | on_peak | 831.6211 |  |  | 1.87 | 2.98 | 95.14 | 100.5848 | 0
6855 | 880.72 | 145.661 | 27.7 | 29.2096 | 29.2096 | 0 | 0 | 0 | 0 | 19.8893 | 19.8893 | 0 | 7.4394 | 831.6211 | 0 | 0.088511 | 6.4637 | 0 | 0 | 75.937 | 29.2096 | on_peak | 831.6211 |  |  | 3.32 | 2.26 | 94.43 | 188.8027 | 0
6856 | 815.98 | 160.603 | 27.3 | 32.2528 | 32.2528 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 783.7272 | 0 | 0.088511 | 6.7994 | 0 | 0 | 75.937 | 32.2528 | on_peak | 783.7272 |  |  | 3.95 | 0 | 96.05 | 219.2986 | 0
6857 | 807.77 | 26.6 | 26.9 | 5.3497 | 5.3497 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 802.4203 | 0 | 0.088511 | 7.1329 | 0 | 0 | 75.937 | 5.3497 | on_peak | 802.4203 |  |  | 0.66 | 0 | 99.34 | 38.1588 | 0
6858 | 800.58 | 11.4 | 26.5 | 2.296 | 2.296 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 798.284 | 0 | 0.088511 | 7.5116 | 0 | 0 | 75.937 | 2.296 | on_peak | 798.284 |  |  | 0.29 | 0 | 99.71 | 17.2468 | 0
6859 | 787.61 | 0 | 26.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 787.61 | 0 | 0.088511 | 7.6897 | 0 | 0 | 75.937 | 0 | on_peak | 787.61 |  |  | 0 | 0 | 100 | 0 | 0
6860 | 761.18 | 0 | 26.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 761.18 | 0 | 0.088511 | 7.779 | 0 | 0 | 75.937 | 0 | on_peak | 761.18 |  |  | 0 | 0 | 100 | 0 | 0
6861 | 821.36 | 0 | 26 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 821.36 | 0 | 0.088511 | 7.7892 | 0 | 0 | 75.937 | 0 | on_peak | 821.36 |  |  | 0 | 0 | 100 | 0 | 0
6862 | 742.81 | 0 | 25.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 742.81 | 0 | 0.05921 | 7.8725 | 0 | 0 | 75.937 | 0 | off_peak | 742.81 |  |  | 0 | 0 | 100 | 0 | 0
6863 | 762.79 | 0 | 25.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 762.79 | 0 | 0.05921 | 7.941 | 0 | 0 | 75.937 | 0 | off_peak | 762.79 |  |  | 0 | 0 | 100 | 0 | 0
6864 | 745.54 | 0 | 26 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 745.54 | 0 | 0.05921 | 7.9433 | 0 | 0 | 75.937 | 0 | off_peak | 745.54 |  |  | 0 | 0 | 100 | 0 | 0
6865 | 647.51 | 0 | 26 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 647.51 | 0 | 0.05921 | 7.8703 | 0 | 0 | 75.937 | 0 | off_peak | 647.51 |  |  | 0 | 0 | 100 | 0 | 0
6866 | 585.55 | 0 | 26 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 585.55 | 0 | 0.05921 | 7.5808 | 0 | 0 | 75.937 | 0 | off_peak | 585.55 |  |  | 0 | 0 | 100 | 0 | 0
6867 | 589.79 | 0 | 25.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 589.79 | 0 | 0.05921 | 7.1767 | 0 | 0 | 75.937 | 0 | off_peak | 589.79 |  |  | 0 | 0 | 100 | 0 | 0
6868 | 568.1 | 0 | 25.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 568.1 | 0 | 0.05921 | 6.7207 | 0 | 0 | 75.937 | 0 | off_peak | 568.1 |  |  | 0 | 0 | 100 | 0 | 0
6869 | 629.13 | 0 | 25.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 629.13 | 0 | 0.05921 | 6.2085 | 0 | 0 | 75.937 | 0 | off_peak | 629.13 |  |  | 0 | 0 | 100 | 0 | 0
6870 | 635.55 | 0 | 25.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 635.55 | 0 | 0.05921 | 5.6647 | 0 | 0 | 75.937 | 0 | off_peak | 635.55 |  |  | 0 | 0 | 100 | 0 | 0
6871 | 663.55 | 11.4296 | 26 | 2.3062 | 0 | 0 | 2.3062 | 2.3062 | 0 | 0 | 0 | 0 | 9.5966 | 663.55 | 0 | 0.05921 | 5.1915 | 0 | 0 | 78.0942 | 0 | off_peak | 663.55 | 100 | 0 | 0 | 0 | 100 | 0 | 0
6872 | 705.18 | 112.739 | 26.3 | 22.7228 | 22.7228 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9.5966 | 682.4572 | 0 | 0.05921 | 4.924 | 0 | 0 | 78.0942 | 22.7228 | off_peak | 682.4572 |  |  | 3.22 | 0 | 96.78 | 111.8865 | 0
6873 | 702.59 | 218.583 | 26.6 | 44.0081 | 44.0081 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9.5966 | 658.5819 | 0 | 0.05921 | 4.7256 | 0 | 0 | 78.0942 | 44.0081 | off_peak | 658.5819 |  |  | 6.26 | 0 | 93.74 | 207.963 | 0
6874 | 711.8 | 428.235 | 27.1 | 86.062 | 86.062 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9.5966 | 625.738 | 0 | 0.05921 | 4.6336 | 0 | 0 | 78.0942 | 86.062 | off_peak | 625.738 |  |  | 12.09 | 0 | 87.91 | 398.7784 | 0
6875 | 714.18 | 313.918 | 27.6 | 62.9734 | 62.9734 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9.5966 | 651.2066 | 0 | 0.05921 | 4.6592 | 0 | 0 | 78.0942 | 62.9734 | off_peak | 651.2066 |  |  | 8.82 | 0 | 91.18 | 293.4077 | 0
6876 | 694.76 | 418.908 | 28 | 83.9127 | 83.9127 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9.5966 | 610.8473 | 0 | 0.05921 | 4.7845 | 0 | 0 | 78.0942 | 83.9127 | off_peak | 610.8473 |  |  | 12.08 | 0 | 87.92 | 401.482 | 0
6877 | 731.27 | 541.58 | 28.4 | 108.3276 | 108.3276 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9.5966 | 622.9424 | 0 | 0.05921 | 4.9909 | 0 | 0 | 78.0942 | 108.3276 | off_peak | 622.9424 |  |  | 14.81 | 0 | 85.19 | 540.6496 | 0
6878 | 686.39 | 310.389 | 28.5 | 62.0618 | 62.0618 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9.5966 | 624.3282 | 0 | 0.05921 | 5.2542 | 0 | 0 | 78.0942 | 62.0618 | off_peak | 624.3282 |  |  | 9.04 | 0 | 90.96 | 326.0842 | 0
6879 | 701.64 | 40.85 | 28.7 | 8.1619 | 8.1619 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 21.1947 | 705.877 | 0 | 0.05921 | 5.428 | 0 | 0 | 78.0942 | 8.1619 | off_peak | 693.4781 | 0 | 100 | 1.16 | 0 | 98.84 | 44.3033 | 0
6880 | 705.45 | 308.905 | 28.6 | 61.7426 | 61.7426 | 0 | 0 | 2.2604 | 2.2604 | 0 | 0 | 0 | 23.3091 | 645.9678 | 0 | 0.05921 | 5.619 | 0 | 0 | 78.0942 | 61.7426 | off_peak | 643.7074 | 0 | 100 | 8.75 | 0 | 91.25 | 346.9306 | 0
6881 | 716.98 | 209.264 | 28.4 | 41.8573 | 29.4583 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 0 | 34.9073 | 687.5217 | 0 | 0.05921 | 5.7965 | 0 | 0 | 89.6923 | 29.4583 | off_peak | 687.5217 | 100 | 0 | 4.11 | 0 | 95.89 | 170.756 | 0
6882 | 628.15 | 30.4404 | 28 | 6.0976 | 0 | 0 | 6.0976 | 6.0976 | 0 | 0 | 0 | 0 | 40.6111 | 628.15 | 0 | 0.05921 | 6.3275 | 0 | 0 | 95.3961 | 0 | off_peak | 628.15 | 100 | 0 | 0 | 0 | 100 | 0 | 0
6883 | 579.75 | 0 | 27.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40.6111 | 579.75 | 0 | 0.05921 | 6.7215 | 0 | 0 | 95.3961 | 0 | off_peak | 579.75 |  |  | 0 | 0 | 100 | 0 | 0
6884 | 606.35 | 0 | 27.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40.6111 | 606.35 | 0 | 0.05921 | 6.2198 | 0 | 0 | 95.3961 | 0 | off_peak | 606.35 |  |  | 0 | 0 | 100 | 0 | 0
6885 | 571.09 | 0 | 27.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40.6111 | 571.09 | 0 | 0.05921 | 6.4708 | 0 | 0 | 95.3961 | 0 | off_peak | 571.09 |  |  | 0 | 0 | 100 | 0 | 0
6886 | 569.71 | 0 | 27.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40.6111 | 569.71 | 0 | 0.05921 | 6.8429 | 0 | 0 | 95.3961 | 0 | off_peak | 569.71 |  |  | 0 | 0 | 100 | 0 | 0
6887 | 586.19 | 0 | 27 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40.6111 | 586.19 | 0 | 0.05921 | 7.2255 | 0 | 0 | 95.3961 | 0 | off_peak | 586.19 |  |  | 0 | 0 | 100 | 0 | 0
6888 | 583.58 | 0 | 26.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40.6111 | 583.58 | 0 | 0.05921 | 7.5498 | 0 | 0 | 95.3961 | 0 | off_peak | 583.58 |  |  | 0 | 0 | 100 | 0 | 0
6889 | 543.58 | 0 | 26.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40.6111 | 543.58 | 0 | 0.05921 | 7.3862 | 0 | 0 | 95.3961 | 0 | off_peak | 543.58 |  |  | 0 | 0 | 100 | 0 | 0
6890 | 589.28 | 0 | 26.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40.6111 | 589.28 | 0 | 0.05921 | 7.0046 | 0 | 0 | 95.3961 | 0 | off_peak | 589.28 |  |  | 0 | 0 | 100 | 0 | 0
6891 | 576.58 | 0 | 26.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40.6111 | 576.58 | 0 | 0.05921 | 6.5898 | 0 | 0 | 95.3961 | 0 | off_peak | 576.58 |  |  | 0 | 0 | 100 | 0 | 0
6892 | 605.84 | 0 | 26.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40.6111 | 605.84 | 0 | 0.05921 | 6.0771 | 0 | 0 | 95.3961 | 0 | off_peak | 605.84 |  |  | 0 | 0 | 100 | 0 | 0
6893 | 614.39 | 0 | 26.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40.6111 | 614.39 | 0 | 0.05921 | 5.5028 | 0 | 0 | 95.3961 | 0 | off_peak | 614.39 |  |  | 0 | 0 | 100 | 0 | 0
6894 | 631.86 | 0 | 26.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40.6111 | 631.86 | 0 | 0.05921 | 4.9202 | 0 | 0 | 95.3961 | 0 | off_peak | 631.86 |  |  | 0 | 0 | 100 | 0 | 0
6895 | 678.38 | 16.3135 | 26.9 | 3.2809 | 0 | 0 | 3.2809 | 3.2809 | 0 | 0 | 0 | 0 | 43.6801 | 678.38 | 0 | 0.05921 | 4.4625 | 0 | 0 | 98.4651 | 0 | off_peak | 678.38 | 100 | 0 | 0 | 0 | 100 | 0 | 0
6896 | 696.93 | 181.658 | 27.5 | 36.4547 | 36.4547 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 43.6801 | 660.4753 | 0 | 0.05921 | 4.0994 | 0 | 0 | 98.4651 | 36.4547 | off_peak | 660.4753 |  |  | 5.23 | 0 | 94.77 | 149.4424 | 0
6897 | 664.21 | 377.98 | 27.9 | 75.7419 | 75.7419 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 43.6801 | 588.4681 | 0 | 0.05921 | 3.8677 | 0 | 0 | 98.4651 | 75.7419 | off_peak | 588.4681 |  |  | 11.4 | 0 | 88.6 | 292.9479 | 0
6898 | 698.98 | 550.607 | 28.2 | 110.2135 | 110.2135 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 43.6801 | 588.7665 | 0 | 0.05921 | 3.7207 | 0 | 0 | 98.4651 | 110.2135 | off_peak | 588.7665 |  |  | 15.77 | 0 | 84.23 | 410.0681 | 0
6899 | 663.73 | 696.116 | 28.5 | 139.1874 | 139.1874 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 43.6801 | 524.5426 | 0 | 0.05921 | 3.6866 | 0 | 0 | 98.4651 | 139.1874 | off_peak | 524.5426 |  |  | 20.97 | 0 | 79.03 | 513.1263 | 0
6900 | 719.19 | 608.535 | 28.7 | 121.5869 | 121.5869 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 43.6801 | 597.6031 | 0 | 0.05921 | 3.7404 | 0 | 0 | 98.4651 | 121.5869 | off_peak | 597.6031 |  |  | 16.91 | 0 | 83.09 | 454.7845 | 0
6901 | 683.56 | 740.619 | 28.8 | 147.9237 | 147.9237 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 43.6801 | 535.6363 | 0 | 0.05921 | 3.8722 | 0 | 0 | 98.4651 | 147.9237 | off_peak | 535.6363 |  |  | 21.64 | 0 | 78.36 | 572.7829 | 0
6902 | 687.64 | 692.502 | 28.7 | 138.3638 | 138.3638 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 43.6801 | 549.2762 | 0 | 0.05921 | 4.1005 | 0 | 0 | 98.4651 | 138.3638 | off_peak | 549.2762 |  |  | 20.12 | 0 | 79.88 | 567.3659 | 0
6903 | 679.57 | 601.285 | 28.5 | 120.226 | 120.226 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 43.6801 | 559.344 | 0 | 0.05921 | 4.2684 | 0 | 0 | 98.4651 | 120.226 | off_peak | 559.344 |  |  | 17.69 | 0 | 82.31 | 513.1707 | 0
6904 | 701.17 | 196.346 | 28.2 | 39.302 | 26.9031 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 0 | 55.2782 | 674.2669 | 0 | 0.05921 | 4.6353 | 0 | 0 | 110.0632 | 26.9031 | off_peak | 674.2669 | 100 | 0 | 3.84 | 0 | 96.16 | 124.7049 | 0
6905 | 676.78 | 55.0033 | 27.9 | 11.0219 | 0 | 0 | 11.0219 | 11.0219 | 0 | 0 | 0 | 0 | 65.5883 | 676.78 | 0 | 0.05921 | 5.088 | 0 | 0 | 120.3733 | 0 | off_peak | 676.78 | 100 | 0 | 0 | 0 | 100 | 0 | 0
6906 | 640.43 | 31.5553 | 27.4 | 6.3347 | 0 | 0 | 6.3347 | 6.3347 | 0 | 0 | 0 | 0 | 71.5139 | 640.43 | 0 | 0.05921 | 5.4952 | 0 | 0 | 126.2989 | 0 | off_peak | 640.43 | 100 | 0 | 0 | 0 | 100 | 0 | 0
6907 | 561.13 | 0 | 27.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 71.5139 | 561.13 | 0 | 0.05921 | 5.8078 | 0 | 0 | 126.2989 | 0 | off_peak | 561.13 |  |  | 0 | 0 | 100 | 0 | 0
6908 | 587.87 | 0 | 27.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 71.5139 | 587.87 | 0 | 0.05921 | 6.1449 | 0 | 0 | 126.2989 | 0 | off_peak | 587.87 |  |  | 0 | 0 | 100 | 0 | 0
6909 | 574.78 | 0 | 27.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 71.5139 | 574.78 | 0 | 0.05921 | 6.3938 | 0 | 0 | 126.2989 | 0 | off_peak | 574.78 |  |  | 0 | 0 | 100 | 0 | 0
6910 | 580.56 | 0 | 27.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 71.5139 | 580.56 | 0 | 0.05921 | 6.6723 | 0 | 0 | 126.2989 | 0 | off_peak | 580.56 |  |  | 0 | 0 | 100 | 0 | 0
6911 | 558.5 | 0 | 27.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 71.5139 | 558.5 | 0 | 0.05921 | 6.9657 | 0 | 0 | 126.2989 | 0 | off_peak | 558.5 |  |  | 0 | 0 | 100 | 0 | 0
6912 | 558.94 | 0 | 27.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 71.5139 | 558.94 | 0 | 0.05921 | 7.1832 | 0 | 0 | 126.2989 | 0 | off_peak | 558.94 |  |  | 0 | 0 | 100 | 0 | 0
6913 | 574.27 | 0 | 27 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 71.5139 | 574.27 | 0 | 0.05921 | 7.0764 | 0 | 0 | 126.2989 | 0 | off_peak | 574.27 |  |  | 0 | 0 | 100 | 0 | 0
6914 | 552.79 | 0 | 27 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 71.5139 | 552.79 | 0 | 0.05921 | 6.6979 | 0 | 0 | 126.2989 | 0 | off_peak | 552.79 |  |  | 0 | 0 | 100 | 0 | 0
6915 | 545.46 | 0 | 26.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 71.5139 | 545.46 | 0 | 0.05921 | 6.1266 | 0 | 0 | 126.2989 | 0 | off_peak | 545.46 |  |  | 0 | 0 | 100 | 0 | 0
6916 | 546.18 | 0 | 26.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 71.5139 | 546.18 | 0 | 0.05921 | 5.4411 | 0 | 0 | 126.2989 | 0 | off_peak | 546.18 |  |  | 0 | 0 | 100 | 0 | 0
6917 | 545.34 | 0 | 26.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 71.5139 | 545.34 | 0 | 0.05921 | 4.755 | 0 | 0 | 126.2989 | 0 | off_peak | 545.34 |  |  | 0 | 0 | 100 | 0 | 0
6918 | 596.73 | 0 | 26.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 71.5139 | 596.73 | 0 | 0.05921 | 4.1146 | 0 | 0 | 126.2989 | 0 | off_peak | 596.73 |  |  | 0 | 0 | 100 | 0 | 0
6919 | 620.79 | 14.3191 | 26.9 | 2.8798 | 0 | 0 | 2.8798 | 2.8798 | 0 | 0 | 0 | 0 | 74.2077 | 620.79 | 0 | 0.05921 | 3.6501 | 0 | 0 | 128.9927 | 0 | off_peak | 620.79 | 100 | 0 | 0 | 0 | 100 | 0 | 0
6920 | 739.27 | 174.264 | 27.4 | 34.9836 | 34.7976 | 0 | 0.18599 | 0.18599 | 0 | 0 | 0 | 0 | 74.3816 | 704.4724 | 0 | 0.05921 | 3.3679 | 0 | 0 | 129.1667 | 34.7976 | off_peak | 704.4724 | 100 | 0 | 4.71 | 0 | 95.29 | 117.193 | 0
6921 | 764.64 | 375.478 | 27.8 | 75.2679 | 75.2679 | 0 | 0 | 0.012012 | 0.012012 | 0 | 0 | 0 | 74.3929 | 689.3841 | 0 | 0.05921 | 3.2095 | 0 | 0 | 129.1667 | 75.2679 | off_peak | 689.3721 | 0 | 100 | 9.84 | 0 | 90.16 | 241.5734 | 0
6922 | 780.25 | 553.708 | 28.1 | 110.8745 | 110.8745 | 0 | 0 | 0.00077583 | 0.00077583 | 0 | 0 | 0 | 74.3936 | 669.3762 | 0 | 0.05921 | 3.1842 | 0 | 0 | 129.1667 | 110.8745 | off_peak | 669.3755 | 0 | 100 | 14.21 | 0 | 85.79 | 353.0472 | 0
6923 | 761.21 | 653.579 | 28.4 | 130.7298 | 130.7298 | 0 | 0 | 5.0108e-05 | 5.0108e-05 | 0 | 0 | 0 | 74.3936 | 630.4803 | 0 | 0.05921 | 3.4168 | 0 | 0 | 129.1667 | 130.7298 | off_peak | 630.4802 | 0 | 100 | 17.17 | 0 | 82.83 | 446.6751 | 0
6924 | 836.24 | 739.001 | 28.5 | 147.7621 | 147.7621 | 0 | 0 | 3.2362e-06 | 3.2362e-06 | 0 | 0 | 0 | 74.3936 | 688.4779 | 0 | 0.05921 | 3.8942 | 0 | 0 | 129.1667 | 147.7621 | off_peak | 688.4779 | 0 | 100 | 17.67 | 0 | 82.33 | 575.4102 | 0
6925 | 807.52 | 621.846 | 28.6 | 124.2918 | 124.2918 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 683.2282 | 0 | 0.088511 | 4.0691 | 0 | 0 | 129.1667 | 124.2918 | on_peak | 683.2282 |  |  | 15.39 | 0 | 84.61 | 505.7546 | 0
6926 | 848.5 | 718.389 | 28.5 | 143.6408 | 143.6408 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 704.8592 | 0 | 0.088511 | 4.0599 | 0 | 0 | 129.1667 | 143.6408 | on_peak | 704.8592 |  |  | 16.93 | 0 | 83.07 | 583.1722 | 0
6927 | 849.58 | 597.754 | 28.4 | 119.5636 | 119.5636 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 730.0164 | 0 | 0.088511 | 3.8898 | 0 | 0 | 129.1667 | 119.5636 | on_peak | 730.0164 |  |  | 14.07 | 0 | 85.93 | 465.0748 | 0
6928 | 819.75 | 427.255 | 28.2 | 85.5224 | 85.5224 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 734.2276 | 0 | 0.088511 | 3.7104 | 0 | 0 | 129.1667 | 85.5224 | on_peak | 734.2276 |  |  | 10.43 | 0 | 89.57 | 317.3194 | 0
6929 | 752.42 | 227.701 | 27.8 | 45.6447 | 45.6447 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 706.7753 | 0 | 0.088511 | 3.6622 | 0 | 0 | 129.1667 | 45.6447 | on_peak | 706.7753 |  |  | 6.07 | 0 | 93.93 | 167.1601 | 0
6930 | 801.09 | 40.7805 | 27.4 | 8.1867 | 8.1867 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 792.9033 | 0 | 0.088511 | 3.792 | 0 | 0 | 129.1667 | 8.1867 | on_peak | 792.9033 |  |  | 1.02 | 0 | 98.98 | 31.044 | 0
6931 | 727.31 | 0 | 27.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 727.31 | 0 | 0.088511 | 4.0732 | 0 | 0 | 129.1667 | 0 | on_peak | 727.31 |  |  | 0 | 0 | 100 | 0 | 0
6932 | 794.67 | 0 | 27 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 794.67 | 0 | 0.088511 | 4.3386 | 0 | 0 | 129.1667 | 0 | on_peak | 794.67 |  |  | 0 | 0 | 100 | 0 | 0
6933 | 796.34 | 0 | 27 | 0 | 0 | 0 | 0 | 0 | 0 | 62.63 | 62.63 | 0 | 7.4394 | 733.71 | 0 | 0.088511 | 4.5765 | 0 | 0 | 129.1667 | 0 | on_peak | 733.71 |  |  | 0 | 7.86 | 92.14 | 0 | 0
6934 | 741.48 | 0 | 26.9 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 19.0375 | 753.8789 | 0 | 0.05921 | 4.7772 | 0 | 0 | 129.1667 | 0 | off_peak | 741.48 | 0 | 100 | 0 | 0 | 100 | 0 | 0
6935 | 775.41 | 0 | 26.9 | 0 | 0 | 0 | 0 | 7.0074 | 7.0074 | 0 | 0 | 0 | 25.5924 | 782.4174 | 0 | 0.05921 | 5.1636 | 0 | 0 | 129.1667 | 0 | off_peak | 775.41 | 0 | 100 | 0 | 0 | 100 | 0 | 0
6936 | 720.09 | 0 | 26.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25.5924 | 720.09 | 0 | 0.05921 | 5.548 | 0 | 0 | 129.1667 | 0 | off_peak | 720.09 |  |  | 0 | 0 | 100 | 0 | 0
6937 | 665.45 | 0 | 26.7 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 37.1905 | 677.8489 | 0 | 0.05921 | 5.7145 | 0 | 0 | 129.1667 | 0 | off_peak | 665.45 | 0 | 100 | 0 | 0 | 100 | 0 | 0
6938 | 611.07 | 0 | 26.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 37.1905 | 611.07 | 0 | 0.05921 | 5.4736 | 0 | 0 | 129.1667 | 0 | off_peak | 611.07 |  |  | 0 | 0 | 100 | 0 | 0
6939 | 563.52 | 0 | 26.7 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 48.7887 | 575.9189 | 0 | 0.05921 | 5.0175 | 0 | 0 | 129.1667 | 0 | off_peak | 563.52 | 0 | 100 | 0 | 0 | 100 | 0 | 0
6940 | 569.86 | 0 | 26.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 48.7887 | 569.86 | 0 | 0.05921 | 4.4072 | 0 | 0 | 129.1667 | 0 | off_peak | 569.86 |  |  | 0 | 0 | 100 | 0 | 0
6941 | 555.44 | 0 | 26.7 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 60.3868 | 567.8389 | 0 | 0.05921 | 3.7386 | 0 | 0 | 129.1667 | 0 | off_peak | 555.44 | 0 | 100 | 0 | 0 | 100 | 0 | 0
6942 | 588.79 | 0 | 26.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60.3868 | 588.79 | 0 | 0.05921 | 3.2231 | 0 | 0 | 129.1667 | 0 | off_peak | 588.79 |  |  | 0 | 0 | 100 | 0 | 0
6943 | 665.89 | 8.55 | 27 | 1.7189 | 0 | 0 | 1.7189 | 1.7189 | 0 | 0 | 0 | 0 | 61.9947 | 665.89 | 0 | 0.05921 | 2.8974 | 0 | 0 | 130.7745 | 0 | off_peak | 665.89 | 100 | 0 | 0 | 0 | 100 | 0 | 0
6944 | 720.33 | 157.897 | 27.6 | 31.6749 | 31.6749 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 73.5928 | 701.0541 | 0 | 0.05921 | 2.6992 | 0 | 0 | 130.7745 | 31.6749 | off_peak | 688.6551 | 0 | 100 | 4.4 | 0 | 95.6 | 85.4983 | 0
6945 | 740.8 | 375.193 | 27.9 | 75.1834 | 75.1834 | 0 | 0 | 0.80079 | 0.80079 | 0 | 0 | 0 | 74.3419 | 666.4174 | 0 | 0.05921 | 2.5759 | 0 | 0 | 130.7745 | 75.1834 | off_peak | 665.6166 | 0 | 100 | 10.15 | 0 | 89.85 | 193.6643 | 0
6946 | 763.52 | 552.83 | 28.2 | 110.6584 | 110.6584 | 0 | 0 | 0.05172 | 0.05172 | 0 | 0 | 0 | 74.3903 | 652.9133 | 0 | 0.05921 | 2.6168 | 0 | 0 | 130.7745 | 110.6584 | off_peak | 652.8616 | 0 | 100 | 14.49 | 0 | 85.51 | 289.5758 | 0
6947 | 734.42 | 685.085 | 28.4 | 137.0317 | 137.0317 | 0 | 0 | 0.0033404 | 0.0033404 | 0 | 0 | 0 | 74.3934 | 597.3917 | 0 | 0.05921 | 2.9453 | 0 | 0 | 130.7745 | 137.0317 | off_peak | 597.3883 | 0 | 100 | 18.66 | 0 | 81.34 | 403.5987 | 0
6948 | 761.35 | 757.705 | 28.5 | 151.502 | 151.502 | 0 | 0 | 0.00021574 | 0.00021574 | 0 | 0 | 0 | 74.3936 | 609.8482 | 0 | 0.05921 | 3.4397 | 0 | 0 | 130.7745 | 151.502 | off_peak | 609.848 | 0 | 100 | 19.9 | 0 | 80.1 | 521.1238 | 0
6949 | 749.65 | 517.792 | 28.5 | 103.5317 | 103.5317 | 0 | 0 | 0 | 0 | 62.63 | 62.63 | 0 | 7.4394 | 583.4883 | 0 | 0.088511 | 3.7073 | 0 | 0 | 130.7745 | 103.5317 | on_peak | 583.4883 |  |  | 13.81 | 8.35 | 77.83 | 383.8228 | 0
6950 | 769.25 | 368.249 | 28.5 | 73.6308 | 73.6308 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 695.6192 | 0 | 0.088511 | 3.5354 | 0 | 0 | 130.7745 | 73.6308 | on_peak | 695.6192 |  |  | 9.57 | 0 | 90.43 | 260.3152 | 0
6951 | 786.9 | 549.809 | 28.4 | 109.9736 | 109.9736 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 676.9264 | 0 | 0.088511 | 3.0994 | 0 | 0 | 130.7745 | 109.9736 | on_peak | 676.9264 |  |  | 13.98 | 0 | 86.02 | 340.8504 | 0
6952 | 673.39 | 192.662 | 28.2 | 38.5646 | 38.5646 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 634.8254 | 0 | 0.088511 | 2.8659 | 0 | 0 | 130.7745 | 38.5646 | on_peak | 634.8254 |  |  | 5.73 | 0 | 94.27 | 110.5205 | 0
6953 | 744.94 | 55.6542 | 28 | 11.1483 | 11.1483 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 733.7917 | 0 | 0.088511 | 2.8308 | 0 | 0 | 130.7745 | 11.1483 | on_peak | 733.7917 |  |  | 1.5 | 0 | 98.5 | 31.559 | 0
6954 | 753.69 | 31.2771 | 27.7 | 6.2721 | 6.2721 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 747.4179 | 0 | 0.088511 | 2.8265 | 0 | 0 | 130.7745 | 6.2721 | on_peak | 747.4179 |  |  | 0.83 | 0 | 99.17 | 17.7277 | 0
6955 | 750.21 | 0 | 27.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 750.21 | 0 | 0.088511 | 2.9341 | 0 | 0 | 130.7745 | 0 | on_peak | 750.21 |  |  | 0 | 0 | 100 | 0 | 0
6956 | 779.36 | 0 | 27.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 779.36 | 0 | 0.088511 | 3.1257 | 0 | 0 | 130.7745 | 0 | on_peak | 779.36 |  |  | 0 | 0 | 100 | 0 | 0
6957 | 731.07 | 0 | 27.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 731.07 | 0 | 0.088511 | 3.4623 | 0 | 0 | 130.7745 | 0 | on_peak | 731.07 |  |  | 0 | 0 | 100 | 0 | 0
6958 | 713.22 | 0 | 27.1 | 0 | 0 | 0 | 0 | 8.7263 | 8.7263 | 0 | 0 | 0 | 15.6021 | 721.9463 | 0 | 0.05921 | 3.9418 | 0 | 0 | 130.7745 | 0 | off_peak | 713.22 | 0 | 100 | 0 | 0 | 100 | 0 | 0
6959 | 728.04 | 0 | 27 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15.6021 | 728.04 | 0 | 0.05921 | 4.5496 | 0 | 0 | 130.7745 | 0 | off_peak | 728.04 |  |  | 0 | 0 | 100 | 0 | 0
6960 | 696.54 | 0 | 26.8 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 27.2003 | 708.9389 | 0 | 0.05921 | 5.2024 | 0 | 0 | 130.7745 | 0 | off_peak | 696.54 | 0 | 100 | 0 | 0 | 100 | 0 | 0
6961 | 658.97 | 0 | 26.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27.2003 | 658.97 | 0 | 0.05921 | 5.3736 | 0 | 0 | 130.7745 | 0 | off_peak | 658.97 |  |  | 0 | 0 | 100 | 0 | 0
6962 | 575.11 | 0 | 26.6 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 38.7984 | 587.5089 | 0 | 0.05921 | 5.1004 | 0 | 0 | 130.7745 | 0 | off_peak | 575.11 | 0 | 100 | 0 | 0 | 100 | 0 | 0
6963 | 549.86 | 0 | 26.5 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 50.3966 | 562.2589 | 0 | 0.05921 | 4.6147 | 0 | 0 | 130.7745 | 0 | off_peak | 549.86 | 0 | 100 | 0 | 0 | 100 | 0 | 0
6964 | 574.58 | 0 | 26.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50.3966 | 574.58 | 0 | 0.05921 | 4.1035 | 0 | 0 | 130.7745 | 0 | off_peak | 574.58 |  |  | 0 | 0 | 100 | 0 | 0
6965 | 564.13 | 0 | 26.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50.3966 | 564.13 | 0 | 0.05921 | 3.4668 | 0 | 0 | 130.7745 | 0 | off_peak | 564.13 |  |  | 0 | 0 | 100 | 0 | 0
6966 | 593.97 | 0 | 26.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50.3966 | 593.97 | 0 | 0.05921 | 3.0803 | 0 | 0 | 130.7745 | 0 | off_peak | 593.97 |  |  | 0 | 0 | 100 | 0 | 0
6967 | 628.32 | 15.217 | 26.3 | 3.067 | 0 | 0 | 3.067 | 12.3989 | 9.3319 | 0 | 0 | 0 | 61.9947 | 637.6519 | 0 | 0.05921 | 2.7972 | 0 | 0 | 133.6435 | 0 | off_peak | 628.32 | 24.74 | 75.26 | 0 | 0 | 100 | 0 | 0
6968 | 651.6 | 179.898 | 26.7 | 36.2064 | 36.2064 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 73.5928 | 627.7925 | 0 | 0.05921 | 2.6588 | 0 | 0 | 133.6435 | 36.2064 | off_peak | 615.3936 | 0 | 100 | 5.56 | 0 | 94.44 | 96.2655 | 0
6969 | 773.27 | 386.326 | 26.9 | 77.6959 | 77.6959 | 0 | 0 | 0.80079 | 0.80079 | 0 | 0 | 0 | 74.3419 | 696.3749 | 0 | 0.05921 | 2.5907 | 0 | 0 | 133.6435 | 77.6959 | off_peak | 695.5741 | 0 | 100 | 10.05 | 0 | 89.95 | 201.2871 | 0
6970 | 754.71 | 566.026 | 27.2 | 113.7125 | 113.7125 | 0 | 0 | 0.05172 | 0.05172 | 0 | 0 | 0 | 74.3903 | 641.0492 | 0 | 0.05921 | 2.6386 | 0 | 0 | 133.6435 | 113.7125 | off_peak | 640.9975 | 0 | 100 | 15.07 | 0 | 84.93 | 300.04 | 0
6971 | 767.09 | 522.631 | 27.5 | 104.8803 | 104.8803 | 0 | 0 | 0.0033404 | 0.0033404 | 0 | 0 | 0 | 74.3934 | 662.2131 | 0 | 0.05921 | 2.9617 | 0 | 0 | 133.6435 | 104.8803 | off_peak | 662.2097 | 0 | 100 | 13.67 | 0 | 86.33 | 310.621 | 0
6972 | 785.82 | 597.304 | 27.9 | 119.6913 | 119.6913 | 0 | 0 | 0.00021574 | 0.00021574 | 0 | 0 | 0 | 74.3936 | 666.1289 | 0 | 0.05921 | 3.5254 | 0 | 0 | 133.6435 | 119.6913 | off_peak | 666.1287 | 0 | 100 | 15.23 | 0 | 84.77 | 421.9643 | 0
6973 | 749.26 | 313.729 | 28.2 | 62.7983 | 62.7983 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 686.4617 | 0 | 0.088511 | 3.7698 | 0 | 0 | 133.6435 | 62.7983 | on_peak | 686.4617 |  |  | 8.38 | 0 | 91.62 | 236.7392 | 0
6974 | 845.24 | 413.776 | 28.4 | 82.7641 | 82.7641 | 0 | 0 | 0 | 0 | 62.63 | 62.63 | 0 | 7.4394 | 699.846 | 0 | 0.088511 | 3.6202 | 62.63 | 0 | 66.6892 | 145.394 | on_peak | 699.846 |  |  | 9.79 | 7.41 | 82.8 | 526.3535 | 0
6975 | 812.17 | 266.576 | 28.5 | 53.3015 | 53.3015 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 758.8685 | 0 | 0.088511 | 3.2141 | 0 | 0 | 66.6892 | 53.3015 | on_peak | 758.8685 |  |  | 6.56 | 0 | 93.44 | 171.3172 | 0
6976 | 780.41 | 163.17 | 28.5 | 32.6256 | 32.6256 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 747.7844 | 0 | 0.088511 | 3.0576 | 0 | 0 | 66.6892 | 32.6256 | on_peak | 747.7844 |  |  | 4.18 | 0 | 95.82 | 99.7551 | 0
6977 | 794.47 | 69.4941 | 28.1 | 13.9155 | 13.9155 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 780.5545 | 0 | 0.088511 | 3.1342 | 0 | 0 | 66.6892 | 13.9155 | on_peak | 780.5545 |  |  | 1.75 | 0 | 98.25 | 43.6138 | 0
6978 | 769.36 | 17.1 | 27.6 | 3.4303 | 3.4303 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 765.9297 | 0 | 0.088511 | 3.3536 | 0 | 0 | 66.6892 | 3.4303 | on_peak | 765.9297 |  |  | 0.45 | 0 | 99.55 | 11.504 | 0
6979 | 781.66 | 0 | 27.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 781.66 | 0 | 0.088511 | 3.6594 | 0 | 0 | 66.6892 | 0 | on_peak | 781.66 |  |  | 0 | 0 | 100 | 0 | 0
6980 | 777.46 | 0 | 27 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 777.46 | 0 | 0.088511 | 4.0225 | 0 | 0 | 66.6892 | 0 | on_peak | 777.46 |  |  | 0 | 0 | 100 | 0 | 0
6981 | 773.12 | 0 | 26.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 773.12 | 0 | 0.088511 | 4.4819 | 0 | 0 | 66.6892 | 0 | on_peak | 773.12 |  |  | 0 | 0 | 100 | 0 | 0
6982 | 761.4 | 0 | 26.5 | 0 | 0 | 0 | 0 | 8.7263 | 8.7263 | 0 | 0 | 0 | 15.6021 | 770.1263 | 0 | 0.05921 | 4.9689 | 0 | 0 | 66.6892 | 0 | off_peak | 761.4 | 0 | 100 | 0 | 0 | 100 | 0 | 0
6983 | 742.24 | 0 | 26.4 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 27.2003 | 754.6389 | 0 | 0.05921 | 5.5079 | 0 | 0 | 66.6892 | 0 | off_peak | 742.24 | 0 | 100 | 0 | 0 | 100 | 0 | 0
6984 | 740.86 | 0 | 26.2 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 38.7984 | 753.2589 | 0 | 0.05921 | 5.9962 | 0 | 0 | 66.6892 | 0 | off_peak | 740.86 | 0 | 100 | 0 | 0 | 100 | 0 | 0
6985 | 707.33 | 0 | 25.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 38.7984 | 707.33 | 0 | 0.05921 | 6.0709 | 0 | 0 | 66.6892 | 0 | off_peak | 707.33 |  |  | 0 | 0 | 100 | 0 | 0
6986 | 632.3 | 0 | 24.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 38.7984 | 632.3 | 0 | 0.05921 | 5.7511 | 0 | 0 | 66.6892 | 0 | off_peak | 632.3 |  |  | 0 | 0 | 100 | 0 | 0
6987 | 609.54 | 0 | 23.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 38.7984 | 609.54 | 0 | 0.05921 | 5.2769 | 0 | 0 | 66.6892 | 0 | off_peak | 609.54 |  |  | 0 | 0 | 100 | 0 | 0
6988 | 612.89 | 0 | 22.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 38.7984 | 612.89 | 0 | 0.05921 | 4.7539 | 0 | 0 | 66.6892 | 0 | off_peak | 612.89 |  |  | 0 | 0 | 100 | 0 | 0
6989 | 603.59 | 0 | 21.7 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 50.3966 | 615.9889 | 0 | 0.05921 | 4.1115 | 0 | 0 | 66.6892 | 0 | off_peak | 603.59 | 0 | 100 | 0 | 0 | 100 | 0 | 0
6990 | 638.59 | 0 | 21.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50.3966 | 638.59 | 0 | 0.05921 | 3.593 | 0 | 0 | 66.6892 | 0 | off_peak | 638.59 |  |  | 0 | 0 | 100 | 0 | 0
6991 | 638.18 | 3.8 | 20.6 | 0.78169 | 0 | 0 | 0.78169 | 12.3989 | 11.6173 | 0 | 0 | 0 | 61.9947 | 649.7973 | 0 | 0.05921 | 3.1956 | 0 | 0 | 67.4204 | 0 | off_peak | 638.18 | 6.3 | 93.7 | 0 | 0 | 100 | 0 | 0
6992 | 749.1 | 67.157 | 20.2 | 13.8343 | 1.4353 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 0 | 73.5928 | 747.6647 | 0 | 0.05921 | 2.9952 | 0 | 0 | 79.0186 | 1.4353 | off_peak | 747.6647 | 100 | 0 | 0.19 | 0 | 99.81 | 4.2992 | 0
6993 | 710.28 | 253.314 | 20.2 | 52.1825 | 52.1825 | 0 | 0 | 0.80079 | 0.80079 | 0 | 0 | 0 | 74.3419 | 658.8983 | 0 | 0.05921 | 2.8805 | 0 | 0 | 79.0186 | 52.1825 | off_peak | 658.0975 | 0 | 100 | 7.35 | 0 | 92.65 | 150.3112 | 0
6994 | 758.85 | 220.682 | 20.4 | 45.4281 | 45.4281 | 0 | 0 | 0.05172 | 0.05172 | 0 | 0 | 0 | 74.3903 | 713.4736 | 0 | 0.05921 | 2.881 | 0 | 0 | 79.0186 | 45.4281 | off_peak | 713.4219 | 0 | 100 | 5.99 | 0 | 94.01 | 130.8778 | 0
6995 | 820.26 | 253.066 | 20.4 | 52.0945 | 52.0945 | 0 | 0 | 0.0033404 | 0.0033404 | 0 | 0 | 0 | 74.3934 | 768.1688 | 0 | 0.05921 | 3.1473 | 0 | 0 | 79.0186 | 52.0945 | off_peak | 768.1655 | 0 | 100 | 6.35 | 0 | 93.65 | 163.9563 | 0
6996 | 836.54 | 190.375 | 20.4 | 39.1893 | 39.1893 | 0 | 0 | 0.00021574 | 0.00021574 | 0 | 0 | 0 | 74.3936 | 797.3509 | 0 | 0.05921 | 3.6656 | 0 | 0 | 79.0186 | 39.1893 | off_peak | 797.3507 | 0 | 100 | 4.68 | 0 | 95.32 | 143.6529 | 0
6997 | 818.7 | 211.106 | 20.2 | 43.4877 | 43.4877 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 775.2123 | 0 | 0.088511 | 3.9888 | 0 | 0 | 79.0186 | 43.4877 | on_peak | 775.2123 |  |  | 5.31 | 0 | 94.69 | 173.4633 | 0
6998 | 830.86 | 100.7 | 19.8 | 20.7735 | 20.7735 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 810.0865 | 0 | 0.088511 | 3.9068 | 0 | 0 | 79.0186 | 20.7735 | on_peak | 810.0865 |  |  | 2.5 | 0 | 97.5 | 81.1574 | 0
6999 | 893.32 | 54.15 | 19.2 | 11.1943 | 11.1943 | 0 | 0 | 0 | 0 | 56.5911 | 56.5911 | 0 | 13.8952 | 825.5346 | 0 | 0.088511 | 3.7999 | 0 | 0 | 79.0186 | 11.1943 | on_peak | 825.5346 |  |  | 1.25 | 6.33 | 92.41 | 42.5372 | 0
7000 | 823.6 | 37.05 | 18.7 | 7.6728 | 7.6728 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13.8952 | 815.9272 | 0 | 0.088511 | 3.8461 | 0 | 0 | 79.0186 | 7.6728 | on_peak | 815.9272 |  |  | 0.93 | 0 | 99.07 | 29.5103 | 0
7001 | 793.3 | 30.67 | 18.5 | 6.356 | 6.356 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13.8952 | 786.944 | 0 | 0.088511 | 4.1009 | 0 | 0 | 79.0186 | 6.356 | on_peak | 786.944 |  |  | 0.8 | 0 | 99.2 | 26.0656 | 0
7002 | 815.73 | 8.55 | 18.6 | 1.7713 | 1.7713 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13.8952 | 813.9587 | 0 | 0.088511 | 4.5003 | 0 | 0 | 79.0186 | 1.7713 | on_peak | 813.9587 |  |  | 0.22 | 0 | 99.78 | 7.9712 | 0
7003 | 818.7 | 0 | 18.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13.8952 | 818.7 | 0 | 0.088511 | 4.8364 | 0 | 0 | 79.0186 | 0 | on_peak | 818.7 |  |  | 0 | 0 | 100 | 0 | 0
7004 | 837.66 | 0 | 19.2 | 0 | 0 | 0 | 0 | 0 | 0 | 6.0389 | 6.0389 | 0 | 7.4394 | 831.6211 | 0 | 0.088511 | 5.2787 | 6.0389 | 0 | 72.5627 | 6.0389 | on_peak | 831.6211 |  |  | 0 | 0.72 | 99.28 | 31.8779 | 0
7005 | 796 | 0 | 19.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 796 | 0 | 0.088511 | 5.6413 | 0 | 0 | 72.5627 | 0 | on_peak | 796 |  |  | 0 | 0 | 100 | 0 | 0
7006 | 775.89 | 0 | 19.8 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 19.0375 | 788.2889 | 0 | 0.05921 | 6.0297 | 0 | 0 | 72.5627 | 0 | off_peak | 775.89 | 0 | 100 | 0 | 0 | 100 | 0 | 0
7007 | 794.9 | 0 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19.0375 | 794.9 | 0 | 0.05921 | 6.2571 | 0 | 0 | 72.5627 | 0 | off_peak | 794.9 |  |  | 0 | 0 | 100 | 0 | 0
7008 | 783.94 | 0 | 20.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19.0375 | 783.94 | 0 | 0.05921 | 6.4169 | 0 | 0 | 72.5627 | 0 | off_peak | 783.94 |  |  | 0 | 0 | 100 | 0 | 0
7009 | 680.26 | 0 | 20.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19.0375 | 680.26 | 0 | 0.05921 | 6.4725 | 0 | 0 | 72.5627 | 0 | off_peak | 680.26 |  |  | 0 | 0 | 100 | 0 | 0
7010 | 611.53 | 0 | 20 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 30.6357 | 623.9289 | 0 | 0.05921 | 6.1492 | 0 | 0 | 72.5627 | 0 | off_peak | 611.53 | 0 | 100 | 0 | 0 | 100 | 0 | 0
7011 | 605.43 | 0 | 19.8 | 0 | 0 | 0 | 0 | 8.7263 | 8.7263 | 0 | 0 | 0 | 38.7984 | 614.1563 | 0 | 0.05921 | 5.7279 | 0 | 0 | 72.5627 | 0 | off_peak | 605.43 | 0 | 100 | 0 | 0 | 100 | 0 | 0
7012 | 611.51 | 0 | 19.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 38.7984 | 611.51 | 0 | 0.05921 | 5.1982 | 0 | 0 | 72.5627 | 0 | off_peak | 611.51 |  |  | 0 | 0 | 100 | 0 | 0
7013 | 620.09 | 0 | 19.6 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 50.3966 | 632.4889 | 0 | 0.05921 | 4.5234 | 0 | 0 | 72.5627 | 0 | off_peak | 620.09 | 0 | 100 | 0 | 0 | 100 | 0 | 0
7014 | 645.8 | 0 | 19.7 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 61.9947 | 658.1989 | 0 | 0.05921 | 3.9923 | 0 | 0 | 72.5627 | 0 | off_peak | 645.8 | 0 | 100 | 0 | 0 | 100 | 0 | 0
7015 | 686.75 | 11.8011 | 20 | 2.4327 | 0 | 0 | 2.4327 | 12.3989 | 9.9662 | 0 | 0 | 0 | 73.5928 | 696.7162 | 0 | 0.05921 | 3.632 | 0 | 0 | 74.8383 | 0 | off_peak | 686.75 | 19.62 | 80.38 | 0 | 0 | 100 | 0 | 0
7016 | 765.36 | 162.136 | 20.6 | 33.3526 | 32.5518 | 0 | 0.80079 | 0.80079 | 0 | 0 | 0 | 0 | 74.3419 | 732.8082 | 0 | 0.05921 | 3.4007 | 0 | 0 | 75.5874 | 32.5518 | off_peak | 732.8082 | 100 | 0 | 4.25 | 0 | 95.75 | 110.6993 | 0
7017 | 821.37 | 359.937 | 21.3 | 73.8581 | 73.8581 | 0 | 0 | 0.05172 | 0.05172 | 0 | 0 | 0 | 74.3903 | 747.5636 | 0 | 0.05921 | 3.2651 | 0 | 0 | 75.5874 | 73.8581 | off_peak | 747.5119 | 0 | 100 | 8.99 | 0 | 91.01 | 241.155 | 0
7018 | 855.73 | 539.936 | 22.1 | 110.4785 | 110.4785 | 0 | 0 | 0.0033404 | 0.0033404 | 0 | 0 | 0 | 74.3934 | 745.2548 | 0 | 0.05921 | 3.2566 | 0 | 0 | 75.5874 | 110.4785 | off_peak | 745.2515 | 0 | 100 | 12.91 | 0 | 87.09 | 359.7797 | 0
7019 | 836.79 | 657.693 | 23.1 | 134.0938 | 134.0938 | 0 | 0 | 0.00021574 | 0.00021574 | 0 | 0 | 0 | 74.3936 | 702.6964 | 0 | 0.05921 | 3.4681 | 0 | 0 | 75.5874 | 134.0938 | off_peak | 702.6962 | 0 | 100 | 16.02 | 0 | 83.98 | 465.0454 | 0
7020 | 882.73 | 422.464 | 24 | 85.8569 | 85.8569 | 0 | 0 | 1.3934e-05 | 1.3934e-05 | 0 | 0 | 0 | 74.3936 | 796.8731 | 0 | 0.05921 | 3.9406 | 0 | 0 | 75.5874 | 85.8569 | off_peak | 796.8731 | 0 | 100 | 9.73 | 0 | 90.27 | 338.3272 | 0
7021 | 839.95 | 475.493 | 24.7 | 96.3913 | 96.3913 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 743.5587 | 0 | 0.088511 | 4.2243 | 0 | 0 | 75.5874 | 96.3913 | on_peak | 743.5587 |  |  | 11.48 | 0 | 88.52 | 407.1882 | 0
7022 | 867.01 | 619.977 | 25.2 | 125.4549 | 125.4549 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 741.5551 | 0 | 0.088511 | 4.1804 | 0 | 0 | 75.5874 | 125.4549 | on_peak | 741.5551 |  |  | 14.47 | 0 | 85.53 | 524.4557 | 0
7023 | 879.03 | 578.569 | 25.5 | 116.9493 | 116.9493 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 762.0807 | 0 | 0.088511 | 3.8631 | 0 | 0 | 75.5874 | 116.9493 | on_peak | 762.0807 |  |  | 13.3 | 0 | 86.7 | 451.7878 | 0
7024 | 839.95 | 405.967 | 25.5 | 82.0603 | 82.0603 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 757.8897 | 0 | 0.088511 | 3.7747 | 0 | 0 | 75.5874 | 82.0603 | on_peak | 757.8897 |  |  | 9.77 | 0 | 90.23 | 309.7545 | 0
7025 | 821.88 | 204.002 | 25.2 | 41.2807 | 41.2807 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 780.5993 | 0 | 0.088511 | 4.0019 | 0 | 0 | 75.5874 | 41.2807 | on_peak | 780.5993 |  |  | 5.02 | 0 | 94.98 | 165.2001 | 0
7026 | 842.7 | 26.0933 | 24.6 | 5.2915 | 5.2915 | 0 | 0 | 0 | 0 | 30.6911 | 30.6911 | 0 | 41.5835 | 806.7174 | 0 | 0.088511 | 4.5263 | 0 | 0 | 75.5874 | 5.2915 | on_peak | 806.7174 |  |  | 0.63 | 3.64 | 95.73 | 23.9511 | 0
7027 | 786.6 | 0 | 24.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 41.5835 | 786.6 | 0 | 0.088511 | 5.1024 | 0 | 0 | 75.5874 | 0 | on_peak | 786.6 |  |  | 0 | 0 | 100 | 0 | 0
7028 | 863.56 | 0 | 23.7 | 0 | 0 | 0 | 0 | 0 | 0 | 31.9389 | 31.9389 | 0 | 7.4394 | 831.6211 | 0 | 0.088511 | 5.3543 | 0 | 0 | 75.5874 | 0 | on_peak | 831.6211 |  |  | 0 | 3.7 | 96.3 | 0 | 0
7029 | 770.81 | 0 | 23.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 770.81 | 0 | 0.088511 | 5.6922 | 0 | 0 | 75.5874 | 0 | on_peak | 770.81 |  |  | 0 | 0 | 100 | 0 | 0
7030 | 777.63 | 0 | 23.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 777.63 | 0 | 0.05921 | 5.8952 | 0 | 0 | 75.5874 | 0 | off_peak | 777.63 |  |  | 0 | 0 | 100 | 0 | 0
7031 | 809.19 | 0 | 23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 809.19 | 0 | 0.05921 | 6.2454 | 0 | 0 | 75.5874 | 0 | off_peak | 809.19 |  |  | 0 | 0 | 100 | 0 | 0
7032 | 780.78 | 0 | 22.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 780.78 | 0 | 0.05921 | 6.6286 | 0 | 0 | 75.5874 | 0 | off_peak | 780.78 |  |  | 0 | 0 | 100 | 0 | 0
7033 | 698.6 | 0 | 22.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 698.6 | 0 | 0.05921 | 6.4382 | 0 | 0 | 75.5874 | 0 | off_peak | 698.6 |  |  | 0 | 0 | 100 | 0 | 0
7034 | 668.7 | 0 | 22.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 668.7 | 0 | 0.05921 | 6.093 | 0 | 0 | 75.5874 | 0 | off_peak | 668.7 |  |  | 0 | 0 | 100 | 0 | 0
7035 | 647.87 | 0 | 21.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 647.87 | 0 | 0.05921 | 5.7171 | 0 | 0 | 75.5874 | 0 | off_peak | 647.87 |  |  | 0 | 0 | 100 | 0 | 0
7036 | 621.1 | 0 | 21.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 621.1 | 0 | 0.05921 | 5.1802 | 0 | 0 | 75.5874 | 0 | off_peak | 621.1 |  |  | 0 | 0 | 100 | 0 | 0
7037 | 634.62 | 0 | 21.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 634.62 | 0 | 0.05921 | 4.6249 | 0 | 0 | 75.5874 | 0 | off_peak | 634.62 |  |  | 0 | 0 | 100 | 0 | 0
7038 | 707.27 | 0 | 21.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 707.27 | 0 | 0.05921 | 4.0982 | 0 | 0 | 75.5874 | 0 | off_peak | 707.27 |  |  | 0 | 0 | 100 | 0 | 0
7039 | 667.91 | 12.8156 | 21.2 | 2.6307 | 2.6307 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 665.2793 | 0 | 0.05921 | 3.6343 | 0 | 0 | 75.5874 | 2.6307 | off_peak | 665.2793 |  |  | 0.39 | 0 | 99.61 | 9.5606 | 0
7040 | 694.08 | 167.613 | 21.7 | 34.3449 | 34.3449 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 659.7351 | 0 | 0.05921 | 3.3611 | 0 | 0 | 75.5874 | 34.3449 | off_peak | 659.7351 |  |  | 4.95 | 0 | 95.05 | 115.4355 | 0
7041 | 756.48 | 370.531 | 22.5 | 75.7078 | 75.7078 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 680.7722 | 0 | 0.05921 | 3.1669 | 0 | 0 | 75.5874 | 75.7078 | off_peak | 680.7722 |  |  | 10.01 | 0 | 89.99 | 239.7588 | 0
7042 | 700.46 | 516.906 | 23.5 | 105.2387 | 105.2387 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 595.2213 | 0 | 0.05921 | 3.0736 | 0 | 0 | 75.5874 | 105.2387 | off_peak | 595.2213 |  |  | 15.02 | 0 | 84.98 | 323.4659 | 0
7043 | 745.13 | 292.375 | 24.6 | 59.2912 | 59.2912 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 685.8388 | 0 | 0.05921 | 3.0954 | 0 | 0 | 75.5874 | 59.2912 | off_peak | 685.8388 |  |  | 7.96 | 0 | 92.04 | 183.5271 | 0
7044 | 728.11 | 678.067 | 25.4 | 137.1108 | 137.1108 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 590.9992 | 0 | 0.05921 | 3.2349 | 0 | 0 | 75.5874 | 137.1108 | off_peak | 590.9992 |  |  | 18.83 | 0 | 81.17 | 443.5372 | 0
7045 | 706.2 | 573.748 | 25.8 | 115.8494 | 115.8494 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 590.3506 | 0 | 0.05921 | 3.501 | 0 | 0 | 75.5874 | 115.8494 | off_peak | 590.3506 |  |  | 16.4 | 0 | 83.6 | 405.5865 | 0
7046 | 693.22 | 440.457 | 26 | 88.8714 | 88.8714 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 604.3486 | 0 | 0.05921 | 3.7506 | 0 | 0 | 75.5874 | 88.8714 | off_peak | 604.3486 |  |  | 12.82 | 0 | 87.18 | 333.3209 | 0
7047 | 711.17 | 337.219 | 25.9 | 68.0656 | 68.0656 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 643.1044 | 0 | 0.05921 | 3.7774 | 0 | 0 | 75.5874 | 68.0656 | off_peak | 643.1044 |  |  | 9.57 | 0 | 90.43 | 257.1138 | 0
7048 | 690.19 | 165.277 | 25.6 | 33.3963 | 33.3963 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 656.7937 | 0 | 0.05921 | 4.0014 | 0 | 0 | 75.5874 | 33.3963 | off_peak | 656.7937 |  |  | 4.84 | 0 | 95.16 | 133.6329 | 0
7049 | 695.05 | 52.6119 | 25.1 | 10.6501 | 10.6501 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 684.3999 | 0 | 0.05921 | 4.3495 | 0 | 0 | 75.5874 | 10.6501 | off_peak | 684.3999 |  |  | 1.53 | 0 | 98.47 | 46.3224 | 0
7050 | 655.66 | 25.6207 | 24.5 | 5.1975 | 0 | 0 | 5.1975 | 5.1975 | 0 | 0 | 0 | 0 | 12.3012 | 655.66 | 0 | 0.05921 | 4.7504 | 0 | 0 | 80.4492 | 0 | off_peak | 655.66 | 100 | 0 | 0 | 0 | 100 | 0 | 0
7051 | 598.7 | 0 | 24.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12.3012 | 598.7 | 0 | 0.05921 | 5.2064 | 0 | 0 | 80.4492 | 0 | off_peak | 598.7 |  |  | 0 | 0 | 100 | 0 | 0
7052 | 589.08 | 0 | 23.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12.3012 | 589.08 | 0 | 0.05921 | 5.6379 | 0 | 0 | 80.4492 | 0 | off_peak | 589.08 |  |  | 0 | 0 | 100 | 0 | 0
7053 | 578.6 | 0 | 23.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12.3012 | 578.6 | 0 | 0.05921 | 6.0591 | 0 | 0 | 80.4492 | 0 | off_peak | 578.6 |  |  | 0 | 0 | 100 | 0 | 0
7054 | 582.04 | 0 | 23.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12.3012 | 582.04 | 0 | 0.05921 | 6.4835 | 0 | 0 | 80.4492 | 0 | off_peak | 582.04 |  |  | 0 | 0 | 100 | 0 | 0
7055 | 577.68 | 0 | 23.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12.3012 | 577.68 | 0 | 0.05921 | 6.8953 | 0 | 0 | 80.4492 | 0 | off_peak | 577.68 |  |  | 0 | 0 | 100 | 0 | 0
7056 | 577.77 | 0 | 23.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12.3012 | 577.77 | 0 | 0.05921 | 6.9404 | 0 | 0 | 80.4492 | 0 | off_peak | 577.77 |  |  | 0 | 0 | 100 | 0 | 0
7057 | 580.27 | 0 | 22.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12.3012 | 580.27 | 0 | 0.05921 | 6.7314 | 0 | 0 | 80.4492 | 0 | off_peak | 580.27 |  |  | 0 | 0 | 100 | 0 | 0
7058 | 604.33 | 0 | 22.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12.3012 | 604.33 | 0 | 0.05921 | 6.2768 | 0 | 0 | 80.4492 | 0 | off_peak | 604.33 |  |  | 0 | 0 | 100 | 0 | 0
7059 | 606.87 | 0 | 22.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12.3012 | 606.87 | 0 | 0.05921 | 5.8426 | 0 | 0 | 80.4492 | 0 | off_peak | 606.87 |  |  | 0 | 0 | 100 | 0 | 0
7060 | 589.79 | 0 | 22.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12.3012 | 589.79 | 0 | 0.05921 | 5.2933 | 0 | 0 | 80.4492 | 0 | off_peak | 589.79 |  |  | 0 | 0 | 100 | 0 | 0
7061 | 602.44 | 0 | 22.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12.3012 | 602.44 | 0 | 0.05921 | 4.7187 | 0 | 0 | 80.4492 | 0 | off_peak | 602.44 |  |  | 0 | 0 | 100 | 0 | 0
7062 | 618.93 | 0 | 22.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12.3012 | 618.93 | 0 | 0.05921 | 4.233 | 0 | 0 | 80.4492 | 0 | off_peak | 618.93 |  |  | 0 | 0 | 100 | 0 | 0
7063 | 653.76 | 11.2661 | 22.7 | 2.3003 | 0 | 0 | 2.3003 | 2.3003 | 0 | 0 | 0 | 0 | 14.4529 | 653.76 | 0 | 0.05921 | 3.8582 | 0 | 0 | 82.601 | 0 | off_peak | 653.76 | 100 | 0 | 0 | 0 | 100 | 0 | 0
7064 | 681.57 | 175.677 | 23.3 | 35.7923 | 35.7923 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14.4529 | 645.7777 | 0 | 0.05921 | 3.5609 | 0 | 0 | 82.601 | 35.7923 | off_peak | 645.7777 |  |  | 5.25 | 0 | 94.75 | 127.4533 | 0
7065 | 666.41 | 382.862 | 24.1 | 77.7808 | 77.7808 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14.4529 | 588.6292 | 0 | 0.05921 | 3.3558 | 0 | 0 | 82.601 | 77.7808 | off_peak | 588.6292 |  |  | 11.67 | 0 | 88.33 | 261.0147 | 0
7066 | 678.66 | 567.341 | 25.1 | 114.8452 | 114.8452 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14.4529 | 563.8148 | 0 | 0.05921 | 3.239 | 0 | 0 | 82.601 | 114.8452 | off_peak | 563.8148 |  |  | 16.92 | 0 | 83.08 | 371.9873 | 0
7067 | 689.22 | 701.589 | 26.1 | 141.5092 | 141.5092 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14.4529 | 547.7108 | 0 | 0.05921 | 3.2163 | 0 | 0 | 82.601 | 141.5092 | off_peak | 547.7108 |  |  | 20.53 | 0 | 79.47 | 455.1401 | 0
7068 | 696.34 | 607.554 | 26.6 | 122.321 | 122.321 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14.4529 | 574.019 | 0 | 0.05921 | 3.2933 | 0 | 0 | 82.601 | 122.321 | off_peak | 574.019 |  |  | 17.57 | 0 | 82.43 | 402.8367 | 0
7069 | 685.33 | 483.524 | 27 | 97.2086 | 97.2086 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14.4529 | 588.1214 | 0 | 0.05921 | 3.46 | 0 | 0 | 82.601 | 97.2086 | off_peak | 588.1214 |  |  | 14.18 | 0 | 85.82 | 336.3393 | 0
7070 | 704.89 | 422.911 | 27.1 | 84.992 | 84.992 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14.4529 | 619.898 | 0 | 0.05921 | 3.7301 | 0 | 0 | 82.601 | 84.992 | off_peak | 619.898 |  |  | 12.06 | 0 | 87.94 | 317.0296 | 0
7071 | 657.55 | 521.451 | 27.1 | 104.7955 | 104.7955 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 26.0511 | 565.1534 | 0 | 0.05921 | 3.9404 | 0 | 0 | 82.601 | 104.7955 | off_peak | 552.7545 | 0 | 100 | 15.94 | 0 | 84.06 | 412.9335 | 0
7072 | 666.59 | 418.702 | 26.9 | 84.2072 | 84.2072 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 37.6492 | 594.7817 | 0 | 0.05921 | 4.0194 | 0 | 0 | 82.601 | 84.2072 | off_peak | 582.3828 | 0 | 100 | 12.63 | 0 | 87.37 | 338.4653 | 0
7073 | 657.51 | 215.004 | 26.5 | 43.3032 | 43.3032 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 37.6492 | 614.2068 | 0 | 0.05921 | 4.2152 | 0 | 0 | 82.601 | 43.3032 | off_peak | 614.2068 |  |  | 6.59 | 0 | 93.41 | 182.5318 | 0
7074 | 602.84 | 29.3058 | 25.8 | 5.9173 | 5.9173 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 37.6492 | 596.9227 | 0 | 0.05921 | 4.5498 | 0 | 0 | 82.601 | 5.9173 | off_peak | 596.9227 |  |  | 0.98 | 0 | 99.02 | 26.9224 | 0
7075 | 562.98 | 0 | 25.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 37.6492 | 562.98 | 0 | 0.05921 | 4.9589 | 0 | 0 | 82.601 | 0 | off_peak | 562.98 |  |  | 0 | 0 | 100 | 0 | 0
7076 | 562.28 | 0 | 25.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 37.6492 | 562.28 | 0 | 0.05921 | 5.4154 | 0 | 0 | 82.601 | 0 | off_peak | 562.28 |  |  | 0 | 0 | 100 | 0 | 0
7077 | 560.68 | 0 | 25 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 49.2474 | 573.0789 | 0 | 0.05921 | 5.86 | 0 | 0 | 82.601 | 0 | off_peak | 560.68 | 0 | 100 | 0 | 0 | 100 | 0 | 0
7078 | 541.8 | 0 | 24.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 49.2474 | 541.8 | 0 | 0.05921 | 6.3953 | 0 | 0 | 82.601 | 0 | off_peak | 541.8 |  |  | 0 | 0 | 100 | 0 | 0
7079 | 566.68 | 0 | 24.6 | 0 | 0 | 0 | 0 | 1.2285 | 1.2285 | 0 | 0 | 0 | 50.3966 | 567.9085 | 0 | 0.05921 | 6.7241 | 0 | 0 | 82.601 | 0 | off_peak | 566.68 | 0 | 100 | 0 | 0 | 100 | 0 | 0
7080 | 550.03 | 0 | 24.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50.3966 | 550.03 | 0 | 0.05921 | 6.7553 | 0 | 0 | 82.601 | 0 | off_peak | 550.03 |  |  | 0 | 0 | 100 | 0 | 0
7081 | 555.53 | 0 | 24.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50.3966 | 555.53 | 0 | 0.05921 | 6.7105 | 0 | 0 | 82.601 | 0 | off_peak | 555.53 |  |  | 0 | 0 | 100 | 0 | 0
7082 | 537.9 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50.3966 | 537.9 | 0 | 0.05921 | 6.3072 | 0 | 0 | 82.601 | 0 | off_peak | 537.9 |  |  | 0 | 0 | 100 | 0 | 0
7083 | 529.02 | 0 | 23.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50.3966 | 529.02 | 0 | 0.05921 | 5.7613 | 0 | 0 | 82.601 | 0 | off_peak | 529.02 |  |  | 0 | 0 | 100 | 0 | 0
7084 | 554.49 | 0 | 23.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50.3966 | 554.49 | 0 | 0.05921 | 5.0799 | 0 | 0 | 82.601 | 0 | off_peak | 554.49 |  |  | 0 | 0 | 100 | 0 | 0
7085 | 543.57 | 0 | 23.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50.3966 | 543.57 | 0 | 0.05921 | 4.375 | 0 | 0 | 82.601 | 0 | off_peak | 543.57 |  |  | 0 | 0 | 100 | 0 | 0
7086 | 572.18 | 0 | 23.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50.3966 | 572.18 | 0 | 0.05921 | 3.7928 | 0 | 0 | 82.601 | 0 | off_peak | 572.18 |  |  | 0 | 0 | 100 | 0 | 0
7087 | 643.38 | 11.3978 | 23.9 | 2.3172 | 2.3172 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 61.9947 | 653.4617 | 0 | 0.05921 | 3.4058 | 0 | 0 | 82.601 | 2.3172 | off_peak | 641.0628 | 0 | 100 | 0.36 | 0 | 99.64 | 7.8918 | 0
7088 | 739.44 | 179.618 | 24.7 | 36.4119 | 36.4119 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 73.5928 | 715.427 | 0 | 0.05921 | 3.1755 | 0 | 0 | 82.601 | 36.4119 | off_peak | 703.0281 | 0 | 100 | 4.92 | 0 | 95.08 | 115.627 | 0
7089 | 765.24 | 388.801 | 25.5 | 78.5905 | 78.5905 | 0 | 0 | 0.80079 | 0.80079 | 0 | 0 | 0 | 74.3419 | 687.4503 | 0 | 0.05921 | 3.0438 | 0 | 0 | 82.601 | 78.5905 | off_peak | 686.6495 | 0 | 100 | 10.27 | 0 | 89.73 | 239.2168 | 0
7090 | 827.56 | 571.916 | 26.2 | 115.3127 | 115.261 | 0 | 0.05172 | 0.05172 | 0 | 0 | 0 | 0 | 74.3903 | 712.299 | 0 | 0.05921 | 3.0536 | 0 | 0 | 82.6493 | 115.261 | off_peak | 712.299 | 100 | 0 | 13.93 | 0 | 86.07 | 351.9591 | 0
7091 | 761.29 | 643.006 | 26.8 | 129.365 | 129.365 | 0 | 0 | 0.0033404 | 0.0033404 | 0 | 0 | 0 | 74.3934 | 631.9284 | 0 | 0.05921 | 3.2996 | 0 | 0 | 82.6493 | 129.365 | off_peak | 631.925 | 0 | 100 | 16.99 | 0 | 83.01 | 426.8532 | 0
7092 | 876.96 | 762.677 | 27.1 | 153.2745 | 153.2745 | 0 | 0 | 0.00021574 | 0.00021574 | 0 | 0 | 0 | 74.3936 | 723.6857 | 0 | 0.05921 | 3.791 | 0 | 0 | 82.6493 | 153.2745 | off_peak | 723.6855 | 0 | 100 | 17.48 | 0 | 82.52 | 581.0571 | 0
7093 | 811.72 | 742.546 | 27.4 | 149.0664 | 149.0664 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 662.6536 | 0 | 0.088511 | 4.091 | 0 | 0 | 82.6493 | 149.0664 | on_peak | 662.6536 |  |  | 18.36 | 0 | 81.64 | 609.8272 | 0
7094 | 842.82 | 717.907 | 27.5 | 144.0678 | 144.0678 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 698.7522 | 0 | 0.088511 | 4.0512 | 0 | 0 | 82.6493 | 144.0678 | on_peak | 698.7522 |  |  | 17.09 | 0 | 82.91 | 583.6443 | 0
7095 | 895.93 | 582.308 | 27.4 | 116.8986 | 116.8986 | 0 | 0 | 0 | 0 | 54.7534 | 54.7534 | 0 | 15.8598 | 724.278 | 0 | 0.088511 | 3.8971 | 0 | 0 | 82.6493 | 116.8986 | on_peak | 724.278 |  |  | 13.05 | 6.11 | 80.84 | 455.565 | 0
7096 | 803.23 | 416.313 | 27.2 | 83.6357 | 83.6357 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15.8598 | 719.5943 | 0 | 0.088511 | 4.0302 | 0 | 0 | 82.6493 | 83.6357 | on_peak | 719.5943 |  |  | 10.41 | 0 | 89.59 | 337.0711 | 0
7097 | 822.73 | 212.439 | 26.7 | 42.7556 | 42.7556 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15.8598 | 779.9744 | 0 | 0.088511 | 4.4235 | 0 | 0 | 82.6493 | 42.7556 | on_peak | 779.9744 |  |  | 5.2 | 0 | 94.8 | 189.1315 | 0
7098 | 839.46 | 26.4223 | 26 | 5.3313 | 5.3313 | 0 | 0 | 0 | 0 | 2.5077 | 2.5077 | 0 | 13.179 | 831.6211 | 0 | 0.088511 | 4.8317 | 0 | 0 | 82.6493 | 5.3313 | on_peak | 831.6211 |  |  | 0.64 | 0.3 | 99.07 | 25.7592 | 0
7099 | 795.12 | 0 | 25.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13.179 | 795.12 | 0 | 0.088511 | 5.3963 | 0 | 0 | 82.6493 | 0 | on_peak | 795.12 |  |  | 0 | 0 | 100 | 0 | 0
7100 | 836.99 | 0 | 25.3 | 0 | 0 | 0 | 0 | 0 | 0 | 5.3689 | 5.3689 | 0 | 7.4394 | 831.6211 | 0 | 0.088511 | 5.8339 | 0 | 0 | 82.6493 | 0 | on_peak | 831.6211 |  |  | 0 | 0.64 | 99.36 | 0 | 0
7101 | 819.8 | 0 | 25.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 819.8 | 0 | 0.088511 | 6.3854 | 0 | 0 | 82.6493 | 0 | on_peak | 819.8 |  |  | 0 | 0 | 100 | 0 | 0
7102 | 777.49 | 0 | 24.9 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 19.0375 | 789.8889 | 0 | 0.05921 | 6.9066 | 0 | 0 | 82.6493 | 0 | off_peak | 777.49 | 0 | 100 | 0 | 0 | 100 | 0 | 0
7103 | 793.43 | 0 | 24.8 | 0 | 0 | 0 | 0 | 8.7263 | 8.7263 | 0 | 0 | 0 | 27.2003 | 802.1563 | 0 | 0.05921 | 7.1231 | 0 | 0 | 82.6493 | 0 | off_peak | 793.43 | 0 | 100 | 0 | 0 | 100 | 0 | 0
7104 | 755.14 | 0 | 24.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27.2003 | 755.14 | 0 | 0.05921 | 7.4132 | 0 | 0 | 82.6493 | 0 | off_peak | 755.14 |  |  | 0 | 0 | 100 | 0 | 0
7105 | 720.4 | 0 | 24.6 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 38.7984 | 732.7989 | 0 | 0.05921 | 7.2752 | 0 | 0 | 82.6493 | 0 | off_peak | 720.4 | 0 | 100 | 0 | 0 | 100 | 0 | 0
7106 | 616.28 | 0 | 24.5 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 50.3966 | 628.6789 | 0 | 0.05921 | 6.7232 | 0 | 0 | 82.6493 | 0 | off_peak | 616.28 | 0 | 100 | 0 | 0 | 100 | 0 | 0
7107 | 622.82 | 0 | 24.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50.3966 | 622.82 | 0 | 0.05921 | 6.2747 | 0 | 0 | 82.6493 | 0 | off_peak | 622.82 |  |  | 0 | 0 | 100 | 0 | 0
7108 | 622.45 | 0 | 24.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50.3966 | 622.45 | 0 | 0.05921 | 5.6266 | 0 | 0 | 82.6493 | 0 | off_peak | 622.45 |  |  | 0 | 0 | 100 | 0 | 0
7109 | 591.14 | 0 | 24.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50.3966 | 591.14 | 0 | 0.05921 | 4.9748 | 0 | 0 | 82.6493 | 0 | off_peak | 591.14 |  |  | 0 | 0 | 100 | 0 | 0
7110 | 629.68 | 0 | 24.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50.3966 | 629.68 | 0 | 0.05921 | 4.3522 | 0 | 0 | 82.6493 | 0 | off_peak | 629.68 |  |  | 0 | 0 | 100 | 0 | 0
7111 | 688.69 | 11.4196 | 24.7 | 2.315 | 0 | 0 | 2.315 | 12.3989 | 10.084 | 0 | 0 | 0 | 61.9947 | 698.774 | 0 | 0.05921 | 3.9423 | 0 | 0 | 84.8148 | 0 | off_peak | 688.69 | 18.67 | 81.33 | 0 | 0 | 100 | 0 | 0
7112 | 750.09 | 176.419 | 25.5 | 35.6605 | 23.2616 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 0 | 73.5928 | 726.8284 | 0 | 0.05921 | 3.7348 | 0 | 0 | 96.4129 | 23.2616 | off_peak | 726.8284 | 100 | 0 | 3.1 | 0 | 96.9 | 86.8767 | 0
7113 | 784.3 | 366.69 | 26.2 | 73.9339 | 73.9339 | 0 | 0 | 0.80079 | 0.80079 | 0 | 0 | 0 | 74.3419 | 711.1668 | 0 | 0.05921 | 3.5881 | 0 | 0 | 96.4129 | 73.9339 | off_peak | 710.3661 | 0 | 100 | 9.43 | 0 | 90.57 | 265.2834 | 0
7114 | 806.28 | 487.952 | 26.7 | 98.2056 | 98.2056 | 0 | 0 | 0.05172 | 0.05172 | 0 | 0 | 0 | 74.3903 | 708.1262 | 0 | 0.05921 | 3.5696 | 0 | 0 | 96.4129 | 98.2056 | off_peak | 708.0744 | 0 | 100 | 12.18 | 0 | 87.82 | 350.556 | 0
7115 | 791.36 | 274.368 | 27.1 | 55.1395 | 55.1395 | 0 | 0 | 0.0033404 | 0.0033404 | 0 | 0 | 0 | 74.3934 | 736.2239 | 0 | 0.05921 | 3.8097 | 0 | 0 | 96.4129 | 55.1395 | off_peak | 736.2205 | 0 | 100 | 6.97 | 0 | 93.03 | 210.0659 | 0
7116 | 895.2 | 294.01 | 27.3 | 59.0441 | 59.0438 | 0 | 0.00021574 | 0.00021574 | 0 | 0 | 0 | 0 | 74.3936 | 836.1562 | 0 | 0.05921 | 4.3091 | 0 | 0 | 96.4131 | 59.0438 | off_peak | 836.1562 | 100 | 0 | 6.6 | 0 | 93.4 | 254.4272 | 0
7117 | 826.58 | 515.256 | 27.5 | 103.4003 | 103.4003 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 723.1797 | 0 | 0.088511 | 4.5587 | 0 | 0 | 96.4131 | 103.4003 | on_peak | 723.1797 |  |  | 12.51 | 0 | 87.49 | 471.3675 | 0
7118 | 869.34 | 705.685 | 27.5 | 141.6151 | 141.6151 | 0 | 0 | 0 | 0 | 19.7422 | 19.7422 | 0 | 53.2884 | 707.9827 | 0 | 0.088511 | 4.6194 | 0 | 0 | 96.4131 | 141.6151 | on_peak | 707.9827 |  |  | 16.29 | 2.27 | 81.44 | 654.1798 | 0
7119 | 926.22 | 581.472 | 27.3 | 116.7731 | 116.7731 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 53.2884 | 809.4469 | 0 | 0.088511 | 4.5639 | 0 | 0 | 96.4131 | 116.7731 | on_peak | 809.4469 |  |  | 12.61 | 0 | 87.39 | 532.9363 | 0
7120 | 833.91 | 409.149 | 27.1 | 82.2263 | 82.2263 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 53.2884 | 751.6837 | 0 | 0.088511 | 4.7006 | 0 | 0 | 96.4131 | 82.2263 | on_peak | 751.6837 |  |  | 9.86 | 0 | 90.14 | 386.5163 | 0
7121 | 846.86 | 208.157 | 26.6 | 41.909 | 41.909 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 53.2884 | 804.951 | 0 | 0.088511 | 4.9615 | 0 | 0 | 96.4131 | 41.909 | on_peak | 804.951 |  |  | 4.95 | 0 | 95.05 | 207.9329 | 0
7122 | 819.46 | 25.1946 | 26 | 5.0835 | 5.0835 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 53.2884 | 814.3765 | 0 | 0.088511 | 5.3417 | 0 | 0 | 96.4131 | 5.0835 | on_peak | 814.3765 |  |  | 0.62 | 0 | 99.38 | 27.155 | 0
7123 | 859.3 | 0 | 25.6 | 0 | 0 | 0 | 0 | 0 | 0 | 27.6789 | 27.6789 | 0 | 23.6984 | 831.6211 | 0 | 0.088511 | 5.6009 | 0 | 0 | 96.4131 | 0 | on_peak | 831.6211 |  |  | 0 | 3.22 | 96.78 | 0 | 0
7124 | 846.83 | 0 | 25.4 | 0 | 0 | 0 | 0 | 0 | 0 | 15.2089 | 15.2089 | 0 | 7.4394 | 831.6211 | 0 | 0.088511 | 5.7898 | 0 | 0 | 96.4131 | 0 | on_peak | 831.6211 |  |  | 0 | 1.8 | 98.2 | 0 | 0
7125 | 826.81 | 0 | 25.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 826.81 | 0 | 0.088511 | 6.0158 | 0 | 0 | 96.4131 | 0 | on_peak | 826.81 |  |  | 0 | 0 | 100 | 0 | 0
7126 | 817.32 | 0 | 25 | 0 | 0 | 0 | 0 | 8.7263 | 8.7263 | 0 | 0 | 0 | 15.6021 | 826.0463 | 0 | 0.05921 | 6.3219 | 0 | 0 | 96.4131 | 0 | off_peak | 817.32 | 0 | 100 | 0 | 0 | 100 | 0 | 0
7127 | 807.6 | 0 | 24.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15.6021 | 807.6 | 0 | 0.05921 | 6.6944 | 0 | 0 | 96.4131 | 0 | off_peak | 807.6 |  |  | 0 | 0 | 100 | 0 | 0
7128 | 806.63 | 0 | 24.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15.6021 | 806.63 | 0 | 0.05921 | 7.0073 | 0 | 0 | 96.4131 | 0 | off_peak | 806.63 |  |  | 0 | 0 | 100 | 0 | 0
7129 | 746.22 | 0 | 24.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15.6021 | 746.22 | 0 | 0.05921 | 7.0681 | 0 | 0 | 96.4131 | 0 | off_peak | 746.22 |  |  | 0 | 0 | 100 | 0 | 0
7130 | 637.35 | 0 | 24.4 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 27.2003 | 649.7489 | 0 | 0.05921 | 6.7347 | 0 | 0 | 96.4131 | 0 | off_peak | 637.35 | 0 | 100 | 0 | 0 | 100 | 0 | 0
7131 | 656.72 | 0 | 24.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27.2003 | 656.72 | 0 | 0.05921 | 6.2591 | 0 | 0 | 96.4131 | 0 | off_peak | 656.72 |  |  | 0 | 0 | 100 | 0 | 0
7132 | 600.02 | 0 | 24.2 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 38.7984 | 612.4189 | 0 | 0.05921 | 6.0266 | 0 | 0 | 96.4131 | 0 | off_peak | 600.02 | 0 | 100 | 0 | 0 | 100 | 0 | 0
7133 | 627.08 | 0 | 24.1 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 50.3966 | 639.4789 | 0 | 0.05921 | 5.3331 | 0 | 0 | 96.4131 | 0 | off_peak | 627.08 | 0 | 100 | 0 | 0 | 100 | 0 | 0
7134 | 650.92 | 0 | 24 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 61.9947 | 663.3189 | 0 | 0.05921 | 4.8169 | 0 | 0 | 96.4131 | 0 | off_peak | 650.92 | 0 | 100 | 0 | 0 | 100 | 0 | 0
7135 | 701.7 | 10.119 | 24.3 | 2.0543 | 0 | 0 | 2.0543 | 12.3989 | 10.3447 | 0 | 0 | 0 | 73.5928 | 712.0447 | 0 | 0.05921 | 4.3543 | 0 | 0 | 98.3347 | 0 | off_peak | 701.7 | 16.57 | 83.43 | 0 | 0 | 100 | 0 | 0
7136 | 795.41 | 171.674 | 25 | 34.764 | 34.764 | 0 | 0 | 0.80079 | 0.80079 | 0 | 0 | 0 | 74.3419 | 761.4468 | 0 | 0.05921 | 4.1221 | 0 | 0 | 98.3347 | 34.764 | off_peak | 760.646 | 0 | 100 | 4.37 | 0 | 95.63 | 143.302 | 0
7137 | 818.59 | 383.594 | 25.7 | 77.482 | 77.4303 | 0 | 0.05172 | 0.05172 | 0 | 0 | 0 | 0 | 74.3903 | 741.1597 | 0 | 0.05921 | 3.973 | 0 | 0 | 98.3831 | 77.4303 | off_peak | 741.1597 | 100 | 0 | 9.46 | 0 | 90.54 | 307.6271 | 0
7138 | 832.7 | 570.357 | 26.2 | 114.9983 | 114.9983 | 0 | 0 | 0.0033404 | 0.0033404 | 0 | 0 | 0 | 74.3934 | 717.705 | 0 | 0.05921 | 4.0012 | 0 | 0 | 98.3831 | 114.9983 | off_peak | 717.7017 | 0 | 100 | 13.81 | 0 | 86.19 | 460.1294 | 0
7139 | 833.16 | 706.749 | 26.7 | 142.2408 | 142.2408 | 0 | 0 | 0.00021574 | 0.00021574 | 0 | 0 | 0 | 74.3936 | 690.9194 | 0 | 0.05921 | 4.2879 | 0 | 0 | 98.3831 | 142.2408 | off_peak | 690.9192 | 0 | 100 | 17.07 | 0 | 82.93 | 609.9208 | 0
7140 | 884.09 | 781.279 | 27.1 | 157.0129 | 157.0129 | 0 | 0 | 1.3934e-05 | 1.3934e-05 | 0 | 0 | 0 | 74.3936 | 727.0771 | 0 | 0.05921 | 4.7112 | 0 | 0 | 98.3831 | 157.0129 | off_peak | 727.0771 | 0 | 100 | 17.76 | 0 | 82.24 | 739.7126 | 0
7141 | 832.78 | 686.859 | 27.4 | 137.8872 | 137.8872 | 0 | 0 | 0 | 0 | 62.63 | 62.63 | 0 | 7.4394 | 632.2628 | 0 | 0.088511 | 5.0108 | 0 | 0 | 98.3831 | 137.8872 | on_peak | 632.2628 |  |  | 16.56 | 7.52 | 75.92 | 690.9241 | 0
7142 | 871.89 | 538.255 | 27.5 | 108.0157 | 108.0157 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 763.8743 | 0 | 0.088511 | 5.0999 | 0 | 0 | 98.3831 | 108.0157 | on_peak | 763.8743 |  |  | 12.39 | 0 | 87.61 | 550.8691 | 0
7143 | 857.58 | 582.472 | 27.6 | 116.8466 | 116.8466 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 740.7334 | 0 | 0.088511 | 5.1435 | 0 | 0 | 98.3831 | 116.8466 | on_peak | 740.7334 |  |  | 13.63 | 0 | 86.37 | 600.9992 | 0
7144 | 762.5 | 417.231 | 27.4 | 83.7593 | 83.7593 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 678.7407 | 0 | 0.088511 | 5.2587 | 0 | 0 | 98.3831 | 83.7593 | on_peak | 678.7407 |  |  | 10.98 | 0 | 89.02 | 440.4659 | 0
7145 | 755.89 | 209.742 | 26.9 | 42.1822 | 42.1822 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 713.7078 | 0 | 0.088511 | 5.4778 | 0 | 0 | 98.3831 | 42.1822 | on_peak | 713.7078 |  |  | 5.58 | 0 | 94.42 | 231.066 | 0
7146 | 751.17 | 24.5542 | 26.1 | 4.9525 | 4.9525 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 746.2175 | 0 | 0.088511 | 5.8876 | 0 | 0 | 98.3831 | 4.9525 | on_peak | 746.2175 |  |  | 0.66 | 0 | 99.34 | 29.1586 | 0
7147 | 776.09 | 0 | 25.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 776.09 | 0 | 0.088511 | 6.2051 | 0 | 0 | 98.3831 | 0 | on_peak | 776.09 |  |  | 0 | 0 | 100 | 0 | 0
7148 | 772.35 | 0 | 25.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 772.35 | 0 | 0.088511 | 6.3825 | 0 | 0 | 98.3831 | 0 | on_peak | 772.35 |  |  | 0 | 0 | 100 | 0 | 0
7149 | 768.39 | 0 | 24.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 768.39 | 0 | 0.088511 | 6.6792 | 0 | 0 | 98.3831 | 0 | on_peak | 768.39 |  |  | 0 | 0 | 100 | 0 | 0
7150 | 743.98 | 0 | 24.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 743.98 | 0 | 0.05921 | 7.0146 | 0 | 0 | 98.3831 | 0 | off_peak | 743.98 |  |  | 0 | 0 | 100 | 0 | 0
7151 | 749.63 | 0 | 24.7 | 0 | 0 | 0 | 0 | 8.7263 | 8.7263 | 0 | 0 | 0 | 15.6021 | 758.3563 | 0 | 0.05921 | 7.2794 | 0 | 0 | 98.3831 | 0 | off_peak | 749.63 | 0 | 100 | 0 | 0 | 100 | 0 | 0
7152 | 741.78 | 0 | 24.7 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 27.2003 | 754.1789 | 0 | 0.05921 | 7.3908 | 0 | 0 | 98.3831 | 0 | off_peak | 741.78 | 0 | 100 | 0 | 0 | 100 | 0 | 0
7153 | 696.37 | 0 | 24.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27.2003 | 696.37 | 0 | 0.05921 | 7.3987 | 0 | 0 | 98.3831 | 0 | off_peak | 696.37 |  |  | 0 | 0 | 100 | 0 | 0
7154 | 636.35 | 0 | 24.7 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 38.7984 | 648.7489 | 0 | 0.05921 | 7.1098 | 0 | 0 | 98.3831 | 0 | off_peak | 636.35 | 0 | 100 | 0 | 0 | 100 | 0 | 0
7155 | 653.68 | 0 | 24.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 38.7984 | 653.68 | 0 | 0.05921 | 6.7026 | 0 | 0 | 98.3831 | 0 | off_peak | 653.68 |  |  | 0 | 0 | 100 | 0 | 0
7156 | 598.57 | 0 | 24.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 38.7984 | 598.57 | 0 | 0.05921 | 6.1779 | 0 | 0 | 98.3831 | 0 | off_peak | 598.57 |  |  | 0 | 0 | 100 | 0 | 0
7157 | 604.61 | 0 | 24.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 38.7984 | 604.61 | 0 | 0.05921 | 5.4949 | 0 | 0 | 98.3831 | 0 | off_peak | 604.61 |  |  | 0 | 0 | 100 | 0 | 0
7158 | 644.55 | 0 | 24.3 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 50.3966 | 656.9489 | 0 | 0.05921 | 4.8439 | 0 | 0 | 98.3831 | 0 | off_peak | 644.55 | 0 | 100 | 0 | 0 | 100 | 0 | 0
7159 | 689.9 | 10.0883 | 24.4 | 2.0473 | 0 | 0 | 2.0473 | 12.3989 | 10.3516 | 0 | 0 | 0 | 61.9947 | 700.2516 | 0 | 0.05921 | 4.4321 | 0 | 0 | 100.2982 | 0 | off_peak | 689.9 | 16.51 | 83.49 | 0 | 0 | 100 | 0 | 0
7160 | 743.92 | 173.885 | 25 | 35.2117 | 35.2117 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 73.5928 | 721.1072 | 0 | 0.05921 | 4.1582 | 0 | 0 | 100.2982 | 35.2117 | off_peak | 708.7083 | 0 | 100 | 4.73 | 0 | 95.27 | 146.4187 | 0
7161 | 787.7 | 381.619 | 25.7 | 77.0831 | 77.0831 | 0 | 0 | 0.80079 | 0.80079 | 0 | 0 | 0 | 74.3419 | 711.4177 | 0 | 0.05921 | 4.0473 | 0 | 0 | 100.2982 | 77.0831 | off_peak | 710.6169 | 0 | 100 | 9.79 | 0 | 90.21 | 311.9774 | 0
7162 | 830.14 | 564.948 | 26.3 | 113.8666 | 113.8666 | 0 | 0 | 0.05172 | 0.05172 | 0 | 0 | 0 | 74.3903 | 716.3252 | 0 | 0.05921 | 4.0562 | 0 | 0 | 100.2982 | 113.8666 | off_peak | 716.2734 | 0 | 100 | 13.72 | 0 | 86.28 | 461.8696 | 0
7163 | 796.64 | 700.568 | 26.8 | 140.9457 | 140.9457 | 0 | 0 | 0.0033404 | 0.0033404 | 0 | 0 | 0 | 74.3934 | 655.6976 | 0 | 0.05921 | 4.2697 | 0 | 0 | 100.2982 | 140.9457 | off_peak | 655.6943 | 0 | 100 | 17.69 | 0 | 82.31 | 601.7909 | 0
7164 | 848.14 | 772.538 | 27.2 | 155.1999 | 155.1999 | 0 | 0 | 0.00021574 | 0.00021574 | 0 | 0 | 0 | 74.3936 | 692.9403 | 0 | 0.05921 | 4.6907 | 0 | 0 | 100.2982 | 155.1999 | off_peak | 692.9401 | 0 | 100 | 18.3 | 0 | 81.7 | 727.9989 | 0
7165 | 789.49 | 776.284 | 27.5 | 155.7827 | 155.7827 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 633.7073 | 0 | 0.088511 | 4.8704 | 0 | 0 | 100.2982 | 155.7827 | on_peak | 633.7073 |  |  | 19.73 | 0 | 80.27 | 758.72 | 0
7166 | 835.27 | 710.709 | 27.7 | 142.5197 | 142.5197 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 692.7503 | 0 | 0.088511 | 4.8427 | 0 | 0 | 100.2982 | 142.5197 | on_peak | 692.7503 |  |  | 17.06 | 0 | 82.94 | 690.1741 | 0
7167 | 855.02 | 584.082 | 27.8 | 117.0844 | 117.0844 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 737.9356 | 0 | 0.088511 | 4.6778 | 0 | 0 | 100.2982 | 117.0844 | on_peak | 737.9356 |  |  | 13.69 | 0 | 86.31 | 547.6939 | 0
7168 | 794.95 | 388.797 | 27.8 | 77.9378 | 77.9378 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 717.0122 | 0 | 0.088511 | 4.7091 | 0 | 0 | 100.2982 | 77.9378 | on_peak | 717.0122 |  |  | 9.8 | 0 | 90.2 | 367.0159 | 0
7169 | 793.47 | 200.626 | 27.5 | 40.2611 | 40.2611 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 753.2089 | 0 | 0.088511 | 4.9784 | 0 | 0 | 100.2982 | 40.2611 | on_peak | 753.2089 |  |  | 5.07 | 0 | 94.93 | 200.4353 | 0
7170 | 820.31 | 23.4368 | 27.2 | 4.7084 | 4.7084 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 815.6016 | 0 | 0.088511 | 5.2603 | 0 | 0 | 100.2982 | 4.7084 | on_peak | 815.6016 |  |  | 0.57 | 0 | 99.43 | 24.7676 | 0
7171 | 778.38 | 0 | 26.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 778.38 | 0 | 0.088511 | 5.7328 | 0 | 0 | 100.2982 | 0 | on_peak | 778.38 |  |  | 0 | 0 | 100 | 0 | 0
7172 | 814.62 | 0 | 26.4 | 0 | 0 | 0 | 0 | 0 | 0 | 62.63 | 62.63 | 0 | 7.4394 | 751.99 | 0 | 0.088511 | 6.0912 | 0 | 0 | 100.2982 | 0 | on_peak | 751.99 |  |  | 0 | 7.69 | 92.31 | 0 | 0
7173 | 795.17 | 0 | 26.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 795.17 | 0 | 0.088511 | 6.4341 | 0 | 0 | 100.2982 | 0 | on_peak | 795.17 |  |  | 0 | 0 | 100 | 0 | 0
7174 | 740.44 | 0 | 25.8 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 19.0375 | 752.8389 | 0 | 0.05921 | 6.7264 | 0 | 0 | 100.2982 | 0 | off_peak | 740.44 | 0 | 100 | 0 | 0 | 100 | 0 | 0
7175 | 775.84 | 0 | 25.6 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 30.6357 | 788.2389 | 0 | 0.05921 | 6.9351 | 0 | 0 | 100.2982 | 0 | off_peak | 775.84 | 0 | 100 | 0 | 0 | 100 | 0 | 0
7176 | 755.83 | 0 | 25.3 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 42.2338 | 768.2289 | 0 | 0.05921 | 7.1101 | 0 | 0 | 100.2982 | 0 | off_peak | 755.83 | 0 | 100 | 0 | 0 | 100 | 0 | 0
7177 | 688.17 | 0 | 25.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 42.2338 | 688.17 | 0 | 0.05921 | 7.0462 | 0 | 0 | 100.2982 | 0 | off_peak | 688.17 |  |  | 0 | 0 | 100 | 0 | 0
7178 | 684.84 | 0 | 24.9 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 53.832 | 697.2389 | 0 | 0.05921 | 6.7525 | 0 | 0 | 100.2982 | 0 | off_peak | 684.84 | 0 | 100 | 0 | 0 | 100 | 0 | 0
7179 | 589.34 | 0 | 24.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 53.832 | 589.34 | 0 | 0.05921 | 6.4154 | 0 | 0 | 100.2982 | 0 | off_peak | 589.34 |  |  | 0 | 0 | 100 | 0 | 0
7180 | 593.33 | 0 | 24.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 53.832 | 593.33 | 0 | 0.05921 | 5.7363 | 0 | 0 | 100.2982 | 0 | off_peak | 593.33 |  |  | 0 | 0 | 100 | 0 | 0
7181 | 634.27 | 0 | 24.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 53.832 | 634.27 | 0 | 0.05921 | 5.0568 | 0 | 0 | 100.2982 | 0 | off_peak | 634.27 |  |  | 0 | 0 | 100 | 0 | 0
7182 | 600.85 | 0 | 24.6 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 65.4301 | 613.2489 | 0 | 0.05921 | 4.5444 | 0 | 0 | 100.2982 | 0 | off_peak | 600.85 | 0 | 100 | 0 | 0 | 100 | 0 | 0
7183 | 708.84 | 9.7978 | 24.8 | 1.9855 | 0 | 0 | 1.9855 | 8.9635 | 6.9781 | 0 | 0 | 0 | 73.8147 | 715.8181 | 0 | 0.05921 | 4.1608 | 0 | 0 | 102.1554 | 0 | off_peak | 708.84 | 22.15 | 77.85 | 0 | 0 | 100 | 0 | 0
7184 | 772.27 | 162.075 | 25.3 | 32.7847 | 32.2058 | 0 | 0.57892 | 0.57892 | 0 | 0 | 0 | 0 | 74.3563 | 740.0642 | 0 | 0.05921 | 3.8908 | 0 | 0 | 102.6969 | 32.2058 | off_peak | 740.0642 | 100 | 0 | 4.17 | 0 | 95.83 | 125.3061 | 0
7185 | 826.74 | 362.45 | 25.9 | 73.1583 | 73.1583 | 0 | 0 | 0.03739 | 0.03739 | 0 | 0 | 0 | 74.3912 | 753.6191 | 0 | 0.05921 | 3.7194 | 0 | 0 | 102.6969 | 73.1583 | off_peak | 753.5817 | 0 | 100 | 8.85 | 0 | 91.15 | 272.1034 | 0
7186 | 859.31 | 541.861 | 26.5 | 109.1343 | 109.1343 | 0 | 0 | 0.0024148 | 0.0024148 | 0 | 0 | 0 | 74.3935 | 750.1781 | 0 | 0.05921 | 3.6538 | 0 | 0 | 102.6969 | 109.1343 | off_peak | 750.1757 | 0 | 100 | 12.7 | 0 | 87.3 | 398.7552 | 0
7187 | 807.37 | 673.558 | 27.1 | 135.3643 | 135.3643 | 0 | 0 | 0.00015596 | 0.00015596 | 0 | 0 | 0 | 74.3936 | 672.0058 | 0 | 0.05921 | 3.8405 | 0 | 0 | 102.6969 | 135.3643 | off_peak | 672.0057 | 0 | 100 | 16.77 | 0 | 83.23 | 519.8674 | 0
7188 | 947.22 | 745.032 | 27.5 | 149.5112 | 149.5112 | 0 | 0 | 1.0073e-05 | 1.0073e-05 | 0 | 0 | 0 | 74.3936 | 797.7089 | 0 | 0.05921 | 4.2642 | 0 | 0 | 102.6969 | 149.5112 | off_peak | 797.7088 | 0 | 100 | 15.78 | 0 | 84.22 | 637.5484 | 0
7189 | 822.22 | 652.895 | 27.9 | 130.831 | 130.831 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 691.389 | 0 | 0.088511 | 4.5591 | 0 | 0 | 102.6969 | 130.831 | on_peak | 691.389 |  |  | 15.91 | 0 | 84.09 | 596.474 | 0
7190 | 843.32 | 690.625 | 28.1 | 138.2908 | 138.2908 | 0 | 0 | 0 | 0 | 62.63 | 62.63 | 0 | 7.4394 | 642.3992 | 0 | 0.088511 | 4.7409 | 0 | 0 | 102.6969 | 138.2908 | on_peak | 642.3992 |  |  | 16.4 | 7.43 | 76.18 | 655.6223 | 0
7191 | 864.75 | 566.531 | 28.1 | 113.4422 | 113.4422 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 751.3078 | 0 | 0.088511 | 4.8145 | 0 | 0 | 102.6969 | 113.4422 | on_peak | 751.3078 |  |  | 13.12 | 0 | 86.88 | 546.1635 | 0
7192 | 795.37 | 393.845 | 27.9 | 78.921 | 78.921 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 716.449 | 0 | 0.088511 | 4.9792 | 0 | 0 | 102.6969 | 78.921 | on_peak | 716.449 |  |  | 9.92 | 0 | 90.08 | 392.9641 | 0
7193 | 768.48 | 194.376 | 27.5 | 39.0069 | 39.0069 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 729.4731 | 0 | 0.088511 | 5.3314 | 0 | 0 | 102.6969 | 39.0069 | on_peak | 729.4731 |  |  | 5.08 | 0 | 94.92 | 207.9601 | 0
7194 | 820.76 | 21.5105 | 26.8 | 4.3277 | 4.3277 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 816.4323 | 0 | 0.088511 | 5.7396 | 0 | 0 | 102.6969 | 4.3277 | on_peak | 816.4323 |  |  | 0.53 | 0 | 99.47 | 24.8391 | 0
7195 | 781.67 | 0 | 26.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 781.67 | 0 | 0.088511 | 6.1439 | 0 | 0 | 102.6969 | 0 | on_peak | 781.67 |  |  | 0 | 0 | 100 | 0 | 0
7196 | 763.66 | 0 | 26.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 763.66 | 0 | 0.088511 | 6.3318 | 0 | 0 | 102.6969 | 0 | on_peak | 763.66 |  |  | 0 | 0 | 100 | 0 | 0
7197 | 770.53 | 0 | 25.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 770.53 | 0 | 0.088511 | 6.6638 | 0 | 0 | 102.6969 | 0 | on_peak | 770.53 |  |  | 0 | 0 | 100 | 0 | 0
7198 | 711.71 | 0 | 25.7 | 0 | 0 | 0 | 0 | 0.030964 | 0.030964 | 0 | 0 | 0 | 7.4683 | 711.741 | 0 | 0.05921 | 6.8684 | 0 | 0 | 102.6969 | 0 | off_peak | 711.71 | 0 | 100 | 0 | 0 | 100 | 0 | 0
7199 | 707.04 | 0 | 25.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4683 | 707.04 | 0 | 0.05921 | 7.1407 | 0 | 0 | 102.6969 | 0 | off_peak | 707.04 |  |  | 0 | 0 | 100 | 0 | 0
7200 | 696.28 | 0 | 25.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4683 | 696.28 | 0 | 0.05921 | 7.178 | 0 | 0 | 102.6969 | 0 | off_peak | 696.28 |  |  | 0 | 0 | 100 | 0 | 0
7201 | 648.53 | 0 | 25.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4683 | 648.53 | 0 | 0.05921 | 6.9475 | 0 | 0 | 102.6969 | 0 | off_peak | 648.53 |  |  | 0 | 0 | 100 | 0 | 0
7202 | 623.24 | 0 | 25.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4683 | 623.24 | 0 | 0.05921 | 6.5721 | 0 | 0 | 102.6969 | 0 | off_peak | 623.24 |  |  | 0 | 0 | 100 | 0 | 0
7203 | 582.52 | 0 | 25.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4683 | 582.52 | 0 | 0.05921 | 6.1853 | 0 | 0 | 102.6969 | 0 | off_peak | 582.52 |  |  | 0 | 0 | 100 | 0 | 0
7204 | 631.65 | 0 | 25.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4683 | 631.65 | 0 | 0.05921 | 5.6958 | 0 | 0 | 102.6969 | 0 | off_peak | 631.65 |  |  | 0 | 0 | 100 | 0 | 0
7205 | 608.52 | 0 | 25.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4683 | 608.52 | 0 | 0.05921 | 5.0805 | 0 | 0 | 102.6969 | 0 | off_peak | 608.52 |  |  | 0 | 0 | 100 | 0 | 0
7206 | 647.41 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4683 | 647.41 | 0 | 0.05921 | 4.6049 | 0 | 0 | 102.6969 | 0 | off_peak | 647.41 |  |  | 0 | 0 | 100 | 0 | 0
7207 | 694.22 | 9.7403 | 25.4 | 1.9696 | 0 | 0 | 1.9696 | 1.9696 | 0 | 0 | 0 | 0 | 9.3107 | 694.22 | 0 | 0.05921 | 4.182 | 0 | 0 | 104.5393 | 0 | off_peak | 694.22 | 100 | 0 | 0 | 0 | 100 | 0 | 0
7208 | 688.61 | 165.446 | 26.1 | 33.3701 | 33.3701 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9.3107 | 655.2399 | 0 | 0.05921 | 3.8973 | 0 | 0 | 104.5393 | 33.3701 | off_peak | 655.2399 |  |  | 4.85 | 0 | 95.15 | 130.0533 | 0
7209 | 739.75 | 369.8 | 26.7 | 74.4262 | 74.4262 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9.3107 | 665.3238 | 0 | 0.05921 | 3.7288 | 0 | 0 | 104.5393 | 74.4262 | off_peak | 665.3238 |  |  | 10.06 | 0 | 89.94 | 277.5216 | 0
7210 | 731.34 | 551.961 | 27.2 | 110.8869 | 110.8869 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9.3107 | 620.4531 | 0 | 0.05921 | 3.6437 | 0 | 0 | 104.5393 | 110.8869 | off_peak | 620.4531 |  |  | 15.16 | 0 | 84.84 | 404.0371 | 0
7211 | 714.24 | 684.762 | 27.5 | 137.4163 | 137.4163 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9.3107 | 576.8237 | 0 | 0.05921 | 3.6654 | 0 | 0 | 104.5393 | 137.4163 | off_peak | 576.8237 |  |  | 19.24 | 0 | 80.76 | 503.6887 | 0
7212 | 713.09 | 756.317 | 27.8 | 151.6104 | 151.6104 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9.3107 | 561.4796 | 0 | 0.05921 | 3.8229 | 0 | 0 | 104.5393 | 151.6104 | off_peak | 561.4796 |  |  | 21.26 | 0 | 78.74 | 579.5953 | 0
7213 | 706.98 | 761.95 | 27.9 | 152.684 | 152.684 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9.3107 | 554.296 | 0 | 0.05921 | 4.0976 | 0 | 0 | 104.5393 | 152.684 | off_peak | 554.296 |  |  | 21.6 | 0 | 78.4 | 625.6436 | 0
7214 | 689.35 | 698.357 | 28 | 139.89 | 139.89 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9.3107 | 549.46 | 0 | 0.05921 | 4.3649 | 0 | 0 | 104.5393 | 139.89 | off_peak | 549.46 |  |  | 20.29 | 0 | 79.71 | 610.6076 | 0
7215 | 724.33 | 574.389 | 27.9 | 115.0995 | 115.0995 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9.3107 | 609.2305 | 0 | 0.05921 | 4.5264 | 0 | 0 | 104.5393 | 115.0995 | off_peak | 609.2305 |  |  | 15.89 | 0 | 84.11 | 520.9844 | 0
7216 | 664.71 | 401.038 | 27.6 | 80.4501 | 80.4501 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9.3107 | 584.2599 | 0 | 0.05921 | 4.7978 | 0 | 0 | 104.5393 | 80.4501 | off_peak | 584.2599 |  |  | 12.1 | 0 | 87.9 | 385.9836 | 0
7217 | 706.52 | 198.37 | 27.2 | 39.8518 | 39.8518 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9.3107 | 666.6682 | 0 | 0.05921 | 5.2822 | 0 | 0 | 104.5393 | 39.8518 | off_peak | 666.6682 |  |  | 5.64 | 0 | 94.36 | 210.5068 | 0
7218 | 642.51 | 22.8662 | 26.6 | 4.6037 | 0 | 0 | 4.6037 | 4.6037 | 0 | 0 | 0 | 0 | 13.6171 | 642.51 | 0 | 0.05921 | 5.6835 | 0 | 0 | 108.8457 | 0 | off_peak | 642.51 | 100 | 0 | 0 | 0 | 100 | 0 | 0
7219 | 568.62 | 0 | 26.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13.6171 | 568.62 | 0 | 0.05921 | 6.0279 | 0 | 0 | 108.8457 | 0 | off_peak | 568.62 |  |  | 0 | 0 | 100 | 0 | 0
7220 | 564.06 | 0 | 26.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13.6171 | 564.06 | 0 | 0.05921 | 6.1925 | 0 | 0 | 108.8457 | 0 | off_peak | 564.06 |  |  | 0 | 0 | 100 | 0 | 0
7221 | 539.13 | 0 | 26 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13.6171 | 539.13 | 0 | 0.05921 | 6.4778 | 0 | 0 | 108.8457 | 0 | off_peak | 539.13 |  |  | 0 | 0 | 100 | 0 | 0
7222 | 549.19 | 0 | 25.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13.6171 | 549.19 | 0 | 0.05921 | 6.6852 | 0 | 0 | 108.8457 | 0 | off_peak | 549.19 |  |  | 0 | 0 | 100 | 0 | 0
7223 | 550.74 | 0 | 25.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13.6171 | 550.74 | 0 | 0.05921 | 6.9686 | 0 | 0 | 108.8457 | 0 | off_peak | 550.74 |  |  | 0 | 0 | 100 | 0 | 0
7224 | 528.14 | 0 | 25.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13.6171 | 528.14 | 0 | 0.05921 | 7.0942 | 0 | 0 | 108.8457 | 0 | off_peak | 528.14 |  |  | 0 | 0 | 100 | 0 | 0
7225 | 569.69 | 0 | 25.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13.6171 | 569.69 | 0 | 0.05921 | 6.8275 | 0 | 0 | 108.8457 | 0 | off_peak | 569.69 |  |  | 0 | 0 | 100 | 0 | 0
7226 | 536.43 | 0 | 25.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13.6171 | 536.43 | 0 | 0.05921 | 6.5149 | 0 | 0 | 108.8457 | 0 | off_peak | 536.43 |  |  | 0 | 0 | 100 | 0 | 0
7227 | 532.58 | 0 | 25.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13.6171 | 532.58 | 0 | 0.05921 | 6.0823 | 0 | 0 | 108.8457 | 0 | off_peak | 532.58 |  |  | 0 | 0 | 100 | 0 | 0
7228 | 562.09 | 0 | 25.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13.6171 | 562.09 | 0 | 0.05921 | 5.6348 | 0 | 0 | 108.8457 | 0 | off_peak | 562.09 |  |  | 0 | 0 | 100 | 0 | 0
7229 | 559.98 | 0 | 25.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13.6171 | 559.98 | 0 | 0.05921 | 5.0456 | 0 | 0 | 108.8457 | 0 | off_peak | 559.98 |  |  | 0 | 0 | 100 | 0 | 0
7230 | 613.4 | 0 | 25.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13.6171 | 613.4 | 0 | 0.05921 | 4.5678 | 0 | 0 | 108.8457 | 0 | off_peak | 613.4 |  |  | 0 | 0 | 100 | 0 | 0
7231 | 612.48 | 8.6369 | 25.6 | 1.7452 | 0 | 0 | 1.7452 | 1.7452 | 0 | 0 | 0 | 0 | 15.2496 | 612.48 | 0 | 0.05921 | 4.166 | 0 | 0 | 110.4782 | 0 | off_peak | 612.48 | 100 | 0 | 0 | 0 | 100 | 0 | 0
7232 | 679.74 | 157.734 | 26.3 | 31.7917 | 31.7917 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15.2496 | 647.9483 | 0 | 0.05921 | 3.9054 | 0 | 0 | 110.4782 | 31.7917 | off_peak | 647.9483 |  |  | 4.68 | 0 | 95.32 | 124.1605 | 0
7233 | 666.64 | 357.524 | 27 | 71.8773 | 71.8773 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15.2496 | 594.7627 | 0 | 0.05921 | 3.7163 | 0 | 0 | 110.4782 | 71.8773 | off_peak | 594.7627 |  |  | 10.78 | 0 | 89.22 | 267.1185 | 0
7234 | 685.22 | 449.001 | 27.5 | 90.1044 | 90.1044 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15.2496 | 595.1156 | 0 | 0.05921 | 3.6002 | 0 | 0 | 110.4782 | 90.1044 | off_peak | 595.1156 |  |  | 13.15 | 0 | 86.85 | 324.3956 | 0
7235 | 678.52 | 589.094 | 27.9 | 118.0461 | 118.0461 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15.2496 | 560.4739 | 0 | 0.05921 | 3.5758 | 0 | 0 | 110.4782 | 118.0461 | off_peak | 560.4739 |  |  | 17.4 | 0 | 82.6 | 422.1066 | 0
7236 | 720.14 | 560.793 | 28.3 | 112.2115 | 112.2115 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 26.8477 | 620.3275 | 0 | 0.05921 | 3.6651 | 0 | 0 | 110.4782 | 112.2115 | off_peak | 607.9285 | 0 | 100 | 15.58 | 0 | 84.42 | 411.2673 | 0
7237 | 679.07 | 696.429 | 28.5 | 139.2499 | 139.2499 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 26.8477 | 539.8201 | 0 | 0.05921 | 3.898 | 0 | 0 | 110.4782 | 139.2499 | off_peak | 539.8201 |  |  | 20.51 | 0 | 79.49 | 542.7965 | 0
7238 | 684.14 | 667.439 | 28.5 | 133.4534 | 133.4534 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 26.8477 | 550.6866 | 0 | 0.05921 | 4.1919 | 0 | 0 | 110.4782 | 133.4534 | off_peak | 550.6866 |  |  | 19.51 | 0 | 80.49 | 559.4243 | 0
7239 | 669.81 | 433.495 | 28.3 | 86.7399 | 86.7399 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 26.8477 | 583.0701 | 0 | 0.05921 | 4.3989 | 0 | 0 | 110.4782 | 86.7399 | off_peak | 583.0701 |  |  | 12.95 | 0 | 87.05 | 381.5607 | 0
7240 | 661.26 | 276.855 | 28 | 55.4577 | 55.4577 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 26.8477 | 605.8023 | 0 | 0.05921 | 4.6327 | 0 | 0 | 110.4782 | 55.4577 | off_peak | 605.8023 |  |  | 8.39 | 0 | 91.61 | 256.9181 | 0
7241 | 659.51 | 188.279 | 27.6 | 37.7696 | 37.7696 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 38.4459 | 634.1393 | 0 | 0.05921 | 5.1288 | 0 | 0 | 110.4782 | 37.7696 | off_peak | 621.7404 | 0 | 100 | 5.73 | 0 | 94.27 | 193.7131 | 0
7242 | 633.76 | 19.0737 | 27.1 | 3.8332 | 0 | 0 | 3.8332 | 12.3989 | 8.5657 | 0 | 0 | 0 | 50.044 | 642.3257 | 0 | 0.05921 | 5.5764 | 0 | 0 | 114.0638 | 0 | off_peak | 633.76 | 30.92 | 69.08 | 0 | 0 | 100 | 0 | 0
7243 | 606.8 | 0 | 26.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50.044 | 606.8 | 0 | 0.05921 | 5.9045 | 0 | 0 | 114.0638 | 0 | off_peak | 606.8 |  |  | 0 | 0 | 100 | 0 | 0
7244 | 589.14 | 0 | 26.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50.044 | 589.14 | 0 | 0.05921 | 6.0813 | 0 | 0 | 114.0638 | 0 | off_peak | 589.14 |  |  | 0 | 0 | 100 | 0 | 0
7245 | 558.75 | 0 | 26.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50.044 | 558.75 | 0 | 0.05921 | 6.3474 | 0 | 0 | 114.0638 | 0 | off_peak | 558.75 |  |  | 0 | 0 | 100 | 0 | 0
7246 | 555.8 | 0 | 26.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50.044 | 555.8 | 0 | 0.05921 | 6.5717 | 0 | 0 | 114.0638 | 0 | off_peak | 555.8 |  |  | 0 | 0 | 100 | 0 | 0
7247 | 545.97 | 0 | 26.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50.044 | 545.97 | 0 | 0.05921 | 6.9617 | 0 | 0 | 114.0638 | 0 | off_peak | 545.97 |  |  | 0 | 0 | 100 | 0 | 0
7248 | 585.71 | 0 | 26.1 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 61.6422 | 598.1089 | 0 | 0.05921 | 7.3155 | 0 | 0 | 114.0638 | 0 | off_peak | 585.71 | 0 | 100 | 0 | 0 | 100 | 0 | 0
7249 | 558.59 | 0 | 26 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 61.6422 | 558.59 | 0 | 0.05921 | 7.2144 | 0 | 0 | 114.0638 | 0 | off_peak | 558.59 |  |  | 0 | 0 | 100 | 0 | 0
7250 | 558.34 | 0 | 25.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 61.6422 | 558.34 | 0 | 0.05921 | 6.828 | 0 | 0 | 114.0638 | 0 | off_peak | 558.34 |  |  | 0 | 0 | 100 | 0 | 0
7251 | 557.91 | 0 | 25.7 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 73.2403 | 570.3089 | 0 | 0.05921 | 6.4177 | 0 | 0 | 114.0638 | 0 | off_peak | 557.91 | 0 | 100 | 0 | 0 | 100 | 0 | 0
7252 | 561.35 | 0 | 25.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 73.2403 | 561.35 | 0 | 0.05921 | 5.8396 | 0 | 0 | 114.0638 | 0 | off_peak | 561.35 |  |  | 0 | 0 | 100 | 0 | 0
7253 | 578.68 | 0 | 25.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 73.2403 | 578.68 | 0 | 0.05921 | 5.0442 | 0 | 0 | 114.0638 | 0 | off_peak | 578.68 |  |  | 0 | 0 | 100 | 0 | 0
7254 | 588.05 | 0 | 25.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 73.2403 | 588.05 | 0 | 0.05921 | 4.4914 | 0 | 0 | 114.0638 | 0 | off_peak | 588.05 |  |  | 0 | 0 | 100 | 0 | 0
7255 | 693.53 | 5.7099 | 25.7 | 1.1533 | 0 | 0 | 1.1533 | 1.1533 | 0 | 0 | 0 | 0 | 74.3192 | 693.53 | 0 | 0.05921 | 4.0619 | 0 | 0 | 115.1427 | 0 | off_peak | 693.53 | 100 | 0 | 0 | 0 | 100 | 0 | 0
7256 | 799.59 | 151.833 | 26.3 | 30.6023 | 30.6023 | 0 | 0 | 0.074489 | 0.074489 | 0 | 0 | 0 | 74.3888 | 769.0622 | 0 | 0.05921 | 3.8296 | 0 | 0 | 115.1427 | 30.6023 | off_peak | 768.9877 | 0 | 100 | 3.83 | 0 | 96.17 | 117.1938 | 0
7257 | 848.1 | 351.101 | 26.8 | 70.6372 | 70.6372 | 0 | 0 | 0.0048109 | 0.0048109 | 0 | 0 | 0 | 74.3933 | 777.4676 | 0 | 0.05921 | 3.6864 | 0 | 0 | 115.1427 | 70.6372 | off_peak | 777.4628 | 0 | 100 | 8.33 | 0 | 91.67 | 260.3991 | 0
7258 | 775.14 | 530.063 | 27.2 | 106.4876 | 106.4876 | 0 | 0 | 0.00031072 | 0.00031072 | 0 | 0 | 0 | 74.3936 | 668.6527 | 0 | 0.05921 | 3.6701 | 0 | 0 | 115.1427 | 106.4876 | off_peak | 668.6524 | 0 | 100 | 13.74 | 0 | 86.26 | 390.8236 | 0
7259 | 782.83 | 661.261 | 27.6 | 132.652 | 132.652 | 0 | 0 | 2.0068e-05 | 2.0068e-05 | 0 | 0 | 0 | 74.3936 | 650.178 | 0 | 0.05921 | 3.9043 | 0 | 0 | 115.1427 | 132.652 | off_peak | 650.178 | 0 | 100 | 16.95 | 0 | 83.05 | 517.9133 | 0
7260 | 866.05 | 732.927 | 27.9 | 146.8682 | 146.8682 | 0 | 0 | 1.2961e-06 | 1.2961e-06 | 0 | 0 | 0 | 74.3936 | 719.1818 | 0 | 0.05921 | 4.317 | 0 | 0 | 115.1427 | 146.8682 | off_peak | 719.1818 | 0 | 100 | 16.96 | 0 | 83.04 | 634.0258 | 0
7261 | 835.3 | 669.62 | 28.1 | 134.0848 | 134.0848 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 701.2152 | 0 | 0.088511 | 4.6002 | 0 | 0 | 115.1427 | 134.0848 | on_peak | 701.2152 |  |  | 16.05 | 0 | 83.95 | 616.8143 | 0
7262 | 851.45 | 669.143 | 28.2 | 133.9405 | 133.9405 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 717.5095 | 0 | 0.088511 | 4.6818 | 0 | 0 | 115.1427 | 133.9405 | on_peak | 717.5095 |  |  | 15.73 | 0 | 84.27 | 627.0805 | 0
7263 | 830.06 | 551.032 | 28.1 | 110.3387 | 110.3387 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 719.7213 | 0 | 0.088511 | 4.7587 | 0 | 0 | 115.1427 | 110.3387 | on_peak | 719.7213 |  |  | 13.29 | 0 | 86.71 | 525.064 | 0
7264 | 831.95 | 380.24 | 27.9 | 76.1947 | 76.1947 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 755.7553 | 0 | 0.088511 | 5.0736 | 0 | 0 | 115.1427 | 76.1947 | on_peak | 755.7553 |  |  | 9.16 | 0 | 90.84 | 386.5813 | 0
7265 | 788.38 | 183.423 | 27.5 | 36.8089 | 36.8089 | 0 | 0 | 0 | 0 | 62.63 | 62.63 | 0 | 7.4394 | 688.9411 | 0 | 0.088511 | 5.5282 | 0 | 0 | 115.1427 | 36.8089 | on_peak | 688.9411 |  |  | 4.67 | 7.94 | 87.39 | 203.4864 | 0
7266 | 817.65 | 15.183 | 27 | 3.0524 | 3.0524 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 814.5976 | 0 | 0.088511 | 5.9484 | 0 | 0 | 115.1427 | 3.0524 | on_peak | 814.5976 |  |  | 0.37 | 0 | 99.63 | 18.157 | 0
7267 | 790.95 | 0 | 26.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 790.95 | 0 | 0.088511 | 6.3506 | 0 | 0 | 115.1427 | 0 | on_peak | 790.95 |  |  | 0 | 0 | 100 | 0 | 0
7268 | 769.7 | 0 | 26.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 769.7 | 0 | 0.088511 | 6.7693 | 0 | 0 | 115.1427 | 0 | on_peak | 769.7 |  |  | 0 | 0 | 100 | 0 | 0
7269 | 779.53 | 0 | 26.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 779.53 | 0 | 0.088511 | 7.1445 | 0 | 0 | 115.1427 | 0 | on_peak | 779.53 |  |  | 0 | 0 | 100 | 0 | 0
7270 | 775 | 0 | 26.4 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 19.0375 | 787.3989 | 0 | 0.05921 | 7.4653 | 0 | 0 | 115.1427 | 0 | off_peak | 775 | 0 | 100 | 0 | 0 | 100 | 0 | 0
7271 | 740.04 | 0 | 26.3 | 0 | 0 | 0 | 0 | 8.7263 | 8.7263 | 0 | 0 | 0 | 27.2003 | 748.7663 | 0 | 0.05921 | 7.7603 | 0 | 0 | 115.1427 | 0 | off_peak | 740.04 | 0 | 100 | 0 | 0 | 100 | 0 | 0
7272 | 756.71 | 0 | 26.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27.2003 | 756.71 | 0 | 0.05921 | 7.8371 | 0 | 0 | 115.1427 | 0 | off_peak | 756.71 |  |  | 0 | 0 | 100 | 0 | 0
7273 | 652.87 | 0 | 26.3 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 38.7984 | 665.2689 | 0 | 0.05921 | 7.758 | 0 | 0 | 115.1427 | 0 | off_peak | 652.87 | 0 | 100 | 0 | 0 | 100 | 0 | 0
7274 | 649.23 | 0 | 26.3 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 50.3966 | 661.6289 | 0 | 0.05921 | 7.3406 | 0 | 0 | 115.1427 | 0 | off_peak | 649.23 | 0 | 100 | 0 | 0 | 100 | 0 | 0
7275 | 610.11 | 0 | 26.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50.3966 | 610.11 | 0 | 0.05921 | 6.8135 | 0 | 0 | 115.1427 | 0 | off_peak | 610.11 |  |  | 0 | 0 | 100 | 0 | 0
7276 | 595.68 | 0 | 26.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50.3966 | 595.68 | 0 | 0.05921 | 6.123 | 0 | 0 | 115.1427 | 0 | off_peak | 595.68 |  |  | 0 | 0 | 100 | 0 | 0
7277 | 636.3 | 0 | 26.1 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 61.9947 | 648.6989 | 0 | 0.05921 | 5.3239 | 0 | 0 | 115.1427 | 0 | off_peak | 636.3 | 0 | 100 | 0 | 0 | 100 | 0 | 0
7278 | 631.42 | 0 | 26.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 61.9947 | 631.42 | 0 | 0.05921 | 5.3177 | 0 | 0 | 115.1427 | 0 | off_peak | 631.42 |  |  | 0 | 0 | 100 | 0 | 0
7279 | 713.68 | 5.7 | 26.4 | 1.1484 | 0 | 0 | 1.1484 | 12.3989 | 11.2505 | 0 | 0 | 0 | 73.5928 | 724.9305 | 0 | 0.05921 | 5.3073 | 0 | 0 | 116.2169 | 0 | off_peak | 713.68 | 9.26 | 90.74 | 0 | 0 | 100 | 0 | 0
7280 | 773.63 | 144.264 | 26.9 | 29.0136 | 29.0136 | 0 | 0 | 0.80079 | 0.80079 | 0 | 0 | 0 | 74.3419 | 745.4172 | 0 | 0.05921 | 5.2993 | 0 | 0 | 116.2169 | 29.0136 | off_peak | 744.6164 | 0 | 100 | 3.75 | 0 | 96.25 | 153.7507 | 0
7281 | 805.32 | 275.558 | 27.4 | 55.3184 | 55.3184 | 0 | 0 | 0.05172 | 0.05172 | 0 | 0 | 0 | 74.3903 | 750.0533 | 0 | 0.05921 | 5.293 | 0 | 0 | 116.2169 | 55.3184 | off_peak | 750.0016 | 0 | 100 | 6.87 | 0 | 93.13 | 292.8025 | 0
7282 | 855.19 | 354.58 | 27.9 | 71.0528 | 71.0528 | 0 | 0 | 0.0033404 | 0.0033404 | 0 | 0 | 0 | 74.3934 | 784.1405 | 0 | 0.05921 | 5.2882 | 0 | 0 | 116.2169 | 71.0528 | off_peak | 784.1372 | 0 | 100 | 8.31 | 0 | 91.69 | 375.7401 | 0
7283 | 856.61 | 530.865 | 28.4 | 106.1844 | 106.1844 | 0 | 0 | 0.00021574 | 0.00021574 | 0 | 0 | 0 | 74.3936 | 750.4259 | 0 | 0.05921 | 5.2843 | 0 | 0 | 116.2169 | 106.1844 | off_peak | 750.4256 | 0 | 100 | 12.4 | 0 | 87.6 | 561.109 | 0
7284 | 917.3 | 693.508 | 28.7 | 138.5648 | 138.5648 | 0 | 0 | 1.3934e-05 | 1.3934e-05 | 0 | 0 | 0 | 74.3936 | 778.7352 | 0 | 0.05921 | 5.2827 | 0 | 0 | 116.2169 | 138.5648 | off_peak | 778.7352 | 0 | 100 | 15.11 | 0 | 84.89 | 731.9994 | 0
7285 | 888.88 | 714.77 | 28.9 | 142.7088 | 142.7088 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 746.1712 | 0 | 0.088511 | 5.2832 | 0 | 0 | 116.2169 | 142.7088 | on_peak | 746.1712 |  |  | 16.05 | 0 | 83.95 | 753.9606 | 0
7286 | 892.45 | 665.013 | 29 | 132.726 | 132.726 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 759.724 | 0 | 0.088511 | 5.2823 | 0 | 0 | 116.2169 | 132.726 | on_peak | 759.724 |  |  | 14.87 | 0 | 85.13 | 701.0954 | 0
7287 | 902.67 | 544.621 | 29 | 108.6976 | 108.6976 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 793.9724 | 0 | 0.088511 | 5.2803 | 0 | 0 | 116.2169 | 108.6976 | on_peak | 793.9724 |  |  | 12.04 | 0 | 87.96 | 573.9598 | 0
7288 | 862.23 | 375.759 | 28.8 | 75.0503 | 75.0503 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 787.1797 | 0 | 0.088511 | 5.2795 | 0 | 0 | 116.2169 | 75.0503 | on_peak | 787.1797 |  |  | 8.7 | 0 | 91.3 | 396.2255 | 0
7289 | 858.18 | 180.072 | 28.4 | 36.0183 | 36.0183 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 822.1617 | 0 | 0.088511 | 5.2835 | 0 | 0 | 116.2169 | 36.0183 | on_peak | 822.1617 |  |  | 4.2 | 0 | 95.8 | 190.3042 | 0
7290 | 867.31 | 16.516 | 27.8 | 3.3108 | 3.3108 | 0 | 0 | 0 | 0 | 32.3781 | 32.3781 | 0 | 39.78 | 831.6211 | 0 | 0.088511 | 5.292 | 0 | 0 | 116.2169 | 3.3108 | on_peak | 831.6211 |  |  | 0.38 | 3.73 | 95.89 | 17.5206 | 0
7291 | 858.51 | 0 | 27.4 | 0 | 0 | 0 | 0 | 0 | 0 | 26.8889 | 26.8889 | 0 | 11.0345 | 831.6211 | 0 | 0.088511 | 5.302 | 0 | 0 | 116.2169 | 0 | on_peak | 831.6211 |  |  | 0 | 3.13 | 96.87 | 0 | 0
7292 | 826.38 | 0 | 24.4 | 0 | 0 | 0 | 0 | 5.2411 | 5.2411 | 0 | 0 | 0 | 15.9371 | 831.6211 | 0 | 0.088511 | 5.3132 | 0 | 0 | 116.2169 | 0 | on_peak | 826.38 | 0 | 100 | 0 | 0 | 100 | 0 | 0
7293 | 839.57 | 0 | 24.4 | 0 | 0 | 0 | 0 | 0 | 0 | 7.9489 | 7.9489 | 0 | 7.4394 | 831.6211 | 0 | 0.088511 | 5.3239 | 0 | 0 | 116.2169 | 0 | on_peak | 831.6211 |  |  | 0 | 0.95 | 99.05 | 0 | 0
7294 | 804.93 | 0 | 24.4 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 19.0375 | 817.3289 | 0 | 0.05921 | 5.3348 | 0 | 0 | 116.2169 | 0 | off_peak | 804.93 | 0 | 100 | 0 | 0 | 100 | 0 | 0
7295 | 809.77 | 0 | 24.4 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 30.6357 | 822.1689 | 0 | 0.05921 | 5.3454 | 0 | 0 | 116.2169 | 0 | off_peak | 809.77 | 0 | 100 | 0 | 0 | 100 | 0 | 0
7296 | 780.31 | 0 | 24.5 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 42.2338 | 792.7089 | 0 | 0.05921 | 5.3561 | 0 | 0 | 116.2169 | 0 | off_peak | 780.31 | 0 | 100 | 0 | 0 | 100 | 0 | 0
7297 | 753.74 | 0 | 24.5 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 53.832 | 766.1389 | 0 | 0.05921 | 5.3654 | 0 | 0 | 116.2169 | 0 | off_peak | 753.74 | 0 | 100 | 0 | 0 | 100 | 0 | 0
7298 | 725.79 | 0 | 24.5 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 65.4301 | 738.1889 | 0 | 0.05921 | 5.372 | 0 | 0 | 116.2169 | 0 | off_peak | 725.79 | 0 | 100 | 0 | 0 | 100 | 0 | 0
7299 | 737.76 | 0 | 24.5 | 0 | 0 | 0 | 0 | 8.9635 | 8.9635 | 0 | 0 | 0 | 73.8147 | 746.7235 | 0 | 0.05921 | 5.3751 | 0 | 0 | 116.2169 | 0 | off_peak | 737.76 | 0 | 100 | 0 | 0 | 100 | 0 | 0
7300 | 685.91 | 0 | 24.5 | 0 | 0 | 0 | 0 | 0.57892 | 0.57892 | 0 | 0 | 0 | 74.3563 | 686.4889 | 0 | 0.05921 | 5.3757 | 0 | 0 | 116.2169 | 0 | off_peak | 685.91 | 0 | 100 | 0 | 0 | 100 | 0 | 0
7301 | 710.11 | 0 | 24.5 | 0 | 0 | 0 | 0 | 0.03739 | 0.03739 | 0 | 0 | 0 | 74.3912 | 710.1474 | 0 | 0.05921 | 5.3727 | 0 | 0 | 116.2169 | 0 | off_peak | 710.11 | 0 | 100 | 0 | 0 | 100 | 0 | 0
7302 | 716.23 | 0 | 24.6 | 0 | 0 | 0 | 0 | 0.0024148 | 0.0024148 | 0 | 0 | 0 | 74.3935 | 716.2324 | 0 | 0.05921 | 5.3684 | 0 | 0 | 116.2169 | 0 | off_peak | 716.23 | 0 | 100 | 0 | 0 | 100 | 0 | 0
7303 | 739.16 | 5.7 | 24.8 | 1.1551 | 1.1551 | 0 | 0 | 0 | 0 | 62.6298 | 62.6298 | 0 | 7.4394 | 675.3751 | 0 | 0.088511 | 5.3711 | 0 | 0 | 116.2169 | 1.1551 | on_peak | 675.3751 |  |  | 0.16 | 8.47 | 91.37 | 6.2041 | 0
7304 | 789.62 | 151.988 | 25.2 | 30.7554 | 30.7554 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 758.8646 | 0 | 0.088511 | 5.379 | 0 | 0 | 116.2169 | 30.7554 | on_peak | 758.8646 |  |  | 3.89 | 0 | 96.11 | 165.4333 | 0
7305 | 828.19 | 351.807 | 25.6 | 71.087 | 71.087 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 757.103 | 0 | 0.088511 | 5.3907 | 0 | 0 | 116.2169 | 71.087 | on_peak | 757.103 |  |  | 8.58 | 0 | 91.42 | 383.2114 | 0
7306 | 846.3 | 528.645 | 26.1 | 106.6267 | 106.6267 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 739.6733 | 0 | 0.088511 | 5.4052 | 0 | 0 | 116.2169 | 106.6267 | on_peak | 739.6733 |  |  | 12.6 | 0 | 87.4 | 576.3377 | 0
7307 | 858.21 | 658.695 | 26.4 | 132.7135 | 132.7135 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 19.0375 | 737.8955 | 0 | 0.05921 | 5.4214 | 0 | 0 | 116.2169 | 132.7135 | off_peak | 725.4965 | 0 | 100 | 15.46 | 0 | 84.54 | 719.4882 | 0
7308 | 875.91 | 727.438 | 26.6 | 146.4577 | 134.0588 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 0 | 30.6357 | 741.8512 | 0 | 0.05921 | 5.4382 | 0 | 0 | 127.8151 | 134.0588 | off_peak | 741.8512 | 100 | 0 | 15.31 | 0 | 84.69 | 729.035 | 0
7309 | 843.31 | 430.185 | 26.7 | 86.5793 | 86.5793 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 42.2338 | 769.1296 | 0 | 0.05921 | 5.453 | 0 | 0 | 127.8151 | 86.5793 | off_peak | 756.7307 | 0 | 100 | 10.27 | 0 | 89.73 | 472.1208 | 0
7310 | 895.95 | 365.315 | 26.7 | 73.5236 | 61.1246 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 0 | 53.832 | 834.8254 | 0 | 0.05921 | 5.4635 | 0 | 0 | 139.4132 | 61.1246 | off_peak | 834.8254 | 100 | 0 | 6.82 | 0 | 93.18 | 333.9572 | 0
7311 | 838.39 | 292.545 | 26.7 | 58.8778 | 46.4789 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 0 | 65.4301 | 791.9111 | 0 | 0.05921 | 5.471 | 0 | 0 | 151.0114 | 46.4789 | off_peak | 791.9111 | 100 | 0 | 5.54 | 0 | 94.46 | 254.286 | 0
7312 | 822.8 | 358.651 | 26.6 | 72.2085 | 72.2085 | 0 | 0 | 8.9635 | 8.9635 | 0 | 0 | 0 | 73.8147 | 759.555 | 0 | 0.05921 | 5.4766 | 0 | 0 | 151.0114 | 72.2085 | off_peak | 750.5915 | 0 | 100 | 8.78 | 0 | 91.22 | 395.4545 | 0
7313 | 821.62 | 158.037 | 26.3 | 31.8527 | 31.2738 | 0 | 0.57892 | 0.57892 | 0 | 0 | 0 | 0 | 74.3563 | 790.3462 | 0 | 0.05921 | 5.4814 | 0 | 0 | 151.5529 | 31.2738 | off_peak | 790.3462 | 100 | 0 | 3.81 | 0 | 96.19 | 171.4229 | 0
7314 | 817.41 | 11.9247 | 25.8 | 2.4078 | 2.3704 | 0 | 0.03739 | 0.03739 | 0 | 0 | 0 | 0 | 74.3912 | 815.0396 | 0 | 0.05921 | 5.4845 | 0 | 0 | 151.5879 | 2.3704 | off_peak | 815.0396 | 100 | 0 | 0.29 | 0 | 99.71 | 13.0005 | 0
7315 | 827.73 | 0 | 25.7 | 0 | 0 | 0 | 0 | 0 | 0 | 2.4859 | 2.4859 | 0 | 71.7337 | 825.2441 | 0 | 0.088511 | 5.4841 | 0 | 0 | 151.5879 | 0 | on_peak | 825.2441 |  |  | 0 | 0.3 | 99.7 | 0 | 0
7316 | 807.41 | 0 | 25.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 71.7337 | 807.41 | 0 | 0.088511 | 5.4796 | 0 | 0 | 151.5879 | 0 | on_peak | 807.41 |  |  | 0 | 0 | 100 | 0 | 0
7317 | 815.42 | 0 | 25.5 | 0 | 0 | 0 | 0 | 0 | 0 | 60.1418 | 60.1418 | 0 | 7.4394 | 755.2782 | 0 | 0.088511 | 5.471 | 0 | 0 | 151.5879 | 0 | on_peak | 755.2782 |  |  | 0 | 7.38 | 92.62 | 0 | 0
7318 | 754.22 | 0 | 25.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 754.22 | 0 | 0.088511 | 5.4606 | 0 | 0 | 151.5879 | 0 | on_peak | 754.22 |  |  | 0 | 0 | 100 | 0 | 0
7319 | 757.23 | 0 | 25.4 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 19.0375 | 769.6289 | 0 | 0.05921 | 5.4469 | 0 | 0 | 151.5879 | 0 | off_peak | 757.23 | 0 | 100 | 0 | 0 | 100 | 0 | 0
7320 | 745.74 | 0 | 25.3 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 30.6357 | 758.1389 | 0 | 0.05921 | 5.4312 | 0 | 0 | 151.5879 | 0 | off_peak | 745.74 | 0 | 100 | 0 | 0 | 100 | 0 | 0
7321 | 721.67 | 0 | 25.1 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 42.2338 | 734.0689 | 0 | 0.05921 | 5.4128 | 0 | 0 | 151.5879 | 0 | off_peak | 721.67 | 0 | 100 | 0 | 0 | 100 | 0 | 0
7322 | 613.21 | 0 | 24.7 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 53.832 | 625.6089 | 0 | 0.05921 | 5.3941 | 0 | 0 | 151.5879 | 0 | off_peak | 613.21 | 0 | 100 | 0 | 0 | 100 | 0 | 0
7323 | 620.31 | 0 | 24 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 65.4301 | 632.7089 | 0 | 0.05921 | 5.3779 | 0 | 0 | 151.5879 | 0 | off_peak | 620.31 | 0 | 100 | 0 | 0 | 100 | 0 | 0
7324 | 615.75 | 0 | 23.2 | 0 | 0 | 0 | 0 | 8.9635 | 8.9635 | 0 | 0 | 0 | 73.8147 | 624.7135 | 0 | 0.05921 | 5.3656 | 0 | 0 | 151.5879 | 0 | off_peak | 615.75 | 0 | 100 | 0 | 0 | 100 | 0 | 0
7325 | 605.13 | 0 | 22.4 | 0 | 0 | 0 | 0 | 0.57892 | 0.57892 | 0 | 0 | 0 | 74.3563 | 605.7089 | 0 | 0.05921 | 5.3572 | 0 | 0 | 151.5879 | 0 | off_peak | 605.13 | 0 | 100 | 0 | 0 | 100 | 0 | 0
7326 | 652.55 | 0 | 22 | 0 | 0 | 0 | 0 | 0.03739 | 0.03739 | 0 | 0 | 0 | 74.3912 | 652.5874 | 0 | 0.05921 | 4.032 | 0 | 0 | 151.5879 | 0 | off_peak | 652.55 | 0 | 100 | 0 | 0 | 100 | 0 | 0
7327 | 665.06 | 0 | 21.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3912 | 665.06 | 0 | 0.088511 | 3.7081 | 0 | 0 | 151.5879 | 0 | on_peak | 665.06 |  |  | 0 | 0 | 100 | 0 | 0
7328 | 720.06 | 100.207 | 22.1 | 20.5038 | 20.5038 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3912 | 699.5562 | 0 | 0.088511 | 3.5317 | 0 | 0 | 151.5879 | 20.5038 | on_peak | 699.5562 |  |  | 2.85 | 0 | 97.15 | 72.4127 | 0
7329 | 796.04 | 211.558 | 22.7 | 43.1952 | 43.1952 | 0 | 0 | 0 | 0 | 62.6277 | 62.6277 | 0 | 7.4394 | 690.2171 | 0 | 0.088511 | 3.4469 | 0 | 0 | 151.5879 | 43.1952 | on_peak | 690.2171 |  |  | 5.43 | 7.87 | 86.71 | 148.8916 | 0
7330 | 796.55 | 346.196 | 23.5 | 70.4833 | 70.4833 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 726.0667 | 0 | 0.088511 | 3.4685 | 0 | 0 | 151.5879 | 70.4833 | on_peak | 726.0667 |  |  | 8.85 | 0 | 91.15 | 244.4692 | 0
7331 | 805.38 | 196.405 | 24.2 | 39.8866 | 39.8866 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 19.0375 | 777.8924 | 0 | 0.05921 | 3.8125 | 0 | 0 | 151.5879 | 39.8866 | off_peak | 765.4934 | 0 | 100 | 4.95 | 0 | 95.05 | 152.0662 | 0
7332 | 815.89 | 302.773 | 24.9 | 61.3336 | 48.9347 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 0 | 30.6357 | 766.9553 | 0 | 0.05921 | 4.2945 | 0 | 0 | 163.186 | 48.9347 | off_peak | 766.9553 | 100 | 0 | 6 | 0 | 94 | 210.1518 | 0
7333 | 784.63 | 267.704 | 25.4 | 54.132 | 54.132 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 42.2338 | 742.8969 | 0 | 0.05921 | 4.5884 | 0 | 0 | 163.186 | 54.132 | off_peak | 730.498 | 0 | 100 | 6.9 | 0 | 93.1 | 248.3788 | 0
7334 | 817.85 | 265.603 | 25.7 | 53.6491 | 53.6491 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 53.832 | 776.5999 | 0 | 0.05921 | 4.5597 | 0 | 0 | 163.186 | 53.6491 | off_peak | 764.2009 | 0 | 100 | 6.56 | 0 | 93.44 | 244.6238 | 0
7335 | 794.03 | 307.284 | 25.8 | 62.0458 | 62.0458 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 65.4301 | 744.3831 | 0 | 0.05921 | 4.1175 | 0 | 0 | 163.186 | 62.0458 | off_peak | 731.9842 | 0 | 100 | 7.81 | 0 | 92.19 | 255.4722 | 0
7336 | 811.1 | 345.245 | 25.7 | 69.7359 | 69.7359 | 0 | 0 | 8.9635 | 8.9635 | 0 | 0 | 0 | 73.8147 | 750.3276 | 0 | 0.05921 | 3.8855 | 0 | 0 | 163.186 | 69.7359 | off_peak | 741.3641 | 0 | 100 | 8.6 | 0 | 91.4 | 270.9606 | 0
7337 | 786.59 | 160.1 | 25.3 | 32.3852 | 32.3852 | 0 | 0 | 0.57892 | 0.57892 | 0 | 0 | 0 | 74.3563 | 754.7837 | 0 | 0.05921 | 3.8382 | 0 | 0 | 163.186 | 32.3852 | off_peak | 754.2048 | 0 | 100 | 4.12 | 0 | 95.88 | 124.3023 | 0
7338 | 776.87 | 11.9045 | 24.6 | 2.4141 | 2.3767 | 0 | 0.03739 | 0.03739 | 0 | 0 | 0 | 0 | 74.3912 | 774.4933 | 0 | 0.05921 | 3.9446 | 0 | 0 | 163.221 | 2.3767 | off_peak | 774.4933 | 100 | 0 | 0.31 | 0 | 99.69 | 9.3754 | 0
7339 | 793.09 | 0 | 24.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3912 | 793.09 | 0 | 0.088511 | 4.1797 | 0 | 0 | 163.221 | 0 | on_peak | 793.09 |  |  | 0 | 0 | 100 | 0 | 0
7340 | 784.95 | 0 | 23.9 | 0 | 0 | 0 | 0 | 0 | 0 | 62.6277 | 62.6277 | 0 | 7.4394 | 722.3223 | 0 | 0.088511 | 4.3219 | 0 | 0 | 163.221 | 0 | on_peak | 722.3223 |  |  | 0 | 7.98 | 92.02 | 0 | 0
7341 | 769.81 | 0 | 23.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 769.81 | 0 | 0.088511 | 4.5266 | 0 | 0 | 163.221 | 0 | on_peak | 769.81 |  |  | 0 | 0 | 100 | 0 | 0
7342 | 736.27 | 0 | 23.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 736.27 | 0 | 0.088511 | 4.8579 | 0 | 0 | 163.221 | 0 | on_peak | 736.27 |  |  | 0 | 0 | 100 | 0 | 0
7343 | 766.93 | 0 | 23.3 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 19.0375 | 779.3289 | 0 | 0.05921 | 5.4222 | 0 | 0 | 163.221 | 0 | off_peak | 766.93 | 0 | 100 | 0 | 0 | 100 | 0 | 0
7344 | 745.54 | 0 | 23.1 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 30.6357 | 757.9389 | 0 | 0.05921 | 5.841 | 0 | 0 | 163.221 | 0 | off_peak | 745.54 | 0 | 100 | 0 | 0 | 100 | 0 | 0
7345 | 669.03 | 0 | 23.1 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 42.2338 | 681.4289 | 0 | 0.05921 | 6.0708 | 0 | 0 | 163.221 | 0 | off_peak | 669.03 | 0 | 100 | 0 | 0 | 100 | 0 | 0
7346 | 623.23 | 0 | 23.1 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 53.832 | 635.6289 | 0 | 0.05921 | 5.971 | 0 | 0 | 163.221 | 0 | off_peak | 623.23 | 0 | 100 | 0 | 0 | 100 | 0 | 0
7347 | 596.71 | 0 | 23.2 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 65.4301 | 609.1089 | 0 | 0.05921 | 5.5427 | 0 | 0 | 163.221 | 0 | off_peak | 596.71 | 0 | 100 | 0 | 0 | 100 | 0 | 0
7348 | 610.34 | 0 | 23.3 | 0 | 0 | 0 | 0 | 8.9635 | 8.9635 | 0 | 0 | 0 | 73.8147 | 619.3035 | 0 | 0.05921 | 5.0085 | 0 | 0 | 163.221 | 0 | off_peak | 610.34 | 0 | 100 | 0 | 0 | 100 | 0 | 0
7349 | 611.85 | 0 | 23.4 | 0 | 0 | 0 | 0 | 0.57892 | 0.57892 | 0 | 0 | 0 | 74.3563 | 612.4289 | 0 | 0.05921 | 4.4291 | 0 | 0 | 163.221 | 0 | off_peak | 611.85 | 0 | 100 | 0 | 0 | 100 | 0 | 0
7350 | 672.68 | 0 | 23.5 | 0 | 0 | 0 | 0 | 0.03739 | 0.03739 | 0 | 0 | 0 | 74.3912 | 672.7174 | 0 | 0.05921 | 3.9546 | 0 | 0 | 163.221 | 0 | off_peak | 672.68 | 0 | 100 | 0 | 0 | 100 | 0 | 0
7351 | 680.49 | 0 | 23.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3912 | 680.49 | 0 | 0.088511 | 3.6616 | 0 | 0 | 163.221 | 0 | on_peak | 680.49 |  |  | 0 | 0 | 100 | 0 | 0
7352 | 754.8 | 136.26 | 24.3 | 27.6622 | 27.6622 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3912 | 727.1378 | 0 | 0.088511 | 3.4612 | 0 | 0 | 163.221 | 27.6622 | on_peak | 727.1378 |  |  | 3.66 | 0 | 96.34 | 95.7432 | 0
7353 | 785.96 | 325.582 | 24.9 | 65.9541 | 65.9541 | 0 | 0 | 0 | 0 | 62.6277 | 62.6277 | 0 | 7.4394 | 657.3782 | 0 | 0.088511 | 3.3354 | 0 | 0 | 163.221 | 65.9541 | on_peak | 657.3782 |  |  | 8.39 | 7.97 | 83.64 | 219.9845 | 0
7354 | 822.42 | 409.228 | 25.3 | 82.7792 | 82.7792 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 739.6408 | 0 | 0.088511 | 3.343 | 0 | 0 | 163.221 | 82.7792 | on_peak | 739.6408 |  |  | 10.07 | 0 | 89.93 | 276.7325 | 0
7355 | 811.26 | 493.285 | 25.7 | 99.6385 | 99.6385 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 19.0375 | 724.0205 | 0 | 0.05921 | 3.6253 | 0 | 0 | 163.221 | 99.6385 | off_peak | 711.6215 | 0 | 100 | 12.28 | 0 | 87.72 | 361.216 | 0
7356 | 861.34 | 545.145 | 25.9 | 110.0342 | 110.0342 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 30.6357 | 763.7047 | 0 | 0.05921 | 4.1856 | 0 | 0 | 163.221 | 110.0342 | off_peak | 751.3058 | 0 | 100 | 12.77 | 0 | 87.23 | 460.5642 | 0
7357 | 802.4 | 359.091 | 26 | 72.4542 | 72.4542 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 42.2338 | 742.3448 | 0 | 0.05921 | 4.5488 | 0 | 0 | 163.221 | 72.4542 | off_peak | 729.9458 | 0 | 100 | 9.03 | 0 | 90.97 | 329.5823 | 0
7358 | 838.65 | 375.324 | 25.9 | 75.7569 | 75.7569 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 53.832 | 775.2921 | 0 | 0.05921 | 4.6124 | 0 | 0 | 163.221 | 75.7569 | off_peak | 762.8931 | 0 | 100 | 9.03 | 0 | 90.97 | 349.4189 | 0
7359 | 886.76 | 370.962 | 25.8 | 74.9035 | 62.5045 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 0 | 65.4301 | 824.2555 | 0 | 0.05921 | 4.354 | 0 | 0 | 174.8192 | 62.5045 | off_peak | 824.2555 | 100 | 0 | 7.05 | 0 | 92.95 | 272.1438 | 0
7360 | 830.75 | 164.087 | 25.6 | 33.1558 | 24.1923 | 0 | 8.9635 | 8.9635 | 0 | 0 | 0 | 0 | 73.8147 | 806.5577 | 0 | 0.05921 | 4.2333 | 0 | 0 | 183.2038 | 24.1923 | off_peak | 806.5577 | 100 | 0 | 2.91 | 0 | 97.09 | 102.4128 | 0
7361 | 808.65 | 65.774 | 25.2 | 13.3096 | 12.7307 | 0 | 0.57892 | 0.57892 | 0 | 0 | 0 | 0 | 74.3563 | 795.9193 | 0 | 0.05921 | 4.2941 | 0 | 0 | 183.7453 | 12.7307 | off_peak | 795.9193 | 100 | 0 | 1.57 | 0 | 98.43 | 54.6667 | 0
7362 | 798.48 | 6.65 | 24.8 | 1.3476 | 1.3102 | 0 | 0.03739 | 0.03739 | 0 | 0 | 0 | 0 | 74.3912 | 797.1698 | 0 | 0.05921 | 4.5535 | 0 | 0 | 183.7803 | 1.3102 | off_peak | 797.1698 | 100 | 0 | 0.16 | 0 | 99.84 | 5.966 | 0
7363 | 799.99 | 0 | 24.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3912 | 799.99 | 0 | 0.088511 | 4.7604 | 0 | 0 | 183.7803 | 0 | on_peak | 799.99 |  |  | 0 | 0 | 100 | 0 | 0
7364 | 791.96 | 0 | 24.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3912 | 791.96 | 0 | 0.088511 | 4.9898 | 0 | 0 | 183.7803 | 0 | on_peak | 791.96 |  |  | 0 | 0 | 100 | 0 | 0
7365 | 799.73 | 0 | 24.4 | 0 | 0 | 0 | 0 | 0 | 0 | 62.6277 | 62.6277 | 0 | 7.4394 | 737.1023 | 0 | 0.088511 | 5.2548 | 0 | 0 | 183.7803 | 0 | on_peak | 737.1023 |  |  | 0 | 7.83 | 92.17 | 0 | 0
7366 | 759.45 | 0 | 24.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 759.45 | 0 | 0.088511 | 5.5106 | 0 | 0 | 183.7803 | 0 | on_peak | 759.45 |  |  | 0 | 0 | 100 | 0 | 0
7367 | 783.71 | 0 | 24.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 783.71 | 0 | 0.05921 | 5.9052 | 0 | 0 | 183.7803 | 0 | off_peak | 783.71 |  |  | 0 | 0 | 100 | 0 | 0
7368 | 792.5 | 0 | 24.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 792.5 | 0 | 0.05921 | 6.1985 | 0 | 0 | 183.7803 | 0 | off_peak | 792.5 |  |  | 0 | 0 | 100 | 0 | 0
7369 | 704.48 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 704.48 | 0 | 0.05921 | 6.1712 | 0 | 0 | 183.7803 | 0 | off_peak | 704.48 |  |  | 0 | 0 | 100 | 0 | 0
7370 | 621.12 | 0 | 23.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 621.12 | 0 | 0.05921 | 5.8949 | 0 | 0 | 183.7803 | 0 | off_peak | 621.12 |  |  | 0 | 0 | 100 | 0 | 0
7371 | 648.8 | 0 | 23.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 648.8 | 0 | 0.05921 | 5.5387 | 0 | 0 | 183.7803 | 0 | off_peak | 648.8 |  |  | 0 | 0 | 100 | 0 | 0
7372 | 638.76 | 0 | 23.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 638.76 | 0 | 0.05921 | 5.2123 | 0 | 0 | 183.7803 | 0 | off_peak | 638.76 |  |  | 0 | 0 | 100 | 0 | 0
7373 | 640.98 | 0 | 23.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 640.98 | 0 | 0.05921 | 4.7648 | 0 | 0 | 183.7803 | 0 | off_peak | 640.98 |  |  | 0 | 0 | 100 | 0 | 0
7374 | 673.18 | 0 | 23.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 673.18 | 0 | 0.05921 | 4.1587 | 0 | 0 | 183.7803 | 0 | off_peak | 673.18 |  |  | 0 | 0 | 100 | 0 | 0
7375 | 677.83 | 0 | 23.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 677.83 | 0 | 0.05921 | 3.8061 | 0 | 0 | 183.7803 | 0 | off_peak | 677.83 |  |  | 0 | 0 | 100 | 0 | 0
7376 | 712.93 | 69.4071 | 24.5 | 14.0802 | 1.6813 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 0 | 19.0375 | 711.2487 | 0 | 0.05921 | 3.5289 | 0 | 0 | 195.3784 | 1.6813 | off_peak | 711.2487 | 100 | 0 | 0.24 | 0 | 99.76 | 5.9331 | 0
7377 | 704.48 | 192.535 | 25.2 | 38.9603 | 38.9603 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 30.6357 | 677.9187 | 0 | 0.05921 | 3.3695 | 0 | 0 | 195.3784 | 38.9603 | off_peak | 665.5197 | 0 | 100 | 5.53 | 0 | 94.47 | 131.2762 | 0
7378 | 709.9 | 346.062 | 25.7 | 69.901 | 69.901 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30.6357 | 639.999 | 0 | 0.05921 | 3.278 | 0 | 0 | 195.3784 | 69.901 | off_peak | 639.999 |  |  | 9.85 | 0 | 90.15 | 229.1356 | 0
7379 | 722.69 | 350.765 | 26.1 | 70.7486 | 70.7486 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30.6357 | 651.9414 | 0 | 0.05921 | 3.2932 | 0 | 0 | 195.3784 | 70.7486 | off_peak | 651.9414 |  |  | 9.79 | 0 | 90.21 | 232.9922 | 0
7380 | 757.27 | 445.105 | 26.4 | 89.6795 | 89.6795 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30.6357 | 667.5905 | 0 | 0.05921 | 3.465 | 0 | 0 | 195.3784 | 89.6795 | off_peak | 667.5905 |  |  | 11.84 | 0 | 88.16 | 310.7384 | 0
7381 | 742.63 | 466.272 | 26.6 | 93.8762 | 93.8762 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30.6357 | 648.7538 | 0 | 0.05921 | 3.878 | 0 | 0 | 195.3784 | 93.8762 | off_peak | 648.7538 |  |  | 12.64 | 0 | 87.36 | 364.0523 | 0
7382 | 747.49 | 471.585 | 26.6 | 94.9459 | 94.9459 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30.6357 | 652.5441 | 0 | 0.05921 | 4.0565 | 0 | 0 | 195.3784 | 94.9459 | off_peak | 652.5441 |  |  | 12.7 | 0 | 87.3 | 385.1522 | 0
7383 | 726.37 | 321.137 | 26.6 | 64.6557 | 64.6557 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30.6357 | 661.7143 | 0 | 0.05921 | 3.9561 | 0 | 0 | 195.3784 | 64.6557 | off_peak | 661.7143 |  |  | 8.9 | 0 | 91.1 | 255.7824 | 0
7384 | 737.8 | 117.785 | 26.4 | 23.7313 | 11.3323 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 0 | 42.2338 | 726.4677 | 0 | 0.05921 | 3.9258 | 0 | 0 | 206.9766 | 11.3323 | off_peak | 726.4677 | 100 | 0 | 1.54 | 0 | 98.46 | 44.4879 | 0
7385 | 748.88 | 55.0358 | 25.9 | 11.1086 | 11.1086 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 42.2338 | 737.7714 | 0 | 0.05921 | 3.8655 | 0 | 0 | 206.9766 | 11.1086 | off_peak | 737.7714 |  |  | 1.48 | 0 | 98.52 | 42.9401 | 0
7386 | 648.93 | 8.55 | 25.5 | 1.7283 | 0 | 0 | 1.7283 | 1.7283 | 0 | 0 | 0 | 0 | 43.8504 | 648.93 | 0 | 0.05921 | 4.018 | 0 | 0 | 208.5932 | 0 | off_peak | 648.93 | 100 | 0 | 0 | 0 | 100 | 0 | 0
7387 | 599.66 | 0 | 25.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 43.8504 | 599.66 | 0 | 0.05921 | 4.2431 | 0 | 0 | 208.5932 | 0 | off_peak | 599.66 |  |  | 0 | 0 | 100 | 0 | 0
7388 | 607.59 | 0 | 25.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 43.8504 | 607.59 | 0 | 0.05921 | 4.5389 | 0 | 0 | 208.5932 | 0 | off_peak | 607.59 |  |  | 0 | 0 | 100 | 0 | 0
7389 | 587.49 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 43.8504 | 587.49 | 0 | 0.05921 | 4.9128 | 0 | 0 | 208.5932 | 0 | off_peak | 587.49 |  |  | 0 | 0 | 100 | 0 | 0
7390 | 595.65 | 0 | 24.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 43.8504 | 595.65 | 0 | 0.05921 | 5.043 | 0 | 0 | 208.5932 | 0 | off_peak | 595.65 |  |  | 0 | 0 | 100 | 0 | 0
7391 | 589.62 | 0 | 24.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 43.8504 | 589.62 | 0 | 0.05921 | 5.4884 | 0 | 0 | 208.5932 | 0 | off_peak | 589.62 |  |  | 0 | 0 | 100 | 0 | 0
7392 | 564.02 | 0 | 24.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 43.8504 | 564.02 | 0 | 0.05921 | 5.7936 | 0 | 0 | 208.5932 | 0 | off_peak | 564.02 |  |  | 0 | 0 | 100 | 0 | 0
7393 | 599.82 | 0 | 24.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 43.8504 | 599.82 | 0 | 0.05921 | 5.7164 | 0 | 0 | 208.5932 | 0 | off_peak | 599.82 |  |  | 0 | 0 | 100 | 0 | 0
7394 | 599.82 | 0 | 24.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 43.8504 | 599.82 | 0 | 0.05921 | 5.4382 | 0 | 0 | 208.5932 | 0 | off_peak | 599.82 |  |  | 0 | 0 | 100 | 0 | 0
7395 | 599.82 | 0 | 24.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 43.8504 | 599.82 | 0 | 0.05921 | 5.1623 | 0 | 0 | 208.5932 | 0 | off_peak | 599.82 |  |  | 0 | 0 | 100 | 0 | 0
7396 | 590.79 | 0 | 24.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 43.8504 | 590.79 | 0 | 0.05921 | 4.8415 | 0 | 0 | 208.5932 | 0 | off_peak | 590.79 |  |  | 0 | 0 | 100 | 0 | 0
7397 | 592.96 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 43.8504 | 592.96 | 0 | 0.05921 | 4.3554 | 0 | 0 | 208.5932 | 0 | off_peak | 592.96 |  |  | 0 | 0 | 100 | 0 | 0
7398 | 641.08 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 43.8504 | 641.08 | 0 | 0.05921 | 0 | 0 | 0 | 208.5932 | 0 | off_peak | 641.08 |  |  | 0 | 0 | 100 | 0 | 0
7399 | 687.68 | 0 | 24.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 43.8504 | 687.68 | 0 | 0.05921 | 3.2484 | 0 | 0 | 208.5932 | 0 | off_peak | 687.68 |  |  | 0 | 0 | 100 | 0 | 0
7400 | 671.74 | 132.824 | 24.8 | 26.9162 | 26.9162 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 43.8504 | 644.8238 | 0 | 0.05921 | 3.0785 | 0 | 0 | 208.5932 | 26.9162 | off_peak | 644.8238 |  |  | 4.01 | 0 | 95.99 | 82.8624 | 0
7401 | 712.45 | 335.703 | 25.4 | 67.882 | 67.882 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 43.8504 | 644.568 | 0 | 0.05921 | 2.9866 | 0 | 0 | 208.5932 | 67.882 | off_peak | 644.568 |  |  | 9.53 | 0 | 90.47 | 202.7332 | 0
7402 | 735.77 | 495.984 | 25.9 | 100.1113 | 100.1113 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 55.4486 | 648.0576 | 0 | 0.05921 | 2.9646 | 0 | 0 | 208.5932 | 100.1113 | off_peak | 635.6587 | 0 | 100 | 13.61 | 0 | 86.39 | 296.7867 | 0
7403 | 686.74 | 570.166 | 26.2 | 114.9598 | 114.9598 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 55.4486 | 571.7802 | 0 | 0.05921 | 3.0015 | 0 | 0 | 208.5932 | 114.9598 | off_peak | 571.7802 |  |  | 16.74 | 0 | 83.26 | 345.0498 | 0
7404 | 765.91 | 668.171 | 26.5 | 134.574 | 134.574 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 55.4486 | 631.336 | 0 | 0.05921 | 3.1911 | 0 | 0 | 208.5932 | 134.574 | off_peak | 631.336 |  |  | 17.57 | 0 | 82.43 | 429.4447 | 0
7405 | 701.46 | 602.346 | 26.6 | 121.2725 | 121.2725 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 55.4486 | 580.1875 | 0 | 0.05921 | 3.4085 | 0 | 0 | 208.5932 | 121.2725 | off_peak | 580.1875 |  |  | 17.29 | 0 | 82.71 | 413.352 | 0
7406 | 716.62 | 532.02 | 26.6 | 107.1135 | 107.1135 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 55.4486 | 609.5065 | 0 | 0.05921 | 3.408 | 0 | 0 | 208.5932 | 107.1135 | off_peak | 609.5065 |  |  | 14.95 | 0 | 85.05 | 365.0375 | 0
7407 | 702.84 | 315.362 | 26.5 | 63.516 | 63.516 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 67.0467 | 651.723 | 0 | 0.05921 | 3.4978 | 0 | 0 | 208.5932 | 63.516 | off_peak | 639.324 | 0 | 100 | 9.04 | 0 | 90.96 | 222.1661 | 0
7408 | 700.28 | 204.423 | 26.2 | 41.2168 | 33.8699 | 0 | 7.3469 | 7.3469 | 0 | 0 | 0 | 0 | 73.9191 | 666.4101 | 0 | 0.05921 | 3.7026 | 0 | 0 | 215.4656 | 33.8699 | off_peak | 666.4101 | 100 | 0 | 4.84 | 0 | 95.16 | 125.4051 | 0
7409 | 698.7 | 109.379 | 25.7 | 22.0934 | 22.0934 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 73.9191 | 676.6066 | 0 | 0.05921 | 4.0023 | 0 | 0 | 215.4656 | 22.0934 | off_peak | 676.6066 |  |  | 3.16 | 0 | 96.84 | 88.4241 | 0
7410 | 638.77 | 13.3452 | 25.1 | 2.7014 | 2.7014 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 73.9191 | 636.0686 | 0 | 0.05921 | 4.3401 | 0 | 0 | 215.4656 | 2.7014 | off_peak | 636.0686 |  |  | 0.42 | 0 | 99.58 | 11.7244 | 0
7411 | 588.39 | 0 | 24.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 73.9191 | 588.39 | 0 | 0.05921 | 4.5983 | 0 | 0 | 215.4656 | 0 | off_peak | 588.39 |  |  | 0 | 0 | 100 | 0 | 0
7412 | 605.35 | 0 | 24.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 73.9191 | 605.35 | 0 | 0.05921 | 4.8169 | 0 | 0 | 215.4656 | 0 | off_peak | 605.35 |  |  | 0 | 0 | 100 | 0 | 0
7413 | 588.66 | 0 | 24.7 | 0 | 0 | 0 | 0 | 0.4745 | 0.4745 | 0 | 0 | 0 | 74.363 | 589.1345 | 0 | 0.05921 | 5.1989 | 0 | 0 | 215.4656 | 0 | off_peak | 588.66 | 0 | 100 | 0 | 0 | 100 | 0 | 0
7414 | 573.07 | 0 | 24.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.363 | 573.07 | 0 | 0.05921 | 5.6732 | 0 | 0 | 215.4656 | 0 | off_peak | 573.07 |  |  | 0 | 0 | 100 | 0 | 0
7415 | 547.88 | 0 | 24.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.363 | 547.88 | 0 | 0.05921 | 5.9096 | 0 | 0 | 215.4656 | 0 | off_peak | 547.88 |  |  | 0 | 0 | 100 | 0 | 0
7416 | 555.87 | 0 | 24.6 | 0 | 0 | 0 | 0 | 0.030646 | 0.030646 | 0 | 0 | 0 | 74.3917 | 555.9006 | 0 | 0.05921 | 5.8726 | 0 | 0 | 215.4656 | 0 | off_peak | 555.87 | 0 | 100 | 0 | 0 | 100 | 0 | 0
7417 | 577.49 | 0 | 24.5 | 0 | 0 | 0 | 0 | 0.0019793 | 0.0019793 | 0 | 0 | 0 | 74.3935 | 577.492 | 0 | 0.05921 | 5.5279 | 0 | 0 | 215.4656 | 0 | off_peak | 577.49 | 0 | 100 | 0 | 0 | 100 | 0 | 0
7418 | 546.45 | 0 | 24.5 | 0 | 0 | 0 | 0 | 0.00012783 | 0.00012783 | 0 | 0 | 0 | 74.3936 | 546.4501 | 0 | 0.05921 | 5.1605 | 0 | 0 | 215.4656 | 0 | off_peak | 546.45 | 0 | 100 | 0 | 0 | 100 | 0 | 0
7419 | 545.41 | 0 | 24.5 | 0 | 0 | 0 | 0 | 8.2563e-06 | 8.2563e-06 | 0 | 0 | 0 | 74.3936 | 545.41 | 0 | 0.05921 | 4.7391 | 0 | 0 | 215.4656 | 0 | off_peak | 545.41 | 0 | 100 | 0 | 0 | 100 | 0 | 0
7420 | 557.12 | 0 | 24.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 557.12 | 0 | 0.05921 | 4.265 | 0 | 0 | 215.4656 | 0 | off_peak | 557.12 |  |  | 0 | 0 | 100 | 0 | 0
7421 | 539.42 | 0 | 24.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 539.42 | 0 | 0.05921 | 3.6875 | 0 | 0 | 215.4656 | 0 | off_peak | 539.42 |  |  | 0 | 0 | 100 | 0 | 0
7422 | 613.87 | 0 | 24.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 613.87 | 0 | 0.05921 | 0 | 0 | 0 | 215.4656 | 0 | off_peak | 613.87 |  |  | 0 | 0 | 100 | 0 | 0
7423 | 644.97 | 0 | 24.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 644.97 | 0 | 0.088511 | 3.2075 | 0 | 0 | 215.4656 | 0 | on_peak | 644.97 |  |  | 0 | 0 | 100 | 0 | 0
7424 | 711.3 | 144.889 | 25.2 | 29.3189 | 29.3189 | 0 | 0 | 0 | 0 | 62.63 | 62.63 | 0 | 7.4394 | 619.3511 | 0 | 0.088511 | 2.9198 | 0 | 0 | 215.4656 | 29.3189 | on_peak | 619.3511 |  |  | 4.12 | 8.81 | 87.07 | 85.6053 | 0
7425 | 749.24 | 349.055 | 25.9 | 70.4546 | 70.4546 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 678.7854 | 0 | 0.088511 | 2.7628 | 0 | 0 | 215.4656 | 70.4546 | on_peak | 678.7854 |  |  | 9.4 | 0 | 90.6 | 194.6542 | 0
7426 | 765.6 | 529.725 | 26.4 | 106.7287 | 106.7287 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 658.8713 | 0 | 0.088511 | 2.6688 | 0 | 0 | 215.4656 | 106.7287 | on_peak | 658.8713 |  |  | 13.94 | 0 | 86.06 | 284.837 | 0
7427 | 797.21 | 662.616 | 26.9 | 133.262 | 120.863 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 0 | 19.0375 | 676.347 | 0 | 0.05921 | 2.7453 | 0 | 0 | 227.0638 | 120.863 | off_peak | 676.347 | 100 | 0 | 15.16 | 0 | 84.84 | 331.8092 | 0
7428 | 902.66 | 733.681 | 27.2 | 147.3937 | 147.3937 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 30.6357 | 767.6652 | 0 | 0.05921 | 3.1023 | 0 | 0 | 227.0638 | 147.3937 | off_peak | 755.2663 | 0 | 100 | 16.33 | 0 | 83.67 | 457.2548 | 0
7429 | 836.11 | 729.119 | 27.4 | 146.3709 | 146.3709 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 42.2338 | 702.138 | 0 | 0.05921 | 3.5941 | 0 | 0 | 227.0638 | 146.3709 | off_peak | 689.7391 | 0 | 100 | 17.51 | 0 | 82.49 | 526.0673 | 0
7430 | 866.07 | 669.061 | 27.5 | 134.2655 | 134.2655 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 53.832 | 744.2035 | 0 | 0.05921 | 3.7582 | 0 | 0 | 227.0638 | 134.2655 | off_peak | 731.8045 | 0 | 100 | 15.5 | 0 | 84.5 | 504.6015 | 0
7431 | 892.65 | 540.511 | 27.5 | 108.4684 | 96.0695 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 0 | 65.4301 | 796.5805 | 0 | 0.05921 | 3.4421 | 0 | 0 | 238.6619 | 96.0695 | off_peak | 796.5805 | 100 | 0 | 10.76 | 0 | 89.24 | 330.6822 | 0
7432 | 806.71 | 367.213 | 27.2 | 73.7717 | 64.8082 | 0 | 8.9635 | 8.9635 | 0 | 0 | 0 | 0 | 73.8147 | 741.9018 | 0 | 0.05921 | 3.3973 | 0 | 0 | 247.0465 | 64.8082 | off_peak | 741.9018 | 100 | 0 | 8.03 | 0 | 91.97 | 220.1726 | 0
7433 | 820.54 | 169.079 | 26.6 | 34.0413 | 33.4624 | 0 | 0.57892 | 0.57892 | 0 | 0 | 0 | 0 | 74.3563 | 787.0776 | 0 | 0.05921 | 3.4944 | 0 | 0 | 247.5881 | 33.4624 | off_peak | 787.0776 | 100 | 0 | 4.08 | 0 | 95.92 | 116.9303 | 0
7434 | 819.32 | 11.2751 | 26 | 2.275 | 2.2376 | 0 | 0.03739 | 0.03739 | 0 | 0 | 0 | 0 | 74.3912 | 817.0824 | 0 | 0.05921 | 3.781 | 0 | 0 | 247.623 | 2.2376 | off_peak | 817.0824 | 100 | 0 | 0.27 | 0 | 99.73 | 8.4604 | 0
7435 | 818.03 | 0 | 25.7 | 0 | 0 | 0 | 0 | 0 | 0 | 62.6277 | 62.6277 | 0 | 7.4394 | 755.4023 | 0 | 0.088511 | 4.1455 | 0 | 0 | 247.623 | 0 | on_peak | 755.4023 |  |  | 0 | 7.66 | 92.34 | 0 | 0
7436 | 805.81 | 0 | 25.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 805.81 | 0 | 0.088511 | 4.5884 | 0 | 0 | 247.623 | 0 | on_peak | 805.81 |  |  | 0 | 0 | 100 | 0 | 0
7437 | 801.21 | 0 | 25.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 801.21 | 0 | 0.088511 | 5.0135 | 0 | 0 | 247.623 | 0 | on_peak | 801.21 |  |  | 0 | 0 | 100 | 0 | 0
7438 | 775.69 | 0 | 25.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 775.69 | 0 | 0.088511 | 5.4705 | 0 | 0 | 247.623 | 0 | on_peak | 775.69 |  |  | 0 | 0 | 100 | 0 | 0
7439 | 814.46 | 0 | 25 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 19.0375 | 826.8589 | 0 | 0.05921 | 6.0031 | 0 | 0 | 247.623 | 0 | off_peak | 814.46 | 0 | 100 | 0 | 0 | 100 | 0 | 0
7440 | 791.17 | 0 | 24.9 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 30.6357 | 803.5689 | 0 | 0.05921 | 6.3401 | 0 | 0 | 247.623 | 0 | off_peak | 791.17 | 0 | 100 | 0 | 0 | 100 | 0 | 0
7441 | 709.51 | 0 | 24.8 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 42.2338 | 721.9089 | 0 | 0.05921 | 6.4098 | 0 | 0 | 247.623 | 0 | off_peak | 709.51 | 0 | 100 | 0 | 0 | 100 | 0 | 0
7442 | 634.06 | 0 | 24.7 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 53.832 | 646.4589 | 0 | 0.05921 | 6.038 | 0 | 0 | 247.623 | 0 | off_peak | 634.06 | 0 | 100 | 0 | 0 | 100 | 0 | 0
7443 | 628.08 | 0 | 24.6 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 65.4301 | 640.4789 | 0 | 0.05921 | 5.6834 | 0 | 0 | 247.623 | 0 | off_peak | 628.08 | 0 | 100 | 0 | 0 | 100 | 0 | 0
7444 | 632.28 | 0 | 24.5 | 0 | 0 | 0 | 0 | 8.9635 | 8.9635 | 0 | 0 | 0 | 73.8147 | 641.2435 | 0 | 0.05921 | 5.3077 | 0 | 0 | 247.623 | 0 | off_peak | 632.28 | 0 | 100 | 0 | 0 | 100 | 0 | 0
7445 | 630.95 | 0 | 24.5 | 0 | 0 | 0 | 0 | 0.57892 | 0.57892 | 0 | 0 | 0 | 74.3563 | 631.5289 | 0 | 0.05921 | 4.8077 | 0 | 0 | 247.623 | 0 | off_peak | 630.95 | 0 | 100 | 0 | 0 | 100 | 0 | 0
7446 | 640.46 | 0 | 24.5 | 0 | 0 | 0 | 0 | 0.03739 | 0.03739 | 0 | 0 | 0 | 74.3912 | 640.4974 | 0 | 0.05921 | 4.0935 | 0 | 0 | 247.623 | 0 | off_peak | 640.46 | 0 | 100 | 0 | 0 | 100 | 0 | 0
7447 | 710.17 | 0 | 24.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3912 | 710.17 | 0 | 0.088511 | 3.5766 | 0 | 0 | 247.623 | 0 | on_peak | 710.17 |  |  | 0 | 0 | 100 | 0 | 0
7448 | 769.92 | 145.466 | 25.3 | 29.4251 | 29.4251 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3912 | 740.4949 | 0 | 0.088511 | 3.2694 | 0 | 0 | 247.623 | 29.4251 | on_peak | 740.4949 |  |  | 3.82 | 0 | 96.18 | 96.2013 | 0
7449 | 797.73 | 344.936 | 25.9 | 69.6232 | 69.6232 | 0 | 0 | 0 | 0 | 62.6277 | 62.6277 | 0 | 7.4394 | 665.479 | 0 | 0.088511 | 3.0857 | 0 | 0 | 247.623 | 69.6232 | on_peak | 665.479 |  |  | 8.73 | 7.85 | 83.42 | 214.8331 | 0
7450 | 867.63 | 496.891 | 26.4 | 100.1133 | 100.1133 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 767.5167 | 0 | 0.088511 | 3.0246 | 0 | 0 | 247.623 | 100.1133 | on_peak | 767.5167 |  |  | 11.54 | 0 | 88.46 | 302.7977 | 0
7451 | 829.45 | 647.418 | 26.8 | 130.2526 | 130.2526 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 19.0375 | 711.5963 | 0 | 0.05921 | 3.0387 | 0 | 0 | 247.623 | 130.2526 | off_peak | 699.1974 | 0 | 100 | 15.7 | 0 | 84.3 | 395.7959 | 0
7452 | 877.45 | 704.924 | 27.1 | 141.6679 | 141.6679 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 30.6357 | 748.181 | 0 | 0.05921 | 3.3315 | 0 | 0 | 247.623 | 141.6679 | off_peak | 735.7821 | 0 | 100 | 16.15 | 0 | 83.85 | 471.9681 | 0
7453 | 878.45 | 722.78 | 27.1 | 145.2564 | 145.2564 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 42.2338 | 745.5925 | 0 | 0.05921 | 3.8129 | 0 | 0 | 247.623 | 145.2564 | off_peak | 733.1936 | 0 | 100 | 16.54 | 0 | 83.46 | 553.8441 | 0
7454 | 858.35 | 658.267 | 27 | 132.3393 | 132.3393 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 53.832 | 738.4096 | 0 | 0.05921 | 4.06 | 0 | 0 | 247.623 | 132.3393 | off_peak | 726.0107 | 0 | 100 | 15.42 | 0 | 84.58 | 537.2952 | 0
7455 | 876.69 | 536.455 | 26.8 | 107.9282 | 107.9282 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 65.4301 | 781.1607 | 0 | 0.05921 | 3.836 | 0 | 0 | 247.623 | 107.9282 | off_peak | 768.7618 | 0 | 100 | 12.31 | 0 | 87.69 | 414.0101 | 0
7456 | 815.07 | 368.982 | 26.4 | 74.3423 | 74.3423 | 0 | 0 | 8.9635 | 8.9635 | 0 | 0 | 0 | 73.8147 | 749.6913 | 0 | 0.05921 | 3.8833 | 0 | 0 | 247.623 | 74.3423 | off_peak | 740.7277 | 0 | 100 | 9.12 | 0 | 90.88 | 288.6948 | 0
7457 | 839.22 | 174.021 | 25.9 | 35.1251 | 35.1251 | 0 | 0 | 0.57892 | 0.57892 | 0 | 0 | 0 | 74.3563 | 804.6738 | 0 | 0.05921 | 4.2271 | 0 | 0 | 247.623 | 35.1251 | off_peak | 804.0949 | 0 | 100 | 4.19 | 0 | 95.81 | 148.4756 | 0
7458 | 885.89 | 12.637 | 25.4 | 2.5553 | 2.5553 | 0 | 0 | 0 | 0 | 30.5073 | 30.5073 | 0 | 41.7426 | 852.8274 | 0 | 0.05921 | 4.6693 | 0 | 0 | 247.623 | 2.5553 | off_peak | 852.8274 |  |  | 0.29 | 3.44 | 96.27 | 11.9316 | 0
7459 | 835.17 | 0 | 25.2 | 0 | 0 | 0 | 0 | 0 | 0 | 9.9259 | 9.9259 | 0 | 31.1313 | 825.2441 | 0 | 0.088511 | 5.0633 | 0 | 0 | 247.623 | 0 | on_peak | 825.2441 |  |  | 0 | 1.19 | 98.81 | 0 | 0
7460 | 825.88 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0.63591 | 0.63591 | 0 | 30.4515 | 825.2441 | 0 | 0.088511 | 5.42 | 0.63591 | 0 | 246.9432 | 0.63591 | on_peak | 825.2441 |  |  | 0 | 0.08 | 99.92 | 3.4466 | 0
7461 | 846.77 | 0 | 24.9 | 0 | 0 | 0 | 0 | 0 | 0 | 21.5259 | 21.5259 | 0 | 7.4394 | 825.2441 | 0 | 0.088511 | 5.6662 | 21.5259 | 0 | 223.9311 | 21.5259 | on_peak | 825.2441 |  |  | 0 | 2.54 | 97.46 | 121.9697 | 0
7462 | 743.49 | 0 | 24.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 743.49 | 0 | 0.088511 | 5.9927 | 0 | 0 | 223.9311 | 0 | on_peak | 743.49 |  |  | 0 | 0 | 100 | 0 | 0
7463 | 815.32 | 0 | 24.7 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 19.0375 | 827.7189 | 0 | 0.05921 | 6.4265 | 0 | 0 | 223.9311 | 0 | off_peak | 815.32 | 0 | 100 | 0 | 0 | 100 | 0 | 0
7464 | 788.34 | 0 | 24.5 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 30.6357 | 800.7389 | 0 | 0.05921 | 6.6952 | 0 | 0 | 223.9311 | 0 | off_peak | 788.34 | 0 | 100 | 0 | 0 | 100 | 0 | 0
7465 | 707.34 | 0 | 24.3 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 42.2338 | 719.7389 | 0 | 0.05921 | 6.6853 | 0 | 0 | 223.9311 | 0 | off_peak | 707.34 | 0 | 100 | 0 | 0 | 100 | 0 | 0
7466 | 642.08 | 0 | 24.2 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 53.832 | 654.4789 | 0 | 0.05921 | 6.3213 | 0 | 0 | 223.9311 | 0 | off_peak | 642.08 | 0 | 100 | 0 | 0 | 100 | 0 | 0
7467 | 614.55 | 0 | 24 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 65.4301 | 626.9489 | 0 | 0.05921 | 5.9029 | 0 | 0 | 223.9311 | 0 | off_peak | 614.55 | 0 | 100 | 0 | 0 | 100 | 0 | 0
7468 | 633.54 | 0 | 23.9 | 0 | 0 | 0 | 0 | 8.9635 | 8.9635 | 0 | 0 | 0 | 73.8147 | 642.5035 | 0 | 0.05921 | 5.5092 | 0 | 0 | 223.9311 | 0 | off_peak | 633.54 | 0 | 100 | 0 | 0 | 100 | 0 | 0
7469 | 618.33 | 0 | 23.9 | 0 | 0 | 0 | 0 | 0.57892 | 0.57892 | 0 | 0 | 0 | 74.3563 | 618.9089 | 0 | 0.05921 | 4.9688 | 0 | 0 | 223.9311 | 0 | off_peak | 618.33 | 0 | 100 | 0 | 0 | 100 | 0 | 0
7470 | 616.3 | 0 | 23.9 | 0 | 0 | 0 | 0 | 0.03739 | 0.03739 | 0 | 0 | 0 | 74.3912 | 616.3374 | 0 | 0.05921 | 4.3268 | 0 | 0 | 223.9311 | 0 | off_peak | 616.3 | 0 | 100 | 0 | 0 | 100 | 0 | 0
7471 | 687.57 | 0 | 24.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3912 | 687.57 | 0 | 0.088511 | 3.7422 | 0 | 0 | 223.9311 | 0 | on_peak | 687.57 |  |  | 0 | 0 | 100 | 0 | 0
7472 | 742.41 | 107.998 | 24.7 | 21.8932 | 21.8932 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3912 | 720.5168 | 0 | 0.088511 | 3.3955 | 0 | 0 | 223.9311 | 21.8932 | on_peak | 720.5168 |  |  | 2.95 | 0 | 97.05 | 74.3382 | 0
7473 | 797.23 | 184.914 | 25.4 | 37.3912 | 37.3912 | 0 | 0 | 0 | 0 | 62.6277 | 62.6277 | 0 | 7.4394 | 697.2111 | 0 | 0.088511 | 3.2067 | 0 | 0 | 223.9311 | 37.3912 | on_peak | 697.2111 |  |  | 4.69 | 7.86 | 87.45 | 119.9014 | 0
7474 | 834.94 | 445.845 | 25.8 | 90.0236 | 90.0236 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 744.9164 | 0 | 0.088511 | 3.1191 | 0 | 0 | 223.9311 | 90.0236 | on_peak | 744.9164 |  |  | 10.78 | 0 | 89.22 | 280.7897 | 0
7475 | 792.93 | 632.632 | 26.2 | 127.5546 | 127.5546 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 19.0375 | 677.7744 | 0 | 0.05921 | 3.1412 | 0 | 0 | 223.9311 | 127.5546 | off_peak | 665.3754 | 0 | 100 | 16.09 | 0 | 83.91 | 400.6795 | 0
7476 | 845 | 716.935 | 26.4 | 144.4476 | 144.4476 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 30.6357 | 712.9513 | 0 | 0.05921 | 3.1578 | 0 | 0 | 223.9311 | 144.4476 | off_peak | 700.5524 | 0 | 100 | 17.09 | 0 | 82.91 | 456.1362 | 0
7477 | 839.9 | 727.165 | 26.5 | 146.4558 | 146.4558 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 42.2338 | 705.8432 | 0 | 0.05921 | 3.9266 | 0 | 0 | 223.9311 | 146.4558 | off_peak | 693.4442 | 0 | 100 | 17.44 | 0 | 82.56 | 575.0769 | 0
7478 | 832.11 | 661.141 | 26.5 | 133.1581 | 120.7592 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 0 | 53.832 | 711.3508 | 0 | 0.05921 | 4.1421 | 0 | 0 | 235.5292 | 120.7592 | off_peak | 711.3508 | 100 | 0 | 14.51 | 0 | 85.49 | 500.1966 | 0
7479 | 868.47 | 537.488 | 26.5 | 108.2536 | 95.8546 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 0 | 65.4301 | 772.6154 | 0 | 0.05921 | 4.0265 | 0 | 0 | 247.1273 | 95.8546 | off_peak | 772.6154 | 100 | 0 | 11.04 | 0 | 88.96 | 385.9582 | 0
7480 | 799.97 | 366.036 | 26.3 | 73.7754 | 64.8119 | 0 | 8.9635 | 8.9635 | 0 | 0 | 0 | 0 | 73.8147 | 735.1581 | 0 | 0.05921 | 4.0703 | 0 | 0 | 255.512 | 64.8119 | off_peak | 735.1581 | 100 | 0 | 8.1 | 0 | 91.9 | 263.8043 | 0
7481 | 797.78 | 168.86 | 25.8 | 34.0957 | 34.0957 | 0 | 0 | 0.57892 | 0.57892 | 0 | 0 | 0 | 74.3563 | 764.2632 | 0 | 0.05921 | 4.3936 | 0 | 0 | 255.512 | 34.0957 | off_peak | 763.6843 | 0 | 100 | 4.27 | 0 | 95.73 | 149.8033 | 0
7482 | 849.31 | 11.2885 | 25.2 | 2.2843 | 2.2843 | 0 | 0 | 0.03739 | 0.03739 | 0 | 0 | 0 | 74.3912 | 847.0631 | 0 | 0.05921 | 4.8342 | 0 | 0 | 255.512 | 2.2843 | off_peak | 847.0257 | 0 | 100 | 0.27 | 0 | 99.73 | 11.0427 | 0
7483 | 805.15 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 62.6277 | 62.6277 | 0 | 7.4394 | 742.5223 | 0 | 0.088511 | 5.1862 | 0 | 0 | 255.512 | 0 | on_peak | 742.5223 |  |  | 0 | 7.78 | 92.22 | 0 | 0
7484 | 804.56 | 0 | 24.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 804.56 | 0 | 0.088511 | 5.6091 | 0 | 0 | 255.512 | 0 | on_peak | 804.56 |  |  | 0 | 0 | 100 | 0 | 0
7485 | 802.83 | 0 | 24.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 802.83 | 0 | 0.088511 | 5.9261 | 0 | 0 | 255.512 | 0 | on_peak | 802.83 |  |  | 0 | 0 | 100 | 0 | 0
7486 | 760.12 | 0 | 24.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 760.12 | 0 | 0.088511 | 6.2504 | 0 | 0 | 255.512 | 0 | on_peak | 760.12 |  |  | 0 | 0 | 100 | 0 | 0
7487 | 811.58 | 0 | 24.7 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 19.0375 | 823.9789 | 0 | 0.05921 | 6.6544 | 0 | 0 | 255.512 | 0 | off_peak | 811.58 | 0 | 100 | 0 | 0 | 100 | 0 | 0
7488 | 777.91 | 0 | 24.5 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 30.6357 | 790.3089 | 0 | 0.05921 | 6.8958 | 0 | 0 | 255.512 | 0 | off_peak | 777.91 | 0 | 100 | 0 | 0 | 100 | 0 | 0
7489 | 674.97 | 0 | 24.3 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 42.2338 | 687.3689 | 0 | 0.05921 | 6.9048 | 0 | 0 | 255.512 | 0 | off_peak | 674.97 | 0 | 100 | 0 | 0 | 100 | 0 | 0
7490 | 607.33 | 0 | 24.1 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 53.832 | 619.7289 | 0 | 0.05921 | 6.5911 | 0 | 0 | 255.512 | 0 | off_peak | 607.33 | 0 | 100 | 0 | 0 | 100 | 0 | 0
7491 | 613.18 | 0 | 23.9 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 65.4301 | 625.5789 | 0 | 0.05921 | 6.1215 | 0 | 0 | 255.512 | 0 | off_peak | 613.18 | 0 | 100 | 0 | 0 | 100 | 0 | 0
7492 | 597.81 | 0 | 23.7 | 0 | 0 | 0 | 0 | 8.9635 | 8.9635 | 0 | 0 | 0 | 73.8147 | 606.7735 | 0 | 0.05921 | 5.5931 | 0 | 0 | 255.512 | 0 | off_peak | 597.81 | 0 | 100 | 0 | 0 | 100 | 0 | 0
7493 | 615.89 | 0 | 23.6 | 0 | 0 | 0 | 0 | 0.57892 | 0.57892 | 0 | 0 | 0 | 74.3563 | 616.4689 | 0 | 0.05921 | 5.0818 | 0 | 0 | 255.512 | 0 | off_peak | 615.89 | 0 | 100 | 0 | 0 | 100 | 0 | 0
7494 | 612.41 | 0 | 23.6 | 0 | 0 | 0 | 0 | 0.03739 | 0.03739 | 0 | 0 | 0 | 74.3912 | 612.4474 | 0 | 0.05921 | 4.5318 | 0 | 0 | 255.512 | 0 | off_peak | 612.41 | 0 | 100 | 0 | 0 | 100 | 0 | 0
7495 | 684.3 | 0 | 23.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3912 | 684.3 | 0 | 0.088511 | 3.969 | 0 | 0 | 255.512 | 0 | on_peak | 684.3 |  |  | 0 | 0 | 100 | 0 | 0
7496 | 774.35 | 121.685 | 24.5 | 24.6856 | 24.6856 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3912 | 749.6644 | 0 | 0.088511 | 3.6096 | 0 | 0 | 255.512 | 24.6856 | on_peak | 749.6644 |  |  | 3.19 | 0 | 96.81 | 89.1056 | 0
7497 | 777.36 | 262.863 | 25.2 | 53.1914 | 53.1914 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3912 | 724.1686 | 0 | 0.088511 | 3.4059 | 0 | 0 | 255.512 | 53.1914 | on_peak | 724.1686 |  |  | 6.84 | 0 | 93.16 | 181.1654 | 0
7498 | 807.3 | 450.673 | 25.6 | 91.0642 | 91.0642 | 0 | 0 | 0 | 0 | 62.6277 | 62.6277 | 0 | 7.4394 | 653.6081 | 0 | 0.088511 | 3.2924 | 0 | 0 | 255.512 | 91.0642 | on_peak | 653.6081 |  |  | 11.28 | 7.76 | 80.96 | 299.822 | 0
7499 | 800.81 | 394.094 | 26 | 79.5167 | 67.1178 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 0 | 19.0375 | 733.6922 | 0 | 0.05921 | 3.3169 | 0 | 0 | 267.1101 | 67.1178 | off_peak | 733.6922 | 100 | 0 | 8.38 | 0 | 91.62 | 222.622 | 0
7500 | 865.21 | 324.611 | 26.2 | 65.4498 | 53.0508 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 0 | 30.6357 | 812.1592 | 0 | 0.05921 | 3.5864 | 0 | 0 | 278.7083 | 53.0508 | off_peak | 812.1592 | 100 | 0 | 6.13 | 0 | 93.87 | 190.2619 | 0
7501 | 823.74 | 272.014 | 26.3 | 54.825 | 42.4261 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 0 | 42.2338 | 781.3139 | 0 | 0.05921 | 4.1171 | 0 | 0 | 290.3064 | 42.4261 | off_peak | 781.3139 | 100 | 0 | 5.15 | 0 | 94.85 | 174.6725 | 0
7502 | 828.34 | 376.649 | 26.3 | 75.9145 | 75.9145 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 53.832 | 764.8245 | 0 | 0.05921 | 4.3399 | 0 | 0 | 290.3064 | 75.9145 | off_peak | 752.4255 | 0 | 100 | 9.16 | 0 | 90.84 | 329.4608 | 0
7503 | 835.97 | 240.731 | 26.2 | 48.5374 | 36.1385 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 0 | 65.4301 | 799.8315 | 0 | 0.05921 | 4.2875 | 0 | 0 | 301.9046 | 36.1385 | off_peak | 799.8315 | 100 | 0 | 4.32 | 0 | 95.68 | 154.9431 | 0
7504 | 799.22 | 278.462 | 25.9 | 56.2059 | 56.2059 | 0 | 0 | 8.9635 | 8.9635 | 0 | 0 | 0 | 73.8147 | 751.9777 | 0 | 0.05921 | 4.3429 | 0 | 0 | 301.9046 | 56.2059 | off_peak | 743.0141 | 0 | 100 | 7.03 | 0 | 92.97 | 244.0981 | 0
7505 | 841.68 | 167.847 | 25.3 | 33.9523 | 33.3734 | 0 | 0.57892 | 0.57892 | 0 | 0 | 0 | 0 | 74.3563 | 808.3066 | 0 | 0.05921 | 4.6815 | 0 | 0 | 302.4461 | 33.3734 | off_peak | 808.3066 | 100 | 0 | 3.97 | 0 | 96.03 | 156.2362 | 0
7506 | 824.11 | 10.3328 | 24.7 | 2.0947 | 2.0573 | 0 | 0.03739 | 0.03739 | 0 | 0 | 0 | 0 | 74.3912 | 822.0527 | 0 | 0.05921 | 5.1586 | 0 | 0 | 302.4811 | 2.0573 | off_peak | 822.0527 | 100 | 0 | 0.25 | 0 | 99.75 | 10.6126 | 0
7507 | 832.37 | 0 | 24.4 | 0 | 0 | 0 | 0 | 0 | 0 | 7.1259 | 7.1259 | 0 | 66.7733 | 825.2441 | 0 | 0.088511 | 5.4606 | 0 | 0 | 302.4811 | 0 | on_peak | 825.2441 |  |  | 0 | 0.86 | 99.14 | 0 | 0
7508 | 867.63 | 0 | 24.1 | 0 | 0 | 0 | 0 | 0 | 0 | 42.3859 | 42.3859 | 0 | 21.4609 | 825.2441 | 0 | 0.088511 | 5.808 | 0 | 0 | 302.4811 | 0 | on_peak | 825.2441 |  |  | 0 | 4.89 | 95.11 | 0 | 0
7509 | 838.36 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 13.1159 | 13.1159 | 0 | 7.4394 | 825.2441 | 0 | 0.088511 | 6.0482 | 0 | 0 | 302.4811 | 0 | on_peak | 825.2441 |  |  | 0 | 1.56 | 98.44 | 0 | 0
7510 | 805.06 | 0 | 23.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 805.06 | 0 | 0.088511 | 6.3997 | 0 | 0 | 302.4811 | 0 | on_peak | 805.06 |  |  | 0 | 0 | 100 | 0 | 0
7511 | 811.01 | 0 | 23.7 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 19.0375 | 823.4089 | 0 | 0.05921 | 6.7131 | 0 | 0 | 302.4811 | 0 | off_peak | 811.01 | 0 | 100 | 0 | 0 | 100 | 0 | 0
7512 | 804.98 | 0 | 23.5 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 30.6357 | 817.3789 | 0 | 0.05921 | 6.8665 | 0 | 0 | 302.4811 | 0 | off_peak | 804.98 | 0 | 100 | 0 | 0 | 100 | 0 | 0
7513 | 712.65 | 0 | 23.4 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 42.2338 | 725.0489 | 0 | 0.05921 | 6.892 | 0 | 0 | 302.4811 | 0 | off_peak | 712.65 | 0 | 100 | 0 | 0 | 100 | 0 | 0
7514 | 605.14 | 0 | 23.3 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 53.832 | 617.5389 | 0 | 0.05921 | 6.6721 | 0 | 0 | 302.4811 | 0 | off_peak | 605.14 | 0 | 100 | 0 | 0 | 100 | 0 | 0
7515 | 632.82 | 0 | 23.2 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 65.4301 | 645.2189 | 0 | 0.05921 | 6.2857 | 0 | 0 | 302.4811 | 0 | off_peak | 632.82 | 0 | 100 | 0 | 0 | 100 | 0 | 0
7516 | 620.34 | 0 | 23 | 0 | 0 | 0 | 0 | 8.9635 | 8.9635 | 0 | 0 | 0 | 73.8147 | 629.3035 | 0 | 0.05921 | 5.968 | 0 | 0 | 302.4811 | 0 | off_peak | 620.34 | 0 | 100 | 0 | 0 | 100 | 0 | 0
7517 | 657.4 | 0 | 22.7 | 0 | 0 | 0 | 0 | 0.57892 | 0.57892 | 0 | 0 | 0 | 74.3563 | 657.9789 | 0 | 0.05921 | 5.4422 | 0 | 0 | 302.4811 | 0 | off_peak | 657.4 | 0 | 100 | 0 | 0 | 100 | 0 | 0
7518 | 660.71 | 0 | 22.4 | 0 | 0 | 0 | 0 | 0.03739 | 0.03739 | 0 | 0 | 0 | 74.3912 | 660.7474 | 0 | 0.05921 | 4.8415 | 0 | 0 | 302.4811 | 0 | off_peak | 660.71 | 0 | 100 | 0 | 0 | 100 | 0 | 0
7519 | 726.16 | 0 | 22.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3912 | 726.16 | 0 | 0.088511 | 4.4083 | 0 | 0 | 302.4811 | 0 | on_peak | 726.16 |  |  | 0 | 0 | 100 | 0 | 0
7520 | 768.31 | 136.514 | 23 | 27.8431 | 27.8431 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3912 | 740.4669 | 0 | 0.088511 | 4.0698 | 0 | 0 | 302.4811 | 27.8431 | on_peak | 740.4669 |  |  | 3.62 | 0 | 96.38 | 113.3172 | 0
7521 | 795.38 | 333.287 | 23.8 | 67.7822 | 67.7822 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3912 | 727.5978 | 0 | 0.088511 | 3.8416 | 0 | 0 | 302.4811 | 67.7822 | on_peak | 727.5978 |  |  | 8.52 | 0 | 91.48 | 260.3926 | 0
7522 | 826.58 | 505.119 | 24.4 | 102.5075 | 102.5075 | 0 | 0 | 0 | 0 | 62.6277 | 62.6277 | 0 | 7.4394 | 661.4447 | 0 | 0.088511 | 3.7301 | 0 | 0 | 302.4811 | 102.5075 | on_peak | 661.4447 |  |  | 12.4 | 7.58 | 80.02 | 382.3633 | 0
7523 | 794.89 | 631.184 | 24.9 | 127.8608 | 127.8608 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 19.0375 | 679.4282 | 0 | 0.05921 | 3.7185 | 0 | 0 | 302.4811 | 127.8608 | off_peak | 667.0292 | 0 | 100 | 16.09 | 0 | 83.91 | 475.4554 | 0
7524 | 828.63 | 702.576 | 25.4 | 142.0668 | 142.0668 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 30.6357 | 698.9622 | 0 | 0.05921 | 3.9056 | 0 | 0 | 302.4811 | 142.0668 | off_peak | 686.5632 | 0 | 100 | 17.14 | 0 | 82.86 | 554.856 | 0
7525 | 792.34 | 579.159 | 25.7 | 116.9842 | 116.9842 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 42.2338 | 687.7548 | 0 | 0.05921 | 4.3035 | 0 | 0 | 302.4811 | 116.9842 | off_peak | 675.3558 | 0 | 100 | 14.76 | 0 | 85.24 | 503.4416 | 0
7526 | 780.67 | 455.181 | 26 | 91.8423 | 79.4434 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 0 | 53.832 | 701.2266 | 0 | 0.05921 | 4.5682 | 0 | 0 | 314.0792 | 79.4434 | off_peak | 701.2266 | 100 | 0 | 10.18 | 0 | 89.82 | 362.9125 | 0
7527 | 821.35 | 397.894 | 26.1 | 80.2545 | 80.2545 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 65.4301 | 753.4945 | 0 | 0.05921 | 4.8967 | 0 | 0 | 314.0792 | 80.2545 | off_peak | 741.0955 | 0 | 100 | 9.77 | 0 | 90.23 | 392.9792 | 0
7528 | 802.42 | 267.501 | 26 | 53.9739 | 53.9739 | 0 | 0 | 8.9635 | 8.9635 | 0 | 0 | 0 | 73.8147 | 757.4096 | 0 | 0.05921 | 5.2464 | 0 | 0 | 314.0792 | 53.9739 | off_peak | 748.4461 | 0 | 100 | 6.73 | 0 | 93.27 | 283.1715 | 0
7529 | 793.06 | 160.225 | 25.6 | 32.3755 | 31.7966 | 0 | 0.57892 | 0.57892 | 0 | 0 | 0 | 0 | 74.3563 | 761.2634 | 0 | 0.05921 | 5.8359 | 0 | 0 | 314.6207 | 31.7966 | off_peak | 761.2634 | 100 | 0 | 4.01 | 0 | 95.99 | 185.5603 | 0
7530 | 810.44 | 9.9912 | 24.9 | 2.0239 | 2.0239 | 0 | 0 | 0.03739 | 0.03739 | 0 | 0 | 0 | 74.3912 | 808.4534 | 0 | 0.05921 | 6.2693 | 0 | 0 | 314.6207 | 2.0239 | off_peak | 808.4161 | 0 | 100 | 0.25 | 0 | 99.75 | 12.6887 | 0
7531 | 797.26 | 0 | 24.7 | 0 | 0 | 0 | 0 | 0 | 0 | 62.6277 | 62.6277 | 0 | 7.4394 | 734.6323 | 0 | 0.088511 | 6.7964 | 0 | 0 | 314.6207 | 0 | on_peak | 734.6323 |  |  | 0 | 7.86 | 92.14 | 0 | 0
7532 | 779.35 | 0 | 24.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 779.35 | 0 | 0.088511 | 7.387 | 0 | 0 | 314.6207 | 0 | on_peak | 779.35 |  |  | 0 | 0 | 100 | 0 | 0
7533 | 807.89 | 0 | 24.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 807.89 | 0 | 0.088511 | 7.6505 | 0 | 0 | 314.6207 | 0 | on_peak | 807.89 |  |  | 0 | 0 | 100 | 0 | 0
7534 | 710.89 | 0 | 23.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 710.89 | 0 | 0.088511 | 7.9318 | 0 | 0 | 314.6207 | 0 | on_peak | 710.89 |  |  | 0 | 0 | 100 | 0 | 0
7535 | 752.64 | 0 | 23.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 752.64 | 0 | 0.05921 | 8.05 | 0 | 0 | 314.6207 | 0 | off_peak | 752.64 |  |  | 0 | 0 | 100 | 0 | 0
7536 | 749.72 | 0 | 23.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 749.72 | 0 | 0.05921 | 8.0333 | 0 | 0 | 314.6207 | 0 | off_peak | 749.72 |  |  | 0 | 0 | 100 | 0 | 0
7537 | 671.7 | 0 | 23.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 671.7 | 0 | 0.05921 | 7.7704 | 0 | 0 | 314.6207 | 0 | off_peak | 671.7 |  |  | 0 | 0 | 100 | 0 | 0
7538 | 599.63 | 0 | 22.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 599.63 | 0 | 0.05921 | 7.282 | 0 | 0 | 314.6207 | 0 | off_peak | 599.63 |  |  | 0 | 0 | 100 | 0 | 0
7539 | 619.86 | 0 | 22.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 619.86 | 0 | 0.05921 | 6.8768 | 0 | 0 | 314.6207 | 0 | off_peak | 619.86 |  |  | 0 | 0 | 100 | 0 | 0
7540 | 544.46 | 0 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 544.46 | 0 | 0.05921 | 6.4641 | 0 | 0 | 314.6207 | 0 | off_peak | 544.46 |  |  | 0 | 0 | 100 | 0 | 0
7541 | 600.23 | 0 | 21.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 600.23 | 0 | 0.05921 | 5.9005 | 0 | 0 | 314.6207 | 0 | off_peak | 600.23 |  |  | 0 | 0 | 100 | 0 | 0
7542 | 660.71 | 0 | 21.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 660.71 | 0 | 0.05921 | 5.4583 | 0 | 0 | 314.6207 | 0 | off_peak | 660.71 |  |  | 0 | 0 | 100 | 0 | 0
7543 | 650.39 | 0 | 21.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 650.39 | 0 | 0.05921 | 4.97 | 0 | 0 | 314.6207 | 0 | off_peak | 650.39 |  |  | 0 | 0 | 100 | 0 | 0
7544 | 719.33 | 121.406 | 22.4 | 24.8148 | 24.8148 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 694.5152 | 0 | 0.05921 | 4.6405 | 0 | 0 | 314.6207 | 24.8148 | off_peak | 694.5152 |  |  | 3.45 | 0 | 96.55 | 115.1534 | 0
7545 | 699.44 | 314.864 | 23.3 | 64.1502 | 64.1502 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 635.2898 | 0 | 0.05921 | 4.3368 | 0 | 0 | 314.6207 | 64.1502 | off_peak | 635.2898 |  |  | 9.17 | 0 | 90.83 | 278.2066 | 0
7546 | 681.83 | 421.15 | 24.2 | 85.5285 | 85.5285 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 596.3015 | 0 | 0.05921 | 4.1267 | 0 | 0 | 314.6207 | 85.5285 | off_peak | 596.3015 |  |  | 12.54 | 0 | 87.46 | 352.9493 | 0
7547 | 688.17 | 598.405 | 25 | 121.177 | 121.177 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 566.993 | 0 | 0.05921 | 4.0289 | 0 | 0 | 314.6207 | 121.177 | off_peak | 566.993 |  |  | 17.61 | 0 | 82.39 | 488.2096 | 0
7548 | 720.34 | 687.489 | 25.7 | 138.8657 | 138.8657 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 581.4743 | 0 | 0.05921 | 4.0483 | 0 | 0 | 314.6207 | 138.8657 | off_peak | 581.4743 |  |  | 19.28 | 0 | 80.72 | 562.1738 | 0
7549 | 690.05 | 693.735 | 26.1 | 139.925 | 139.925 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 550.125 | 0 | 0.05921 | 4.2142 | 0 | 0 | 314.6207 | 139.925 | off_peak | 550.125 |  |  | 20.28 | 0 | 79.72 | 589.6686 | 0
7550 | 704.39 | 632.656 | 26.3 | 127.5133 | 127.5133 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 576.8767 | 0 | 0.05921 | 4.5267 | 0 | 0 | 314.6207 | 127.5133 | off_peak | 576.8767 |  |  | 18.1 | 0 | 81.9 | 577.2197 | 0
7551 | 687.14 | 514.439 | 26.3 | 103.6864 | 103.6864 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 583.4536 | 0 | 0.05921 | 5.0135 | 0 | 0 | 314.6207 | 103.6864 | off_peak | 583.4536 |  |  | 15.09 | 0 | 84.91 | 519.8361 | 0
7552 | 724.61 | 348.282 | 26.1 | 70.2478 | 70.2478 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 654.3622 | 0 | 0.05921 | 5.5158 | 0 | 0 | 314.6207 | 70.2478 | off_peak | 654.3622 |  |  | 9.69 | 0 | 90.31 | 387.4706 | 0
7553 | 724.61 | 158.176 | 25.5 | 31.973 | 31.973 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 692.637 | 0 | 0.05921 | 6.0386 | 0 | 0 | 314.6207 | 31.973 | off_peak | 692.637 |  |  | 4.41 | 0 | 95.59 | 193.071 | 0
7554 | 631.81 | 9.8589 | 24.9 | 1.9971 | 0 | 0 | 1.9971 | 1.9971 | 0 | 0 | 0 | 0 | 9.3075 | 631.81 | 0 | 0.05921 | 6.4354 | 0 | 0 | 316.4889 | 0 | off_peak | 631.81 | 100 | 0 | 0 | 0 | 100 | 0 | 0
7555 | 591.87 | 0 | 24.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9.3075 | 591.87 | 0 | 0.05921 | 6.9736 | 0 | 0 | 316.4889 | 0 | off_peak | 591.87 |  |  | 0 | 0 | 100 | 0 | 0
7556 | 598.02 | 0 | 24.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9.3075 | 598.02 | 0 | 0.05921 | 7.5396 | 0 | 0 | 316.4889 | 0 | off_peak | 598.02 |  |  | 0 | 0 | 100 | 0 | 0
7557 | 588.04 | 0 | 24.1 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 20.9057 | 600.4389 | 0 | 0.05921 | 7.8531 | 0 | 0 | 316.4889 | 0 | off_peak | 588.04 | 0 | 100 | 0 | 0 | 100 | 0 | 0
7558 | 618.88 | 0 | 23.9 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 32.5038 | 631.2789 | 0 | 0.05921 | 8.0127 | 0 | 0 | 316.4889 | 0 | off_peak | 618.88 | 0 | 100 | 0 | 0 | 100 | 0 | 0
7559 | 588.31 | 0 | 23.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 32.5038 | 588.31 | 0 | 0.05921 | 7.9355 | 0 | 0 | 316.4889 | 0 | off_peak | 588.31 |  |  | 0 | 0 | 100 | 0 | 0
7560 | 604.76 | 0 | 23.6 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 44.102 | 617.1589 | 0 | 0.05921 | 7.793 | 0 | 0 | 316.4889 | 0 | off_peak | 604.76 | 0 | 100 | 0 | 0 | 100 | 0 | 0
7561 | 612.06 | 0 | 23.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 44.102 | 612.06 | 0 | 0.05921 | 7.5078 | 0 | 0 | 316.4889 | 0 | off_peak | 612.06 |  |  | 0 | 0 | 100 | 0 | 0
7562 | 605.16 | 0 | 23.3 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 55.7001 | 617.5589 | 0 | 0.05921 | 6.9923 | 0 | 0 | 316.4889 | 0 | off_peak | 605.16 | 0 | 100 | 0 | 0 | 100 | 0 | 0
7563 | 602.31 | 0 | 23.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 55.7001 | 602.31 | 0 | 0.05921 | 6.5683 | 0 | 0 | 316.4889 | 0 | off_peak | 602.31 |  |  | 0 | 0 | 100 | 0 | 0
7564 | 597.79 | 0 | 23.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 55.7001 | 597.79 | 0 | 0.05921 | 6.2601 | 0 | 0 | 316.4889 | 0 | off_peak | 597.79 |  |  | 0 | 0 | 100 | 0 | 0
7565 | 601.38 | 0 | 23.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 55.7001 | 601.38 | 0 | 0.05921 | 5.7862 | 0 | 0 | 316.4889 | 0 | off_peak | 601.38 |  |  | 0 | 0 | 100 | 0 | 0
7566 | 622.79 | 0 | 23.1 | 0 | 0 | 0 | 0 | 6.7292 | 6.7292 | 0 | 0 | 0 | 61.9947 | 629.5192 | 0 | 0.05921 | 5.2719 | 0 | 0 | 316.4889 | 0 | off_peak | 622.79 | 0 | 100 | 0 | 0 | 100 | 0 | 0
7567 | 709.13 | 0 | 23.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 61.9947 | 709.13 | 0 | 0.05921 | 4.7218 | 0 | 0 | 316.4889 | 0 | off_peak | 709.13 |  |  | 0 | 0 | 100 | 0 | 0
7568 | 709.8 | 100.325 | 23.8 | 20.4036 | 20.4036 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 61.9947 | 689.3964 | 0 | 0.05921 | 4.3191 | 0 | 0 | 316.4889 | 20.4036 | off_peak | 689.3964 |  |  | 2.87 | 0 | 97.13 | 88.125 | 0
7569 | 720.83 | 324.602 | 24.4 | 65.8739 | 65.8739 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 61.9947 | 654.9561 | 0 | 0.05921 | 4.0356 | 0 | 0 | 316.4889 | 65.8739 | off_peak | 654.9561 |  |  | 9.14 | 0 | 90.86 | 265.8425 | 0
7570 | 760.68 | 454.147 | 24.9 | 91.9979 | 91.9979 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 61.9947 | 668.6821 | 0 | 0.05921 | 3.8409 | 0 | 0 | 316.4889 | 91.9979 | off_peak | 668.6821 |  |  | 12.09 | 0 | 87.91 | 353.3536 | 0
7571 | 733.22 | 507.873 | 25.2 | 102.7702 | 102.7702 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 61.9947 | 630.4498 | 0 | 0.05921 | 3.7447 | 0 | 0 | 316.4889 | 102.7702 | off_peak | 630.4498 |  |  | 14.02 | 0 | 85.98 | 384.8423 | 0
7572 | 755.29 | 670.242 | 25.4 | 135.5286 | 135.5286 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 61.9947 | 619.7614 | 0 | 0.05921 | 3.7664 | 0 | 0 | 316.4889 | 135.5286 | off_peak | 619.7614 |  |  | 17.94 | 0 | 82.06 | 510.4545 | 0
7573 | 723.19 | 596.067 | 25.5 | 120.4863 | 120.4863 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 61.9947 | 602.7037 | 0 | 0.05921 | 3.8749 | 0 | 0 | 316.4889 | 120.4863 | off_peak | 602.7037 |  |  | 16.66 | 0 | 83.34 | 466.8687 | 0
7574 | 689.6 | 591.348 | 25.5 | 119.5324 | 119.5324 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 61.9947 | 570.0676 | 0 | 0.05921 | 4.1591 | 0 | 0 | 316.4889 | 119.5324 | off_peak | 570.0676 |  |  | 17.33 | 0 | 82.67 | 497.1451 | 0
7575 | 706.25 | 464.766 | 25.4 | 93.9796 | 93.9796 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 61.9947 | 612.2704 | 0 | 0.05921 | 4.7224 | 0 | 0 | 316.4889 | 93.9796 | off_peak | 612.2704 |  |  | 13.31 | 0 | 86.69 | 443.8103 | 0
7576 | 684.85 | 326.141 | 25.2 | 65.996 | 65.996 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 61.9947 | 618.854 | 0 | 0.05921 | 5.2338 | 0 | 0 | 316.4889 | 65.996 | off_peak | 618.854 |  |  | 9.64 | 0 | 90.36 | 345.4069 | 0
7577 | 685.92 | 142.691 | 24.8 | 28.9157 | 28.9157 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 61.9947 | 657.0043 | 0 | 0.05921 | 5.6393 | 0 | 0 | 316.4889 | 28.9157 | off_peak | 657.0043 |  |  | 4.22 | 0 | 95.78 | 163.0642 | 0
7578 | 649.03 | 8.75 | 24.3 | 1.7764 | 0 | 0 | 1.7764 | 12.3989 | 10.6226 | 0 | 0 | 0 | 73.5928 | 659.6526 | 0 | 0.05921 | 6.0268 | 0 | 0 | 318.1505 | 0 | off_peak | 649.03 | 14.33 | 85.67 | 0 | 0 | 100 | 0 | 0
7579 | 575.77 | 0 | 24.1 | 0 | 0 | 0 | 0 | 0.80079 | 0.80079 | 0 | 0 | 0 | 74.3419 | 576.5708 | 0 | 0.05921 | 6.3875 | 0 | 0 | 318.1505 | 0 | off_peak | 575.77 | 0 | 100 | 0 | 0 | 100 | 0 | 0
7580 | 567.92 | 0 | 24 | 0 | 0 | 0 | 0 | 0.05172 | 0.05172 | 0 | 0 | 0 | 74.3903 | 567.9717 | 0 | 0.05921 | 6.7362 | 0 | 0 | 318.1505 | 0 | off_peak | 567.92 | 0 | 100 | 0 | 0 | 100 | 0 | 0
7581 | 561.89 | 0 | 23.9 | 0 | 0 | 0 | 0 | 0.0033404 | 0.0033404 | 0 | 0 | 0 | 74.3934 | 561.8933 | 0 | 0.05921 | 7.0445 | 0 | 0 | 318.1505 | 0 | off_peak | 561.89 | 0 | 100 | 0 | 0 | 100 | 0 | 0
7582 | 580.94 | 0 | 23.8 | 0 | 0 | 0 | 0 | 0.00021574 | 0.00021574 | 0 | 0 | 0 | 74.3936 | 580.9402 | 0 | 0.05921 | 7.2483 | 0 | 0 | 318.1505 | 0 | off_peak | 580.94 | 0 | 100 | 0 | 0 | 100 | 0 | 0
7583 | 571.51 | 0 | 23.8 | 0 | 0 | 0 | 0 | 1.4896e-05 | 1.4896e-05 | 0 | 0 | 0 | 74.3936 | 571.51 | 0 | 0.05921 | 7.4462 | 0 | 0 | 318.1505 | 0 | off_peak | 571.51 | 0 | 100 | 0 | 0 | 100 | 0 | 0
7584 | 558.43 | 0 | 23.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 558.43 | 0 | 0.05921 | 7.3991 | 0 | 0 | 318.1505 | 0 | off_peak | 558.43 |  |  | 0 | 0 | 100 | 0 | 0
7585 | 564.11 | 0 | 23.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 564.11 | 0 | 0.05921 | 7.3144 | 0 | 0 | 318.1505 | 0 | off_peak | 564.11 |  |  | 0 | 0 | 100 | 0 | 0
7586 | 544.96 | 0 | 23.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 544.96 | 0 | 0.05921 | 6.9712 | 0 | 0 | 318.1505 | 0 | off_peak | 544.96 |  |  | 0 | 0 | 100 | 0 | 0
7587 | 545.63 | 0 | 23.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 545.63 | 0 | 0.05921 | 6.5379 | 0 | 0 | 318.1505 | 0 | off_peak | 545.63 |  |  | 0 | 0 | 100 | 0 | 0
7588 | 543.45 | 0 | 23.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 543.45 | 0 | 0.05921 | 6.0459 | 0 | 0 | 318.1505 | 0 | off_peak | 543.45 |  |  | 0 | 0 | 100 | 0 | 0
7589 | 582.62 | 0 | 23.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 582.62 | 0 | 0.05921 | 5.3823 | 0 | 0 | 318.1505 | 0 | off_peak | 582.62 |  |  | 0 | 0 | 100 | 0 | 0
7590 | 591.11 | 0 | 23.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 591.11 | 0 | 0.05921 | 4.7634 | 0 | 0 | 318.1505 | 0 | off_peak | 591.11 |  |  | 0 | 0 | 100 | 0 | 0
7591 | 665.52 | 0 | 23.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 665.52 | 0 | 0.088511 | 4.2058 | 0 | 0 | 318.1505 | 0 | on_peak | 665.52 |  |  | 0 | 0 | 100 | 0 | 0
7592 | 784.44 | 73.0065 | 24.4 | 14.8157 | 14.8157 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 769.6243 | 0 | 0.088511 | 3.8891 | 0 | 0 | 318.1505 | 14.8157 | on_peak | 769.6243 |  |  | 1.89 | 0 | 98.11 | 57.6195 | 0
7593 | 797.32 | 280.306 | 25.1 | 56.7415 | 56.7415 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 740.5785 | 0 | 0.088511 | 3.6844 | 0 | 0 | 318.1505 | 56.7415 | on_peak | 740.5785 |  |  | 7.12 | 0 | 92.88 | 209.0607 | 0
7594 | 764.49 | 195.465 | 25.5 | 39.5104 | 39.5104 | 0 | 0 | 0 | 0 | 62.63 | 62.63 | 0 | 7.4394 | 662.3496 | 0 | 0.088511 | 3.5733 | 0 | 0 | 318.1505 | 39.5104 | on_peak | 662.3496 |  |  | 5.17 | 8.19 | 86.64 | 141.1809 | 0
7595 | 808.12 | 502.132 | 25.8 | 101.3889 | 88.9899 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 0 | 19.0375 | 719.1301 | 0 | 0.05921 | 3.6423 | 0 | 0 | 329.7487 | 88.9899 | off_peak | 719.1301 | 100 | 0 | 11.01 | 0 | 88.99 | 324.1263 | 0
7596 | 848.89 | 391.548 | 26 | 79.003 | 79.003 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 30.6357 | 782.2859 | 0 | 0.05921 | 3.9064 | 0 | 0 | 329.7487 | 79.003 | off_peak | 769.887 | 0 | 100 | 9.31 | 0 | 90.69 | 308.62 | 0
7597 | 799.61 | 296.125 | 26.1 | 59.7278 | 47.3289 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 0 | 42.2338 | 752.2811 | 0 | 0.05921 | 4.3408 | 0 | 0 | 341.3468 | 47.3289 | off_peak | 752.2811 | 100 | 0 | 5.92 | 0 | 94.08 | 205.4461 | 0
7598 | 824.37 | 473.836 | 26 | 95.6064 | 83.2074 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 0 | 53.832 | 741.1626 | 0 | 0.05921 | 4.6307 | 0 | 0 | 352.945 | 83.2074 | off_peak | 741.1626 | 100 | 0 | 10.09 | 0 | 89.91 | 385.3061 | 0
7599 | 834.21 | 354.974 | 25.9 | 71.6493 | 71.6493 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 65.4301 | 774.9596 | 0 | 0.05921 | 4.9545 | 0 | 0 | 352.945 | 71.6493 | off_peak | 762.5607 | 0 | 100 | 8.59 | 0 | 91.41 | 354.9849 | 0
7600 | 810.74 | 215.173 | 25.6 | 43.4784 | 43.4784 | 0 | 0 | 8.9635 | 8.9635 | 0 | 0 | 0 | 73.8147 | 776.2251 | 0 | 0.05921 | 5.216 | 0 | 0 | 352.945 | 43.4784 | off_peak | 767.2616 | 0 | 100 | 5.36 | 0 | 94.64 | 226.7853 | 0
7601 | 819.92 | 140.991 | 25.1 | 28.5404 | 28.5404 | 0 | 0 | 0.57892 | 0.57892 | 0 | 0 | 0 | 74.3563 | 791.9585 | 0 | 0.05921 | 5.4057 | 0 | 0 | 352.945 | 28.5404 | off_peak | 791.3796 | 0 | 100 | 3.48 | 0 | 96.52 | 154.2799 | 0
7602 | 834.39 | 5.7 | 24.6 | 1.1559 | 1.1185 | 0 | 0.03739 | 0.03739 | 0 | 0 | 0 | 0 | 74.3912 | 833.2715 | 0 | 0.05921 | 5.6515 | 0 | 0 | 352.9799 | 1.1185 | off_peak | 833.2715 | 100 | 0 | 0.13 | 0 | 99.87 | 6.3214 | 0
7603 | 818.21 | 0 | 24.4 | 0 | 0 | 0 | 0 | 0 | 0 | 55.3818 | 55.3818 | 0 | 15.1856 | 762.8282 | 0 | 0.088511 | 5.7926 | 0 | 0 | 352.9799 | 0 | on_peak | 762.8282 |  |  | 0 | 6.77 | 93.23 | 0 | 0
7604 | 832.49 | 0 | 24.3 | 0 | 0 | 0 | 0 | 0 | 0 | 7.2459 | 7.2459 | 0 | 7.4394 | 825.2441 | 0 | 0.088511 | 6.0224 | 0 | 0 | 352.9799 | 0 | on_peak | 825.2441 |  |  | 0 | 0.87 | 99.13 | 0 | 0
7605 | 815.39 | 0 | 24.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 815.39 | 0 | 0.088511 | 6.2823 | 0 | 0 | 352.9799 | 0 | on_peak | 815.39 |  |  | 0 | 0 | 100 | 0 | 0
7606 | 783.34 | 0 | 24.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 783.34 | 0 | 0.088511 | 6.353 | 0 | 0 | 352.9799 | 0 | on_peak | 783.34 |  |  | 0 | 0 | 100 | 0 | 0
7607 | 812.73 | 0 | 24.3 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 19.0375 | 825.1289 | 0 | 0.05921 | 6.3542 | 0 | 0 | 352.9799 | 0 | off_peak | 812.73 | 0 | 100 | 0 | 0 | 100 | 0 | 0
7608 | 781.38 | 0 | 24.2 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 30.6357 | 793.7789 | 0 | 0.05921 | 6.5279 | 0 | 0 | 352.9799 | 0 | off_peak | 781.38 | 0 | 100 | 0 | 0 | 100 | 0 | 0
7609 | 731.97 | 0 | 24.1 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 42.2338 | 744.3689 | 0 | 0.05921 | 6.6038 | 0 | 0 | 352.9799 | 0 | off_peak | 731.97 | 0 | 100 | 0 | 0 | 100 | 0 | 0
7610 | 679.03 | 0 | 24 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 53.832 | 691.4289 | 0 | 0.05921 | 6.4208 | 0 | 0 | 352.9799 | 0 | off_peak | 679.03 | 0 | 100 | 0 | 0 | 100 | 0 | 0
7611 | 599.83 | 0 | 23.9 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 65.4301 | 612.2289 | 0 | 0.05921 | 6.0778 | 0 | 0 | 352.9799 | 0 | off_peak | 599.83 | 0 | 100 | 0 | 0 | 100 | 0 | 0
7612 | 625.17 | 0 | 23.9 | 0 | 0 | 0 | 0 | 8.9635 | 8.9635 | 0 | 0 | 0 | 73.8147 | 634.1335 | 0 | 0.05921 | 5.6503 | 0 | 0 | 352.9799 | 0 | off_peak | 625.17 | 0 | 100 | 0 | 0 | 100 | 0 | 0
7613 | 599.37 | 0 | 23.9 | 0 | 0 | 0 | 0 | 0.57892 | 0.57892 | 0 | 0 | 0 | 74.3563 | 599.9489 | 0 | 0.05921 | 5.1585 | 0 | 0 | 352.9799 | 0 | off_peak | 599.37 | 0 | 100 | 0 | 0 | 100 | 0 | 0
7614 | 640.95 | 0 | 23.9 | 0 | 0 | 0 | 0 | 0.03739 | 0.03739 | 0 | 0 | 0 | 74.3912 | 640.9874 | 0 | 0.05921 | 4.5449 | 0 | 0 | 352.9799 | 0 | off_peak | 640.95 | 0 | 100 | 0 | 0 | 100 | 0 | 0
7615 | 740.31 | 0 | 24.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3912 | 740.31 | 0 | 0.088511 | 4.0226 | 0 | 0 | 352.9799 | 0 | on_peak | 740.31 |  |  | 0 | 0 | 100 | 0 | 0
7616 | 742.78 | 53.0706 | 24.8 | 10.7545 | 10.7545 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3912 | 732.0255 | 0 | 0.088511 | 3.7282 | 0 | 0 | 352.9799 | 10.7545 | on_peak | 732.0255 |  |  | 1.45 | 0 | 98.55 | 40.0956 | 0
7617 | 746.44 | 143.326 | 25.5 | 28.9713 | 28.9713 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3912 | 717.4687 | 0 | 0.088511 | 3.5217 | 0 | 0 | 352.9799 | 28.9713 | on_peak | 717.4687 |  |  | 3.88 | 0 | 96.12 | 102.0278 | 0
7618 | 813.13 | 250.647 | 25.9 | 50.5916 | 50.5916 | 0 | 0 | 0 | 0 | 62.6277 | 62.6277 | 0 | 7.4394 | 699.9107 | 0 | 0.088511 | 3.4294 | 0 | 0 | 352.9799 | 50.5916 | on_peak | 699.9107 |  |  | 6.22 | 7.7 | 86.08 | 173.4994 | 0
7619 | 769.5 | 327.786 | 26.2 | 66.0899 | 66.0899 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 19.0375 | 715.809 | 0 | 0.05921 | 3.4481 | 0 | 0 | 352.9799 | 66.0899 | off_peak | 703.4101 | 0 | 100 | 8.59 | 0 | 91.41 | 227.8817 | 0
7620 | 847.86 | 403.939 | 26.4 | 81.3854 | 81.3854 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 30.6357 | 778.8736 | 0 | 0.05921 | 3.7706 | 0 | 0 | 352.9799 | 81.3854 | off_peak | 766.4746 | 0 | 100 | 9.6 | 0 | 90.4 | 306.8755 | 0
7621 | 785.26 | 426.342 | 26.4 | 85.8991 | 85.8991 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 42.2338 | 711.7598 | 0 | 0.05921 | 4.265 | 0 | 0 | 352.9799 | 85.8991 | off_peak | 699.3609 | 0 | 100 | 10.94 | 0 | 89.06 | 366.3633 | 0
7622 | 795.32 | 236.14 | 26.4 | 47.5773 | 47.5773 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 53.832 | 760.1416 | 0 | 0.05921 | 4.5793 | 0 | 0 | 352.9799 | 47.5773 | off_peak | 747.7427 | 0 | 100 | 5.98 | 0 | 94.02 | 217.8722 | 0
7623 | 801.45 | 252.069 | 26.2 | 50.8235 | 50.8235 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 65.4301 | 763.0255 | 0 | 0.05921 | 4.7423 | 0 | 0 | 352.9799 | 50.8235 | off_peak | 750.6265 | 0 | 100 | 6.34 | 0 | 93.66 | 241.0209 | 0
7624 | 766.2 | 134.334 | 26 | 27.1047 | 27.1047 | 0 | 0 | 8.9635 | 8.9635 | 0 | 0 | 0 | 73.8147 | 748.0588 | 0 | 0.05921 | 4.9566 | 0 | 0 | 352.9799 | 27.1047 | off_peak | 739.0953 | 0 | 100 | 3.54 | 0 | 96.46 | 134.346 | 0
7625 | 778.36 | 38.1999 | 25.6 | 7.7188 | 7.7188 | 0 | 0 | 0.57892 | 0.57892 | 0 | 0 | 0 | 74.3563 | 771.2201 | 0 | 0.05921 | 5.0888 | 0 | 0 | 352.9799 | 7.7188 | off_peak | 770.6412 | 0 | 100 | 0.99 | 0 | 99.01 | 39.2792 | 0
7626 | 800.78 | 4.75 | 25.2 | 0.96118 | 0.92379 | 0 | 0.03739 | 0.03739 | 0 | 0 | 0 | 0 | 74.3912 | 799.8562 | 0 | 0.05921 | 5.2062 | 0 | 0 | 353.0149 | 0.92379 | off_peak | 799.8562 | 100 | 0 | 0.12 | 0 | 99.88 | 4.8095 | 0
7627 | 734.64 | 0 | 25.1 | 0 | 0 | 0 | 0 | 0 | 0 | 62.6277 | 62.6277 | 0 | 7.4394 | 672.0123 | 0 | 0.088511 | 5.3551 | 62.6277 | 0 | 286.063 | 62.6277 | on_peak | 672.0123 |  |  | 0 | 8.52 | 91.48 | 335.3787 | 0
7628 | 758.15 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 758.15 | 0 | 0.088511 | 5.657 | 0 | 0 | 286.063 | 0 | on_peak | 758.15 |  |  | 0 | 0 | 100 | 0 | 0
7629 | 762 | 0 | 24.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 762 | 0 | 0.088511 | 5.6922 | 0 | 0 | 286.063 | 0 | on_peak | 762 |  |  | 0 | 0 | 100 | 0 | 0
7630 | 690.15 | 0 | 24.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 690.15 | 0 | 0.088511 | 5.7615 | 0 | 0 | 286.063 | 0 | on_peak | 690.15 |  |  | 0 | 0 | 100 | 0 | 0
7631 | 721.79 | 0 | 24.6 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 19.0375 | 734.1889 | 0 | 0.05921 | 5.8217 | 0 | 0 | 286.063 | 0 | off_peak | 721.79 | 0 | 100 | 0 | 0 | 100 | 0 | 0
7632 | 736.6 | 0 | 24.5 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 30.6357 | 748.9989 | 0 | 0.05921 | 6.0414 | 0 | 0 | 286.063 | 0 | off_peak | 736.6 | 0 | 100 | 0 | 0 | 100 | 0 | 0
7633 | 681.07 | 0 | 24.3 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 42.2338 | 693.4689 | 0 | 0.05921 | 6.1854 | 0 | 0 | 286.063 | 0 | off_peak | 681.07 | 0 | 100 | 0 | 0 | 100 | 0 | 0
7634 | 602.8 | 0 | 24.2 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 53.832 | 615.1989 | 0 | 0.05921 | 5.9875 | 0 | 0 | 286.063 | 0 | off_peak | 602.8 | 0 | 100 | 0 | 0 | 100 | 0 | 0
7635 | 564.15 | 0 | 24.1 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 65.4301 | 576.5489 | 0 | 0.05921 | 5.7147 | 0 | 0 | 286.063 | 0 | off_peak | 564.15 | 0 | 100 | 0 | 0 | 100 | 0 | 0
7636 | 548.03 | 0 | 24 | 0 | 0 | 0 | 0 | 8.9635 | 8.9635 | 0 | 0 | 0 | 73.8147 | 556.9935 | 0 | 0.05921 | 12.0494 | 0 | 0 | 286.063 | 0 | off_peak | 548.03 | 0 | 100 | 0 | 0 | 100 | 0 | 0
7637 | 592.37 | 0 | 23.9 | 0 | 0 | 0 | 0 | 0.57892 | 0.57892 | 0 | 0 | 0 | 74.3563 | 592.9489 | 0 | 0.05921 | 11.9749 | 0 | 0 | 286.063 | 0 | off_peak | 592.37 | 0 | 100 | 0 | 0 | 100 | 0 | 0
7638 | 597.61 | 0 | 23.9 | 0 | 0 | 0 | 0 | 0.03739 | 0.03739 | 0 | 0 | 0 | 74.3912 | 597.6474 | 0 | 0.05921 | 11.8001 | 0 | 0 | 286.063 | 0 | off_peak | 597.61 | 0 | 100 | 0 | 0 | 100 | 0 | 0
7639 | 697.23 | 0 | 24.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3912 | 697.23 | 0 | 0.088511 | 3.8923 | 0 | 0 | 286.063 | 0 | on_peak | 697.23 |  |  | 0 | 0 | 100 | 0 | 0
7640 | 754.96 | 7.6 | 24.8 | 1.5401 | 1.5401 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3912 | 753.4199 | 0 | 0.088511 | 3.602 | 0 | 0 | 286.063 | 1.5401 | on_peak | 753.4199 |  |  | 0.2 | 0 | 99.8 | 5.5475 | 0
7641 | 837.28 | 17.1 | 25.4 | 3.4578 | 3.4578 | 0 | 0 | 0 | 0 | 8.5781 | 8.5781 | 0 | 65.2208 | 825.2441 | 0 | 0.088511 | 3.4129 | 0 | 0 | 286.063 | 3.4578 | on_peak | 825.2441 |  |  | 0.41 | 1.02 | 98.56 | 11.8011 | 0
7642 | 804.25 | 49.4 | 25.8 | 9.9747 | 9.9747 | 0 | 0 | 0 | 0 | 54.0496 | 54.0496 | 0 | 7.4394 | 740.2257 | 0 | 0.088511 | 3.3199 | 0 | 0 | 286.063 | 9.9747 | on_peak | 740.2257 |  |  | 1.24 | 6.72 | 92.04 | 33.1152 | 0
7643 | 758.78 | 67.45 | 26.1 | 13.6045 | 13.6045 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 19.0375 | 757.5744 | 0 | 0.05921 | 3.3312 | 0 | 0 | 286.063 | 13.6045 | off_peak | 745.1755 | 0 | 100 | 1.79 | 0 | 98.21 | 45.3188 | 0
7644 | 821.85 | 38.95 | 26.3 | 7.8505 | 0 | 0 | 7.8505 | 12.3989 | 4.5485 | 0 | 0 | 0 | 30.6357 | 826.3985 | 0 | 0.05921 | 3.6704 | 0 | 0 | 293.4065 | 0 | off_peak | 821.85 | 63.32 | 36.68 | 0 | 0 | 100 | 0 | 0
7645 | 771.87 | 52.25 | 26.4 | 10.5273 | 10.5273 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 42.2338 | 773.7416 | 0 | 0.05921 | 4.134 | 0 | 0 | 293.4065 | 10.5273 | off_peak | 761.3427 | 0 | 100 | 1.36 | 0 | 98.64 | 43.5195 | 0
7646 | 814.74 | 53.2 | 26.5 | 10.7148 | 10.7148 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 53.832 | 816.4241 | 0 | 0.05921 | 4.4683 | 0 | 0 | 293.4065 | 10.7148 | off_peak | 804.0252 | 0 | 100 | 1.32 | 0 | 98.68 | 47.8774 | 0
7647 | 818.59 | 27.55 | 26.4 | 5.5508 | 0 | 0 | 5.5508 | 12.3989 | 6.8482 | 0 | 0 | 0 | 65.4301 | 825.4382 | 0 | 0.05921 | 4.6827 | 0 | 0 | 298.5987 | 0 | off_peak | 818.59 | 44.77 | 55.23 | 0 | 0 | 100 | 0 | 0
7648 | 785.04 | 18.05 | 26.2 | 3.6393 | 0 | 0 | 3.6393 | 8.9635 | 5.3242 | 0 | 0 | 0 | 73.8147 | 790.3642 | 0 | 0.05921 | 4.8906 | 0 | 0 | 302.003 | 0 | off_peak | 785.04 | 40.6 | 59.4 | 0 | 0 | 100 | 0 | 0
7649 | 772.64 | 12.35 | 25.8 | 2.4937 | 1.9148 | 0 | 0.57892 | 0.57892 | 0 | 0 | 0 | 0 | 74.3563 | 770.7252 | 0 | 0.05921 | 5.034 | 0 | 0 | 302.5445 | 1.9148 | off_peak | 770.7252 | 100 | 0 | 0.25 | 0 | 99.75 | 9.6388 | 0
7650 | 835.89 | 2.85 | 25.3 | 0.5765 | 0.53911 | 0 | 0.03739 | 0.03739 | 0 | 0 | 0 | 0 | 74.3912 | 835.3509 | 0 | 0.05921 | 5.1109 | 0 | 0 | 302.5795 | 0.53911 | off_peak | 835.3509 | 100 | 0 | 0.06 | 0 | 99.94 | 2.7554 | 0
7651 | 796.26 | 0 | 25.1 | 0 | 0 | 0 | 0 | 0 | 0 | 62.6277 | 62.6277 | 0 | 7.4394 | 733.6323 | 0 | 0.088511 | 5.0555 | 0 | 0 | 302.5795 | 0 | on_peak | 733.6323 |  |  | 0 | 7.87 | 92.13 | 0 | 0
7652 | 756.02 | 0 | 24.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 756.02 | 0 | 0.088511 | 4.9887 | 0 | 0 | 302.5795 | 0 | on_peak | 756.02 |  |  | 0 | 0 | 100 | 0 | 0
7653 | 799.42 | 0 | 24.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 799.42 | 0 | 0.088511 | 4.9767 | 0 | 0 | 302.5795 | 0 | on_peak | 799.42 |  |  | 0 | 0 | 100 | 0 | 0
7654 | 741.11 | 0 | 24.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 741.11 | 0 | 0.088511 | 4.9847 | 0 | 0 | 302.5795 | 0 | on_peak | 741.11 |  |  | 0 | 0 | 100 | 0 | 0
7655 | 787.73 | 0 | 24.7 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 19.0375 | 800.1289 | 0 | 0.05921 | 5.1059 | 0 | 0 | 302.5795 | 0 | off_peak | 787.73 | 0 | 100 | 0 | 0 | 100 | 0 | 0
7656 | 743.31 | 0 | 24.5 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 30.6357 | 755.7089 | 0 | 0.05921 | 5.2509 | 0 | 0 | 302.5795 | 0 | off_peak | 743.31 | 0 | 100 | 0 | 0 | 100 | 0 | 0
7657 | 692.68 | 0 | 24.4 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 42.2338 | 705.0789 | 0 | 0.05921 | 5.3496 | 0 | 0 | 302.5795 | 0 | off_peak | 692.68 | 0 | 100 | 0 | 0 | 100 | 0 | 0
7658 | 645.14 | 0 | 24.2 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 53.832 | 657.5389 | 0 | 0.05921 | 5.1976 | 0 | 0 | 302.5795 | 0 | off_peak | 645.14 | 0 | 100 | 0 | 0 | 100 | 0 | 0
7659 | 633.91 | 0 | 24.1 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 65.4301 | 646.3089 | 0 | 0.05921 | 5.0128 | 0 | 0 | 302.5795 | 0 | off_peak | 633.91 | 0 | 100 | 0 | 0 | 100 | 0 | 0
7660 | 637.05 | 0 | 24 | 0 | 0 | 0 | 0 | 8.9635 | 8.9635 | 0 | 0 | 0 | 73.8147 | 646.0135 | 0 | 0.05921 | 4.6165 | 0 | 0 | 302.5795 | 0 | off_peak | 637.05 | 0 | 100 | 0 | 0 | 100 | 0 | 0
7661 | 633.16 | 0 | 24 | 0 | 0 | 0 | 0 | 0.57892 | 0.57892 | 0 | 0 | 0 | 74.3563 | 633.7389 | 0 | 0.05921 | 4.1689 | 0 | 0 | 302.5795 | 0 | off_peak | 633.16 | 0 | 100 | 0 | 0 | 100 | 0 | 0
7662 | 610.05 | 0 | 24 | 0 | 0 | 0 | 0 | 0.03739 | 0.03739 | 0 | 0 | 0 | 74.3912 | 610.0874 | 0 | 0.05921 | 3.6186 | 0 | 0 | 302.5795 | 0 | off_peak | 610.05 | 0 | 100 | 0 | 0 | 100 | 0 | 0
7663 | 655.22 | 0 | 24.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3912 | 655.22 | 0 | 0.088511 | 3.2636 | 0 | 0 | 302.5795 | 0 | on_peak | 655.22 |  |  | 0 | 0 | 100 | 0 | 0
7664 | 734.27 | 76.4866 | 24.9 | 15.4941 | 15.4941 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3912 | 718.7759 | 0 | 0.088511 | 3.0081 | 0 | 0 | 302.5795 | 15.4941 | on_peak | 718.7759 |  |  | 2.11 | 0 | 97.89 | 46.6075 | 0
7665 | 750.49 | 251.227 | 25.7 | 50.7453 | 50.7453 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3912 | 699.7447 | 0 | 0.088511 | 2.8701 | 0 | 0 | 302.5795 | 50.7453 | on_peak | 699.7447 |  |  | 6.76 | 0 | 93.24 | 145.6444 | 0
7666 | 729.83 | 420.516 | 26.1 | 84.8173 | 84.8173 | 0 | 0 | 0 | 0 | 62.6277 | 62.6277 | 0 | 7.4394 | 582.385 | 0 | 0.088511 | 2.7837 | 0 | 0 | 302.5795 | 84.8173 | on_peak | 582.385 |  |  | 11.62 | 8.58 | 79.8 | 236.1018 | 0
7667 | 760.27 | 518.004 | 26.5 | 104.3294 | 104.3294 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 19.0375 | 668.3396 | 0 | 0.05921 | 2.7962 | 0 | 0 | 302.5795 | 104.3294 | off_peak | 655.9406 | 0 | 100 | 13.72 | 0 | 86.28 | 291.7228 | 0
7668 | 773.02 | 407.838 | 26.8 | 82.052 | 82.052 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 30.6357 | 703.3669 | 0 | 0.05921 | 3.1157 | 0 | 0 | 302.5795 | 82.052 | off_peak | 690.968 | 0 | 100 | 10.61 | 0 | 89.39 | 255.6458 | 0
7669 | 734.98 | 446.432 | 26.9 | 89.7841 | 77.3852 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 0 | 42.2338 | 657.5948 | 0 | 0.05921 | 3.5807 | 0 | 0 | 314.1777 | 77.3852 | off_peak | 657.5948 | 100 | 0 | 10.53 | 0 | 89.47 | 277.09 | 0
7670 | 749.41 | 377.181 | 27 | 75.8292 | 75.8292 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 53.832 | 685.9797 | 0 | 0.05921 | 3.974 | 0 | 0 | 314.1777 | 75.8292 | off_peak | 673.5808 | 0 | 100 | 10.12 | 0 | 89.88 | 301.3463 | 0
7671 | 733.17 | 466.074 | 26.9 | 93.7344 | 93.7344 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 65.4301 | 651.8345 | 0 | 0.05921 | 4.2949 | 0 | 0 | 314.1777 | 93.7344 | off_peak | 639.4356 | 0 | 100 | 12.78 | 0 | 87.22 | 402.5804 | 0
7672 | 733.82 | 309.039 | 26.7 | 62.1974 | 62.1974 | 0 | 0 | 8.9635 | 8.9635 | 0 | 0 | 0 | 73.8147 | 680.5861 | 0 | 0.05921 | 4.5661 | 0 | 0 | 314.1777 | 62.1974 | off_peak | 671.6226 | 0 | 100 | 8.48 | 0 | 91.52 | 284.002 | 0
7673 | 759.04 | 131.599 | 26.2 | 26.5337 | 25.9548 | 0 | 0.57892 | 0.57892 | 0 | 0 | 0 | 0 | 74.3563 | 733.0852 | 0 | 0.05921 | 4.6914 | 0 | 0 | 314.7192 | 25.9548 | off_peak | 733.0852 | 100 | 0 | 3.42 | 0 | 96.58 | 121.7636 | 0
7674 | 778.3 | 3.803 | 25.4 | 0.76899 | 0.7316 | 0 | 0.03739 | 0.03739 | 0 | 0 | 0 | 0 | 74.3912 | 777.5684 | 0 | 0.05921 | 4.7371 | 0 | 0 | 314.7542 | 0.7316 | off_peak | 777.5684 | 100 | 0 | 0.09 | 0 | 99.91 | 3.4656 | 0
7675 | 767.89 | 0 | 25.1 | 0 | 0 | 0 | 0 | 0 | 0 | 62.6277 | 62.6277 | 0 | 7.4394 | 705.2623 | 0 | 0.088511 | 4.837 | 0 | 0 | 314.7542 | 0 | on_peak | 705.2623 |  |  | 0 | 8.16 | 91.84 | 0 | 0
7676 | 802.56 | 0 | 24.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 802.56 | 0 | 0.088511 | 4.9231 | 0 | 0 | 314.7542 | 0 | on_peak | 802.56 |  |  | 0 | 0 | 100 | 0 | 0
7677 | 786.81 | 0 | 24.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 786.81 | 0 | 0.088511 | 5.017 | 0 | 0 | 314.7542 | 0 | on_peak | 786.81 |  |  | 0 | 0 | 100 | 0 | 0
7678 | 715.12 | 0 | 24.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 715.12 | 0 | 0.088511 | 5.1202 | 0 | 0 | 314.7542 | 0 | on_peak | 715.12 |  |  | 0 | 0 | 100 | 0 | 0
7679 | 738.87 | 0 | 24 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 19.0375 | 751.2689 | 0 | 0.05921 | 5.2746 | 0 | 0 | 314.7542 | 0 | off_peak | 738.87 | 0 | 100 | 0 | 0 | 100 | 0 | 0
7680 | 725.73 | 0 | 23.9 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 30.6357 | 738.1289 | 0 | 0.05921 | 5.5504 | 0 | 0 | 314.7542 | 0 | off_peak | 725.73 | 0 | 100 | 0 | 0 | 100 | 0 | 0
7681 | 698.16 | 0 | 23.8 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 42.2338 | 710.5589 | 0 | 0.05921 | 5.7383 | 0 | 0 | 314.7542 | 0 | off_peak | 698.16 | 0 | 100 | 0 | 0 | 100 | 0 | 0
7682 | 639.51 | 0 | 23.7 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 53.832 | 651.9089 | 0 | 0.05921 | 0.12884 | 0 | 0 | 314.7542 | 0 | off_peak | 639.51 | 0 | 100 | 0 | 0 | 100 | 0 | 0
7683 | 582.16 | 0 | 23.7 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 65.4301 | 594.5589 | 0 | 0.05921 | 0.12229 | 0 | 0 | 314.7542 | 0 | off_peak | 582.16 | 0 | 100 | 0 | 0 | 100 | 0 | 0
7684 | 602.14 | 0 | 23.7 | 0 | 0 | 0 | 0 | 8.9635 | 8.9635 | 0 | 0 | 0 | 73.8147 | 611.1035 | 0 | 0.05921 | 0.10348 | 0 | 0 | 314.7542 | 0 | off_peak | 602.14 | 0 | 100 | 0 | 0 | 100 | 0 | 0
7685 | 576.22 | 0 | 23.5 | 0 | 0 | 0 | 0 | 0.57892 | 0.57892 | 0 | 0 | 0 | 74.3563 | 576.7989 | 0 | 0.05921 | 0.10021 | 0 | 0 | 314.7542 | 0 | off_peak | 576.22 | 0 | 100 | 0 | 0 | 100 | 0 | 0
7686 | 615.11 | 0 | 23.4 | 0 | 0 | 0 | 0 | 0.03739 | 0.03739 | 0 | 0 | 0 | 74.3912 | 615.1474 | 0 | 0.05921 | 0.094888 | 0 | 0 | 314.7542 | 0 | off_peak | 615.11 | 0 | 100 | 0 | 0 | 100 | 0 | 0
7687 | 711.94 | 0 | 23.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3912 | 711.94 | 0 | 0.088511 | 3.5333 | 0 | 0 | 314.7542 | 0 | on_peak | 711.94 |  |  | 0 | 0 | 100 | 0 | 0
7688 | 736.51 | 98.5039 | 24.1 | 20.0117 | 20.0117 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3912 | 716.4983 | 0 | 0.088511 | 3.1479 | 0 | 0 | 314.7542 | 20.0117 | on_peak | 716.4983 |  |  | 2.72 | 0 | 97.28 | 62.995 | 0
7689 | 819.37 | 290.317 | 24.7 | 58.8527 | 58.8527 | 0 | 0 | 0 | 0 | 62.6277 | 62.6277 | 0 | 7.4394 | 697.8896 | 0 | 0.088511 | 2.9451 | 0 | 0 | 314.7542 | 58.8527 | on_peak | 697.8896 |  |  | 7.18 | 7.64 | 85.17 | 173.3251 | 0
7690 | 799.53 | 470.137 | 25.2 | 95.1342 | 95.1342 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 704.3958 | 0 | 0.088511 | 2.8508 | 0 | 0 | 314.7542 | 95.1342 | on_peak | 704.3958 |  |  | 11.9 | 0 | 88.1 | 271.2072 | 0
7691 | 809.23 | 609.694 | 25.8 | 123.1075 | 123.1075 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 19.0375 | 698.5215 | 0 | 0.05921 | 2.8985 | 0 | 0 | 314.7542 | 123.1075 | off_peak | 686.1225 | 0 | 100 | 15.21 | 0 | 84.79 | 356.8327 | 0
7692 | 871.76 | 682.195 | 26.3 | 137.498 | 137.498 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 30.6357 | 746.661 | 0 | 0.05921 | 3.1776 | 0 | 0 | 314.7542 | 137.498 | off_peak | 734.262 | 0 | 100 | 15.77 | 0 | 84.23 | 436.9096 | 0
7693 | 808.25 | 689.15 | 26.6 | 138.7491 | 138.7491 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 42.2338 | 681.8999 | 0 | 0.05921 | 3.6452 | 0 | 0 | 314.7542 | 138.7491 | off_peak | 669.5009 | 0 | 100 | 17.17 | 0 | 82.83 | 505.7724 | 0
7694 | 830.3 | 628.76 | 26.7 | 126.5447 | 126.5447 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 53.832 | 716.1543 | 0 | 0.05921 | 3.9656 | 0 | 0 | 314.7542 | 126.5447 | off_peak | 703.7553 | 0 | 100 | 15.24 | 0 | 84.76 | 501.8223 | 0
7695 | 826.57 | 508.118 | 26.6 | 102.3012 | 102.3012 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 65.4301 | 736.6677 | 0 | 0.05921 | 4.1938 | 0 | 0 | 314.7542 | 102.3012 | off_peak | 724.2688 | 0 | 100 | 12.38 | 0 | 87.62 | 429.0322 | 0
7696 | 792.57 | 340.769 | 26.2 | 68.7076 | 68.7076 | 0 | 0 | 8.9635 | 8.9635 | 0 | 0 | 0 | 73.8147 | 732.8259 | 0 | 0.05921 | 4.4314 | 0 | 0 | 314.7542 | 68.7076 | off_peak | 723.8624 | 0 | 100 | 8.67 | 0 | 91.33 | 304.4685 | 0
7697 | 774.07 | 149.364 | 25.7 | 30.17 | 29.5911 | 0 | 0.57892 | 0.57892 | 0 | 0 | 0 | 0 | 74.3563 | 744.4789 | 0 | 0.05921 | 4.5878 | 0 | 0 | 315.2957 | 29.5911 | off_peak | 744.4789 | 100 | 0 | 3.82 | 0 | 96.18 | 135.7582 | 0
7698 | 797.38 | 5.7144 | 25.1 | 1.1568 | 1.1194 | 0 | 0.03739 | 0.03739 | 0 | 0 | 0 | 0 | 74.3912 | 796.2606 | 0 | 0.05921 | 4.7463 | 0 | 0 | 315.3307 | 1.1194 | off_peak | 796.2606 | 100 | 0 | 0.14 | 0 | 99.86 | 5.3128 | 0
7699 | 791.63 | 0 | 24.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3912 | 791.63 | 0 | 0.088511 | 5.0741 | 0 | 0 | 315.3307 | 0 | on_peak | 791.63 |  |  | 0 | 0 | 100 | 0 | 0
7700 | 799.9 | 0 | 24.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3912 | 799.9 | 0 | 0.088511 | 5.2738 | 0 | 0 | 315.3307 | 0 | on_peak | 799.9 |  |  | 0 | 0 | 100 | 0 | 0
7701 | 771.02 | 0 | 24.2 | 0 | 0 | 0 | 0 | 0 | 0 | 62.6277 | 62.6277 | 0 | 7.4394 | 708.3923 | 0 | 0.088511 | 5.4959 | 0 | 0 | 315.3307 | 0 | on_peak | 708.3923 |  |  | 0 | 8.12 | 91.88 | 0 | 0
7702 | 737.45 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 737.45 | 0 | 0.088511 | 5.8465 | 0 | 0 | 315.3307 | 0 | on_peak | 737.45 |  |  | 0 | 0 | 100 | 0 | 0
7703 | 754.29 | 0 | 23.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 754.29 | 0 | 0.05921 | 6.1155 | 0 | 0 | 315.3307 | 0 | off_peak | 754.29 |  |  | 0 | 0 | 100 | 0 | 0
7704 | 726.15 | 0 | 23.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 726.15 | 0 | 0.05921 | 6.1851 | 0 | 0 | 315.3307 | 0 | off_peak | 726.15 |  |  | 0 | 0 | 100 | 0 | 0
7705 | 670.89 | 0 | 23.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 670.89 | 0 | 0.05921 | 6.0609 | 0 | 0 | 315.3307 | 0 | off_peak | 670.89 |  |  | 0 | 0 | 100 | 0 | 0
7706 | 602.42 | 0 | 23.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 602.42 | 0 | 0.05921 | 5.7476 | 0 | 0 | 315.3307 | 0 | off_peak | 602.42 |  |  | 0 | 0 | 100 | 0 | 0
7707 | 585.68 | 0 | 23.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 585.68 | 0 | 0.05921 | 5.4094 | 0 | 0 | 315.3307 | 0 | off_peak | 585.68 |  |  | 0 | 0 | 100 | 0 | 0
7708 | 603.43 | 0 | 23.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 603.43 | 0 | 0.05921 | 5.0126 | 0 | 0 | 315.3307 | 0 | off_peak | 603.43 |  |  | 0 | 0 | 100 | 0 | 0
7709 | 584.76 | 0 | 23.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 584.76 | 0 | 0.05921 | 4.6082 | 0 | 0 | 315.3307 | 0 | off_peak | 584.76 |  |  | 0 | 0 | 100 | 0 | 0
7710 | 622.52 | 0 | 23.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 622.52 | 0 | 0.05921 | 4.1754 | 0 | 0 | 315.3307 | 0 | off_peak | 622.52 |  |  | 0 | 0 | 100 | 0 | 0
7711 | 649.02 | 0 | 23.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 649.02 | 0 | 0.05921 | 3.7217 | 0 | 0 | 315.3307 | 0 | off_peak | 649.02 |  |  | 0 | 0 | 100 | 0 | 0
7712 | 693.1 | 101.635 | 23.5 | 20.6922 | 20.6922 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 672.4078 | 0 | 0.05921 | 3.3771 | 0 | 0 | 315.3307 | 20.6922 | off_peak | 672.4078 |  |  | 2.99 | 0 | 97.01 | 69.8798 | 0
7713 | 678.96 | 248.183 | 23.9 | 50.4561 | 50.4561 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 628.5039 | 0 | 0.05921 | 3.0822 | 0 | 0 | 315.3307 | 50.4561 | off_peak | 628.5039 |  |  | 7.43 | 0 | 92.57 | 155.5159 | 0
7714 | 701.95 | 427.994 | 24.3 | 86.8872 | 86.8872 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 615.0628 | 0 | 0.05921 | 2.9319 | 0 | 0 | 315.3307 | 86.8872 | off_peak | 615.0628 |  |  | 12.38 | 0 | 87.62 | 254.7474 | 0
7715 | 673.43 | 404.746 | 24.8 | 82.0201 | 82.0201 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 591.4099 | 0 | 0.05921 | 2.8709 | 0 | 0 | 315.3307 | 82.0201 | off_peak | 591.4099 |  |  | 12.18 | 0 | 87.82 | 235.4748 | 0
7716 | 702.72 | 194.982 | 25.2 | 39.4554 | 39.4554 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 663.2646 | 0 | 0.05921 | 2.9356 | 0 | 0 | 315.3307 | 39.4554 | off_peak | 663.2646 |  |  | 5.61 | 0 | 94.39 | 115.8267 | 0
7717 | 694.56 | 169.1 | 25.4 | 34.1934 | 34.1934 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 660.3666 | 0 | 0.05921 | 3.1724 | 0 | 0 | 315.3307 | 34.1934 | off_peak | 660.3666 |  |  | 4.92 | 0 | 95.08 | 108.4753 | 0
7718 | 672.24 | 189.517 | 25.5 | 38.3081 | 38.3081 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 633.9319 | 0 | 0.05921 | 3.4325 | 0 | 0 | 315.3307 | 38.3081 | off_peak | 633.9319 |  |  | 5.7 | 0 | 94.3 | 131.4913 | 0
7719 | 679.46 | 342.853 | 25.4 | 69.3278 | 69.3278 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 610.1322 | 0 | 0.05921 | 3.6744 | 0 | 0 | 315.3307 | 69.3278 | off_peak | 610.1322 |  |  | 10.2 | 0 | 89.8 | 254.739 | 0
7720 | 675.87 | 125.914 | 25.2 | 25.4792 | 25.4792 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 650.3908 | 0 | 0.05921 | 3.8755 | 0 | 0 | 315.3307 | 25.4792 | off_peak | 650.3908 |  |  | 3.77 | 0 | 96.23 | 98.7458 | 0
7721 | 644.66 | 106.273 | 25 | 21.5203 | 21.5203 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 623.1397 | 0 | 0.05921 | 4.1195 | 0 | 0 | 315.3307 | 21.5203 | off_peak | 623.1397 |  |  | 3.34 | 0 | 96.66 | 88.6521 | 0
7722 | 616.52 | 3.8 | 24.7 | 0.77033 | 0.77033 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 615.7497 | 0 | 0.05921 | 4.3264 | 0 | 0 | 315.3307 | 0.77033 | off_peak | 615.7497 |  |  | 0.12 | 0 | 99.88 | 3.3327 | 0
7723 | 589.3 | 0 | 24.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 589.3 | 0 | 0.05921 | 4.4 | 0 | 0 | 315.3307 | 0 | off_peak | 589.3 |  |  | 0 | 0 | 100 | 0 | 0
7724 | 553.16 | 0 | 24.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 553.16 | 0 | 0.05921 | 4.389 | 0 | 0 | 315.3307 | 0 | off_peak | 553.16 |  |  | 0 | 0 | 100 | 0 | 0
7725 | 559.93 | 0 | 24.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 559.93 | 0 | 0.05921 | 4.67 | 0 | 0 | 315.3307 | 0 | off_peak | 559.93 |  |  | 0 | 0 | 100 | 0 | 0
7726 | 551.02 | 0 | 24.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 551.02 | 0 | 0.05921 | 4.8954 | 0 | 0 | 315.3307 | 0 | off_peak | 551.02 |  |  | 0 | 0 | 100 | 0 | 0
7727 | 577.51 | 0 | 24.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 577.51 | 0 | 0.05921 | 5.1585 | 0 | 0 | 315.3307 | 0 | off_peak | 577.51 |  |  | 0 | 0 | 100 | 0 | 0
7728 | 553.41 | 0 | 24.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 553.41 | 0 | 0.05921 | 5.3654 | 0 | 0 | 315.3307 | 0 | off_peak | 553.41 |  |  | 0 | 0 | 100 | 0 | 0
7729 | 548.72 | 0 | 24.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 548.72 | 0 | 0.05921 | 5.3561 | 0 | 0 | 315.3307 | 0 | off_peak | 548.72 |  |  | 0 | 0 | 100 | 0 | 0
7730 | 554.41 | 0 | 24.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 554.41 | 0 | 0.05921 | 5.0538 | 0 | 0 | 315.3307 | 0 | off_peak | 554.41 |  |  | 0 | 0 | 100 | 0 | 0
7731 | 586.53 | 0 | 24.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 586.53 | 0 | 0.05921 | 4.7478 | 0 | 0 | 315.3307 | 0 | off_peak | 586.53 |  |  | 0 | 0 | 100 | 0 | 0
7732 | 524.94 | 0 | 24.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 524.94 | 0 | 0.05921 | 4.434 | 0 | 0 | 315.3307 | 0 | off_peak | 524.94 |  |  | 0 | 0 | 100 | 0 | 0
7733 | 552.35 | 0 | 24.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 552.35 | 0 | 0.05921 | 4.0399 | 0 | 0 | 315.3307 | 0 | off_peak | 552.35 |  |  | 0 | 0 | 100 | 0 | 0
7734 | 619.35 | 0 | 24.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 619.35 | 0 | 0.05921 | 3.6295 | 0 | 0 | 315.3307 | 0 | off_peak | 619.35 |  |  | 0 | 0 | 100 | 0 | 0
7735 | 653.9 | 0 | 24.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 653.9 | 0 | 0.05921 | 3.1546 | 0 | 0 | 315.3307 | 0 | off_peak | 653.9 |  |  | 0 | 0 | 100 | 0 | 0
7736 | 676.77 | 109.582 | 24.6 | 22.2223 | 22.2223 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 19.0375 | 666.9466 | 0 | 0.05921 | 2.8117 | 0 | 0 | 315.3307 | 22.2223 | off_peak | 654.5477 | 0 | 100 | 3.28 | 0 | 96.72 | 62.4817 | 0
7737 | 738.66 | 299.54 | 25.1 | 60.635 | 60.635 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19.0375 | 678.025 | 0 | 0.05921 | 2.5873 | 0 | 0 | 315.3307 | 60.635 | off_peak | 678.025 |  |  | 8.21 | 0 | 91.79 | 156.8815 | 0
7738 | 677.7 | 473.782 | 25.5 | 95.7682 | 95.7682 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19.0375 | 581.9318 | 0 | 0.05921 | 2.4544 | 0 | 0 | 315.3307 | 95.7682 | off_peak | 581.9318 |  |  | 14.13 | 0 | 85.87 | 235.0567 | 0
7739 | 701.56 | 604.962 | 25.9 | 122.1079 | 122.1079 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19.0375 | 579.4521 | 0 | 0.05921 | 2.4003 | 0 | 0 | 315.3307 | 122.1079 | off_peak | 579.4521 |  |  | 17.41 | 0 | 82.59 | 293.0931 | 0
7740 | 742.51 | 673.912 | 26.1 | 135.9268 | 135.9268 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19.0375 | 606.5832 | 0 | 0.05921 | 2.4312 | 0 | 0 | 315.3307 | 135.9268 | off_peak | 606.5832 |  |  | 18.31 | 0 | 81.69 | 330.4678 | 0
7741 | 680.56 | 677.736 | 26.2 | 136.6487 | 136.6487 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19.0375 | 543.9113 | 0 | 0.05921 | 2.6038 | 0 | 0 | 315.3307 | 136.6487 | off_peak | 543.9113 |  |  | 20.08 | 0 | 79.92 | 355.8025 | 0
7742 | 691.65 | 601.66 | 26.2 | 121.3098 | 121.3098 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 30.6357 | 582.7391 | 0 | 0.05921 | 2.8479 | 0 | 0 | 315.3307 | 121.3098 | off_peak | 570.3402 | 0 | 100 | 17.54 | 0 | 82.46 | 345.4763 | 0
7743 | 737.1 | 456.349 | 26.2 | 92.0115 | 92.0115 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 42.2338 | 657.4875 | 0 | 0.05921 | 2.845 | 0 | 0 | 315.3307 | 92.0115 | off_peak | 645.0885 | 0 | 100 | 12.48 | 0 | 87.52 | 261.7746 | 0
7744 | 692.4 | 202.56 | 25.9 | 40.8855 | 40.8855 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 53.832 | 663.9134 | 0 | 0.05921 | 2.9657 | 0 | 0 | 315.3307 | 40.8855 | off_peak | 651.5145 | 0 | 100 | 5.9 | 0 | 94.1 | 121.2534 | 0
7745 | 669.19 | 87.5852 | 25.5 | 17.7041 | 8.9777 | 0 | 8.7263 | 8.7263 | 0 | 0 | 0 | 0 | 61.9947 | 660.2123 | 0 | 0.05921 | 3.3356 | 0 | 0 | 323.4934 | 8.9777 | off_peak | 660.2123 | 100 | 0 | 1.34 | 0 | 98.66 | 29.9458 | 0
7746 | 605.86 | 4.75 | 25.1 | 0.96153 | 0.96153 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 61.9947 | 604.8985 | 0 | 0.05921 | 3.6566 | 0 | 0 | 323.4934 | 0.96153 | off_peak | 604.8985 |  |  | 0.16 | 0 | 99.84 | 3.5159 | 0
7747 | 592.23 | 0 | 24.9 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 73.5928 | 604.6289 | 0 | 0.05921 | 4.0924 | 0 | 0 | 323.4934 | 0 | off_peak | 592.23 | 0 | 100 | 0 | 0 | 100 | 0 | 0
7748 | 577.69 | 0 | 24.8 | 0 | 0 | 0 | 0 | 0.80079 | 0.80079 | 0 | 0 | 0 | 74.3419 | 578.4908 | 0 | 0.05921 | 4.439 | 0 | 0 | 323.4934 | 0 | off_peak | 577.69 | 0 | 100 | 0 | 0 | 100 | 0 | 0
7749 | 569.54 | 0 | 24.8 | 0 | 0 | 0 | 0 | 0.05172 | 0.05172 | 0 | 0 | 0 | 74.3903 | 569.5917 | 0 | 0.05921 | 4.7621 | 0 | 0 | 323.4934 | 0 | off_peak | 569.54 | 0 | 100 | 0 | 0 | 100 | 0 | 0
7750 | 558.84 | 0 | 24.7 | 0 | 0 | 0 | 0 | 0.0033404 | 0.0033404 | 0 | 0 | 0 | 74.3934 | 558.8433 | 0 | 0.05921 | 5.0121 | 0 | 0 | 323.4934 | 0 | off_peak | 558.84 | 0 | 100 | 0 | 0 | 100 | 0 | 0
7751 | 552.31 | 0 | 24.6 | 0 | 0 | 0 | 0 | 0.00021574 | 0.00021574 | 0 | 0 | 0 | 74.3936 | 552.3102 | 0 | 0.05921 | 5.4841 | 0 | 0 | 323.4934 | 0 | off_peak | 552.31 | 0 | 100 | 0 | 0 | 100 | 0 | 0
7752 | 563.78 | 0 | 24.5 | 0 | 0 | 0 | 0 | 1.4896e-05 | 1.4896e-05 | 0 | 0 | 0 | 74.3936 | 563.78 | 0 | 0.05921 | 5.7875 | 0 | 0 | 323.4934 | 0 | off_peak | 563.78 | 0 | 100 | 0 | 0 | 100 | 0 | 0
7753 | 537.73 | 0 | 24.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 537.73 | 0 | 0.05921 | 5.6849 | 0 | 0 | 323.4934 | 0 | off_peak | 537.73 |  |  | 0 | 0 | 100 | 0 | 0
7754 | 546.87 | 0 | 24.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 546.87 | 0 | 0.05921 | 5.3669 | 0 | 0 | 323.4934 | 0 | off_peak | 546.87 |  |  | 0 | 0 | 100 | 0 | 0
7755 | 523.42 | 0 | 24.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 523.42 | 0 | 0.05921 | 5.0503 | 0 | 0 | 323.4934 | 0 | off_peak | 523.42 |  |  | 0 | 0 | 100 | 0 | 0
7756 | 578.32 | 0 | 24.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 578.32 | 0 | 0.05921 | 4.6875 | 0 | 0 | 323.4934 | 0 | off_peak | 578.32 |  |  | 0 | 0 | 100 | 0 | 0
7757 | 549.67 | 0 | 24.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 549.67 | 0 | 0.05921 | 4.2121 | 0 | 0 | 323.4934 | 0 | off_peak | 549.67 |  |  | 0 | 0 | 100 | 0 | 0
7758 | 584.71 | 0 | 24.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 584.71 | 0 | 0.05921 | 3.6872 | 0 | 0 | 323.4934 | 0 | off_peak | 584.71 |  |  | 0 | 0 | 100 | 0 | 0
7759 | 661.46 | 0 | 24.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 661.46 | 0 | 0.088511 | 3.1563 | 0 | 0 | 323.4934 | 0 | on_peak | 661.46 |  |  | 0 | 0 | 100 | 0 | 0
7760 | 703.26 | 109.181 | 24.9 | 22.1171 | 22.1171 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 681.1429 | 0 | 0.088511 | 2.8239 | 0 | 0 | 323.4934 | 22.1171 | on_peak | 681.1429 |  |  | 3.14 | 0 | 96.86 | 62.4573 | 0
7761 | 739.96 | 300.686 | 25.4 | 60.8012 | 60.8012 | 0 | 0 | 0 | 0 | 62.63 | 62.63 | 0 | 7.4394 | 616.5288 | 0 | 0.088511 | 2.6346 | 0 | 0 | 323.4934 | 60.8012 | on_peak | 616.5288 |  |  | 8.22 | 8.46 | 83.32 | 160.1857 | 0
7762 | 796.41 | 475.995 | 25.8 | 96.1114 | 96.1114 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 700.2986 | 0 | 0.088511 | 2.577 | 0 | 0 | 323.4934 | 96.1114 | on_peak | 700.2986 |  |  | 12.07 | 0 | 87.93 | 247.6788 | 0
7763 | 755.62 | 607.232 | 26.1 | 122.4775 | 122.4775 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 19.0375 | 645.5414 | 0 | 0.05921 | 2.5728 | 0 | 0 | 323.4934 | 122.4775 | off_peak | 633.1425 | 0 | 100 | 16.21 | 0 | 83.79 | 315.1082 | 0
7764 | 790.98 | 679.974 | 26.3 | 137.0503 | 137.0503 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 30.6357 | 666.3286 | 0 | 0.05921 | 2.8208 | 0 | 0 | 323.4934 | 137.0503 | off_peak | 653.9297 | 0 | 100 | 17.33 | 0 | 82.67 | 386.5958 | 0
7765 | 805.07 | 685.381 | 26.4 | 138.0902 | 138.0902 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 42.2338 | 679.3788 | 0 | 0.05921 | 3.2535 | 0 | 0 | 323.4934 | 138.0902 | off_peak | 666.9798 | 0 | 100 | 17.15 | 0 | 82.85 | 449.2746 | 0
7766 | 795.83 | 623.118 | 26.5 | 125.5 | 125.5 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 53.832 | 682.7289 | 0 | 0.05921 | 3.6187 | 0 | 0 | 323.4934 | 125.5 | off_peak | 670.33 | 0 | 100 | 15.77 | 0 | 84.23 | 454.1458 | 0
7767 | 836.28 | 506.435 | 26.4 | 102.0362 | 102.0362 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 65.4301 | 746.6427 | 0 | 0.05921 | 3.7532 | 0 | 0 | 323.4934 | 102.0362 | off_peak | 734.2438 | 0 | 100 | 12.2 | 0 | 87.8 | 382.9615 | 0
7768 | 788.98 | 338.752 | 26.3 | 68.2762 | 59.3127 | 0 | 8.9635 | 8.9635 | 0 | 0 | 0 | 0 | 73.8147 | 729.6673 | 0 | 0.05921 | 3.876 | 0 | 0 | 331.878 | 59.3127 | off_peak | 729.6673 | 100 | 0 | 7.52 | 0 | 92.48 | 229.8984 | 0
7769 | 809.51 | 150.264 | 25.9 | 30.3299 | 30.3299 | 0 | 0 | 0.57892 | 0.57892 | 0 | 0 | 0 | 74.3563 | 779.759 | 0 | 0.05921 | 4.2218 | 0 | 0 | 331.878 | 30.3299 | off_peak | 779.1801 | 0 | 100 | 3.75 | 0 | 96.25 | 128.0452 | 0
7770 | 830.8 | 5.7 | 25.5 | 1.1522 | 1.1522 | 0 | 0 | 0.03739 | 0.03739 | 0 | 0 | 0 | 74.3912 | 829.6852 | 0 | 0.05921 | 4.6548 | 0 | 0 | 331.878 | 1.1522 | off_peak | 829.6478 | 0 | 100 | 0.14 | 0 | 99.86 | 5.3631 | 0
7771 | 781.22 | 0 | 25.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3912 | 781.22 | 0 | 0.088511 | 5.0009 | 0 | 0 | 331.878 | 0 | on_peak | 781.22 |  |  | 0 | 0 | 100 | 0 | 0
7772 | 794.43 | 0 | 25.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3912 | 794.43 | 0 | 0.088511 | 5.2609 | 0 | 0 | 331.878 | 0 | on_peak | 794.43 |  |  | 0 | 0 | 100 | 0 | 0
7773 | 782.6 | 0 | 25.1 | 0 | 0 | 0 | 0 | 0 | 0 | 62.6277 | 62.6277 | 0 | 7.4394 | 719.9723 | 0 | 0.088511 | 5.5134 | 0 | 0 | 331.878 | 0 | on_peak | 719.9723 |  |  | 0 | 8 | 92 | 0 | 0
7774 | 734.85 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 734.85 | 0 | 0.088511 | 5.8572 | 0 | 0 | 331.878 | 0 | on_peak | 734.85 |  |  | 0 | 0 | 100 | 0 | 0
7775 | 786.82 | 0 | 25 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 19.0375 | 799.2189 | 0 | 0.05921 | 6.0485 | 0 | 0 | 331.878 | 0 | off_peak | 786.82 | 0 | 100 | 0 | 0 | 100 | 0 | 0
7776 | 767.59 | 0 | 25 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 30.6357 | 779.9889 | 0 | 0.05921 | 6.1626 | 0 | 0 | 331.878 | 0 | off_peak | 767.59 | 0 | 100 | 0 | 0 | 100 | 0 | 0
7777 | 733.09 | 0 | 25 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 42.2338 | 745.4889 | 0 | 0.05921 | 6.1601 | 0 | 0 | 331.878 | 0 | off_peak | 733.09 | 0 | 100 | 0 | 0 | 100 | 0 | 0
7778 | 644.44 | 0 | 25 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 53.832 | 656.8389 | 0 | 0.05921 | 5.9043 | 0 | 0 | 331.878 | 0 | off_peak | 644.44 | 0 | 100 | 0 | 0 | 100 | 0 | 0
7779 | 646.33 | 0 | 24.9 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 65.4301 | 658.7289 | 0 | 0.05921 | 5.5767 | 0 | 0 | 331.878 | 0 | off_peak | 646.33 | 0 | 100 | 0 | 0 | 100 | 0 | 0
7780 | 644.63 | 0 | 24.9 | 0 | 0 | 0 | 0 | 8.9635 | 8.9635 | 0 | 0 | 0 | 73.8147 | 653.5935 | 0 | 0.05921 | 5.215 | 0 | 0 | 331.878 | 0 | off_peak | 644.63 | 0 | 100 | 0 | 0 | 100 | 0 | 0
7781 | 623.21 | 0 | 24.8 | 0 | 0 | 0 | 0 | 0.57892 | 0.57892 | 0 | 0 | 0 | 74.3563 | 623.7889 | 0 | 0.05921 | 4.8051 | 0 | 0 | 331.878 | 0 | off_peak | 623.21 | 0 | 100 | 0 | 0 | 100 | 0 | 0
7782 | 644.5 | 0 | 24.8 | 0 | 0 | 0 | 0 | 0.03739 | 0.03739 | 0 | 0 | 0 | 74.3912 | 644.5374 | 0 | 0.05921 | 4.2769 | 0 | 0 | 331.878 | 0 | off_peak | 644.5 | 0 | 100 | 0 | 0 | 100 | 0 | 0
7783 | 734.26 | 0 | 24.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3912 | 734.26 | 0 | 0.088511 | 3.7757 | 0 | 0 | 331.878 | 0 | on_peak | 734.26 |  |  | 0 | 0 | 100 | 0 | 0
7784 | 804.58 | 104.053 | 25.1 | 21.0631 | 21.0631 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3912 | 783.5169 | 0 | 0.088511 | 3.3904 | 0 | 0 | 331.878 | 21.0631 | on_peak | 783.5169 |  |  | 2.62 | 0 | 97.38 | 71.4122 | 0
7785 | 812.3 | 294.805 | 25.5 | 59.5906 | 59.5906 | 0 | 0 | 0 | 0 | 62.6277 | 62.6277 | 0 | 7.4394 | 690.0817 | 0 | 0.088511 | 3.1332 | 0 | 0 | 331.878 | 59.5906 | on_peak | 690.0817 |  |  | 7.34 | 7.71 | 84.95 | 186.7114 | 0
7786 | 793.06 | 470.129 | 25.7 | 94.9612 | 94.9612 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 698.0988 | 0 | 0.088511 | 3.0086 | 0 | 0 | 331.878 | 94.9612 | on_peak | 698.0988 |  |  | 11.97 | 0 | 88.03 | 285.6979 | 0
7787 | 793.06 | 602.242 | 26.1 | 121.4711 | 121.4711 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 19.0375 | 683.9879 | 0 | 0.05921 | 3.0201 | 0 | 0 | 331.878 | 121.4711 | off_peak | 671.5889 | 0 | 100 | 15.32 | 0 | 84.68 | 366.8545 | 0
7788 | 901.34 | 654.11 | 26.3 | 131.8374 | 131.8374 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 30.6357 | 781.9016 | 0 | 0.05921 | 3.2452 | 0 | 0 | 331.878 | 131.8374 | off_peak | 769.5026 | 0 | 100 | 14.63 | 0 | 85.37 | 427.8368 | 0
7789 | 764.85 | 675.098 | 26.6 | 135.9199 | 135.9199 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 42.2338 | 641.329 | 0 | 0.05921 | 3.5278 | 0 | 0 | 331.878 | 135.9199 | off_peak | 628.9301 | 0 | 100 | 17.77 | 0 | 82.23 | 479.5019 | 0
7790 | 814.91 | 599.418 | 26.7 | 120.6393 | 120.6393 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 53.832 | 706.6697 | 0 | 0.05921 | 3.8485 | 0 | 0 | 331.878 | 120.6393 | off_peak | 694.2707 | 0 | 100 | 14.8 | 0 | 85.2 | 464.286 | 0
7791 | 861.1 | 505.371 | 26.7 | 101.7113 | 101.7113 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 65.4301 | 771.7876 | 0 | 0.05921 | 4.0715 | 0 | 0 | 331.878 | 101.7113 | off_peak | 759.3887 | 0 | 100 | 11.81 | 0 | 88.19 | 414.1198 | 0
7792 | 784.63 | 339.333 | 26.5 | 68.3439 | 59.3803 | 0 | 8.9635 | 8.9635 | 0 | 0 | 0 | 0 | 73.8147 | 725.2497 | 0 | 0.05921 | 4.2915 | 0 | 0 | 340.2627 | 59.3803 | off_peak | 725.2497 | 100 | 0 | 7.57 | 0 | 92.43 | 254.8313 | 0
7793 | 818.21 | 149.468 | 25.9 | 30.1692 | 29.5903 | 0 | 0.57892 | 0.57892 | 0 | 0 | 0 | 0 | 74.3563 | 788.6197 | 0 | 0.05921 | 4.6082 | 0 | 0 | 340.8042 | 29.5903 | off_peak | 788.6197 | 100 | 0 | 3.62 | 0 | 96.38 | 136.3578 | 0
7794 | 823.3 | 5.7 | 25.2 | 1.1534 | 1.116 | 0 | 0.03739 | 0.03739 | 0 | 0 | 0 | 0 | 74.3912 | 822.184 | 0 | 0.05921 | 4.8708 | 0 | 0 | 340.8392 | 1.116 | off_peak | 822.184 | 100 | 0 | 0.14 | 0 | 99.86 | 5.436 | 0
7795 | 791.65 | 0 | 24.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3912 | 791.65 | 0 | 0.088511 | 5.1531 | 0 | 0 | 340.8392 | 0 | on_peak | 791.65 |  |  | 0 | 0 | 100 | 0 | 0
7796 | 797.2 | 0 | 23.5 | 0 | 0 | 0 | 0 | 0 | 0 | 62.6277 | 62.6277 | 0 | 7.4394 | 734.5723 | 0 | 0.088511 | 5.518 | 62.6277 | 0 | 273.8873 | 62.6277 | on_peak | 734.5723 |  |  | 0 | 7.86 | 92.14 | 345.5782 | 0
7797 | 792.09 | 0 | 22.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 792.09 | 0 | 0.088511 | 5.7779 | 0 | 0 | 273.8873 | 0 | on_peak | 792.09 |  |  | 0 | 0 | 100 | 0 | 0
7798 | 755.84 | 0 | 21.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 755.84 | 0 | 0.088511 | 6.1219 | 0 | 0 | 273.8873 | 0 | on_peak | 755.84 |  |  | 0 | 0 | 100 | 0 | 0
7799 | 802.21 | 0 | 21.1 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 19.0375 | 814.6089 | 0 | 0.05921 | 6.3005 | 0 | 0 | 273.8873 | 0 | off_peak | 802.21 | 0 | 100 | 0 | 0 | 100 | 0 | 0
7800 | 755.35 | 0 | 20.8 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 30.6357 | 767.7489 | 0 | 0.05921 | 6.3091 | 0 | 0 | 273.8873 | 0 | off_peak | 755.35 | 0 | 100 | 0 | 0 | 100 | 0 | 0
7801 | 711.78 | 0 | 20.2 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 42.2338 | 724.1789 | 0 | 0.05921 | 6.177 | 0 | 0 | 273.8873 | 0 | off_peak | 711.78 | 0 | 100 | 0 | 0 | 100 | 0 | 0
7802 | 643.33 | 0 | 19.7 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 53.832 | 655.7289 | 0 | 0.05921 | 5.8984 | 0 | 0 | 273.8873 | 0 | off_peak | 643.33 | 0 | 100 | 0 | 0 | 100 | 0 | 0
7803 | 590.65 | 0 | 19.3 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 65.4301 | 603.0489 | 0 | 0.05921 | 5.5973 | 0 | 0 | 273.8873 | 0 | off_peak | 590.65 | 0 | 100 | 0 | 0 | 100 | 0 | 0
7804 | 582.95 | 0 | 19 | 0 | 0 | 0 | 0 | 8.9635 | 8.9635 | 0 | 0 | 0 | 73.8147 | 591.9135 | 0 | 0.05921 | 5.2024 | 0 | 0 | 273.8873 | 0 | off_peak | 582.95 | 0 | 100 | 0 | 0 | 100 | 0 | 0
7805 | 587.26 | 0 | 18.7 | 0 | 0 | 0 | 0 | 0.57892 | 0.57892 | 0 | 0 | 0 | 74.3563 | 587.8389 | 0 | 0.05921 | 4.779 | 0 | 0 | 273.8873 | 0 | off_peak | 587.26 | 0 | 100 | 0 | 0 | 100 | 0 | 0
7806 | 577.93 | 0 | 18.3 | 0 | 0 | 0 | 0 | 0.03739 | 0.03739 | 0 | 0 | 0 | 74.3912 | 577.9674 | 0 | 0.05921 | 4.2552 | 0 | 0 | 273.8873 | 0 | off_peak | 577.93 | 0 | 100 | 0 | 0 | 100 | 0 | 0
7807 | 657.2 | 0 | 17.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3912 | 657.2 | 0 | 0.088511 | 3.7851 | 0 | 0 | 273.8873 | 0 | on_peak | 657.2 |  |  | 0 | 0 | 100 | 0 | 0
7808 | 724.17 | 108.249 | 17.7 | 22.4965 | 22.4965 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3912 | 701.6735 | 0 | 0.088511 | 3.4064 | 0 | 0 | 273.8873 | 22.4965 | on_peak | 701.6735 |  |  | 3.11 | 0 | 96.89 | 76.632 | 0
7809 | 784.61 | 300.59 | 18.2 | 62.3596 | 62.3596 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3912 | 722.2504 | 0 | 0.088511 | 3.1548 | 0 | 0 | 273.8873 | 62.3596 | on_peak | 722.2504 |  |  | 7.95 | 0 | 92.05 | 196.7348 | 0
7810 | 814.57 | 473.7 | 19.1 | 97.9617 | 97.9617 | 0 | 0 | 0 | 0 | 62.6277 | 62.6277 | 0 | 7.4394 | 653.9806 | 0 | 0.088511 | 3.0032 | 0 | 0 | 273.8873 | 97.9617 | on_peak | 653.9806 |  |  | 12.03 | 7.69 | 80.29 | 294.2018 | 0
7811 | 789.31 | 602.028 | 20.1 | 124.0612 | 124.0612 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 19.0375 | 677.6478 | 0 | 0.05921 | 3.0004 | 0 | 0 | 273.8873 | 124.0612 | off_peak | 665.2488 | 0 | 100 | 15.72 | 0 | 84.28 | 372.2358 | 0
7812 | 850.84 | 673.411 | 20.9 | 138.3785 | 138.3785 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 30.6357 | 724.8605 | 0 | 0.05921 | 3.1731 | 0 | 0 | 273.8873 | 138.3785 | off_peak | 712.4615 | 0 | 100 | 16.26 | 0 | 83.74 | 439.094 | 0
7813 | 826.62 | 628.331 | 21.4 | 128.886 | 128.886 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 42.2338 | 710.1329 | 0 | 0.05921 | 3.4416 | 0 | 0 | 273.8873 | 128.886 | off_peak | 697.734 | 0 | 100 | 15.59 | 0 | 84.41 | 443.5709 | 0
7814 | 834.01 | 540.321 | 21.7 | 110.7149 | 98.3159 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 0 | 53.832 | 735.6941 | 0 | 0.05921 | 3.7955 | 0 | 0 | 285.4855 | 98.3159 | off_peak | 735.6941 | 100 | 0 | 11.79 | 0 | 88.21 | 373.1599 | 0
7815 | 803.1 | 310.768 | 21.8 | 63.6555 | 63.6555 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 65.4301 | 751.8435 | 0 | 0.05921 | 4.1043 | 0 | 0 | 285.4855 | 63.6555 | off_peak | 739.4445 | 0 | 100 | 7.93 | 0 | 92.07 | 261.2626 | 0
7816 | 792.2 | 280.898 | 21.6 | 57.5781 | 57.5781 | 0 | 0 | 8.9635 | 8.9635 | 0 | 0 | 0 | 73.8147 | 743.5855 | 0 | 0.05921 | 4.4829 | 0 | 0 | 285.4855 | 57.5781 | off_peak | 734.6219 | 0 | 100 | 7.27 | 0 | 92.73 | 258.1186 | 0
7817 | 741.24 | 109.023 | 21 | 22.3951 | 22.3951 | 0 | 0 | 0.57892 | 0.57892 | 0 | 0 | 0 | 74.3563 | 719.4238 | 0 | 0.05921 | 4.869 | 0 | 0 | 285.4855 | 22.3951 | off_peak | 718.8449 | 0 | 100 | 3.02 | 0 | 96.98 | 109.041 | 0
7818 | 805.36 | 5.7 | 20.3 | 1.1738 | 1.1738 | 0 | 0 | 0.03739 | 0.03739 | 0 | 0 | 0 | 74.3912 | 804.2236 | 0 | 0.05921 | 5.1733 | 0 | 0 | 285.4855 | 1.1738 | off_peak | 804.1862 | 0 | 100 | 0.15 | 0 | 99.85 | 6.0723 | 0
7819 | 787.79 | 0 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3912 | 787.79 | 0 | 0.088511 | 5.411 | 0 | 0 | 285.4855 | 0 | on_peak | 787.79 |  |  | 0 | 0 | 100 | 0 | 0
7820 | 823.14 | 0 | 19.5 | 0 | 0 | 0 | 0 | 0 | 0 | 62.6277 | 62.6277 | 0 | 7.4394 | 760.5123 | 0 | 0.088511 | 5.666 | 0 | 0 | 285.4855 | 0 | on_peak | 760.5123 |  |  | 0 | 7.61 | 92.39 | 0 | 0
7821 | 758.65 | 0 | 19.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 758.65 | 0 | 0.088511 | 5.8818 | 0 | 0 | 285.4855 | 0 | on_peak | 758.65 |  |  | 0 | 0 | 100 | 0 | 0
7822 | 729.98 | 0 | 19.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 729.98 | 0 | 0.088511 | 6.1138 | 0 | 0 | 285.4855 | 0 | on_peak | 729.98 |  |  | 0 | 0 | 100 | 0 | 0
7823 | 730.96 | 0 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 730.96 | 0 | 0.05921 | 6.357 | 0 | 0 | 285.4855 | 0 | off_peak | 730.96 |  |  | 0 | 0 | 100 | 0 | 0
7824 | 755.12 | 0 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 755.12 | 0 | 0.05921 | 6.4403 | 0 | 0 | 285.4855 | 0 | off_peak | 755.12 |  |  | 0 | 0 | 100 | 0 | 0
7825 | 664.88 | 0 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 664.88 | 0 | 0.05921 | 6.2718 | 0 | 0 | 285.4855 | 0 | off_peak | 664.88 |  |  | 0 | 0 | 100 | 0 | 0
7826 | 618.13 | 0 | 19 | 0 | 0 | 0 | 0 | 8.7263 | 8.7263 | 0 | 0 | 0 | 15.6021 | 626.8563 | 0 | 0.05921 | 6.0016 | 0 | 0 | 285.4855 | 0 | off_peak | 618.13 | 0 | 100 | 0 | 0 | 100 | 0 | 0
7827 | 584.46 | 0 | 18.8 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 27.2003 | 596.8589 | 0 | 0.05921 | 5.6225 | 0 | 0 | 285.4855 | 0 | off_peak | 584.46 | 0 | 100 | 0 | 0 | 100 | 0 | 0
7828 | 579.93 | 0 | 18.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27.2003 | 579.93 | 0 | 0.05921 | 5.3078 | 0 | 0 | 285.4855 | 0 | off_peak | 579.93 |  |  | 0 | 0 | 100 | 0 | 0
7829 | 599.58 | 0 | 17.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27.2003 | 599.58 | 0 | 0.05921 | 4.8944 | 0 | 0 | 285.4855 | 0 | off_peak | 599.58 |  |  | 0 | 0 | 100 | 0 | 0
7830 | 694.59 | 0 | 17.2 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 38.7984 | 706.9889 | 0 | 0.05921 | 4.343 | 0 | 0 | 285.4855 | 0 | off_peak | 694.59 | 0 | 100 | 0 | 0 | 100 | 0 | 0
7831 | 746.25 | 0 | 16.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 38.7984 | 746.25 | 0 | 0.05921 | 3.8951 | 0 | 0 | 285.4855 | 0 | on_peak | 746.25 |  |  | 0 | 0 | 100 | 0 | 0
7832 | 785.19 | 85.0137 | 16.1 | 17.7669 | 5.3679 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 0 | 50.3966 | 779.8221 | 0 | 0.05921 | 3.4785 | 0 | 0 | 297.0836 | 5.3679 | on_peak | 779.8221 | 100 | 0 | 0.68 | 0 | 99.32 | 18.6723 | 0
7833 | 815.16 | 279.805 | 16.2 | 58.4555 | 58.4555 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50.3966 | 756.7045 | 0 | 0.05921 | 3.2555 | 0 | 0 | 297.0836 | 58.4555 | on_peak | 756.7045 |  |  | 7.17 | 0 | 92.83 | 190.3048 | 0
7834 | 789.01 | 444.607 | 16.7 | 92.7231 | 92.7231 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50.3966 | 696.2869 | 0 | 0.05921 | 3.0846 | 0 | 0 | 297.0836 | 92.7231 | on_peak | 696.2869 |  |  | 11.75 | 0 | 88.25 | 286.0152 | 0
7835 | 734.9 | 450.601 | 17.3 | 93.7761 | 93.7761 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50.3966 | 641.1239 | 0 | 0.05921 | 3.0266 | 0 | 0 | 297.0836 | 93.7761 | off_peak | 641.1239 |  |  | 12.76 | 0 | 87.24 | 283.8225 | 0
7836 | 764.71 | 609.325 | 18 | 126.4977 | 126.4977 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50.3966 | 638.2123 | 0 | 0.05921 | 3.0979 | 0 | 0 | 297.0836 | 126.4977 | off_peak | 638.2123 |  |  | 16.54 | 0 | 83.46 | 391.8715 | 0
7837 | 714.85 | 633.629 | 18.5 | 131.3123 | 131.3123 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50.3966 | 583.5377 | 0 | 0.05921 | 3.1817 | 0 | 0 | 297.0836 | 131.3123 | off_peak | 583.5377 |  |  | 18.37 | 0 | 81.63 | 417.7962 | 0
7838 | 716.4 | 565.071 | 18.9 | 116.9397 | 116.9397 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50.3966 | 599.4603 | 0 | 0.05921 | 3.3957 | 0 | 0 | 297.0836 | 116.9397 | off_peak | 599.4603 |  |  | 16.32 | 0 | 83.68 | 397.0966 | 0
7839 | 651.78 | 419.914 | 19.1 | 86.8387 | 86.8387 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50.3966 | 564.9413 | 0 | 0.05921 | 3.5377 | 0 | 0 | 297.0836 | 86.8387 | off_peak | 564.9413 |  |  | 13.32 | 0 | 86.68 | 307.2122 | 0
7840 | 580.68 | 241.206 | 19 | 49.8993 | 49.8993 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50.3966 | 530.7807 | 0 | 0.05921 | 3.7929 | 0 | 0 | 297.0836 | 49.8993 | off_peak | 530.7807 |  |  | 8.59 | 0 | 91.41 | 189.2631 | 0
7841 | 587.75 | 132.556 | 18.5 | 27.4707 | 27.4707 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50.3966 | 560.2793 | 0 | 0.05921 | 4.1014 | 0 | 0 | 297.0836 | 27.4707 | off_peak | 560.2793 |  |  | 4.67 | 0 | 95.33 | 112.6697 | 0
7842 | 562.58 | 4.75 | 17.9 | 0.98646 | 0.98646 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50.3966 | 561.5935 | 0 | 0.05921 | 4.489 | 0 | 0 | 297.0836 | 0.98646 | off_peak | 561.5935 |  |  | 0.18 | 0 | 99.82 | 4.4282 | 0
7843 | 574.06 | 0 | 17.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50.3966 | 574.06 | 0 | 0.05921 | 4.9773 | 0 | 0 | 297.0836 | 0 | on_peak | 574.06 |  |  | 0 | 0 | 100 | 0 | 0
7844 | 572.38 | 0 | 17.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50.3966 | 572.38 | 0 | 0.05921 | 5.3235 | 0 | 0 | 297.0836 | 0 | on_peak | 572.38 |  |  | 0 | 0 | 100 | 0 | 0
7845 | 538.79 | 0 | 17.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50.3966 | 538.79 | 0 | 0.05921 | 5.5427 | 0 | 0 | 297.0836 | 0 | on_peak | 538.79 |  |  | 0 | 0 | 100 | 0 | 0
7846 | 574.96 | 0 | 17.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50.3966 | 574.96 | 0 | 0.05921 | 5.5908 | 0 | 0 | 297.0836 | 0 | on_peak | 574.96 |  |  | 0 | 0 | 100 | 0 | 0
7847 | 519.62 | 0 | 17.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50.3966 | 519.62 | 0 | 0.05921 | 5.6258 | 0 | 0 | 297.0836 | 0 | off_peak | 519.62 |  |  | 0 | 0 | 100 | 0 | 0
7848 | 532.08 | 0 | 17.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50.3966 | 532.08 | 0 | 0.05921 | 5.4908 | 0 | 0 | 297.0836 | 0 | off_peak | 532.08 |  |  | 0 | 0 | 100 | 0 | 0
7849 | 529.01 | 0 | 17.3 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 61.9947 | 541.4089 | 0 | 0.05921 | 5.1505 | 0 | 0 | 297.0836 | 0 | off_peak | 529.01 | 0 | 100 | 0 | 0 | 100 | 0 | 0
7850 | 544.17 | 0 | 17.4 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 73.5928 | 556.5689 | 0 | 0.05921 | 4.7386 | 0 | 0 | 297.0836 | 0 | off_peak | 544.17 | 0 | 100 | 0 | 0 | 100 | 0 | 0
7851 | 524.15 | 0 | 17.5 | 0 | 0 | 0 | 0 | 0.80079 | 0.80079 | 0 | 0 | 0 | 74.3419 | 524.9508 | 0 | 0.05921 | 4.4717 | 0 | 0 | 297.0836 | 0 | off_peak | 524.15 | 0 | 100 | 0 | 0 | 100 | 0 | 0
7852 | 563.94 | 0 | 17.6 | 0 | 0 | 0 | 0 | 0.05172 | 0.05172 | 0 | 0 | 0 | 74.3903 | 563.9917 | 0 | 0.05921 | 4.2237 | 0 | 0 | 297.0836 | 0 | off_peak | 563.94 | 0 | 100 | 0 | 0 | 100 | 0 | 0
7853 | 543.19 | 0 | 17.6 | 0 | 0 | 0 | 0 | 0.0033404 | 0.0033404 | 0 | 0 | 0 | 74.3934 | 543.1933 | 0 | 0.05921 | 3.9604 | 0 | 0 | 297.0836 | 0 | off_peak | 543.19 | 0 | 100 | 0 | 0 | 100 | 0 | 0
7854 | 638.69 | 0 | 17.7 | 0 | 0 | 0 | 0 | 0.00021574 | 0.00021574 | 0 | 0 | 0 | 74.3936 | 638.6902 | 0 | 0.05921 | 3.5829 | 0 | 0 | 297.0836 | 0 | off_peak | 638.69 | 0 | 100 | 0 | 0 | 100 | 0 | 0
7855 | 724.16 | 0 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 724.16 | 0 | 0.088511 | 3.2524 | 0 | 0 | 297.0836 | 0 | on_peak | 724.16 |  |  | 0 | 0 | 100 | 0 | 0
7856 | 727.98 | 92.4943 | 19 | 19.1347 | 19.1347 | 0 | 0 | 0 | 0 | 62.63 | 62.63 | 0 | 7.4394 | 646.2154 | 0 | 0.088511 | 2.9311 | 0 | 0 | 297.0836 | 19.1347 | on_peak | 646.2154 |  |  | 2.63 | 8.6 | 88.77 | 56.0854 | 0
7857 | 714.28 | 271.463 | 20.2 | 55.9212 | 55.9212 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 658.3588 | 0 | 0.088511 | 2.7416 | 0 | 0 | 297.0836 | 55.9212 | on_peak | 658.3588 |  |  | 7.83 | 0 | 92.17 | 153.3155 | 0
7858 | 743.73 | 434.563 | 21.1 | 89.2345 | 89.2345 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 654.4955 | 0 | 0.088511 | 2.6466 | 0 | 0 | 297.0836 | 89.2345 | on_peak | 654.4955 |  |  | 12 | 0 | 88 | 236.169 | 0
7859 | 696.13 | 389.039 | 21.9 | 79.6596 | 79.6596 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 19.0375 | 628.8694 | 0 | 0.05921 | 2.6711 | 0 | 0 | 297.0836 | 79.6596 | off_peak | 616.4704 | 0 | 100 | 11.44 | 0 | 88.56 | 212.7773 | 0
7860 | 757.98 | 83.6 | 22.6 | 17.0753 | 17.0753 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 30.6357 | 753.3037 | 0 | 0.05921 | 2.826 | 0 | 0 | 297.0836 | 17.0753 | off_peak | 740.9047 | 0 | 100 | 2.25 | 0 | 97.75 | 48.2553 | 0
7861 | 705.09 | 143.45 | 23.1 | 29.2473 | 16.8484 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 0 | 42.2338 | 688.2416 | 0 | 0.05921 | 3.0352 | 0 | 0 | 308.6818 | 16.8484 | off_peak | 688.2416 | 100 | 0 | 2.39 | 0 | 97.61 | 51.1387 | 0
7862 | 717.44 | 109.25 | 23.3 | 22.2585 | 22.2585 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 53.832 | 707.5804 | 0 | 0.05921 | 3.343 | 0 | 0 | 308.6818 | 22.2585 | off_peak | 695.1815 | 0 | 100 | 3.1 | 0 | 96.9 | 74.4099 | 0
7863 | 676.52 | 72.2 | 23.4 | 14.7047 | 2.3058 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 0 | 65.4301 | 674.2142 | 0 | 0.05921 | 3.6279 | 0 | 0 | 320.2799 | 2.3058 | off_peak | 674.2142 | 100 | 0 | 0.34 | 0 | 99.66 | 8.3652 | 0
7864 | 626.23 | 60.8 | 23.3 | 12.3873 | 3.4238 | 0 | 8.9635 | 8.9635 | 0 | 0 | 0 | 0 | 73.8147 | 622.8062 | 0 | 0.05921 | 3.9113 | 0 | 0 | 328.6645 | 3.4238 | off_peak | 622.8062 | 100 | 0 | 0.55 | 0 | 99.45 | 13.3915 | 0
7865 | 627.04 | 18.05 | 22.8 | 3.6841 | 3.1052 | 0 | 0.57892 | 0.57892 | 0 | 0 | 0 | 0 | 74.3563 | 623.9348 | 0 | 0.05921 | 4.0398 | 0 | 0 | 329.2061 | 3.1052 | off_peak | 623.9348 | 100 | 0 | 0.5 | 0 | 99.5 | 12.5443 | 0
7866 | 579.64 | 0 | 22.1 | 0 | 0 | 0 | 0 | 0.03739 | 0.03739 | 0 | 0 | 0 | 74.3912 | 579.6774 | 0 | 0.05921 | 4.1667 | 0 | 0 | 329.2061 | 0 | off_peak | 579.64 | 0 | 100 | 0 | 0 | 100 | 0 | 0
7867 | 546.18 | 0 | 21.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3912 | 546.18 | 0 | 0.088511 | 4.2436 | 0 | 0 | 329.2061 | 0 | on_peak | 546.18 |  |  | 0 | 0 | 100 | 0 | 0
7868 | 555.92 | 0 | 21.6 | 0 | 0 | 0 | 0 | 0 | 0 | 62.6277 | 62.6277 | 0 | 7.4394 | 493.2923 | 0 | 0.088511 | 4.283 | 0 | 0 | 329.2061 | 0 | on_peak | 493.2923 |  |  | 0 | 11.27 | 88.73 | 0 | 0
7869 | 548.86 | 0 | 21.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 548.86 | 0 | 0.088511 | 4.3269 | 0 | 0 | 329.2061 | 0 | on_peak | 548.86 |  |  | 0 | 0 | 100 | 0 | 0
7870 | 534.61 | 0 | 21.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 534.61 | 0 | 0.088511 | 4.4249 | 0 | 0 | 329.2061 | 0 | on_peak | 534.61 |  |  | 0 | 0 | 100 | 0 | 0
7871 | 540.45 | 0 | 20.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 540.45 | 0 | 0.05921 | 4.6149 | 0 | 0 | 329.2061 | 0 | off_peak | 540.45 |  |  | 0 | 0 | 100 | 0 | 0
7872 | 546.83 | 0 | 20.7 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 19.0375 | 559.2289 | 0 | 0.05921 | 4.8618 | 0 | 0 | 329.2061 | 0 | off_peak | 546.83 | 0 | 100 | 0 | 0 | 100 | 0 | 0
7873 | 531.33 | 0 | 20.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19.0375 | 531.33 | 0 | 0.05921 | 4.8831 | 0 | 0 | 329.2061 | 0 | off_peak | 531.33 |  |  | 0 | 0 | 100 | 0 | 0
7874 | 521.67 | 0 | 20.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19.0375 | 521.67 | 0 | 0.05921 | 4.7082 | 0 | 0 | 329.2061 | 0 | off_peak | 521.67 |  |  | 0 | 0 | 100 | 0 | 0
7875 | 541.59 | 0 | 20.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19.0375 | 541.59 | 0 | 0.05921 | 4.5343 | 0 | 0 | 329.2061 | 0 | off_peak | 541.59 |  |  | 0 | 0 | 100 | 0 | 0
7876 | 535.78 | 0 | 20.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19.0375 | 535.78 | 0 | 0.05921 | 4.2777 | 0 | 0 | 329.2061 | 0 | off_peak | 535.78 |  |  | 0 | 0 | 100 | 0 | 0
7877 | 554.38 | 0 | 20.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19.0375 | 554.38 | 0 | 0.05921 | 3.9782 | 0 | 0 | 329.2061 | 0 | off_peak | 554.38 |  |  | 0 | 0 | 100 | 0 | 0
7878 | 637.45 | 0 | 20.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19.0375 | 637.45 | 0 | 0.05921 | 3.5886 | 0 | 0 | 329.2061 | 0 | off_peak | 637.45 |  |  | 0 | 0 | 100 | 0 | 0
7879 | 663.35 | 0 | 20.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19.0375 | 663.35 | 0 | 0.05921 | 3.1895 | 0 | 0 | 329.2061 | 0 | off_peak | 663.35 |  |  | 0 | 0 | 100 | 0 | 0
7880 | 662.65 | 56.5062 | 21 | 11.6073 | 11.6073 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19.0375 | 651.0427 | 0 | 0.05921 | 2.9349 | 0 | 0 | 329.2061 | 11.6073 | off_peak | 651.0427 |  |  | 1.75 | 0 | 98.25 | 34.0661 | 0
7881 | 690.51 | 260.557 | 21.9 | 53.3516 | 53.3516 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19.0375 | 637.1584 | 0 | 0.05921 | 2.7542 | 0 | 0 | 329.2061 | 53.3516 | off_peak | 637.1584 |  |  | 7.73 | 0 | 92.27 | 146.942 | 0
7882 | 690.36 | 423.23 | 22.7 | 86.4137 | 86.4137 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19.0375 | 603.9463 | 0 | 0.05921 | 2.6751 | 0 | 0 | 329.2061 | 86.4137 | off_peak | 603.9463 |  |  | 12.52 | 0 | 87.48 | 231.1644 | 0
7883 | 674.31 | 557.594 | 23.4 | 113.5632 | 113.5632 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19.0375 | 560.7468 | 0 | 0.05921 | 2.6569 | 0 | 0 | 329.2061 | 113.5632 | off_peak | 560.7468 |  |  | 16.84 | 0 | 83.16 | 301.7268 | 0
7884 | 697.98 | 457.38 | 23.9 | 92.9862 | 92.9862 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19.0375 | 604.9938 | 0 | 0.05921 | 2.7254 | 0 | 0 | 329.2061 | 92.9862 | off_peak | 604.9938 |  |  | 13.32 | 0 | 86.68 | 253.4261 | 0
7885 | 681.63 | 275.779 | 24.2 | 56.0061 | 56.0061 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19.0375 | 625.6239 | 0 | 0.05921 | 2.899 | 0 | 0 | 329.2061 | 56.0061 | off_peak | 625.6239 |  |  | 8.22 | 0 | 91.78 | 162.359 | 0
7886 | 680.19 | 258.542 | 24.4 | 52.4678 | 52.4678 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19.0375 | 627.7222 | 0 | 0.05921 | 3.2485 | 0 | 0 | 329.2061 | 52.4678 | off_peak | 627.7222 |  |  | 7.71 | 0 | 92.29 | 170.443 | 0
7887 | 669.13 | 298.434 | 24.5 | 60.5417 | 60.5417 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19.0375 | 608.5883 | 0 | 0.05921 | 3.345 | 0 | 0 | 329.2061 | 60.5417 | off_peak | 608.5883 |  |  | 9.05 | 0 | 90.95 | 202.514 | 0
7888 | 668.67 | 297.516 | 24.4 | 60.3771 | 60.3771 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19.0375 | 608.2929 | 0 | 0.05921 | 3.4847 | 0 | 0 | 329.2061 | 60.3771 | off_peak | 608.2929 |  |  | 9.03 | 0 | 90.97 | 210.3956 | 0
7889 | 659.9 | 98.7024 | 24 | 20.0592 | 7.6602 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 0 | 30.6357 | 652.2398 | 0 | 0.05921 | 3.5754 | 0 | 0 | 340.8042 | 7.6602 | off_peak | 652.2398 | 100 | 0 | 1.16 | 0 | 98.84 | 27.3886 | 0
7890 | 596.92 | 0 | 23.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30.6357 | 596.92 | 0 | 0.05921 | 3.813 | 0 | 0 | 340.8042 | 0 | off_peak | 596.92 |  |  | 0 | 0 | 100 | 0 | 0
7891 | 574.58 | 0 | 23.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30.6357 | 574.58 | 0 | 0.05921 | 4.0144 | 0 | 0 | 340.8042 | 0 | off_peak | 574.58 |  |  | 0 | 0 | 100 | 0 | 0
7892 | 558.34 | 0 | 22.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30.6357 | 558.34 | 0 | 0.05921 | 4.1166 | 0 | 0 | 340.8042 | 0 | off_peak | 558.34 |  |  | 0 | 0 | 100 | 0 | 0
7893 | 516.98 | 0 | 22.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30.6357 | 516.98 | 0 | 0.05921 | 4.278 | 0 | 0 | 340.8042 | 0 | off_peak | 516.98 |  |  | 0 | 0 | 100 | 0 | 0
7894 | 572.95 | 0 | 22.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30.6357 | 572.95 | 0 | 0.05921 | 4.5109 | 0 | 0 | 340.8042 | 0 | off_peak | 572.95 |  |  | 0 | 0 | 100 | 0 | 0
7895 | 534.29 | 0 | 22.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30.6357 | 534.29 | 0 | 0.05921 | 4.9358 | 0 | 0 | 340.8042 | 0 | off_peak | 534.29 |  |  | 0 | 0 | 100 | 0 | 0
7896 | 543.39 | 0 | 22 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 42.2338 | 555.7889 | 0 | 0.05921 | 5.3037 | 0 | 0 | 340.8042 | 0 | off_peak | 543.39 | 0 | 100 | 0 | 0 | 100 | 0 | 0
7897 | 545.92 | 0 | 21.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 42.2338 | 545.92 | 0 | 0.05921 | 5.3785 | 0 | 0 | 340.8042 | 0 | off_peak | 545.92 |  |  | 0 | 0 | 100 | 0 | 0
7898 | 542.58 | 0 | 21.8 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 53.832 | 554.9789 | 0 | 0.05921 | 5.1534 | 0 | 0 | 340.8042 | 0 | off_peak | 542.58 | 0 | 100 | 0 | 0 | 100 | 0 | 0
7899 | 544.48 | 0 | 21.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 53.832 | 544.48 | 0 | 0.05921 | 4.8438 | 0 | 0 | 340.8042 | 0 | off_peak | 544.48 |  |  | 0 | 0 | 100 | 0 | 0
7900 | 531.09 | 0 | 21.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 53.832 | 531.09 | 0 | 0.05921 | 4.5998 | 0 | 0 | 340.8042 | 0 | off_peak | 531.09 |  |  | 0 | 0 | 100 | 0 | 0
7901 | 538.51 | 0 | 21.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 53.832 | 538.51 | 0 | 0.05921 | 4.3267 | 0 | 0 | 340.8042 | 0 | off_peak | 538.51 |  |  | 0 | 0 | 100 | 0 | 0
7902 | 591.58 | 0 | 21.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 53.832 | 591.58 | 0 | 0.05921 | 3.8761 | 0 | 0 | 340.8042 | 0 | off_peak | 591.58 |  |  | 0 | 0 | 100 | 0 | 0
7903 | 684.34 | 0 | 21.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 53.832 | 684.34 | 0 | 0.05921 | 3.4534 | 0 | 0 | 340.8042 | 0 | off_peak | 684.34 |  |  | 0 | 0 | 100 | 0 | 0
7904 | 708.39 | 91.7106 | 22.3 | 18.7519 | 18.7519 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 53.832 | 689.6381 | 0 | 0.05921 | 3.1383 | 0 | 0 | 340.8042 | 18.7519 | off_peak | 689.6381 |  |  | 2.65 | 0 | 97.35 | 58.8489 | 0
7905 | 679.51 | 273.736 | 23.2 | 55.7907 | 55.7907 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 53.832 | 623.7193 | 0 | 0.05921 | 2.9192 | 0 | 0 | 340.8042 | 55.7907 | off_peak | 623.7193 |  |  | 8.21 | 0 | 91.79 | 162.8649 | 0
7906 | 678.53 | 331.775 | 23.7 | 67.4989 | 67.4989 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 53.832 | 611.0311 | 0 | 0.05921 | 2.7888 | 0 | 0 | 340.8042 | 67.4989 | off_peak | 611.0311 |  |  | 9.95 | 0 | 90.05 | 188.2431 | 0
7907 | 675.93 | 323.388 | 24.1 | 65.6982 | 65.6982 | 0 | 0 | 8.7263 | 8.7263 | 0 | 0 | 0 | 61.9947 | 618.9581 | 0 | 0.05921 | 2.7273 | 0 | 0 | 340.8042 | 65.6982 | off_peak | 610.2318 | 0 | 100 | 9.72 | 0 | 90.28 | 179.1781 | 0
7908 | 720.63 | 298.453 | 24.4 | 60.5673 | 60.5673 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 61.9947 | 660.0627 | 0 | 0.05921 | 2.7639 | 0 | 0 | 340.8042 | 60.5673 | off_peak | 660.0627 |  |  | 8.4 | 0 | 91.6 | 167.4009 | 0
7909 | 712.92 | 178.943 | 24.6 | 36.2881 | 36.2881 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 61.9947 | 676.6319 | 0 | 0.05921 | 2.9411 | 0 | 0 | 340.8042 | 36.2881 | off_peak | 676.6319 |  |  | 5.09 | 0 | 94.91 | 106.728 | 0
7910 | 655.12 | 142.5 | 24.6 | 28.8978 | 28.8978 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 61.9947 | 626.2222 | 0 | 0.05921 | 3.2298 | 0 | 0 | 340.8042 | 28.8978 | off_peak | 626.2222 |  |  | 4.41 | 0 | 95.59 | 93.3353 | 0
7911 | 706.7 | 162.894 | 24.6 | 33.0335 | 33.0335 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 61.9947 | 673.6665 | 0 | 0.05921 | 3.8336 | 0 | 0 | 340.8042 | 33.0335 | off_peak | 673.6665 |  |  | 4.67 | 0 | 95.33 | 126.6385 | 0
7912 | 661.26 | 127.097 | 24.4 | 25.7927 | 25.7927 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 61.9947 | 635.4673 | 0 | 0.05921 | 4.297 | 0 | 0 | 340.8042 | 25.7927 | off_peak | 635.4673 |  |  | 3.9 | 0 | 96.1 | 110.8316 | 0
7913 | 666.5 | 42.3562 | 23.8 | 8.6142 | 8.6142 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 61.9947 | 657.8858 | 0 | 0.05921 | 4.6673 | 0 | 0 | 340.8042 | 8.6142 | off_peak | 657.8858 |  |  | 1.29 | 0 | 98.71 | 40.2047 | 0
7914 | 610.57 | 0 | 23.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 61.9947 | 610.57 | 0 | 0.05921 | 5.0921 | 0 | 0 | 340.8042 | 0 | off_peak | 610.57 |  |  | 0 | 0 | 100 | 0 | 0
7915 | 544.46 | 0 | 23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 61.9947 | 544.46 | 0 | 0.05921 | 5.3059 | 0 | 0 | 340.8042 | 0 | off_peak | 544.46 |  |  | 0 | 0 | 100 | 0 | 0
7916 | 567.12 | 0 | 22.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 61.9947 | 567.12 | 0 | 0.05921 | 5.423 | 0 | 0 | 340.8042 | 0 | off_peak | 567.12 |  |  | 0 | 0 | 100 | 0 | 0
7917 | 542.77 | 0 | 22.8 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 73.5928 | 555.1689 | 0 | 0.05921 | 5.4696 | 0 | 0 | 340.8042 | 0 | off_peak | 542.77 | 0 | 100 | 0 | 0 | 100 | 0 | 0
7918 | 548.86 | 0 | 22.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 73.5928 | 548.86 | 0 | 0.05921 | 5.5937 | 0 | 0 | 340.8042 | 0 | off_peak | 548.86 |  |  | 0 | 0 | 100 | 0 | 0
7919 | 557.1 | 0 | 22.8 | 0 | 0 | 0 | 0 | 0.80079 | 0.80079 | 0 | 0 | 0 | 74.3419 | 557.9008 | 0 | 0.05921 | 5.8544 | 0 | 0 | 340.8042 | 0 | off_peak | 557.1 | 0 | 100 | 0 | 0 | 100 | 0 | 0
7920 | 535.04 | 0 | 22.7 | 0 | 0 | 0 | 0 | 0.05172 | 0.05172 | 0 | 0 | 0 | 74.3903 | 535.0917 | 0 | 0.05921 | 5.9859 | 0 | 0 | 340.8042 | 0 | off_peak | 535.04 | 0 | 100 | 0 | 0 | 100 | 0 | 0
7921 | 543.99 | 0 | 22.6 | 0 | 0 | 0 | 0 | 0.0033404 | 0.0033404 | 0 | 0 | 0 | 74.3934 | 543.9933 | 0 | 0.05921 | 6.0698 | 0 | 0 | 340.8042 | 0 | off_peak | 543.99 | 0 | 100 | 0 | 0 | 100 | 0 | 0
7922 | 547 | 0 | 22.5 | 0 | 0 | 0 | 0 | 0.00021574 | 0.00021574 | 0 | 0 | 0 | 74.3936 | 547.0002 | 0 | 0.05921 | 5.8413 | 0 | 0 | 340.8042 | 0 | off_peak | 547 | 0 | 100 | 0 | 0 | 100 | 0 | 0
7923 | 552.31 | 0 | 22.5 | 0 | 0 | 0 | 0 | 1.4896e-05 | 1.4896e-05 | 0 | 0 | 0 | 74.3936 | 552.31 | 0 | 0.05921 | 5.5657 | 0 | 0 | 340.8042 | 0 | off_peak | 552.31 | 0 | 100 | 0 | 0 | 100 | 0 | 0
7924 | 531.98 | 0 | 22.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 531.98 | 0 | 0.05921 | 5.1625 | 0 | 0 | 340.8042 | 0 | off_peak | 531.98 |  |  | 0 | 0 | 100 | 0 | 0
7925 | 553.43 | 0 | 22.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 553.43 | 0 | 0.05921 | 4.7232 | 0 | 0 | 340.8042 | 0 | off_peak | 553.43 |  |  | 0 | 0 | 100 | 0 | 0
7926 | 605.99 | 0 | 22.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 605.99 | 0 | 0.05921 | 4.1422 | 0 | 0 | 340.8042 | 0 | off_peak | 605.99 |  |  | 0 | 0 | 100 | 0 | 0
7927 | 656.84 | 0 | 22.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 656.84 | 0 | 0.088511 | 3.595 | 0 | 0 | 340.8042 | 0 | on_peak | 656.84 |  |  | 0 | 0 | 100 | 0 | 0
7928 | 789.44 | 89.3391 | 23.2 | 18.2084 | 18.2084 | 0 | 0 | 0 | 0 | 62.63 | 62.63 | 0 | 7.4394 | 708.6016 | 0 | 0.088511 | 3.3065 | 0 | 0 | 340.8042 | 18.2084 | on_peak | 708.6016 |  |  | 2.31 | 7.93 | 89.76 | 60.2063 | 0
7929 | 842.29 | 273.212 | 23.9 | 55.5445 | 55.5445 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 786.7455 | 0 | 0.088511 | 3.1385 | 0 | 0 | 340.8042 | 55.5445 | on_peak | 786.7455 |  |  | 6.59 | 0 | 93.41 | 174.3278 | 0
7930 | 797.04 | 445.91 | 24.3 | 90.5243 | 90.5243 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 706.5157 | 0 | 0.088511 | 3.0298 | 0 | 0 | 340.8042 | 90.5243 | on_peak | 706.5157 |  |  | 11.36 | 0 | 88.64 | 274.2712 | 0
7931 | 814.4 | 575.905 | 24.6 | 116.7887 | 116.7887 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 19.0375 | 710.0102 | 0 | 0.05921 | 3.0609 | 0 | 0 | 340.8042 | 116.7887 | off_peak | 697.6113 | 0 | 100 | 14.34 | 0 | 85.66 | 357.4786 | 0
7932 | 837.29 | 649.788 | 24.8 | 131.6768 | 131.6768 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 30.6357 | 718.0121 | 0 | 0.05921 | 3.4081 | 0 | 0 | 340.8042 | 131.6768 | off_peak | 705.6132 | 0 | 100 | 15.73 | 0 | 84.27 | 448.7614 | 0
7933 | 775.79 | 660.493 | 24.9 | 133.798 | 133.798 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 42.2338 | 654.391 | 0 | 0.05921 | 3.8411 | 0 | 0 | 340.8042 | 133.798 | off_peak | 641.992 | 0 | 100 | 17.25 | 0 | 82.75 | 513.927 | 0
7934 | 843.16 | 603.964 | 24.9 | 122.3467 | 122.3467 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 53.832 | 733.2122 | 0 | 0.05921 | 4.0856 | 0 | 0 | 340.8042 | 122.3467 | off_peak | 720.8133 | 0 | 100 | 14.51 | 0 | 85.49 | 499.8609 | 0
7935 | 814.15 | 489.904 | 24.8 | 99.277 | 86.878 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 0 | 65.4301 | 727.272 | 0 | 0.05921 | 4.2822 | 0 | 0 | 352.4024 | 86.878 | off_peak | 727.272 | 100 | 0 | 10.67 | 0 | 89.33 | 372.0318 | 0
7936 | 757.03 | 328.016 | 24.6 | 66.5189 | 66.5189 | 0 | 0 | 8.9635 | 8.9635 | 0 | 0 | 0 | 73.8147 | 699.4747 | 0 | 0.05921 | 4.362 | 0 | 0 | 352.4024 | 66.5189 | off_peak | 690.5111 | 0 | 100 | 8.79 | 0 | 91.21 | 290.1558 | 0
7937 | 794.87 | 142.667 | 24.3 | 28.9629 | 28.9629 | 0 | 0 | 0.57892 | 0.57892 | 0 | 0 | 0 | 74.3563 | 766.486 | 0 | 0.05921 | 4.308 | 0 | 0 | 352.4024 | 28.9629 | off_peak | 765.9071 | 0 | 100 | 3.64 | 0 | 96.36 | 124.7714 | 0
7938 | 783.4 | 0 | 24.1 | 0 | 0 | 0 | 0 | 0.03739 | 0.03739 | 0 | 0 | 0 | 74.3912 | 783.4374 | 0 | 0.05921 | 4.2819 | 0 | 0 | 352.4024 | 0 | off_peak | 783.4 | 0 | 100 | 0 | 0 | 100 | 0 | 0
7939 | 776.77 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3912 | 776.77 | 0 | 0.088511 | 4.2134 | 0 | 0 | 352.4024 | 0 | on_peak | 776.77 |  |  | 0 | 0 | 100 | 0 | 0
7940 | 774.54 | 0 | 24.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3912 | 774.54 | 0 | 0.088511 | 4.0762 | 0 | 0 | 352.4024 | 0 | on_peak | 774.54 |  |  | 0 | 0 | 100 | 0 | 0
7941 | 770.38 | 0 | 24.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3912 | 770.38 | 0 | 0.088511 | 4.1399 | 0 | 0 | 352.4024 | 0 | on_peak | 770.38 |  |  | 0 | 0 | 100 | 0 | 0
7942 | 734.78 | 0 | 24.2 | 0 | 0 | 0 | 0 | 0 | 0 | 62.6277 | 62.6277 | 0 | 7.4394 | 672.1523 | 0 | 0.088511 | 4.536 | 62.6277 | 0 | 285.4505 | 62.6277 | on_peak | 672.1523 |  |  | 0 | 8.52 | 91.48 | 284.0764 | 0
7943 | 763.22 | 0 | 24.1 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 19.0375 | 775.6189 | 0 | 0.05921 | 5.146 | 0 | 0 | 285.4505 | 0 | off_peak | 763.22 | 0 | 100 | 0 | 0 | 100 | 0 | 0
7944 | 707.56 | 0 | 24.1 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 30.6357 | 719.9589 | 0 | 0.05921 | 5.5986 | 0 | 0 | 285.4505 | 0 | off_peak | 707.56 | 0 | 100 | 0 | 0 | 100 | 0 | 0
7945 | 698.34 | 0 | 24 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 42.2338 | 710.7389 | 0 | 0.05921 | 5.7424 | 0 | 0 | 285.4505 | 0 | off_peak | 698.34 | 0 | 100 | 0 | 0 | 100 | 0 | 0
7946 | 527.57 | 0 | 24 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 53.832 | 539.9689 | 0 | 0.05921 | 5.5482 | 0 | 0 | 285.4505 | 0 | off_peak | 527.57 | 0 | 100 | 0 | 0 | 100 | 0 | 0
7947 | 518.43 | 0 | 23.9 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 65.4301 | 530.8289 | 0 | 0.05921 | 5.2059 | 0 | 0 | 285.4505 | 0 | off_peak | 518.43 | 0 | 100 | 0 | 0 | 100 | 0 | 0
7948 | 491.52 | 0 | 23.9 | 0 | 0 | 0 | 0 | 8.9635 | 8.9635 | 0 | 0 | 0 | 73.8147 | 500.4835 | 0 | 0.05921 | 4.7662 | 0 | 0 | 285.4505 | 0 | off_peak | 491.52 | 0 | 100 | 0 | 0 | 100 | 0 | 0
7949 | 493.74 | 0 | 23.8 | 0 | 0 | 0 | 0 | 0.57892 | 0.57892 | 0 | 0 | 0 | 74.3563 | 494.3189 | 0 | 0.05921 | 4.2057 | 0 | 0 | 285.4505 | 0 | off_peak | 493.74 | 0 | 100 | 0 | 0 | 100 | 0 | 0
7950 | 522.28 | 0 | 23.8 | 0 | 0 | 0 | 0 | 0.03739 | 0.03739 | 0 | 0 | 0 | 74.3912 | 522.3174 | 0 | 0.05921 | 3.5487 | 0 | 0 | 285.4505 | 0 | off_peak | 522.28 | 0 | 100 | 0 | 0 | 100 | 0 | 0
7951 | 608.86 | 0 | 23.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3912 | 608.86 | 0 | 0.088511 | 3.2356 | 0 | 0 | 285.4505 | 0 | on_peak | 608.86 |  |  | 0 | 0 | 100 | 0 | 0
7952 | 679.17 | 89.0772 | 24.1 | 18.0966 | 18.0966 | 0 | 0 | 0 | 0 | 62.6277 | 62.6277 | 0 | 7.4394 | 598.4457 | 0 | 0.088511 | 2.9961 | 0 | 0 | 285.4505 | 18.0966 | on_peak | 598.4457 |  |  | 2.66 | 9.22 | 88.11 | 54.2188 | 0
7953 | 773.43 | 272.779 | 24.4 | 55.3571 | 55.3571 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 718.0729 | 0 | 0.088511 | 2.8439 | 0 | 0 | 285.4505 | 55.3571 | on_peak | 718.0729 |  |  | 7.16 | 0 | 92.84 | 157.4289 | 0
7954 | 738.23 | 441.794 | 24.7 | 89.5599 | 89.5599 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 648.6701 | 0 | 0.088511 | 2.7487 | 0 | 0 | 285.4505 | 89.5599 | on_peak | 648.6701 |  |  | 12.13 | 0 | 87.87 | 246.1711 | 0
7955 | 654.05 | 525.788 | 24.9 | 106.5104 | 106.5104 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 19.0375 | 559.9385 | 0 | 0.05921 | 2.8067 | 0 | 0 | 285.4505 | 106.5104 | off_peak | 547.5396 | 0 | 100 | 16.28 | 0 | 83.72 | 298.9471 | 0
7956 | 769.07 | 535.579 | 25 | 108.4547 | 96.0558 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 0 | 30.6357 | 673.0142 | 0 | 0.05921 | 3.085 | 0 | 0 | 297.0486 | 96.0558 | off_peak | 673.0142 | 100 | 0 | 12.49 | 0 | 87.51 | 296.3278 | 0
7957 | 776.23 | 586.378 | 25 | 118.7415 | 118.7415 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 42.2338 | 669.8874 | 0 | 0.05921 | 3.6102 | 0 | 0 | 297.0486 | 118.7415 | off_peak | 657.4885 | 0 | 100 | 15.3 | 0 | 84.7 | 428.6817 | 0
7958 | 785.7 | 548.101 | 24.9 | 111.0304 | 111.0304 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 53.832 | 687.0685 | 0 | 0.05921 | 3.9001 | 0 | 0 | 297.0486 | 111.0304 | off_peak | 674.6696 | 0 | 100 | 14.13 | 0 | 85.87 | 433.0268 | 0
7959 | 831.56 | 408.183 | 24.8 | 82.7166 | 82.7166 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 65.4301 | 761.2424 | 0 | 0.05921 | 4.0539 | 0 | 0 | 297.0486 | 82.7166 | off_peak | 748.8434 | 0 | 100 | 9.95 | 0 | 90.05 | 335.3281 | 0
7960 | 772.28 | 288.581 | 24.6 | 58.5218 | 58.5218 | 0 | 0 | 8.9635 | 8.9635 | 0 | 0 | 0 | 73.8147 | 722.7217 | 0 | 0.05921 | 3.9198 | 0 | 0 | 297.0486 | 58.5218 | off_peak | 713.7582 | 0 | 100 | 7.58 | 0 | 92.42 | 229.3954 | 0
7961 | 746.35 | 79.1328 | 24.5 | 16.0532 | 15.4743 | 0 | 0.57892 | 0.57892 | 0 | 0 | 0 | 0 | 74.3563 | 730.8757 | 0 | 0.05921 | 3.8759 | 0 | 0 | 297.5902 | 15.4743 | off_peak | 730.8757 | 100 | 0 | 2.07 | 0 | 97.93 | 59.9774 | 0
7962 | 824.82 | 0 | 24.3 | 0 | 0 | 0 | 0 | 0.03739 | 0.03739 | 0 | 0 | 0 | 74.3912 | 824.8574 | 0 | 0.05921 | 3.7755 | 0 | 0 | 297.5902 | 0 | off_peak | 824.82 | 0 | 100 | 0 | 0 | 100 | 0 | 0
7963 | 800.05 | 0 | 24.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3912 | 800.05 | 0 | 0.088511 | 3.8124 | 0 | 0 | 297.5902 | 0 | on_peak | 800.05 |  |  | 0 | 0 | 100 | 0 | 0
7964 | 756.94 | 0 | 24.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3912 | 756.94 | 0 | 0.088511 | 3.8791 | 0 | 0 | 297.5902 | 0 | on_peak | 756.94 |  |  | 0 | 0 | 100 | 0 | 0
7965 | 784.05 | 0 | 24.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3912 | 784.05 | 0 | 0.088511 | 4.0715 | 0 | 0 | 297.5902 | 0 | on_peak | 784.05 |  |  | 0 | 0 | 100 | 0 | 0
7966 | 740.57 | 0 | 24.5 | 0 | 0 | 0 | 0 | 0 | 0 | 62.6277 | 62.6277 | 0 | 7.4394 | 677.9423 | 0 | 0.088511 | 4.2875 | 62.6277 | 0 | 230.6383 | 62.6277 | on_peak | 677.9423 |  |  | 0 | 8.46 | 91.54 | 268.5157 | 0
7967 | 747.79 | 0 | 24.5 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 19.0375 | 760.1889 | 0 | 0.05921 | 4.6652 | 0 | 0 | 230.6383 | 0 | off_peak | 747.79 | 0 | 100 | 0 | 0 | 100 | 0 | 0
7968 | 728.89 | 0 | 24.4 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 30.6357 | 741.2889 | 0 | 0.05921 | 5.137 | 0 | 0 | 230.6383 | 0 | off_peak | 728.89 | 0 | 100 | 0 | 0 | 100 | 0 | 0
7969 | 663.77 | 0 | 24.4 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 42.2338 | 676.1689 | 0 | 0.05921 | 5.3733 | 0 | 0 | 230.6383 | 0 | off_peak | 663.77 | 0 | 100 | 0 | 0 | 100 | 0 | 0
7970 | 596.82 | 0 | 24.3 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 53.832 | 609.2189 | 0 | 0.05921 | 5.2729 | 0 | 0 | 230.6383 | 0 | off_peak | 596.82 | 0 | 100 | 0 | 0 | 100 | 0 | 0
7971 | 577.21 | 0 | 24.2 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 65.4301 | 589.6089 | 0 | 0.05921 | 5.0585 | 0 | 0 | 230.6383 | 0 | off_peak | 577.21 | 0 | 100 | 0 | 0 | 100 | 0 | 0
7972 | 588.96 | 0 | 24.1 | 0 | 0 | 0 | 0 | 8.9635 | 8.9635 | 0 | 0 | 0 | 73.8147 | 597.9235 | 0 | 0.05921 | 4.7111 | 0 | 0 | 230.6383 | 0 | off_peak | 588.96 | 0 | 100 | 0 | 0 | 100 | 0 | 0
7973 | 577.25 | 0 | 24.1 | 0 | 0 | 0 | 0 | 0.57892 | 0.57892 | 0 | 0 | 0 | 74.3563 | 577.8289 | 0 | 0.05921 | 4.3265 | 0 | 0 | 230.6383 | 0 | off_peak | 577.25 | 0 | 100 | 0 | 0 | 100 | 0 | 0
7974 | 624.67 | 0 | 24 | 0 | 0 | 0 | 0 | 0.03739 | 0.03739 | 0 | 0 | 0 | 74.3912 | 624.7074 | 0 | 0.05921 | 3.7879 | 0 | 0 | 230.6383 | 0 | off_peak | 624.67 | 0 | 100 | 0 | 0 | 100 | 0 | 0
7975 | 701.78 | 0 | 24.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3912 | 701.78 | 0 | 0.088511 | 3.5089 | 0 | 0 | 230.6383 | 0 | on_peak | 701.78 |  |  | 0 | 0 | 100 | 0 | 0
7976 | 744.06 | 55.2306 | 24.3 | 11.2124 | 11.2124 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3912 | 732.8476 | 0 | 0.088511 | 3.3484 | 0 | 0 | 230.6383 | 11.2124 | on_peak | 732.8476 |  |  | 1.51 | 0 | 98.49 | 37.5441 | 0
7977 | 749.03 | 197.861 | 24.6 | 40.1245 | 40.1245 | 0 | 0 | 0 | 0 | 62.6277 | 62.6277 | 0 | 7.4394 | 646.2777 | 0 | 0.088511 | 3.2179 | 0 | 0 | 230.6383 | 40.1245 | on_peak | 646.2777 |  |  | 5.36 | 8.36 | 86.28 | 129.1185 | 0
7978 | 740.07 | 286.915 | 24.8 | 58.1421 | 58.1421 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 681.9279 | 0 | 0.088511 | 3.1943 | 0 | 0 | 230.6383 | 58.1421 | on_peak | 681.9279 |  |  | 7.86 | 0 | 92.14 | 185.7217 | 0
7979 | 715.1 | 358.56 | 24.9 | 72.6345 | 72.6345 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 19.0375 | 654.8644 | 0 | 0.05921 | 3.3054 | 0 | 0 | 230.6383 | 72.6345 | off_peak | 642.4655 | 0 | 100 | 10.16 | 0 | 89.84 | 240.0878 | 0
7980 | 790.05 | 438.943 | 24.9 | 88.918 | 88.918 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 30.6357 | 713.531 | 0 | 0.05921 | 3.7566 | 0 | 0 | 230.6383 | 88.918 | off_peak | 701.132 | 0 | 100 | 11.25 | 0 | 88.75 | 334.0265 | 0
7981 | 745.19 | 484.009 | 24.8 | 98.0824 | 98.0824 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 42.2338 | 659.5065 | 0 | 0.05921 | 4.3608 | 0 | 0 | 230.6383 | 98.0824 | off_peak | 647.1076 | 0 | 100 | 13.16 | 0 | 86.84 | 427.7169 | 0
7982 | 841.12 | 387.395 | 24.7 | 78.5322 | 78.5322 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 53.832 | 774.9867 | 0 | 0.05921 | 4.634 | 0 | 0 | 230.6383 | 78.5322 | off_peak | 762.5878 | 0 | 100 | 9.34 | 0 | 90.66 | 363.9151 | 0
7983 | 846.71 | 246.224 | 24.6 | 49.9322 | 49.9322 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 65.4301 | 809.1768 | 0 | 0.05921 | 4.3323 | 0 | 0 | 230.6383 | 49.9322 | off_peak | 796.7778 | 0 | 100 | 5.9 | 0 | 94.1 | 216.3209 | 0
7984 | 852.74 | 127.031 | 24.3 | 25.7886 | 25.7886 | 0 | 0 | 8.9635 | 8.9635 | 0 | 0 | 0 | 73.8147 | 835.9149 | 0 | 0.05921 | 3.6713 | 0 | 0 | 230.6383 | 25.7886 | off_peak | 826.9514 | 0 | 100 | 3.02 | 0 | 96.98 | 94.6775 | 0
7985 | 816.11 | 38.3677 | 24 | 7.7974 | 7.7974 | 0 | 0 | 0.57892 | 0.57892 | 0 | 0 | 0 | 74.3563 | 808.8915 | 0 | 0.05921 | 3.314 | 0 | 0 | 230.6383 | 7.7974 | off_peak | 808.3126 | 0 | 100 | 0.96 | 0 | 99.04 | 25.8404 | 0
7986 | 794.41 | 0 | 23.7 | 0 | 0 | 0 | 0 | 0.03739 | 0.03739 | 0 | 0 | 0 | 74.3912 | 794.4474 | 0 | 0.05921 | 3.0319 | 0 | 0 | 230.6383 | 0 | off_peak | 794.41 | 0 | 100 | 0 | 0 | 100 | 0 | 0
7987 | 819.32 | 0 | 23.7 | 0 | 0 | 0 | 0 | 0 | 0 | 62.6277 | 62.6277 | 0 | 7.4394 | 756.6923 | 0 | 0.088511 | 2.8678 | 62.6277 | 0 | 163.6864 | 62.6277 | on_peak | 756.6923 |  |  | 0 | 7.64 | 92.36 | 179.6045 | 0
7988 | 820.61 | 0 | 23.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 820.61 | 0 | 0.088511 | 2.8171 | 0 | 0 | 163.6864 | 0 | on_peak | 820.61 |  |  | 0 | 0 | 100 | 0 | 0
7989 | 808.91 | 0 | 23.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 808.91 | 0 | 0.088511 | 2.9751 | 0 | 0 | 163.6864 | 0 | on_peak | 808.91 |  |  | 0 | 0 | 100 | 0 | 0
7990 | 779.12 | 0 | 23.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 779.12 | 0 | 0.088511 | 3.4139 | 0 | 0 | 163.6864 | 0 | on_peak | 779.12 |  |  | 0 | 0 | 100 | 0 | 0
7991 | 807.57 | 0 | 23.5 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 19.0375 | 819.9689 | 0 | 0.05921 | 4.1555 | 0 | 0 | 163.6864 | 0 | off_peak | 807.57 | 0 | 100 | 0 | 0 | 100 | 0 | 0
7992 | 780.34 | 0 | 23.5 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 30.6357 | 792.7389 | 0 | 0.05921 | 4.7528 | 0 | 0 | 163.6864 | 0 | off_peak | 780.34 | 0 | 100 | 0 | 0 | 100 | 0 | 0
7993 | 724.6 | 0 | 23.4 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 42.2338 | 736.9989 | 0 | 0.05921 | 5.0657 | 0 | 0 | 163.6864 | 0 | off_peak | 724.6 | 0 | 100 | 0 | 0 | 100 | 0 | 0
7994 | 618.68 | 0 | 23.4 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 53.832 | 631.0789 | 0 | 0.05921 | 4.9781 | 0 | 0 | 163.6864 | 0 | off_peak | 618.68 | 0 | 100 | 0 | 0 | 100 | 0 | 0
7995 | 614.11 | 0 | 23.3 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 65.4301 | 626.5089 | 0 | 0.05921 | 4.7881 | 0 | 0 | 163.6864 | 0 | off_peak | 614.11 | 0 | 100 | 0 | 0 | 100 | 0 | 0
7996 | 609.4 | 0 | 23.2 | 0 | 0 | 0 | 0 | 8.9635 | 8.9635 | 0 | 0 | 0 | 73.8147 | 618.3635 | 0 | 0.05921 | 4.4865 | 0 | 0 | 163.6864 | 0 | off_peak | 609.4 | 0 | 100 | 0 | 0 | 100 | 0 | 0
7997 | 600.55 | 0 | 23.1 | 0 | 0 | 0 | 0 | 0.57892 | 0.57892 | 0 | 0 | 0 | 74.3563 | 601.1289 | 0 | 0.05921 | 4.1446 | 0 | 0 | 163.6864 | 0 | off_peak | 600.55 | 0 | 100 | 0 | 0 | 100 | 0 | 0
7998 | 590.07 | 0 | 22.9 | 0 | 0 | 0 | 0 | 0.03739 | 0.03739 | 0 | 0 | 0 | 74.3912 | 590.1074 | 0 | 0.05921 | 3.7279 | 0 | 0 | 163.6864 | 0 | off_peak | 590.07 | 0 | 100 | 0 | 0 | 100 | 0 | 0
7999 | 593.49 | 0 | 22.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3912 | 593.49 | 0 | 0.088511 | 3.4242 | 0 | 0 | 163.6864 | 0 | on_peak | 593.49 |  |  | 0 | 0 | 100 | 0 | 0
8000 | 721.37 | 73.5965 | 22.9 | 15.016 | 15.016 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3912 | 706.354 | 0 | 0.088511 | 3.23 | 0 | 0 | 163.6864 | 15.016 | on_peak | 706.354 |  |  | 2.08 | 0 | 97.92 | 48.5014 | 0
8001 | 738.73 | 247.357 | 23 | 50.4504 | 50.4504 | 0 | 0 | 0 | 0 | 62.6277 | 62.6277 | 0 | 7.4394 | 625.6518 | 0 | 0.088511 | 3.1463 | 0 | 0 | 163.6864 | 50.4504 | on_peak | 625.6518 |  |  | 6.83 | 8.48 | 84.69 | 158.7339 | 0
8002 | 771.65 | 389.243 | 23.2 | 79.3325 | 79.3325 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 692.3175 | 0 | 0.088511 | 3.1237 | 0 | 0 | 163.6864 | 79.3325 | on_peak | 692.3175 |  |  | 10.28 | 0 | 89.72 | 247.813 | 0
8003 | 746.16 | 476.498 | 23.5 | 97.0119 | 84.613 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 0 | 19.0375 | 661.547 | 0 | 0.05921 | 3.224 | 0 | 0 | 175.2846 | 84.613 | off_peak | 661.547 | 100 | 0 | 11.34 | 0 | 88.66 | 272.7933 | 0
8004 | 808.26 | 512.083 | 24 | 104.0701 | 104.0701 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 30.6357 | 716.5888 | 0 | 0.05921 | 3.663 | 0 | 0 | 175.2846 | 104.0701 | off_peak | 704.1899 | 0 | 100 | 12.88 | 0 | 87.12 | 381.2048 | 0
8005 | 778.56 | 610.302 | 24.3 | 123.8976 | 111.4987 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 0 | 42.2338 | 667.0613 | 0 | 0.05921 | 4.2927 | 0 | 0 | 186.8827 | 111.4987 | off_peak | 667.0613 | 100 | 0 | 14.32 | 0 | 85.68 | 478.6257 | 0
8006 | 838.13 | 606.401 | 24.6 | 122.973 | 122.973 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 53.832 | 727.5559 | 0 | 0.05921 | 4.5323 | 0 | 0 | 186.8827 | 122.973 | off_peak | 715.157 | 0 | 100 | 14.67 | 0 | 85.33 | 557.3453 | 0
8007 | 815.85 | 489.262 | 24.6 | 99.2182 | 99.2182 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 65.4301 | 729.0307 | 0 | 0.05921 | 4.1529 | 0 | 0 | 186.8827 | 99.2182 | off_peak | 716.6318 | 0 | 100 | 12.16 | 0 | 87.84 | 412.0409 | 0
8008 | 776.83 | 326.932 | 24.5 | 66.3229 | 66.3229 | 0 | 0 | 8.9635 | 8.9635 | 0 | 0 | 0 | 73.8147 | 719.4706 | 0 | 0.05921 | 3.6456 | 0 | 0 | 186.8827 | 66.3229 | off_peak | 710.5071 | 0 | 100 | 8.54 | 0 | 91.46 | 241.7876 | 0
8009 | 786.92 | 138.825 | 24 | 28.2133 | 28.2133 | 0 | 0 | 0.57892 | 0.57892 | 0 | 0 | 0 | 74.3563 | 759.2857 | 0 | 0.05921 | 3.345 | 0 | 0 | 186.8827 | 28.2133 | off_peak | 758.7067 | 0 | 100 | 3.59 | 0 | 96.41 | 94.3739 | 0
8010 | 764.48 | 0 | 23.4 | 0 | 0 | 0 | 0 | 0.03739 | 0.03739 | 0 | 0 | 0 | 74.3912 | 764.5174 | 0 | 0.05921 | 3.2441 | 0 | 0 | 186.8827 | 0 | off_peak | 764.48 | 0 | 100 | 0 | 0 | 100 | 0 | 0
8011 | 755.82 | 0 | 23.1 | 0 | 0 | 0 | 0 | 0 | 0 | 62.6277 | 62.6277 | 0 | 7.4394 | 693.1923 | 0 | 0.088511 | 3.3663 | 0 | 0 | 186.8827 | 0 | on_peak | 693.1923 |  |  | 0 | 8.29 | 91.71 | 0 | 0
8012 | 792.56 | 0 | 19.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 792.56 | 0 | 0.088511 | 3.6243 | 0 | 0 | 186.8827 | 0 | on_peak | 792.56 |  |  | 0 | 0 | 100 | 0 | 0
8013 | 743.72 | 0 | 19.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 743.72 | 0 | 0.088511 | 4.0287 | 0 | 0 | 186.8827 | 0 | on_peak | 743.72 |  |  | 0 | 0 | 100 | 0 | 0
8014 | 745.65 | 0 | 19.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 745.65 | 0 | 0.088511 | 4.4585 | 0 | 0 | 186.8827 | 0 | on_peak | 745.65 |  |  | 0 | 0 | 100 | 0 | 0
8015 | 737.9 | 0 | 19.4 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 19.0375 | 750.2989 | 0 | 0.05921 | 4.7881 | 0 | 0 | 186.8827 | 0 | off_peak | 737.9 | 0 | 100 | 0 | 0 | 100 | 0 | 0
8016 | 700.09 | 0 | 19.2 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 30.6357 | 712.4889 | 0 | 0.05921 | 5.2189 | 0 | 0 | 186.8827 | 0 | off_peak | 700.09 | 0 | 100 | 0 | 0 | 100 | 0 | 0
8017 | 674.2 | 0 | 19 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 42.2338 | 686.5989 | 0 | 0.05921 | 5.3984 | 0 | 0 | 186.8827 | 0 | off_peak | 674.2 | 0 | 100 | 0 | 0 | 100 | 0 | 0
8018 | 626.16 | 0 | 18.9 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 53.832 | 638.5589 | 0 | 0.05921 | 5.2709 | 0 | 0 | 186.8827 | 0 | off_peak | 626.16 | 0 | 100 | 0 | 0 | 100 | 0 | 0
8019 | 551.83 | 0 | 18.9 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 65.4301 | 564.2289 | 0 | 0.05921 | 5.0009 | 0 | 0 | 186.8827 | 0 | off_peak | 551.83 | 0 | 100 | 0 | 0 | 100 | 0 | 0
8020 | 591.1 | 0 | 18.9 | 0 | 0 | 0 | 0 | 8.9635 | 8.9635 | 0 | 0 | 0 | 73.8147 | 600.0635 | 0 | 0.05921 | 4.6182 | 0 | 0 | 186.8827 | 0 | off_peak | 591.1 | 0 | 100 | 0 | 0 | 100 | 0 | 0
8021 | 604.18 | 0 | 18.9 | 0 | 0 | 0 | 0 | 0.57892 | 0.57892 | 0 | 0 | 0 | 74.3563 | 604.7589 | 0 | 0.05921 | 4.2272 | 0 | 0 | 186.8827 | 0 | off_peak | 604.18 | 0 | 100 | 0 | 0 | 100 | 0 | 0
8022 | 617.26 | 0 | 19 | 0 | 0 | 0 | 0 | 0.03739 | 0.03739 | 0 | 0 | 0 | 74.3912 | 617.2974 | 0 | 0.05921 | 3.7587 | 0 | 0 | 186.8827 | 0 | off_peak | 617.26 | 0 | 100 | 0 | 0 | 100 | 0 | 0
8023 | 693.54 | 0 | 19.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3912 | 693.54 | 0 | 0.088511 | 3.1779 | 0 | 0 | 186.8827 | 0 | on_peak | 693.54 |  |  | 0 | 0 | 100 | 0 | 0
8024 | 718.84 | 62.8728 | 19.8 | 12.9701 | 12.9701 | 0 | 0 | 0 | 0 | 62.6277 | 62.6277 | 0 | 7.4394 | 643.2422 | 0 | 0.088511 | 2.9383 | 0 | 0 | 186.8827 | 12.9701 | on_peak | 643.2422 |  |  | 1.8 | 8.71 | 89.48 | 38.1103 | 0
8025 | 737.18 | 257.791 | 20.5 | 53.0484 | 53.0484 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 684.1316 | 0 | 0.088511 | 2.7897 | 0 | 0 | 186.8827 | 53.0484 | on_peak | 684.1316 |  |  | 7.2 | 0 | 92.8 | 147.9865 | 0
8026 | 758.04 | 423.971 | 21.3 | 86.9977 | 86.9977 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 671.0423 | 0 | 0.088511 | 2.6929 | 0 | 0 | 186.8827 | 86.9977 | on_peak | 671.0423 |  |  | 11.48 | 0 | 88.52 | 234.276 | 0
8027 | 788.25 | 467.26 | 22.1 | 95.608 | 95.608 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 19.0375 | 705.041 | 0 | 0.05921 | 2.7303 | 0 | 0 | 186.8827 | 95.608 | off_peak | 692.642 | 0 | 100 | 12.13 | 0 | 87.87 | 261.0363 | 0
8028 | 823.48 | 311.743 | 22.8 | 63.6279 | 51.229 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 0 | 30.6357 | 772.251 | 0 | 0.05921 | 2.9998 | 0 | 0 | 198.4809 | 51.229 | off_peak | 772.251 | 100 | 0 | 6.22 | 0 | 93.78 | 153.6787 | 0
8029 | 822.97 | 116.554 | 23.3 | 23.7466 | 23.7466 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 42.2338 | 811.6223 | 0 | 0.05921 | 3.5939 | 0 | 0 | 198.4809 | 23.7466 | off_peak | 799.2234 | 0 | 100 | 2.89 | 0 | 97.11 | 85.3437 | 0
8030 | 855.72 | 324.432 | 23.7 | 66.0049 | 66.0049 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 53.832 | 802.114 | 0 | 0.05921 | 3.8189 | 0 | 0 | 198.4809 | 66.0049 | off_peak | 789.7151 | 0 | 100 | 7.71 | 0 | 92.29 | 252.0674 | 0
8031 | 832.84 | 337.297 | 23.8 | 68.5977 | 68.5977 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 65.4301 | 776.6412 | 0 | 0.05921 | 3.9149 | 0 | 0 | 198.4809 | 68.5977 | off_peak | 764.2423 | 0 | 100 | 8.24 | 0 | 91.76 | 268.5503 | 0
8032 | 787.03 | 309.939 | 23.7 | 63.0564 | 54.0928 | 0 | 8.9635 | 8.9635 | 0 | 0 | 0 | 0 | 73.8147 | 732.9372 | 0 | 0.05921 | 3.9168 | 0 | 0 | 206.8655 | 54.0928 | off_peak | 732.9372 | 100 | 0 | 6.87 | 0 | 93.13 | 211.8726 | 0
8033 | 791.36 | 131.817 | 23.3 | 26.8563 | 26.2774 | 0 | 0.57892 | 0.57892 | 0 | 0 | 0 | 0 | 74.3563 | 765.0826 | 0 | 0.05921 | 4.1267 | 0 | 0 | 207.407 | 26.2774 | off_peak | 765.0826 | 100 | 0 | 3.32 | 0 | 96.68 | 108.4393 | 0
8034 | 757.87 | 0 | 22.8 | 0 | 0 | 0 | 0 | 0.03739 | 0.03739 | 0 | 0 | 0 | 74.3912 | 757.9074 | 0 | 0.05921 | 4.429 | 0 | 0 | 207.407 | 0 | off_peak | 757.87 | 0 | 100 | 0 | 0 | 100 | 0 | 0
8035 | 780.36 | 0 | 22.5 | 0 | 0 | 0 | 0 | 0 | 0 | 57.3333 | 57.3333 | 0 | 13.0994 | 723.0267 | 0 | 0.088511 | 4.862 | 0 | 0 | 207.407 | 0 | on_peak | 723.0267 |  |  | 0 | 7.35 | 92.65 | 0 | 0
8036 | 813.53 | 0 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 5.2944 | 5.2944 | 0 | 7.4394 | 808.2356 | 0 | 0.088511 | 5.1492 | 5.2944 | 0 | 201.747 | 5.2944 | on_peak | 808.2356 |  |  | 0 | 0.65 | 99.35 | 27.262 | 0
8037 | 762.37 | 0 | 21.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 762.37 | 0 | 0.088511 | 5.4467 | 0 | 0 | 201.747 | 0 | on_peak | 762.37 |  |  | 0 | 0 | 100 | 0 | 0
8038 | 734.39 | 0 | 21.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 734.39 | 0 | 0.088511 | 5.6563 | 0 | 0 | 201.747 | 0 | on_peak | 734.39 |  |  | 0 | 0 | 100 | 0 | 0
8039 | 758.62 | 0 | 21.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 758.62 | 0 | 0.05921 | 5.9538 | 0 | 0 | 201.747 | 0 | off_peak | 758.62 |  |  | 0 | 0 | 100 | 0 | 0
8040 | 724.53 | 0 | 20.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 724.53 | 0 | 0.05921 | 6.1008 | 0 | 0 | 201.747 | 0 | off_peak | 724.53 |  |  | 0 | 0 | 100 | 0 | 0
8041 | 659.4 | 0 | 20.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 659.4 | 0 | 0.05921 | 6.0464 | 0 | 0 | 201.747 | 0 | off_peak | 659.4 |  |  | 0 | 0 | 100 | 0 | 0
8042 | 632.95 | 0 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 632.95 | 0 | 0.05921 | 5.7369 | 0 | 0 | 201.747 | 0 | off_peak | 632.95 |  |  | 0 | 0 | 100 | 0 | 0
8043 | 591.66 | 0 | 19.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 591.66 | 0 | 0.05921 | 5.4872 | 0 | 0 | 201.747 | 0 | off_peak | 591.66 |  |  | 0 | 0 | 100 | 0 | 0
8044 | 600.3 | 0 | 19.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 600.3 | 0 | 0.05921 | 5.1764 | 0 | 0 | 201.747 | 0 | off_peak | 600.3 |  |  | 0 | 0 | 100 | 0 | 0
8045 | 592.24 | 0 | 19.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 592.24 | 0 | 0.05921 | 4.7516 | 0 | 0 | 201.747 | 0 | off_peak | 592.24 |  |  | 0 | 0 | 100 | 0 | 0
8046 | 649.26 | 0 | 18.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 649.26 | 0 | 0.05921 | 4.2911 | 0 | 0 | 201.747 | 0 | off_peak | 649.26 |  |  | 0 | 0 | 100 | 0 | 0
8047 | 705.51 | 0 | 18.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 705.51 | 0 | 0.05921 | 3.8528 | 0 | 0 | 201.747 | 0 | off_peak | 705.51 |  |  | 0 | 0 | 100 | 0 | 0
8048 | 708.08 | 76.2188 | 18.8 | 15.7788 | 3.3799 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 0 | 19.0375 | 704.7001 | 0 | 0.05921 | 3.4679 | 0 | 0 | 213.3452 | 3.3799 | off_peak | 704.7001 | 100 | 0 | 0.48 | 0 | 99.52 | 11.7211 | 0
8049 | 738.83 | 255.819 | 19.3 | 52.8664 | 52.8664 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19.0375 | 685.9636 | 0 | 0.05921 | 3.2395 | 0 | 0 | 213.3452 | 52.8664 | off_peak | 685.9636 |  |  | 7.16 | 0 | 92.84 | 171.2603 | 0
8050 | 718.07 | 427.724 | 20.3 | 88.0796 | 88.0796 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19.0375 | 629.9904 | 0 | 0.05921 | 3.0905 | 0 | 0 | 213.3452 | 88.0796 | off_peak | 629.9904 |  |  | 12.27 | 0 | 87.73 | 272.207 | 0
8051 | 736.24 | 538.943 | 21.5 | 110.5111 | 110.5111 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19.0375 | 625.7289 | 0 | 0.05921 | 3.0516 | 0 | 0 | 213.3452 | 110.5111 | off_peak | 625.7289 |  |  | 15.01 | 0 | 84.99 | 337.232 | 0
8052 | 796.62 | 619.214 | 22.5 | 126.5194 | 126.5194 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19.0375 | 670.1006 | 0 | 0.05921 | 3.1299 | 0 | 0 | 213.3452 | 126.5194 | off_peak | 670.1006 |  |  | 15.88 | 0 | 84.12 | 395.9939 | 0
8053 | 757.31 | 645.809 | 23.2 | 131.6238 | 131.6238 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19.0375 | 625.6862 | 0 | 0.05921 | 3.3557 | 0 | 0 | 213.3452 | 131.6238 | off_peak | 625.6862 |  |  | 17.38 | 0 | 82.62 | 441.6875 | 0
8054 | 686.23 | 463.948 | 23.7 | 94.3892 | 94.3892 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19.0375 | 591.8408 | 0 | 0.05921 | 3.662 | 0 | 0 | 213.3452 | 94.3892 | off_peak | 591.8408 |  |  | 13.75 | 0 | 86.25 | 345.6557 | 0
8055 | 693.61 | 347.674 | 24 | 70.6574 | 70.6574 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19.0375 | 622.9526 | 0 | 0.05921 | 4.1233 | 0 | 0 | 213.3452 | 70.6574 | off_peak | 622.9526 |  |  | 10.19 | 0 | 89.81 | 291.3417 | 0
8056 | 693.82 | 320.318 | 24 | 65.0979 | 65.0979 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 30.6357 | 641.121 | 0 | 0.05921 | 4.64 | 0 | 0 | 213.3452 | 65.0979 | off_peak | 628.7221 | 0 | 100 | 9.38 | 0 | 90.62 | 302.0515 | 0
8057 | 694.09 | 126.376 | 23.5 | 25.7293 | 25.7293 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30.6357 | 668.3607 | 0 | 0.05921 | 5.1315 | 0 | 0 | 213.3452 | 25.7293 | off_peak | 668.3607 |  |  | 3.71 | 0 | 96.29 | 132.0304 | 0
8058 | 637.97 | 0 | 22.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30.6357 | 637.97 | 0 | 0.05921 | 5.6278 | 0 | 0 | 213.3452 | 0 | off_peak | 637.97 |  |  | 0 | 0 | 100 | 0 | 0
8059 | 584.03 | 0 | 22.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30.6357 | 584.03 | 0 | 0.05921 | 5.8628 | 0 | 0 | 213.3452 | 0 | off_peak | 584.03 |  |  | 0 | 0 | 100 | 0 | 0
8060 | 606.93 | 0 | 22.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30.6357 | 606.93 | 0 | 0.05921 | 6.1233 | 0 | 0 | 213.3452 | 0 | off_peak | 606.93 |  |  | 0 | 0 | 100 | 0 | 0
8061 | 568.67 | 0 | 22.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30.6357 | 568.67 | 0 | 0.05921 | 6.3492 | 0 | 0 | 213.3452 | 0 | off_peak | 568.67 |  |  | 0 | 0 | 100 | 0 | 0
8062 | 583.35 | 0 | 21.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30.6357 | 583.35 | 0 | 0.05921 | 6.3652 | 0 | 0 | 213.3452 | 0 | off_peak | 583.35 |  |  | 0 | 0 | 100 | 0 | 0
8063 | 588.85 | 0 | 21.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30.6357 | 588.85 | 0 | 0.05921 | 6.4393 | 0 | 0 | 213.3452 | 0 | off_peak | 588.85 |  |  | 0 | 0 | 100 | 0 | 0
8064 | 593.48 | 0 | 21.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30.6357 | 593.48 | 0 | 0.05921 | 6.3645 | 0 | 0 | 213.3452 | 0 | off_peak | 593.48 |  |  | 0 | 0 | 100 | 0 | 0
8065 | 584.87 | 0 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30.6357 | 584.87 | 0 | 0.05921 | 6.2535 | 0 | 0 | 213.3452 | 0 | off_peak | 584.87 |  |  | 0 | 0 | 100 | 0 | 0
8066 | 575.64 | 0 | 20.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30.6357 | 575.64 | 0 | 0.05921 | 5.923 | 0 | 0 | 213.3452 | 0 | off_peak | 575.64 |  |  | 0 | 0 | 100 | 0 | 0
8067 | 596.9 | 0 | 20.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30.6357 | 596.9 | 0 | 0.05921 | 5.6633 | 0 | 0 | 213.3452 | 0 | off_peak | 596.9 |  |  | 0 | 0 | 100 | 0 | 0
8068 | 585.62 | 0 | 20.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30.6357 | 585.62 | 0 | 0.05921 | 5.3072 | 0 | 0 | 213.3452 | 0 | off_peak | 585.62 |  |  | 0 | 0 | 100 | 0 | 0
8069 | 576.18 | 0 | 20.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30.6357 | 576.18 | 0 | 0.05921 | 4.9316 | 0 | 0 | 213.3452 | 0 | off_peak | 576.18 |  |  | 0 | 0 | 100 | 0 | 0
8070 | 647.2 | 0 | 20.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30.6357 | 647.2 | 0 | 0.05921 | 4.4044 | 0 | 0 | 213.3452 | 0 | off_peak | 647.2 |  |  | 0 | 0 | 100 | 0 | 0
8071 | 699.86 | 0 | 20.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30.6357 | 699.86 | 0 | 0.05921 | 3.9389 | 0 | 0 | 213.3452 | 0 | off_peak | 699.86 |  |  | 0 | 0 | 100 | 0 | 0
8072 | 723.79 | 68.8243 | 20.8 | 14.1476 | 1.7487 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 0 | 42.2338 | 722.0413 | 0 | 0.05921 | 3.554 | 0 | 0 | 224.9433 | 1.7487 | off_peak | 722.0413 | 100 | 0 | 0.24 | 0 | 99.76 | 6.2149 | 0
8073 | 731.5 | 229.816 | 21.4 | 47.1409 | 47.1409 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 42.2338 | 684.3591 | 0 | 0.05921 | 3.2627 | 0 | 0 | 224.9433 | 47.1409 | off_peak | 684.3591 |  |  | 6.44 | 0 | 93.56 | 153.8079 | 0
8074 | 714.4 | 416.469 | 22.2 | 85.1851 | 85.1851 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 42.2338 | 629.2149 | 0 | 0.05921 | 3.0968 | 0 | 0 | 224.9433 | 85.1851 | off_peak | 629.2149 |  |  | 11.92 | 0 | 88.08 | 263.799 | 0
8075 | 699.44 | 556.09 | 23.2 | 113.3379 | 113.3379 | 0 | 0 | 8.7263 | 8.7263 | 0 | 0 | 0 | 50.3966 | 594.8284 | 0 | 0.05921 | 3.0193 | 0 | 0 | 224.9433 | 113.3379 | off_peak | 586.1021 | 0 | 100 | 16.2 | 0 | 83.8 | 342.2059 | 0
8076 | 736.36 | 586.178 | 24 | 119.1284 | 119.1284 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50.3966 | 617.2316 | 0 | 0.05921 | 3.0506 | 0 | 0 | 224.9433 | 119.1284 | off_peak | 617.2316 |  |  | 16.18 | 0 | 83.82 | 363.4077 | 0
8077 | 722.26 | 447.664 | 24.4 | 90.8478 | 90.8478 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 61.9947 | 643.8112 | 0 | 0.05921 | 3.1905 | 0 | 0 | 224.9433 | 90.8478 | off_peak | 631.4122 | 0 | 100 | 12.58 | 0 | 87.42 | 289.8526 | 0
8078 | 724.38 | 469.165 | 24.6 | 95.1427 | 95.1427 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 61.9947 | 629.2373 | 0 | 0.05921 | 3.4825 | 0 | 0 | 224.9433 | 95.1427 | off_peak | 629.2373 |  |  | 13.13 | 0 | 86.87 | 331.3385 | 0
8079 | 708.18 | 381.567 | 24.7 | 77.3508 | 77.3508 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 61.9947 | 630.8292 | 0 | 0.05921 | 3.943 | 0 | 0 | 224.9433 | 77.3508 | off_peak | 630.8292 |  |  | 10.92 | 0 | 89.08 | 304.9955 | 0
8080 | 750.17 | 289.907 | 24.5 | 58.8118 | 58.8118 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 61.9947 | 691.3582 | 0 | 0.05921 | 4.5004 | 0 | 0 | 224.9433 | 58.8118 | off_peak | 691.3582 |  |  | 7.84 | 0 | 92.16 | 264.6759 | 0
8081 | 729.39 | 110.784 | 24 | 22.5145 | 10.1156 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 0 | 73.5928 | 719.2744 | 0 | 0.05921 | 4.9505 | 0 | 0 | 236.5415 | 10.1156 | off_peak | 719.2744 | 100 | 0 | 1.39 | 0 | 98.61 | 50.0768 | 0
8082 | 646 | 0 | 23.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 73.5928 | 646 | 0 | 0.05921 | 5.3099 | 0 | 0 | 236.5415 | 0 | off_peak | 646 |  |  | 0 | 0 | 100 | 0 | 0
8083 | 610.44 | 0 | 23.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 73.5928 | 610.44 | 0 | 0.05921 | 5.6828 | 0 | 0 | 236.5415 | 0 | off_peak | 610.44 |  |  | 0 | 0 | 100 | 0 | 0
8084 | 593.79 | 0 | 23.3 | 0 | 0 | 0 | 0 | 0.80079 | 0.80079 | 0 | 0 | 0 | 74.3419 | 594.5908 | 0 | 0.05921 | 6.0088 | 0 | 0 | 236.5415 | 0 | off_peak | 593.79 | 0 | 100 | 0 | 0 | 100 | 0 | 0
8085 | 571.84 | 0 | 23.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3419 | 571.84 | 0 | 0.05921 | 6.2145 | 0 | 0 | 236.5415 | 0 | off_peak | 571.84 |  |  | 0 | 0 | 100 | 0 | 0
8086 | 624.4 | 0 | 23.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3419 | 624.4 | 0 | 0.05921 | 6.4375 | 0 | 0 | 236.5415 | 0 | off_peak | 624.4 |  |  | 0 | 0 | 100 | 0 | 0
8087 | 595.57 | 0 | 23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3419 | 595.57 | 0 | 0.05921 | 6.6548 | 0 | 0 | 236.5415 | 0 | off_peak | 595.57 |  |  | 0 | 0 | 100 | 0 | 0
8088 | 582.06 | 0 | 23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3419 | 582.06 | 0 | 0.05921 | 6.7331 | 0 | 0 | 236.5415 | 0 | off_peak | 582.06 |  |  | 0 | 0 | 100 | 0 | 0
8089 | 625.55 | 0 | 23 | 0 | 0 | 0 | 0 | 0.05172 | 0.05172 | 0 | 0 | 0 | 74.3903 | 625.6017 | 0 | 0.05921 | 6.6764 | 0 | 0 | 236.5415 | 0 | off_peak | 625.55 | 0 | 100 | 0 | 0 | 100 | 0 | 0
8090 | 577.74 | 0 | 22.9 | 0 | 0 | 0 | 0 | 0.0033404 | 0.0033404 | 0 | 0 | 0 | 74.3934 | 577.7433 | 0 | 0.05921 | 6.3324 | 0 | 0 | 236.5415 | 0 | off_peak | 577.74 | 0 | 100 | 0 | 0 | 100 | 0 | 0
8091 | 578.8 | 0 | 22.9 | 0 | 0 | 0 | 0 | 0.00021574 | 0.00021574 | 0 | 0 | 0 | 74.3936 | 578.8002 | 0 | 0.05921 | 5.9753 | 0 | 0 | 236.5415 | 0 | off_peak | 578.8 | 0 | 100 | 0 | 0 | 100 | 0 | 0
8092 | 577 | 0 | 22.8 | 0 | 0 | 0 | 0 | 1.4896e-05 | 1.4896e-05 | 0 | 0 | 0 | 74.3936 | 577 | 0 | 0.05921 | 5.5297 | 0 | 0 | 236.5415 | 0 | off_peak | 577 | 0 | 100 | 0 | 0 | 100 | 0 | 0
8093 | 611.26 | 0 | 22.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 611.26 | 0 | 0.05921 | 4.9385 | 0 | 0 | 236.5415 | 0 | off_peak | 611.26 |  |  | 0 | 0 | 100 | 0 | 0
8094 | 640.39 | 0 | 22.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 640.39 | 0 | 0.05921 | 4.2473 | 0 | 0 | 236.5415 | 0 | off_peak | 640.39 |  |  | 0 | 0 | 100 | 0 | 0
8095 | 745.25 | 0 | 23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 745.25 | 0 | 0.088511 | 3.7546 | 0 | 0 | 236.5415 | 0 | on_peak | 745.25 |  |  | 0 | 0 | 100 | 0 | 0
8096 | 733.07 | 76.1285 | 23.5 | 15.4993 | 15.4993 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 717.5707 | 0 | 0.088511 | 3.3544 | 0 | 0 | 236.5415 | 15.4993 | on_peak | 717.5707 |  |  | 2.11 | 0 | 97.89 | 51.9902 | 0
8097 | 760.24 | 258.204 | 24.1 | 52.4557 | 52.4557 | 0 | 0 | 0 | 0 | 62.63 | 62.63 | 0 | 7.4394 | 645.1543 | 0 | 0.088511 | 3.1216 | 0 | 0 | 236.5415 | 52.4557 | on_peak | 645.1543 |  |  | 6.9 | 8.24 | 84.86 | 163.745 | 0
8098 | 794.56 | 383.601 | 24.6 | 77.7911 | 77.7911 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 716.7689 | 0 | 0.088511 | 3.0152 | 0 | 0 | 236.5415 | 77.7911 | on_peak | 716.7689 |  |  | 9.79 | 0 | 90.21 | 234.5539 | 0
8099 | 760.75 | 373.111 | 24.9 | 75.5822 | 63.1832 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 0 | 19.0375 | 697.5668 | 0 | 0.05921 | 3.043 | 0 | 0 | 248.1396 | 63.1832 | off_peak | 697.5668 | 100 | 0 | 8.31 | 0 | 91.69 | 192.2685 | 0
8100 | 853.18 | 326.262 | 25.1 | 66.0443 | 53.6453 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 0 | 30.6357 | 799.5347 | 0 | 0.05921 | 3.3017 | 0 | 0 | 259.7378 | 53.6453 | off_peak | 799.5347 | 100 | 0 | 6.29 | 0 | 93.71 | 177.1188 | 0
8101 | 786.12 | 499.173 | 25.2 | 101.0098 | 101.0098 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 42.2338 | 697.5092 | 0 | 0.05921 | 3.7831 | 0 | 0 | 259.7378 | 101.0098 | off_peak | 685.1102 | 0 | 100 | 12.85 | 0 | 87.15 | 382.1323 | 0
8102 | 844.88 | 579.453 | 25.2 | 117.2547 | 117.2547 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 53.832 | 740.0242 | 0 | 0.05921 | 4.0681 | 0 | 0 | 259.7378 | 117.2547 | off_peak | 727.6253 | 0 | 100 | 13.88 | 0 | 86.12 | 477.0094 | 0
8103 | 886.24 | 473.998 | 25.1 | 95.95 | 95.95 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 65.4301 | 802.6889 | 0 | 0.05921 | 4.2975 | 0 | 0 | 259.7378 | 95.95 | off_peak | 790.29 | 0 | 100 | 10.83 | 0 | 89.17 | 412.3416 | 0
8104 | 840.19 | 312.629 | 25 | 63.3074 | 63.3074 | 0 | 0 | 8.9635 | 8.9635 | 0 | 0 | 0 | 73.8147 | 785.8462 | 0 | 0.05921 | 4.5265 | 0 | 0 | 259.7378 | 63.3074 | off_peak | 776.8826 | 0 | 100 | 7.53 | 0 | 92.47 | 286.5627 | 0
8105 | 832.37 | 132.543 | 24.6 | 26.8786 | 26.2997 | 0 | 0.57892 | 0.57892 | 0 | 0 | 0 | 0 | 74.3563 | 806.0703 | 0 | 0.05921 | 4.6909 | 0 | 0 | 260.2793 | 26.2997 | off_peak | 806.0703 | 100 | 0 | 3.16 | 0 | 96.84 | 123.368 | 0
8106 | 840.72 | 0 | 24.2 | 0 | 0 | 0 | 0 | 0.03739 | 0.03739 | 0 | 0 | 0 | 74.3912 | 840.7574 | 0 | 0.05921 | 5.0258 | 0 | 0 | 260.2793 | 0 | off_peak | 840.72 | 0 | 100 | 0 | 0 | 100 | 0 | 0
8107 | 819.17 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 10.9344 | 10.9344 | 0 | 62.7018 | 808.2356 | 0 | 0.088511 | 5.1722 | 0 | 0 | 260.2793 | 0 | on_peak | 808.2356 |  |  | 0 | 1.33 | 98.67 | 0 | 0
8108 | 829.19 | 0 | 23.9 | 0 | 0 | 0 | 0 | 0 | 0 | 20.9544 | 20.9544 | 0 | 40.3006 | 808.2356 | 0 | 0.088511 | 5.3286 | 0 | 0 | 260.2793 | 0 | on_peak | 808.2356 |  |  | 0 | 2.53 | 97.47 | 0 | 0
8109 | 834.85 | 0 | 23.9 | 0 | 0 | 0 | 0 | 0 | 0 | 26.6144 | 26.6144 | 0 | 11.8486 | 808.2356 | 0 | 0.088511 | 5.4614 | 26.6144 | 0 | 231.8273 | 26.6144 | on_peak | 808.2356 |  |  | 0 | 3.19 | 96.81 | 145.3533 | 0
8110 | 812.36 | 0 | 23.9 | 0 | 0 | 0 | 0 | 0 | 0 | 4.1244 | 4.1244 | 0 | 7.4394 | 808.2356 | 0 | 0.088511 | 5.7825 | 0 | 0 | 231.8273 | 0 | on_peak | 808.2356 |  |  | 0 | 0.51 | 99.49 | 0 | 0
8111 | 839.35 | 0 | 23.8 | 0 | 0 | 0 | 0 | 1.4074 | 1.4074 | 0 | 0 | 0 | 8.7559 | 840.7574 | 0 | 0.05921 | 5.9209 | 0 | 0 | 231.8273 | 0 | off_peak | 839.35 | 0 | 100 | 0 | 0 | 100 | 0 | 0
8112 | 802.8 | 0 | 23.7 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 20.354 | 815.1989 | 0 | 0.05921 | 6.257 | 0 | 0 | 231.8273 | 0 | off_peak | 802.8 | 0 | 100 | 0 | 0 | 100 | 0 | 0
8113 | 737.37 | 0 | 23.7 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 31.9522 | 749.7689 | 0 | 0.05921 | 6.3312 | 0 | 0 | 231.8273 | 0 | off_peak | 737.37 | 0 | 100 | 0 | 0 | 100 | 0 | 0
8114 | 669.58 | 0 | 23.6 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 43.5503 | 681.9789 | 0 | 0.05921 | 6.0736 | 0 | 0 | 231.8273 | 0 | off_peak | 669.58 | 0 | 100 | 0 | 0 | 100 | 0 | 0
8115 | 640.17 | 0 | 23.6 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 55.1484 | 652.5689 | 0 | 0.05921 | 5.7642 | 0 | 0 | 231.8273 | 0 | off_peak | 640.17 | 0 | 100 | 0 | 0 | 100 | 0 | 0
8116 | 663.43 | 0 | 23.5 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 66.7466 | 675.8289 | 0 | 0.05921 | 5.2719 | 0 | 0 | 231.8273 | 0 | off_peak | 663.43 | 0 | 100 | 0 | 0 | 100 | 0 | 0
8117 | 633.13 | 0 | 23.5 | 0 | 0 | 0 | 0 | 7.6471 | 7.6471 | 0 | 0 | 0 | 73.8998 | 640.7771 | 0 | 0.05921 | 4.7312 | 0 | 0 | 231.8273 | 0 | off_peak | 633.13 | 0 | 100 | 0 | 0 | 100 | 0 | 0
8118 | 715.19 | 0 | 23.6 | 0 | 0 | 0 | 0 | 0.49389 | 0.49389 | 0 | 0 | 0 | 74.3617 | 715.6839 | 0 | 0.05921 | 4.1168 | 0 | 0 | 231.8273 | 0 | off_peak | 715.19 | 0 | 100 | 0 | 0 | 100 | 0 | 0
8119 | 763.88 | 0 | 23.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3617 | 763.88 | 0 | 0.088511 | 3.5719 | 0 | 0 | 231.8273 | 0 | on_peak | 763.88 |  |  | 0 | 0 | 100 | 0 | 0
8120 | 744.28 | 70.1718 | 24.4 | 14.2405 | 14.2405 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3617 | 730.0395 | 0 | 0.088511 | 3.1921 | 0 | 0 | 231.8273 | 14.2405 | on_peak | 730.0395 |  |  | 1.91 | 0 | 98.09 | 45.4568 | 0
8121 | 807.09 | 244.621 | 25.1 | 49.5179 | 49.5179 | 0 | 0 | 0 | 0 | 62.6002 | 62.6002 | 0 | 7.4394 | 694.9719 | 0 | 0.088511 | 2.9653 | 0 | 0 | 231.8273 | 49.5179 | on_peak | 694.9719 |  |  | 6.14 | 7.76 | 86.11 | 146.8344 | 0
8122 | 809.97 | 412.485 | 25.6 | 83.3478 | 83.3478 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 726.6222 | 0 | 0.088511 | 2.861 | 0 | 0 | 231.8273 | 83.3478 | on_peak | 726.6222 |  |  | 10.29 | 0 | 89.71 | 238.4539 | 0
8123 | 771.03 | 541.627 | 26 | 109.2846 | 109.2846 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 19.0375 | 674.1443 | 0 | 0.05921 | 2.9141 | 0 | 0 | 231.8273 | 109.2846 | off_peak | 661.7454 | 0 | 100 | 14.17 | 0 | 85.83 | 318.4616 | 0
8124 | 865.51 | 614.396 | 26.3 | 123.8329 | 123.8329 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 30.6357 | 754.076 | 0 | 0.05921 | 3.1791 | 0 | 0 | 231.8273 | 123.8329 | off_peak | 741.6771 | 0 | 100 | 14.31 | 0 | 85.69 | 393.6747 | 0
8125 | 808.54 | 626.599 | 26.4 | 126.2468 | 126.2468 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 42.2338 | 694.6921 | 0 | 0.05921 | 3.6155 | 0 | 0 | 231.8273 | 126.2468 | off_peak | 682.2932 | 0 | 100 | 15.61 | 0 | 84.39 | 456.443 | 0
8126 | 851.66 | 572.725 | 26.5 | 115.3505 | 115.3505 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 53.832 | 748.7084 | 0 | 0.05921 | 3.9514 | 0 | 0 | 231.8273 | 115.3505 | off_peak | 736.3095 | 0 | 100 | 13.54 | 0 | 86.46 | 455.8014 | 0
8127 | 858.36 | 463.253 | 26.4 | 93.3359 | 93.3359 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 65.4301 | 777.423 | 0 | 0.05921 | 3.7378 | 0 | 0 | 231.8273 | 93.3359 | off_peak | 765.0241 | 0 | 100 | 10.87 | 0 | 89.13 | 348.8681 | 0
8128 | 787 | 307.622 | 26.1 | 62.0468 | 62.0468 | 0 | 0 | 8.9635 | 8.9635 | 0 | 0 | 0 | 73.8147 | 733.9168 | 0 | 0.05921 | 3.6837 | 0 | 0 | 231.8273 | 62.0468 | off_peak | 724.9532 | 0 | 100 | 7.88 | 0 | 92.12 | 228.5614 | 0
8129 | 797.53 | 89.3448 | 25.6 | 18.0532 | 17.4743 | 0 | 0.57892 | 0.57892 | 0 | 0 | 0 | 0 | 74.3563 | 780.0557 | 0 | 0.05921 | 3.7021 | 0 | 0 | 232.3688 | 17.4743 | off_peak | 780.0557 | 100 | 0 | 2.19 | 0 | 97.81 | 64.6921 | 0
8130 | 819.57 | 0 | 25.1 | 0 | 0 | 0 | 0 | 0.03739 | 0.03739 | 0 | 0 | 0 | 74.3912 | 819.6074 | 0 | 0.05921 | 3.8138 | 0 | 0 | 232.3688 | 0 | off_peak | 819.57 | 0 | 100 | 0 | 0 | 100 | 0 | 0
8131 | 790.5 | 0 | 24.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3912 | 790.5 | 0 | 0.088511 | 4.0061 | 0 | 0 | 232.3688 | 0 | on_peak | 790.5 |  |  | 0 | 0 | 100 | 0 | 0
8132 | 789.19 | 0 | 24.5 | 0 | 0 | 0 | 0 | 0 | 0 | 62.6277 | 62.6277 | 0 | 7.4394 | 726.5623 | 0 | 0.088511 | 4.384 | 62.6277 | 0 | 165.4169 | 62.6277 | on_peak | 726.5623 |  |  | 0 | 7.94 | 92.06 | 274.5612 | 0
8133 | 778.96 | 0 | 24.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 778.96 | 0 | 0.088511 | 4.5915 | 0 | 0 | 165.4169 | 0 | on_peak | 778.96 |  |  | 0 | 0 | 100 | 0 | 0
8134 | 755.61 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 755.61 | 0 | 0.088511 | 4.7817 | 0 | 0 | 165.4169 | 0 | on_peak | 755.61 |  |  | 0 | 0 | 100 | 0 | 0
8135 | 729.13 | 0 | 23.8 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 19.0375 | 741.5289 | 0 | 0.05921 | 5.0874 | 0 | 0 | 165.4169 | 0 | off_peak | 729.13 | 0 | 100 | 0 | 0 | 100 | 0 | 0
8136 | 748.58 | 0 | 23.6 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 30.6357 | 760.9789 | 0 | 0.05921 | 5.4275 | 0 | 0 | 165.4169 | 0 | off_peak | 748.58 | 0 | 100 | 0 | 0 | 100 | 0 | 0
8137 | 686.47 | 0 | 23.4 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 42.2338 | 698.8689 | 0 | 0.05921 | 5.5671 | 0 | 0 | 165.4169 | 0 | off_peak | 686.47 | 0 | 100 | 0 | 0 | 100 | 0 | 0
8138 | 589.72 | 0 | 23.2 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 53.832 | 602.1189 | 0 | 0.05921 | 5.3304 | 0 | 0 | 165.4169 | 0 | off_peak | 589.72 | 0 | 100 | 0 | 0 | 100 | 0 | 0
8139 | 618.54 | 0 | 23.1 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 65.4301 | 630.9389 | 0 | 0.05921 | 5.0395 | 0 | 0 | 165.4169 | 0 | off_peak | 618.54 | 0 | 100 | 0 | 0 | 100 | 0 | 0
8140 | 610.86 | 0 | 23.1 | 0 | 0 | 0 | 0 | 8.9635 | 8.9635 | 0 | 0 | 0 | 73.8147 | 619.8235 | 0 | 0.05921 | 4.6479 | 0 | 0 | 165.4169 | 0 | off_peak | 610.86 | 0 | 100 | 0 | 0 | 100 | 0 | 0
8141 | 584.25 | 0 | 23.1 | 0 | 0 | 0 | 0 | 0.57892 | 0.57892 | 0 | 0 | 0 | 74.3563 | 584.8289 | 0 | 0.05921 | 4.1703 | 0 | 0 | 165.4169 | 0 | off_peak | 584.25 | 0 | 100 | 0 | 0 | 100 | 0 | 0
8142 | 661.78 | 0 | 23.2 | 0 | 0 | 0 | 0 | 0.03739 | 0.03739 | 0 | 0 | 0 | 74.3912 | 661.8174 | 0 | 0.05921 | 3.5286 | 0 | 0 | 165.4169 | 0 | off_peak | 661.78 | 0 | 100 | 0 | 0 | 100 | 0 | 0
8143 | 718.55 | 0 | 23.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3912 | 718.55 | 0 | 0.088511 | 3.1439 | 0 | 0 | 165.4169 | 0 | on_peak | 718.55 |  |  | 0 | 0 | 100 | 0 | 0
8144 | 745.93 | 69.3714 | 23.6 | 14.1185 | 14.1185 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3912 | 731.8115 | 0 | 0.088511 | 2.836 | 0 | 0 | 165.4169 | 14.1185 | on_peak | 731.8115 |  |  | 1.89 | 0 | 98.11 | 40.0407 | 0
8145 | 766.29 | 245.822 | 24.2 | 49.9223 | 49.9223 | 0 | 0 | 0 | 0 | 62.6277 | 62.6277 | 0 | 7.4394 | 653.7399 | 0 | 0.088511 | 2.6695 | 0 | 0 | 165.4169 | 49.9223 | on_peak | 653.7399 |  |  | 6.51 | 8.17 | 85.31 | 133.2669 | 0
8146 | 769.37 | 417.416 | 24.7 | 84.618 | 84.618 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 684.752 | 0 | 0.088511 | 2.6122 | 0 | 0 | 165.4169 | 84.618 | on_peak | 684.752 |  |  | 11 | 0 | 89 | 221.0406 | 0
8147 | 759.79 | 547.265 | 25.2 | 110.7414 | 110.7414 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 19.0375 | 661.4476 | 0 | 0.05921 | 2.7029 | 0 | 0 | 165.4169 | 110.7414 | off_peak | 649.0486 | 0 | 100 | 14.58 | 0 | 85.42 | 299.3256 | 0
8148 | 772.22 | 623.668 | 25.6 | 126.02 | 126.02 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 30.6357 | 658.599 | 0 | 0.05921 | 2.9642 | 0 | 0 | 165.4169 | 126.02 | off_peak | 646.2 | 0 | 100 | 16.32 | 0 | 83.68 | 373.554 | 0
8149 | 665.97 | 636.049 | 25.7 | 128.4753 | 128.4753 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 42.2338 | 549.8936 | 0 | 0.05921 | 3.582 | 0 | 0 | 165.4169 | 128.4753 | off_peak | 537.4947 | 0 | 100 | 19.29 | 0 | 80.71 | 460.2045 | 0
8150 | 716.81 | 584.865 | 25.7 | 118.1367 | 118.1367 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 53.832 | 611.0722 | 0 | 0.05921 | 3.8953 | 0 | 0 | 165.4169 | 118.1367 | off_peak | 598.6733 | 0 | 100 | 16.48 | 0 | 83.52 | 460.1791 | 0
8151 | 754.11 | 475.382 | 25.3 | 96.1609 | 96.1609 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 65.4301 | 670.3481 | 0 | 0.05921 | 3.6604 | 0 | 0 | 165.4169 | 96.1609 | off_peak | 657.9491 | 0 | 100 | 12.75 | 0 | 87.25 | 351.99 | 0
8152 | 673.99 | 317.105 | 24.5 | 64.3293 | 64.3293 | 0 | 0 | 8.9635 | 8.9635 | 0 | 0 | 0 | 73.8147 | 618.6242 | 0 | 0.05921 | 3.1345 | 0 | 0 | 165.4169 | 64.3293 | off_peak | 609.6607 | 0 | 100 | 9.54 | 0 | 90.46 | 201.6385 | 0
8153 | 684.72 | 137.004 | 23.4 | 27.9031 | 27.3242 | 0 | 0.57892 | 0.57892 | 0 | 0 | 0 | 0 | 74.3563 | 657.3958 | 0 | 0.05921 | 2.7734 | 0 | 0 | 165.9585 | 27.3242 | off_peak | 657.3958 | 100 | 0 | 3.99 | 0 | 96.01 | 75.7816 | 0
8154 | 691.99 | 4.75 | 22.4 | 0.97088 | 0.93349 | 0 | 0.03739 | 0.03739 | 0 | 0 | 0 | 0 | 74.3912 | 691.0565 | 0 | 0.05921 | 2.7255 | 0 | 0 | 165.9934 | 0.93349 | off_peak | 691.0565 | 100 | 0 | 0.13 | 0 | 99.87 | 2.5443 | 0
8155 | 668.69 | 0 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3912 | 668.69 | 0 | 0.088511 | 2.6962 | 0 | 0 | 165.9934 | 0 | on_peak | 668.69 |  |  | 0 | 0 | 100 | 0 | 0
8156 | 672.16 | 0 | 21.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3912 | 672.16 | 0 | 0.088511 | 2.7115 | 0 | 0 | 165.9934 | 0 | on_peak | 672.16 |  |  | 0 | 0 | 100 | 0 | 0
8157 | 660.78 | 0 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3912 | 660.78 | 0 | 0.088511 | 2.7954 | 0 | 0 | 165.9934 | 0 | on_peak | 660.78 |  |  | 0 | 0 | 100 | 0 | 0
8158 | 614.26 | 0 | 20.7 | 0 | 0 | 0 | 0 | 0 | 0 | 62.6277 | 62.6277 | 0 | 7.4394 | 551.6323 | 0 | 0.088511 | 3.18 | 62.6277 | 0 | 99.0416 | 62.6277 | on_peak | 551.6323 |  |  | 0 | 10.2 | 89.8 | 199.1587 | 0
8159 | 691.96 | 0 | 20.3 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 19.0375 | 704.3589 | 0 | 0.05921 | 3.9087 | 0 | 0 | 99.0416 | 0 | off_peak | 691.96 | 0 | 100 | 0 | 0 | 100 | 0 | 0
8160 | 642.56 | 0 | 19.8 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 30.6357 | 654.9589 | 0 | 0.05921 | 4.6672 | 0 | 0 | 99.0416 | 0 | off_peak | 642.56 | 0 | 100 | 0 | 0 | 100 | 0 | 0
8161 | 602.04 | 0 | 19.5 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 42.2338 | 614.4389 | 0 | 0.05921 | 4.9449 | 0 | 0 | 99.0416 | 0 | off_peak | 602.04 | 0 | 100 | 0 | 0 | 100 | 0 | 0
8162 | 567.09 | 0 | 19.3 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 53.832 | 579.4889 | 0 | 0.05921 | 4.8515 | 0 | 0 | 99.0416 | 0 | off_peak | 567.09 | 0 | 100 | 0 | 0 | 100 | 0 | 0
8163 | 541.87 | 0 | 19.3 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 65.4301 | 554.2689 | 0 | 0.05921 | 4.6732 | 0 | 0 | 99.0416 | 0 | off_peak | 541.87 | 0 | 100 | 0 | 0 | 100 | 0 | 0
8164 | 520.71 | 0 | 19.3 | 0 | 0 | 0 | 0 | 8.9635 | 8.9635 | 0 | 0 | 0 | 73.8147 | 529.6735 | 0 | 0.05921 | 4.4204 | 0 | 0 | 99.0416 | 0 | off_peak | 520.71 | 0 | 100 | 0 | 0 | 100 | 0 | 0
8165 | 551.92 | 0 | 19.3 | 0 | 0 | 0 | 0 | 0.57892 | 0.57892 | 0 | 0 | 0 | 74.3563 | 552.4989 | 0 | 0.05921 | 3.9619 | 0 | 0 | 99.0416 | 0 | off_peak | 551.92 | 0 | 100 | 0 | 0 | 100 | 0 | 0
8166 | 626 | 0 | 19.5 | 0 | 0 | 0 | 0 | 0.03739 | 0.03739 | 0 | 0 | 0 | 74.3912 | 626.0374 | 0 | 0.05921 | 3.4721 | 0 | 0 | 99.0416 | 0 | off_peak | 626 | 0 | 100 | 0 | 0 | 100 | 0 | 0
8167 | 652.71 | 0 | 19.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3912 | 652.71 | 0 | 0.088511 | 3.1838 | 0 | 0 | 99.0416 | 0 | on_peak | 652.71 |  |  | 0 | 0 | 100 | 0 | 0
8168 | 676.35 | 69.6868 | 20.4 | 14.3453 | 14.3453 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3912 | 662.0047 | 0 | 0.088511 | 3.0116 | 0 | 0 | 99.0416 | 14.3453 | on_peak | 662.0047 |  |  | 2.12 | 0 | 97.88 | 43.2017 | 0
8169 | 682.54 | 247.883 | 21.3 | 50.8649 | 50.8649 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3912 | 631.6751 | 0 | 0.088511 | 2.9352 | 0 | 0 | 99.0416 | 50.8649 | on_peak | 631.6751 |  |  | 7.45 | 0 | 92.55 | 149.2964 | 0
8170 | 729.5 | 416.896 | 22.2 | 85.2724 | 85.2724 | 0 | 0 | 0 | 0 | 62.6277 | 62.6277 | 0 | 7.4394 | 581.5999 | 0 | 0.088511 | 2.9007 | 0 | 0 | 99.0416 | 85.2724 | on_peak | 581.5999 |  |  | 11.69 | 8.59 | 79.73 | 247.3474 | 0
8171 | 690.85 | 546.684 | 23.2 | 111.4209 | 99.0219 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 0 | 19.0375 | 591.8281 | 0 | 0.05921 | 3.0032 | 0 | 0 | 110.6397 | 99.0219 | off_peak | 591.8281 | 100 | 0 | 14.33 | 0 | 85.67 | 297.3792 | 0
8172 | 693.91 | 623.813 | 23.9 | 126.8224 | 126.8224 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 30.6357 | 579.4866 | 0 | 0.05921 | 3.4732 | 0 | 0 | 110.6397 | 126.8224 | off_peak | 567.0876 | 0 | 100 | 18.28 | 0 | 81.72 | 440.4733 | 0
8173 | 737.69 | 613.73 | 24.2 | 124.6383 | 124.6383 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 42.2338 | 625.4507 | 0 | 0.05921 | 4.0433 | 0 | 0 | 110.6397 | 124.6383 | off_peak | 613.0517 | 0 | 100 | 16.9 | 0 | 83.1 | 503.9506 | 0
8174 | 782.25 | 429.421 | 24.3 | 87.1769 | 74.7779 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 0 | 53.832 | 707.4721 | 0 | 0.05921 | 4.5096 | 0 | 0 | 122.2379 | 74.7779 | off_peak | 707.4721 | 100 | 0 | 9.56 | 0 | 90.44 | 337.221 | 0
8175 | 821.08 | 263.733 | 24.3 | 53.5405 | 53.5405 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 65.4301 | 779.9384 | 0 | 0.05921 | 4.1203 | 0 | 0 | 122.2379 | 53.5405 | off_peak | 767.5395 | 0 | 100 | 6.52 | 0 | 93.48 | 220.6045 | 0
8176 | 772.34 | 230.72 | 24 | 46.889 | 46.889 | 0 | 0 | 8.9635 | 8.9635 | 0 | 0 | 0 | 73.8147 | 734.4145 | 0 | 0.05921 | 3.4554 | 0 | 0 | 122.2379 | 46.889 | off_peak | 725.451 | 0 | 100 | 6.07 | 0 | 93.93 | 162.0211 | 0
8177 | 824.83 | 83.3097 | 23.7 | 16.9492 | 16.3703 | 0 | 0.57892 | 0.57892 | 0 | 0 | 0 | 0 | 74.3563 | 808.4597 | 0 | 0.05921 | 3.1698 | 0 | 0 | 122.7794 | 16.3703 | off_peak | 808.4597 | 100 | 0 | 1.98 | 0 | 98.02 | 51.8909 | 0
8178 | 773.06 | 4.75 | 23.4 | 0.96742 | 0.96742 | 0 | 0 | 0.03739 | 0.03739 | 0 | 0 | 0 | 74.3912 | 772.13 | 0 | 0.05921 | 2.9476 | 0 | 0 | 122.7794 | 0.96742 | off_peak | 772.0926 | 0 | 100 | 0.13 | 0 | 99.87 | 2.8515 | 0
8179 | 783.67 | 0 | 23.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3912 | 783.67 | 0 | 0.088511 | 2.8729 | 0 | 0 | 122.7794 | 0 | on_peak | 783.67 |  |  | 0 | 0 | 100 | 0 | 0
8180 | 787.3 | 0 | 23.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3912 | 787.3 | 0 | 0.088511 | 3.0015 | 0 | 0 | 122.7794 | 0 | on_peak | 787.3 |  |  | 0 | 0 | 100 | 0 | 0
8181 | 748.88 | 0 | 23.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3912 | 748.88 | 0 | 0.088511 | 3.109 | 0 | 0 | 122.7794 | 0 | on_peak | 748.88 |  |  | 0 | 0 | 100 | 0 | 0
8182 | 777.29 | 0 | 23.1 | 0 | 0 | 0 | 0 | 0 | 0 | 62.6277 | 62.6277 | 0 | 7.4394 | 714.6623 | 0 | 0.088511 | 3.4043 | 0 | 0 | 122.7794 | 0 | on_peak | 714.6623 |  |  | 0 | 8.06 | 91.94 | 0 | 0
8183 | 729.95 | 0 | 23.1 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 19.0375 | 742.3489 | 0 | 0.05921 | 4.0264 | 0 | 0 | 122.7794 | 0 | off_peak | 729.95 | 0 | 100 | 0 | 0 | 100 | 0 | 0
8184 | 731.98 | 0 | 23 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 30.6357 | 744.3789 | 0 | 0.05921 | 4.6051 | 0 | 0 | 122.7794 | 0 | off_peak | 731.98 | 0 | 100 | 0 | 0 | 100 | 0 | 0
8185 | 724.89 | 0 | 22.9 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 42.2338 | 737.2889 | 0 | 0.05921 | 4.9029 | 0 | 0 | 122.7794 | 0 | off_peak | 724.89 | 0 | 100 | 0 | 0 | 100 | 0 | 0
8186 | 643.13 | 0 | 22.8 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 53.832 | 655.5289 | 0 | 0.05921 | 4.7717 | 0 | 0 | 122.7794 | 0 | off_peak | 643.13 | 0 | 100 | 0 | 0 | 100 | 0 | 0
8187 | 622.93 | 0 | 22.7 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 65.4301 | 635.3289 | 0 | 0.05921 | 4.6346 | 0 | 0 | 122.7794 | 0 | off_peak | 622.93 | 0 | 100 | 0 | 0 | 100 | 0 | 0
8188 | 617.95 | 0 | 22.6 | 0 | 0 | 0 | 0 | 8.9635 | 8.9635 | 0 | 0 | 0 | 73.8147 | 626.9135 | 0 | 0.05921 | 4.3747 | 0 | 0 | 122.7794 | 0 | off_peak | 617.95 | 0 | 100 | 0 | 0 | 100 | 0 | 0
8189 | 622.01 | 0 | 22.6 | 0 | 0 | 0 | 0 | 0.57892 | 0.57892 | 0 | 0 | 0 | 74.3563 | 622.5889 | 0 | 0.05921 | 3.9337 | 0 | 0 | 122.7794 | 0 | off_peak | 622.01 | 0 | 100 | 0 | 0 | 100 | 0 | 0
8190 | 694.21 | 0 | 22.7 | 0 | 0 | 0 | 0 | 0.03739 | 0.03739 | 0 | 0 | 0 | 74.3912 | 694.2474 | 0 | 0.05921 | 3.4979 | 0 | 0 | 122.7794 | 0 | off_peak | 694.21 | 0 | 100 | 0 | 0 | 100 | 0 | 0
8191 | 694.19 | 0 | 22.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3912 | 694.19 | 0 | 0.088511 | 3.0064 | 0 | 0 | 122.7794 | 0 | on_peak | 694.19 |  |  | 0 | 0 | 100 | 0 | 0
8192 | 748.05 | 68.184 | 23.3 | 13.8918 | 13.8918 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3912 | 734.1582 | 0 | 0.088511 | 2.731 | 0 | 0 | 122.7794 | 13.8918 | on_peak | 734.1582 |  |  | 1.86 | 0 | 98.14 | 37.9388 | 0
8193 | 794.99 | 246.791 | 23.9 | 50.1731 | 50.1731 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3912 | 744.8169 | 0 | 0.088511 | 2.6215 | 0 | 0 | 122.7794 | 50.1731 | on_peak | 744.8169 |  |  | 6.31 | 0 | 93.69 | 131.53 | 0
8194 | 838.43 | 420.353 | 24.3 | 85.336 | 85.336 | 0 | 0 | 0 | 0 | 62.6277 | 62.6277 | 0 | 7.4394 | 690.4663 | 0 | 0.088511 | 2.5838 | 0 | 0 | 122.7794 | 85.336 | on_peak | 690.4663 |  |  | 10.18 | 7.47 | 82.35 | 220.4928 | 0
8195 | 782.87 | 553.783 | 24.6 | 112.3025 | 112.3025 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 19.0375 | 682.9664 | 0 | 0.05921 | 2.6994 | 0 | 0 | 122.7794 | 112.3025 | off_peak | 670.5675 | 0 | 100 | 14.34 | 0 | 85.66 | 303.1472 | 0
8196 | 866.54 | 618.604 | 24.7 | 125.4026 | 125.4026 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 30.6357 | 753.5363 | 0 | 0.05921 | 3.0307 | 0 | 0 | 122.7794 | 125.4026 | off_peak | 741.1374 | 0 | 100 | 14.47 | 0 | 85.53 | 380.0569 | 0
8197 | 815.34 | 642.261 | 24.7 | 130.1983 | 130.1983 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 42.2338 | 697.5406 | 0 | 0.05921 | 3.5494 | 0 | 0 | 122.7794 | 130.1983 | off_peak | 685.1417 | 0 | 100 | 15.97 | 0 | 84.03 | 462.1234 | 0
8198 | 884.51 | 589.728 | 24.5 | 119.6349 | 119.6349 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 53.832 | 777.2741 | 0 | 0.05921 | 3.873 | 0 | 0 | 122.7794 | 119.6349 | off_peak | 764.8751 | 0 | 100 | 13.53 | 0 | 86.47 | 463.3432 | 0
8199 | 852.38 | 480.104 | 24.3 | 97.4661 | 97.4661 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 65.4301 | 767.3129 | 0 | 0.05921 | 3.8985 | 0 | 0 | 122.7794 | 97.4661 | off_peak | 754.9139 | 0 | 100 | 11.43 | 0 | 88.57 | 379.9667 | 0
8200 | 789.49 | 322.538 | 24.1 | 65.5256 | 65.5256 | 0 | 0 | 8.9635 | 8.9635 | 0 | 0 | 0 | 73.8147 | 732.928 | 0 | 0.05921 | 3.8229 | 0 | 0 | 122.7794 | 65.5256 | off_peak | 723.9644 | 0 | 100 | 8.3 | 0 | 91.7 | 250.495 | 0
8201 | 846.17 | 140.603 | 23.8 | 28.5951 | 28.5951 | 0 | 0 | 0.57892 | 0.57892 | 0 | 0 | 0 | 74.3563 | 818.1538 | 0 | 0.05921 | 3.7839 | 0 | 0 | 122.7794 | 28.5951 | off_peak | 817.5749 | 0 | 100 | 3.38 | 0 | 96.62 | 108.2003 | 0
8202 | 804.88 | 5.7 | 23.7 | 1.1597 | 1.1223 | 0 | 0.03739 | 0.03739 | 0 | 0 | 0 | 0 | 74.3912 | 803.7577 | 0 | 0.05921 | 3.7263 | 0 | 0 | 122.8144 | 1.1223 | off_peak | 803.7577 | 100 | 0 | 0.14 | 0 | 99.86 | 4.1819 | 0
8203 | 761.44 | 0 | 23.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3912 | 761.44 | 0 | 0.088511 | 3.8132 | 0 | 0 | 122.8144 | 0 | on_peak | 761.44 |  |  | 0 | 0 | 100 | 0 | 0
8204 | 821.93 | 0 | 23.7 | 0 | 0 | 0 | 0 | 0 | 0 | 62.6277 | 62.6277 | 0 | 7.4394 | 759.3023 | 0 | 0.088511 | 4.0131 | 62.6277 | 0 | 55.8625 | 62.6277 | on_peak | 759.3023 |  |  | 0 | 7.62 | 92.38 | 251.3332 | 0
8205 | 777.48 | 0 | 23.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 777.48 | 0 | 0.088511 | 4.3228 | 0 | 0 | 55.8625 | 0 | on_peak | 777.48 |  |  | 0 | 0 | 100 | 0 | 0
8206 | 763.05 | 0 | 23.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 763.05 | 0 | 0.088511 | 4.5133 | 0 | 0 | 55.8625 | 0 | on_peak | 763.05 |  |  | 0 | 0 | 100 | 0 | 0
8207 | 761.35 | 0 | 23.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 761.35 | 0 | 0.05921 | 4.651 | 0 | 0 | 55.8625 | 0 | off_peak | 761.35 |  |  | 0 | 0 | 100 | 0 | 0
8208 | 766.17 | 0 | 23.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 766.17 | 0 | 0.05921 | 4.9344 | 0 | 0 | 55.8625 | 0 | off_peak | 766.17 |  |  | 0 | 0 | 100 | 0 | 0
8209 | 665.56 | 0 | 23.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 665.56 | 0 | 0.05921 | 5.0206 | 0 | 0 | 55.8625 | 0 | off_peak | 665.56 |  |  | 0 | 0 | 100 | 0 | 0
8210 | 679.44 | 0 | 23.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 679.44 | 0 | 0.05921 | 4.7976 | 0 | 0 | 55.8625 | 0 | off_peak | 679.44 |  |  | 0 | 0 | 100 | 0 | 0
8211 | 625.94 | 0 | 23.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 625.94 | 0 | 0.05921 | 4.6145 | 0 | 0 | 55.8625 | 0 | off_peak | 625.94 |  |  | 0 | 0 | 100 | 0 | 0
8212 | 613.42 | 0 | 23.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 613.42 | 0 | 0.05921 | 4.3652 | 0 | 0 | 55.8625 | 0 | off_peak | 613.42 |  |  | 0 | 0 | 100 | 0 | 0
8213 | 653.64 | 0 | 23.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 653.64 | 0 | 0.05921 | 4.0716 | 0 | 0 | 55.8625 | 0 | off_peak | 653.64 |  |  | 0 | 0 | 100 | 0 | 0
8214 | 715.04 | 0 | 23.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 715.04 | 0 | 0.05921 | 3.7138 | 0 | 0 | 55.8625 | 0 | off_peak | 715.04 |  |  | 0 | 0 | 100 | 0 | 0
8215 | 732.79 | 0 | 23.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 732.79 | 0 | 0.05921 | 3.263 | 0 | 0 | 55.8625 | 0 | off_peak | 732.79 |  |  | 0 | 0 | 100 | 0 | 0
8216 | 768.77 | 67.1255 | 23.9 | 13.6467 | 1.2478 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 0 | 19.0375 | 767.5222 | 0 | 0.05921 | 2.9545 | 0 | 0 | 67.4607 | 1.2478 | off_peak | 767.5222 | 100 | 0 | 0.16 | 0 | 99.84 | 3.6866 | 0
8217 | 764.61 | 152.346 | 24.3 | 30.9278 | 30.9278 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19.0375 | 733.6822 | 0 | 0.05921 | 2.7763 | 0 | 0 | 67.4607 | 30.9278 | off_peak | 733.6822 |  |  | 4.04 | 0 | 95.96 | 85.865 | 0
8218 | 789.88 | 394.332 | 24.6 | 79.9672 | 79.9672 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19.0375 | 709.9128 | 0 | 0.05921 | 2.6744 | 0 | 0 | 67.4607 | 79.9672 | off_peak | 709.9128 |  |  | 10.12 | 0 | 89.88 | 213.8639 | 0
8219 | 749.75 | 309.425 | 24.8 | 62.7037 | 62.7037 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19.0375 | 687.0463 | 0 | 0.05921 | 2.6368 | 0 | 0 | 67.4607 | 62.7037 | off_peak | 687.0463 |  |  | 8.36 | 0 | 91.64 | 165.34 | 0
8220 | 771.58 | 386.965 | 25 | 78.3604 | 78.3604 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19.0375 | 693.2196 | 0 | 0.05921 | 2.6975 | 0 | 0 | 67.4607 | 78.3604 | off_peak | 693.2196 |  |  | 10.16 | 0 | 89.84 | 211.3764 | 0
8221 | 706.61 | 381.493 | 24.9 | 77.2801 | 77.2801 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19.0375 | 629.3299 | 0 | 0.05921 | 2.922 | 0 | 0 | 67.4607 | 77.2801 | off_peak | 629.3299 |  |  | 10.94 | 0 | 89.06 | 225.8107 | 0
8222 | 692.61 | 416.805 | 24.8 | 84.4638 | 84.4638 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19.0375 | 608.1462 | 0 | 0.05921 | 3.2206 | 0 | 0 | 67.4607 | 84.4638 | off_peak | 608.1462 |  |  | 12.19 | 0 | 87.81 | 272.0199 | 0
8223 | 676.89 | 317.404 | 24.7 | 64.3437 | 51.9448 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 0 | 30.6357 | 624.9452 | 0 | 0.05921 | 3.4392 | 0 | 0 | 79.0588 | 51.9448 | off_peak | 624.9452 | 100 | 0 | 7.67 | 0 | 92.33 | 178.6506 | 0
8224 | 677.46 | 127.223 | 24.7 | 25.7905 | 17.4429 | 0 | 8.3476 | 8.3476 | 0 | 0 | 0 | 0 | 38.4441 | 660.0171 | 0 | 0.05921 | 3.5968 | 0 | 0 | 86.8673 | 17.4429 | off_peak | 660.0171 | 100 | 0 | 2.57 | 0 | 97.43 | 62.7388 | 0
8225 | 684.29 | 85.0687 | 24.5 | 17.2574 | 17.2574 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 38.4441 | 667.0326 | 0 | 0.05921 | 3.8324 | 0 | 0 | 86.8673 | 17.2574 | off_peak | 667.0326 |  |  | 2.52 | 0 | 97.48 | 66.1368 | 0
8226 | 614.78 | 2.85 | 24.4 | 0.57837 | 0.57837 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 50.0423 | 626.6006 | 0 | 0.05921 | 4.1246 | 0 | 0 | 86.8673 | 0.57837 | off_peak | 614.2016 | 0 | 100 | 0.09 | 0 | 99.91 | 2.3855 | 0
8227 | 579.83 | 0 | 24.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50.0423 | 579.83 | 0 | 0.05921 | 4.3167 | 0 | 0 | 86.8673 | 0 | off_peak | 579.83 |  |  | 0 | 0 | 100 | 0 | 0
8228 | 579.17 | 0 | 24.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50.0423 | 579.17 | 0 | 0.05921 | 4.6181 | 0 | 0 | 86.8673 | 0 | off_peak | 579.17 |  |  | 0 | 0 | 100 | 0 | 0
8229 | 563.63 | 0 | 24.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50.0423 | 563.63 | 0 | 0.05921 | 4.926 | 0 | 0 | 86.8673 | 0 | off_peak | 563.63 |  |  | 0 | 0 | 100 | 0 | 0
8230 | 576.22 | 0 | 24.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50.0423 | 576.22 | 0 | 0.05921 | 5.3027 | 0 | 0 | 86.8673 | 0 | off_peak | 576.22 |  |  | 0 | 0 | 100 | 0 | 0
8231 | 541.57 | 0 | 24.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50.0423 | 541.57 | 0 | 0.05921 | 5.6973 | 0 | 0 | 86.8673 | 0 | off_peak | 541.57 |  |  | 0 | 0 | 100 | 0 | 0
8232 | 542.62 | 0 | 24.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50.0423 | 542.62 | 0 | 0.05921 | 5.8948 | 0 | 0 | 86.8673 | 0 | off_peak | 542.62 |  |  | 0 | 0 | 100 | 0 | 0
8233 | 578.66 | 0 | 24.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50.0423 | 578.66 | 0 | 0.05921 | 5.8443 | 0 | 0 | 86.8673 | 0 | off_peak | 578.66 |  |  | 0 | 0 | 100 | 0 | 0
8234 | 562.92 | 0 | 24.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50.0423 | 562.92 | 0 | 0.05921 | 5.535 | 0 | 0 | 86.8673 | 0 | off_peak | 562.92 |  |  | 0 | 0 | 100 | 0 | 0
8235 | 553.76 | 0 | 24.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50.0423 | 553.76 | 0 | 0.05921 | 5.2942 | 0 | 0 | 86.8673 | 0 | off_peak | 553.76 |  |  | 0 | 0 | 100 | 0 | 0
8236 | 565.62 | 0 | 24.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50.0423 | 565.62 | 0 | 0.05921 | 5.0582 | 0 | 0 | 86.8673 | 0 | off_peak | 565.62 |  |  | 0 | 0 | 100 | 0 | 0
8237 | 570.41 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50.0423 | 570.41 | 0 | 0.05921 | 4.7191 | 0 | 0 | 86.8673 | 0 | off_peak | 570.41 |  |  | 0 | 0 | 100 | 0 | 0
8238 | 638.5 | 0 | 23.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50.0423 | 638.5 | 0 | 0.05921 | 4.288 | 0 | 0 | 86.8673 | 0 | off_peak | 638.5 |  |  | 0 | 0 | 100 | 0 | 0
8239 | 658.74 | 0 | 23.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50.0423 | 658.74 | 0 | 0.05921 | 3.8871 | 0 | 0 | 86.8673 | 0 | off_peak | 658.74 |  |  | 0 | 0 | 100 | 0 | 0
8240 | 723.37 | 64.4164 | 23.7 | 13.1054 | 13.1054 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50.0423 | 710.2646 | 0 | 0.05921 | 3.5491 | 0 | 0 | 86.8673 | 13.1054 | off_peak | 710.2646 |  |  | 1.81 | 0 | 98.19 | 46.5122 | 0
8241 | 691.42 | 243.637 | 23.9 | 49.5319 | 37.1329 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 0 | 61.6404 | 654.2871 | 0 | 0.05921 | 3.3178 | 0 | 0 | 98.4654 | 37.1329 | off_peak | 654.2871 | 100 | 0 | 5.37 | 0 | 94.63 | 123.1984 | 0
8242 | 723.74 | 417.277 | 24.1 | 84.7724 | 84.7724 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 61.6404 | 638.9676 | 0 | 0.05921 | 3.1742 | 0 | 0 | 98.4654 | 84.7724 | off_peak | 638.9676 |  |  | 11.71 | 0 | 88.29 | 269.0847 | 0
8243 | 723.01 | 549.907 | 24.6 | 111.5165 | 111.5165 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 61.6404 | 611.4935 | 0 | 0.05921 | 3.1023 | 0 | 0 | 98.4654 | 111.5165 | off_peak | 611.4935 |  |  | 15.42 | 0 | 84.58 | 345.9628 | 0
8244 | 717.04 | 629.575 | 25.2 | 127.3971 | 127.3971 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 61.6404 | 589.6429 | 0 | 0.05921 | 3.0767 | 0 | 0 | 98.4654 | 127.3971 | off_peak | 589.6429 |  |  | 17.77 | 0 | 82.23 | 391.9623 | 0
8245 | 752.81 | 644.565 | 25.6 | 130.2425 | 130.2425 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 61.6404 | 622.5675 | 0 | 0.05921 | 3.2395 | 0 | 0 | 98.4654 | 130.2425 | off_peak | 622.5675 |  |  | 17.3 | 0 | 82.7 | 421.9207 | 0
8246 | 678.86 | 592.22 | 25.8 | 119.5792 | 119.5792 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 61.6404 | 559.2808 | 0 | 0.05921 | 3.4679 | 0 | 0 | 98.4654 | 119.5792 | off_peak | 559.2808 |  |  | 17.61 | 0 | 82.39 | 414.6933 | 0
8247 | 698.97 | 479.887 | 25.9 | 96.8623 | 96.8623 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 61.6404 | 602.1077 | 0 | 0.05921 | 3.8544 | 0 | 0 | 98.4654 | 96.8623 | off_peak | 602.1077 |  |  | 13.86 | 0 | 86.14 | 373.3444 | 0
8248 | 697.77 | 321.877 | 25.7 | 65.0158 | 65.0158 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 61.6404 | 632.7542 | 0 | 0.05921 | 4.2162 | 0 | 0 | 98.4654 | 65.0158 | off_peak | 632.7542 |  |  | 9.32 | 0 | 90.68 | 274.1229 | 0
8249 | 621.44 | 140.267 | 25.3 | 28.3734 | 28.3734 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 73.2386 | 605.4655 | 0 | 0.05921 | 4.6911 | 0 | 0 | 98.4654 | 28.3734 | off_peak | 593.0666 | 0 | 100 | 4.57 | 0 | 95.43 | 133.1024 | 0
8250 | 625.17 | 5.7 | 24.8 | 1.1551 | 0 | 0 | 1.1551 | 1.1551 | 0 | 0 | 0 | 0 | 74.319 | 625.17 | 0 | 0.05921 | 5.0413 | 0 | 0 | 99.5459 | 0 | off_peak | 625.17 | 100 | 0 | 0 | 0 | 100 | 0 | 0
8251 | 590.45 | 0 | 24.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.319 | 590.45 | 0 | 0.05921 | 5.3481 | 0 | 0 | 99.5459 | 0 | off_peak | 590.45 |  |  | 0 | 0 | 100 | 0 | 0
8252 | 548.02 | 0 | 24 | 0 | 0 | 0 | 0 | 0.074602 | 0.074602 | 0 | 0 | 0 | 74.3888 | 548.0946 | 0 | 0.05921 | 5.6933 | 0 | 0 | 99.5459 | 0 | off_peak | 548.02 | 0 | 100 | 0 | 0 | 100 | 0 | 0
8253 | 556.28 | 0 | 23.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3888 | 556.28 | 0 | 0.05921 | 5.9958 | 0 | 0 | 99.5459 | 0 | off_peak | 556.28 |  |  | 0 | 0 | 100 | 0 | 0
8254 | 542.29 | 0 | 23.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3888 | 542.29 | 0 | 0.05921 | 6.1012 | 0 | 0 | 99.5459 | 0 | off_peak | 542.29 |  |  | 0 | 0 | 100 | 0 | 0
8255 | 561.9 | 0 | 23.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3888 | 561.9 | 0 | 0.05921 | 6.1993 | 0 | 0 | 99.5459 | 0 | off_peak | 561.9 |  |  | 0 | 0 | 100 | 0 | 0
8256 | 550.06 | 0 | 22.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3888 | 550.06 | 0 | 0.05921 | 6.3538 | 0 | 0 | 99.5459 | 0 | off_peak | 550.06 |  |  | 0 | 0 | 100 | 0 | 0
8257 | 568.2 | 0 | 22.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3888 | 568.2 | 0 | 0.05921 | 6.404 | 0 | 0 | 99.5459 | 0 | off_peak | 568.2 |  |  | 0 | 0 | 100 | 0 | 0
8258 | 518.06 | 0 | 22.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3888 | 518.06 | 0 | 0.05921 | 6.1155 | 0 | 0 | 99.5459 | 0 | off_peak | 518.06 |  |  | 0 | 0 | 100 | 0 | 0
8259 | 524.82 | 0 | 22.6 | 0 | 0 | 0 | 0 | 0.0048182 | 0.0048182 | 0 | 0 | 0 | 74.3933 | 524.8248 | 0 | 0.05921 | 5.8511 | 0 | 0 | 99.5459 | 0 | off_peak | 524.82 | 0 | 100 | 0 | 0 | 100 | 0 | 0
8260 | 535.87 | 0 | 22.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3933 | 535.87 | 0 | 0.05921 | 5.4807 | 0 | 0 | 99.5459 | 0 | off_peak | 535.87 |  |  | 0 | 0 | 100 | 0 | 0
8261 | 545.51 | 0 | 22.7 | 0 | 0 | 0 | 0 | 0.00031119 | 0.00031119 | 0 | 0 | 0 | 74.3936 | 545.5103 | 0 | 0.05921 | 4.975 | 0 | 0 | 99.5459 | 0 | off_peak | 545.51 | 0 | 100 | 0 | 0 | 100 | 0 | 0
8262 | 629.6 | 0 | 22.7 | 0 | 0 | 0 | 0 | 2.1486e-05 | 2.1486e-05 | 0 | 0 | 0 | 74.3936 | 629.6 | 0 | 0.05921 | 4.2949 | 0 | 0 | 99.5459 | 0 | off_peak | 629.6 | 0 | 100 | 0 | 0 | 100 | 0 | 0
8263 | 717.62 | 0 | 22.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 717.62 | 0 | 0.088511 | 3.8525 | 0 | 0 | 99.5459 | 0 | on_peak | 717.62 |  |  | 0 | 0 | 100 | 0 | 0
8264 | 745.99 | 61.789 | 23.3 | 12.5888 | 12.5888 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 733.4012 | 0 | 0.088511 | 3.4777 | 0 | 0 | 99.5459 | 12.5888 | on_peak | 733.4012 |  |  | 1.69 | 0 | 98.31 | 43.7801 | 0
8265 | 792.17 | 237.019 | 24 | 48.1691 | 48.1691 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 744.0009 | 0 | 0.088511 | 3.3079 | 0 | 0 | 99.5459 | 48.1691 | on_peak | 744.0009 |  |  | 6.08 | 0 | 93.92 | 159.3366 | 0
8266 | 834.89 | 409.102 | 24.5 | 82.9923 | 82.9923 | 0 | 0 | 0 | 0 | 62.63 | 62.63 | 0 | 7.4394 | 689.2677 | 0 | 0.088511 | 3.2041 | 0 | 0 | 99.5459 | 82.9923 | on_peak | 689.2677 |  |  | 9.94 | 7.5 | 82.56 | 265.9155 | 0
8267 | 773.26 | 541.605 | 25 | 109.675 | 109.675 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 19.0375 | 675.9839 | 0 | 0.05921 | 3.2335 | 0 | 0 | 99.5459 | 109.675 | off_peak | 663.585 | 0 | 100 | 14.18 | 0 | 85.82 | 354.6396 | 0
8268 | 848.94 | 620.397 | 25.4 | 125.4495 | 125.4495 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 30.6357 | 735.8895 | 0 | 0.05921 | 3.5116 | 0 | 0 | 99.5459 | 125.4495 | off_peak | 723.4905 | 0 | 100 | 14.78 | 0 | 85.22 | 440.5318 | 0
8269 | 764.17 | 635.129 | 25.7 | 128.2895 | 128.2895 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 42.2338 | 648.2794 | 0 | 0.05921 | 4.0317 | 0 | 0 | 99.5459 | 128.2895 | off_peak | 635.8805 | 0 | 100 | 16.79 | 0 | 83.21 | 517.2191 | 0
8270 | 805.37 | 584.552 | 25.9 | 117.9883 | 105.5893 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 0 | 53.832 | 699.7807 | 0 | 0.05921 | 4.3627 | 0 | 0 | 111.144 | 105.5893 | off_peak | 699.7807 | 100 | 0 | 13.11 | 0 | 86.89 | 460.6548 | 0
8271 | 812.61 | 476.298 | 26 | 96.1031 | 96.1031 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 65.4301 | 728.9058 | 0 | 0.05921 | 4.1654 | 0 | 0 | 111.144 | 96.1031 | off_peak | 716.5069 | 0 | 100 | 11.83 | 0 | 88.17 | 400.3097 | 0
8272 | 812.32 | 319.714 | 26 | 64.509 | 64.509 | 0 | 0 | 8.9635 | 8.9635 | 0 | 0 | 0 | 73.8147 | 756.7745 | 0 | 0.05921 | 3.8378 | 0 | 0 | 111.144 | 64.509 | off_peak | 747.811 | 0 | 100 | 7.94 | 0 | 92.06 | 247.5698 | 0
8273 | 786.82 | 139.637 | 25.6 | 28.2154 | 28.2154 | 0 | 0 | 0.57892 | 0.57892 | 0 | 0 | 0 | 74.3563 | 759.1835 | 0 | 0.05921 | 3.6669 | 0 | 0 | 111.144 | 28.2154 | off_peak | 758.6046 | 0 | 100 | 3.59 | 0 | 96.41 | 103.463 | 0
8274 | 790.03 | 5.7 | 25 | 1.1542 | 1.1169 | 0 | 0.03739 | 0.03739 | 0 | 0 | 0 | 0 | 74.3912 | 788.9131 | 0 | 0.05921 | 3.5838 | 0 | 0 | 111.179 | 1.1169 | off_peak | 788.9131 | 100 | 0 | 0.14 | 0 | 99.86 | 4.0026 | 0
8275 | 772.2 | 0 | 24.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3912 | 772.2 | 0 | 0.088511 | 3.4702 | 0 | 0 | 111.179 | 0 | on_peak | 772.2 |  |  | 0 | 0 | 100 | 0 | 0
8276 | 773.51 | 0 | 24.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3912 | 773.51 | 0 | 0.088511 | 3.4181 | 0 | 0 | 111.179 | 0 | on_peak | 773.51 |  |  | 0 | 0 | 100 | 0 | 0
8277 | 747.82 | 0 | 24.1 | 0 | 0 | 0 | 0 | 0 | 0 | 62.6277 | 62.6277 | 0 | 7.4394 | 685.1923 | 0 | 0.088511 | 3.5831 | 0 | 0 | 111.179 | 0 | on_peak | 685.1923 |  |  | 0 | 8.37 | 91.63 | 0 | 0
8278 | 728.23 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 728.23 | 0 | 0.088511 | 3.9084 | 0 | 0 | 111.179 | 0 | on_peak | 728.23 |  |  | 0 | 0 | 100 | 0 | 0
8279 | 720.86 | 0 | 23.9 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 19.0375 | 733.2589 | 0 | 0.05921 | 4.4478 | 0 | 0 | 111.179 | 0 | off_peak | 720.86 | 0 | 100 | 0 | 0 | 100 | 0 | 0
8280 | 723.14 | 0 | 23.9 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 30.6357 | 735.5389 | 0 | 0.05921 | 5.1664 | 0 | 0 | 111.179 | 0 | off_peak | 723.14 | 0 | 100 | 0 | 0 | 100 | 0 | 0
8281 | 697.02 | 0 | 23.9 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 42.2338 | 709.4189 | 0 | 0.05921 | 5.5353 | 0 | 0 | 111.179 | 0 | off_peak | 697.02 | 0 | 100 | 0 | 0 | 100 | 0 | 0
8282 | 649.74 | 0 | 23.9 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 53.832 | 662.1389 | 0 | 0.05921 | 5.3624 | 0 | 0 | 111.179 | 0 | off_peak | 649.74 | 0 | 100 | 0 | 0 | 100 | 0 | 0
8283 | 608.9 | 0 | 24 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 65.4301 | 621.2989 | 0 | 0.05921 | 5.1038 | 0 | 0 | 111.179 | 0 | off_peak | 608.9 | 0 | 100 | 0 | 0 | 100 | 0 | 0
8284 | 593.98 | 0 | 24 | 0 | 0 | 0 | 0 | 8.9635 | 8.9635 | 0 | 0 | 0 | 73.8147 | 602.9435 | 0 | 0.05921 | 4.8704 | 0 | 0 | 111.179 | 0 | off_peak | 593.98 | 0 | 100 | 0 | 0 | 100 | 0 | 0
8285 | 568.02 | 0 | 24 | 0 | 0 | 0 | 0 | 0.57892 | 0.57892 | 0 | 0 | 0 | 74.3563 | 568.5989 | 0 | 0.05921 | 4.4445 | 0 | 0 | 111.179 | 0 | off_peak | 568.02 | 0 | 100 | 0 | 0 | 100 | 0 | 0
8286 | 636.01 | 0 | 24.1 | 0 | 0 | 0 | 0 | 0.03739 | 0.03739 | 0 | 0 | 0 | 74.3912 | 636.0474 | 0 | 0.05921 | 3.8831 | 0 | 0 | 111.179 | 0 | off_peak | 636.01 | 0 | 100 | 0 | 0 | 100 | 0 | 0
8287 | 691.27 | 0 | 24.2 | 0 | 0 | 0 | 0 | 0 | 0 | 62.6277 | 62.6277 | 0 | 7.4394 | 628.6423 | 0 | 0.088511 | 3.5565 | 0 | 0 | 111.179 | 0 | on_peak | 628.6423 |  |  | 0 | 9.06 | 90.94 | 0 | 0
8288 | 674.7 | 59.7128 | 24.7 | 12.1049 | 12.1049 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 662.5951 | 0 | 0.088511 | 3.2495 | 0 | 0 | 111.179 | 12.1049 | on_peak | 662.5951 |  |  | 1.79 | 0 | 98.21 | 39.3345 | 0
8289 | 734.13 | 237.335 | 25.2 | 48.0257 | 48.0257 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 686.1043 | 0 | 0.088511 | 3.1603 | 0 | 0 | 111.179 | 48.0257 | on_peak | 686.1043 |  |  | 6.54 | 0 | 93.46 | 151.7744 | 0
8290 | 744.84 | 411.85 | 25.5 | 83.2495 | 83.2495 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 661.5905 | 0 | 0.088511 | 3.1705 | 0 | 0 | 111.179 | 83.2495 | on_peak | 661.5905 |  |  | 11.18 | 0 | 88.82 | 263.9467 | 0
8291 | 724.73 | 546.326 | 25.7 | 110.3522 | 110.3522 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 19.0375 | 626.7767 | 0 | 0.05921 | 3.2236 | 0 | 0 | 111.179 | 110.3522 | off_peak | 614.3778 | 0 | 100 | 15.23 | 0 | 84.77 | 355.7366 | 0
8292 | 792.57 | 625.592 | 26 | 126.2263 | 113.8274 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 0 | 30.6357 | 678.7426 | 0 | 0.05921 | 3.5723 | 0 | 0 | 122.7772 | 113.8274 | off_peak | 678.7426 | 100 | 0 | 14.36 | 0 | 85.64 | 406.62 | 0
8293 | 749.9 | 640.278 | 26.1 | 129.1429 | 129.1429 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 42.2338 | 633.1561 | 0 | 0.05921 | 4.3203 | 0 | 0 | 122.7772 | 129.1429 | off_peak | 620.7571 | 0 | 100 | 17.22 | 0 | 82.78 | 557.9393 | 0
8294 | 782.98 | 588.223 | 26.2 | 118.6006 | 106.2016 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 0 | 53.832 | 676.7784 | 0 | 0.05921 | 4.773 | 0 | 0 | 134.3753 | 106.2016 | off_peak | 676.7784 | 100 | 0 | 13.56 | 0 | 86.44 | 506.9023 | 0
8295 | 821.71 | 479.894 | 26.1 | 96.7937 | 84.3948 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 0 | 65.4301 | 737.3152 | 0 | 0.05921 | 4.3812 | 0 | 0 | 145.9735 | 84.3948 | off_peak | 737.3152 | 100 | 0 | 10.27 | 0 | 89.73 | 369.7487 | 0
8296 | 740.05 | 323.191 | 25.9 | 65.2341 | 65.2341 | 0 | 0 | 8.9635 | 8.9635 | 0 | 0 | 0 | 73.8147 | 683.7794 | 0 | 0.05921 | 3.8852 | 0 | 0 | 145.9735 | 65.2341 | off_peak | 674.8159 | 0 | 100 | 8.81 | 0 | 91.19 | 253.446 | 0
8297 | 768.6 | 142.338 | 25.4 | 28.7819 | 28.7819 | 0 | 0 | 0.57892 | 0.57892 | 0 | 0 | 0 | 74.3563 | 740.397 | 0 | 0.05921 | 3.5813 | 0 | 0 | 145.9735 | 28.7819 | off_peak | 739.8181 | 0 | 100 | 3.74 | 0 | 96.26 | 103.0766 | 0
8298 | 742.67 | 5.702 | 24.9 | 1.1551 | 1.1177 | 0 | 0.03739 | 0.03739 | 0 | 0 | 0 | 0 | 74.3912 | 741.5523 | 0 | 0.05921 | 3.4352 | 0 | 0 | 146.0084 | 1.1177 | off_peak | 741.5523 | 100 | 0 | 0.15 | 0 | 99.85 | 3.8394 | 0
8299 | 724.57 | 0 | 24.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3912 | 724.57 | 0 | 0.088511 | 3.4633 | 0 | 0 | 146.0084 | 0 | on_peak | 724.57 |  |  | 0 | 0 | 100 | 0 | 0
8300 | 752.62 | 0 | 24.5 | 0 | 0 | 0 | 0 | 0 | 0 | 62.6277 | 62.6277 | 0 | 7.4394 | 689.9923 | 0 | 0.088511 | 3.5527 | 0 | 0 | 146.0084 | 0 | on_peak | 689.9923 |  |  | 0 | 8.32 | 91.68 | 0 | 0
8301 | 726.35 | 0 | 24.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 726.35 | 0 | 0.088511 | 3.8267 | 0 | 0 | 146.0084 | 0 | on_peak | 726.35 |  |  | 0 | 0 | 100 | 0 | 0
8302 | 712.22 | 0 | 24.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 712.22 | 0 | 0.088511 | 4.0078 | 0 | 0 | 146.0084 | 0 | on_peak | 712.22 |  |  | 0 | 0 | 100 | 0 | 0
8303 | 764.46 | 0 | 24.3 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 19.0375 | 776.8589 | 0 | 0.05921 | 4.456 | 0 | 0 | 146.0084 | 0 | off_peak | 764.46 | 0 | 100 | 0 | 0 | 100 | 0 | 0
8304 | 710.41 | 0 | 24.3 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 30.6357 | 722.8089 | 0 | 0.05921 | 5.1078 | 0 | 0 | 146.0084 | 0 | off_peak | 710.41 | 0 | 100 | 0 | 0 | 100 | 0 | 0
8305 | 671.28 | 0 | 24.3 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 42.2338 | 683.6789 | 0 | 0.05921 | 5.3965 | 0 | 0 | 146.0084 | 0 | off_peak | 671.28 | 0 | 100 | 0 | 0 | 100 | 0 | 0
8306 | 661.16 | 0 | 24.4 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 53.832 | 673.5589 | 0 | 0.05921 | 5.3429 | 0 | 0 | 146.0084 | 0 | off_peak | 661.16 | 0 | 100 | 0 | 0 | 100 | 0 | 0
8307 | 651.59 | 0 | 24.5 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 65.4301 | 663.9889 | 0 | 0.05921 | 5.1667 | 0 | 0 | 146.0084 | 0 | off_peak | 651.59 | 0 | 100 | 0 | 0 | 100 | 0 | 0
8308 | 610.03 | 0 | 24.6 | 0 | 0 | 0 | 0 | 8.9635 | 8.9635 | 0 | 0 | 0 | 73.8147 | 618.9935 | 0 | 0.05921 | 4.9029 | 0 | 0 | 146.0084 | 0 | off_peak | 610.03 | 0 | 100 | 0 | 0 | 100 | 0 | 0
8309 | 596.27 | 0 | 24.6 | 0 | 0 | 0 | 0 | 0.57892 | 0.57892 | 0 | 0 | 0 | 74.3563 | 596.8489 | 0 | 0.05921 | 4.4856 | 0 | 0 | 146.0084 | 0 | off_peak | 596.27 | 0 | 100 | 0 | 0 | 100 | 0 | 0
8310 | 684.57 | 0 | 24.7 | 0 | 0 | 0 | 0 | 0.03739 | 0.03739 | 0 | 0 | 0 | 74.3912 | 684.6074 | 0 | 0.05921 | 4.0755 | 0 | 0 | 146.0084 | 0 | off_peak | 684.57 | 0 | 100 | 0 | 0 | 100 | 0 | 0
8311 | 683.14 | 0 | 24.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3912 | 683.14 | 0 | 0.088511 | 3.6221 | 0 | 0 | 146.0084 | 0 | on_peak | 683.14 |  |  | 0 | 0 | 100 | 0 | 0
8312 | 719.15 | 58.9433 | 25.1 | 11.9317 | 11.9317 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3912 | 707.2183 | 0 | 0.088511 | 3.3661 | 0 | 0 | 146.0084 | 11.9317 | on_peak | 707.2183 |  |  | 1.66 | 0 | 98.34 | 40.1637 | 0
8313 | 748.15 | 233.976 | 25.5 | 47.2949 | 47.2949 | 0 | 0 | 0 | 0 | 62.6277 | 62.6277 | 0 | 7.4394 | 638.2274 | 0 | 0.088511 | 3.2569 | 0 | 0 | 146.0084 | 47.2949 | on_peak | 638.2274 |  |  | 6.32 | 8.37 | 85.31 | 154.037 | 0
8314 | 773.87 | 403.621 | 26 | 81.439 | 81.439 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 692.431 | 0 | 0.088511 | 3.2114 | 0 | 0 | 146.0084 | 81.439 | on_peak | 692.431 |  |  | 10.52 | 0 | 89.48 | 261.5295 | 0
8315 | 748.37 | 535.345 | 26.4 | 107.861 | 107.861 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 19.0375 | 652.908 | 0 | 0.05921 | 3.3249 | 0 | 0 | 146.0084 | 107.861 | off_peak | 640.509 | 0 | 100 | 14.41 | 0 | 85.59 | 358.6297 | 0
8316 | 799.3 | 613.72 | 26.7 | 123.5177 | 111.1188 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 0 | 30.6357 | 688.1812 | 0 | 0.05921 | 3.331 | 0 | 0 | 157.6066 | 111.1188 | off_peak | 688.1812 | 100 | 0 | 13.9 | 0 | 86.1 | 370.1366 | 0
8317 | 735.7 | 619.478 | 26.7 | 124.6766 | 112.2776 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 0 | 42.2338 | 623.4224 | 0 | 0.05921 | 4.1638 | 0 | 0 | 169.2047 | 112.2776 | off_peak | 623.4224 | 100 | 0 | 15.26 | 0 | 84.74 | 467.5054 | 0
8318 | 801.13 | 541.669 | 26.6 | 109.0562 | 109.0562 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 53.832 | 704.4728 | 0 | 0.05921 | 4.5308 | 0 | 0 | 169.2047 | 109.0562 | off_peak | 692.0738 | 0 | 100 | 13.61 | 0 | 86.39 | 494.1096 | 0
8319 | 816.25 | 472.219 | 26.4 | 95.1424 | 82.7435 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 0 | 65.4301 | 733.5065 | 0 | 0.05921 | 4.7718 | 0 | 0 | 180.8029 | 82.7435 | off_peak | 733.5065 | 100 | 0 | 10.14 | 0 | 89.86 | 394.8378 | 0
8320 | 730.72 | 315.653 | 26.1 | 63.6666 | 54.7031 | 0 | 8.9635 | 8.9635 | 0 | 0 | 0 | 0 | 73.8147 | 676.0169 | 0 | 0.05921 | 4.7573 | 0 | 0 | 189.1875 | 54.7031 | off_peak | 676.0169 | 100 | 0 | 7.49 | 0 | 92.51 | 260.2391 | 0
8321 | 768.09 | 135.494 | 25.4 | 27.398 | 27.398 | 0 | 0 | 0.57892 | 0.57892 | 0 | 0 | 0 | 74.3563 | 741.2709 | 0 | 0.05921 | 4.6783 | 0 | 0 | 189.1875 | 27.398 | off_peak | 740.692 | 0 | 100 | 3.57 | 0 | 96.43 | 128.1752 | 0
8322 | 777.59 | 4.767 | 24.7 | 0.96635 | 0.92896 | 0 | 0.03739 | 0.03739 | 0 | 0 | 0 | 0 | 74.3912 | 776.661 | 0 | 0.05921 | 4.4948 | 0 | 0 | 189.2225 | 0.92896 | off_peak | 776.661 | 100 | 0 | 0.12 | 0 | 99.88 | 4.1755 | 0
8323 | 741.88 | 0 | 24.5 | 0 | 0 | 0 | 0 | 0 | 0 | 62.6277 | 62.6277 | 0 | 7.4394 | 679.2523 | 0 | 0.088511 | 4.4957 | 62.6277 | 0 | 122.2706 | 62.6277 | on_peak | 679.2523 |  |  | 0 | 8.44 | 91.56 | 281.5537 | 0
8324 | 755.98 | 0 | 23.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 755.98 | 0 | 0.088511 | 4.5511 | 0 | 0 | 122.2706 | 0 | on_peak | 755.98 |  |  | 0 | 0 | 100 | 0 | 0
8325 | 775.78 | 0 | 22.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 775.78 | 0 | 0.088511 | 4.6248 | 0 | 0 | 122.2706 | 0 | on_peak | 775.78 |  |  | 0 | 0 | 100 | 0 | 0
8326 | 722.6 | 0 | 21.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 722.6 | 0 | 0.088511 | 4.5872 | 0 | 0 | 122.2706 | 0 | on_peak | 722.6 |  |  | 0 | 0 | 100 | 0 | 0
8327 | 731.71 | 0 | 21 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 19.0375 | 744.1089 | 0 | 0.05921 | 4.7945 | 0 | 0 | 122.2706 | 0 | off_peak | 731.71 | 0 | 100 | 0 | 0 | 100 | 0 | 0
8328 | 770.64 | 0 | 20.7 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 30.6357 | 783.0389 | 0 | 0.05921 | 5.3071 | 0 | 0 | 122.2706 | 0 | off_peak | 770.64 | 0 | 100 | 0 | 0 | 100 | 0 | 0
8329 | 691.46 | 0 | 20.5 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 42.2338 | 703.8589 | 0 | 0.05921 | 5.5635 | 0 | 0 | 122.2706 | 0 | off_peak | 691.46 | 0 | 100 | 0 | 0 | 100 | 0 | 0
8330 | 596.54 | 0 | 20.4 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 53.832 | 608.9389 | 0 | 0.05921 | 5.5519 | 0 | 0 | 122.2706 | 0 | off_peak | 596.54 | 0 | 100 | 0 | 0 | 100 | 0 | 0
8331 | 581.75 | 0 | 20.2 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 65.4301 | 594.1489 | 0 | 0.05921 | 5.249 | 0 | 0 | 122.2706 | 0 | off_peak | 581.75 | 0 | 100 | 0 | 0 | 100 | 0 | 0
8332 | 544.63 | 0 | 20 | 0 | 0 | 0 | 0 | 8.9635 | 8.9635 | 0 | 0 | 0 | 73.8147 | 553.5935 | 0 | 0.05921 | 4.9338 | 0 | 0 | 122.2706 | 0 | off_peak | 544.63 | 0 | 100 | 0 | 0 | 100 | 0 | 0
8333 | 536.3 | 0 | 19.8 | 0 | 0 | 0 | 0 | 0.57892 | 0.57892 | 0 | 0 | 0 | 74.3563 | 536.8789 | 0 | 0.05921 | 4.5255 | 0 | 0 | 122.2706 | 0 | off_peak | 536.3 | 0 | 100 | 0 | 0 | 100 | 0 | 0
8334 | 694.5 | 0 | 19.5 | 0 | 0 | 0 | 0 | 0.03739 | 0.03739 | 0 | 0 | 0 | 74.3912 | 694.5374 | 0 | 0.05921 | 4.0386 | 0 | 0 | 122.2706 | 0 | off_peak | 694.5 | 0 | 100 | 0 | 0 | 100 | 0 | 0
8335 | 758.16 | 0 | 19.5 | 0 | 0 | 0 | 0 | 0 | 0 | 62.6277 | 62.6277 | 0 | 7.4394 | 695.5323 | 0 | 0.088511 | 3.6421 | 62.6277 | 0 | 55.3187 | 62.6277 | on_peak | 695.5323 |  |  | 0 | 8.26 | 91.74 | 228.0979 | 0
8336 | 771.77 | 55.1315 | 19.9 | 11.3691 | 11.3691 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 760.4009 | 0 | 0.088511 | 3.3622 | 0 | 0 | 55.3187 | 11.3691 | on_peak | 760.4009 |  |  | 1.47 | 0 | 98.53 | 38.2247 | 0
8337 | 812.38 | 226.279 | 20.6 | 46.5473 | 46.5473 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 765.8327 | 0 | 0.088511 | 3.1975 | 0 | 0 | 55.3187 | 46.5473 | on_peak | 765.8327 |  |  | 5.73 | 0 | 94.27 | 148.8373 | 0
8338 | 806.78 | 395.432 | 21.3 | 81.1416 | 81.1416 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 725.6384 | 0 | 0.088511 | 3.1504 | 0 | 0 | 55.3187 | 81.1416 | on_peak | 725.6384 |  |  | 10.06 | 0 | 89.94 | 255.6287 | 0
8339 | 789.48 | 526.436 | 21.8 | 107.8314 | 107.8314 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 19.0375 | 694.0476 | 0 | 0.05921 | 3.2059 | 0 | 0 | 55.3187 | 107.8314 | off_peak | 681.6486 | 0 | 100 | 13.66 | 0 | 86.34 | 345.6929 | 0
8340 | 789.41 | 574.936 | 22.1 | 117.64 | 105.2411 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 0 | 30.6357 | 684.1689 | 0 | 0.05921 | 3.4724 | 0 | 0 | 66.9169 | 105.2411 | off_peak | 684.1689 | 100 | 0 | 13.33 | 0 | 86.67 | 365.4406 | 0
8341 | 763.75 | 554.358 | 22.3 | 113.3486 | 113.3486 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 42.2338 | 662.8003 | 0 | 0.05921 | 3.9722 | 0 | 0 | 66.9169 | 113.3486 | off_peak | 650.4014 | 0 | 100 | 14.84 | 0 | 85.16 | 450.2491 | 0
8342 | 795.35 | 562.951 | 22.4 | 115.0646 | 115.0646 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 53.832 | 692.6843 | 0 | 0.05921 | 4.3861 | 0 | 0 | 66.9169 | 115.0646 | off_peak | 680.2854 | 0 | 100 | 14.47 | 0 | 85.53 | 504.6878 | 0
8343 | 835.59 | 471.854 | 22.4 | 96.4448 | 96.4448 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 65.4301 | 751.5442 | 0 | 0.05921 | 4.5226 | 0 | 0 | 66.9169 | 96.4448 | off_peak | 739.1452 | 0 | 100 | 11.54 | 0 | 88.46 | 436.1792 | 0
8344 | 761.17 | 319.741 | 22.1 | 65.4235 | 65.4235 | 0 | 0 | 8.9635 | 8.9635 | 0 | 0 | 0 | 73.8147 | 704.71 | 0 | 0.05921 | 4.5638 | 0 | 0 | 66.9169 | 65.4235 | off_peak | 695.7465 | 0 | 100 | 8.6 | 0 | 91.4 | 298.5829 | 0
8345 | 729 | 141.788 | 21.4 | 29.0842 | 29.0842 | 0 | 0 | 0.57892 | 0.57892 | 0 | 0 | 0 | 74.3563 | 700.4947 | 0 | 0.05921 | 4.4182 | 0 | 0 | 66.9169 | 29.0842 | off_peak | 699.9158 | 0 | 100 | 3.99 | 0 | 96.01 | 128.4996 | 0
8346 | 766.68 | 5.7455 | 20.7 | 1.1815 | 1.1441 | 0 | 0.03739 | 0.03739 | 0 | 0 | 0 | 0 | 74.3912 | 765.5359 | 0 | 0.05921 | 4.3188 | 0 | 0 | 66.9519 | 1.1441 | off_peak | 765.5359 | 100 | 0 | 0.15 | 0 | 99.85 | 4.9411 | 0
8347 | 743 | 0 | 20.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3912 | 743 | 0 | 0.088511 | 4.2354 | 0 | 0 | 66.9519 | 0 | on_peak | 743 |  |  | 0 | 0 | 100 | 0 | 0
8348 | 739.3 | 0 | 19.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3912 | 739.3 | 0 | 0.088511 | 4.3554 | 0 | 0 | 66.9519 | 0 | on_peak | 739.3 |  |  | 0 | 0 | 100 | 0 | 0
8349 | 768.72 | 0 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3912 | 768.72 | 0 | 0.088511 | 4.4193 | 0 | 0 | 66.9519 | 0 | on_peak | 768.72 |  |  | 0 | 0 | 100 | 0 | 0
8350 | 712.97 | 0 | 18.4 | 0 | 0 | 0 | 0 | 0 | 0 | 62.6277 | 62.6277 | 0 | 7.4394 | 650.3423 | 0 | 0.088511 | 4.5959 | 62.6277 | 0 | 0 | 62.6277 | on_peak | 650.3423 |  |  | 0 | 8.78 | 91.22 | 287.8332 | 0
8351 | 741.56 | 0 | 17.8 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 19.0375 | 753.9589 | 0 | 0.05921 | 4.9059 | 0 | 0 | 0 | 0 | off_peak | 741.56 | 0 | 100 | 0 | 0 | 100 | 0 | 0
8352 | 765.99 | 0 | 17.2 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 30.6357 | 778.3889 | 0 | 0.05921 | 5.1804 | 0 | 0 | 0 | 0 | off_peak | 765.99 | 0 | 100 | 0 | 0 | 100 | 0 | 0
8353 | 696.04 | 0 | 16.5 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 42.2338 | 708.4389 | 0 | 0.05921 | 5.3967 | 0 | 0 | 0 | 0 | off_peak | 696.04 | 0 | 100 | 0 | 0 | 100 | 0 | 0
8354 | 641.33 | 0 | 16 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 53.832 | 653.7289 | 0 | 0.05921 | 5.3038 | 0 | 0 | 0 | 0 | off_peak | 641.33 | 0 | 100 | 0 | 0 | 100 | 0 | 0
8355 | 622.78 | 0 | 15.4 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 65.4301 | 635.1789 | 0 | 0.05921 | 5.1346 | 0 | 0 | 0 | 0 | off_peak | 622.78 | 0 | 100 | 0 | 0 | 100 | 0 | 0
8356 | 603.28 | 0 | 15 | 0 | 0 | 0 | 0 | 8.9635 | 8.9635 | 0 | 0 | 0 | 73.8147 | 612.2435 | 0 | 0.05921 | 4.8096 | 0 | 0 | 0 | 0 | off_peak | 603.28 | 0 | 100 | 0 | 0 | 100 | 0 | 0
8357 | 603.85 | 0 | 14.7 | 0 | 0 | 0 | 0 | 0.57892 | 0.57892 | 0 | 0 | 0 | 74.3563 | 604.4289 | 0 | 0.05921 | 4.4523 | 0 | 0 | 0 | 0 | off_peak | 603.85 | 0 | 100 | 0 | 0 | 100 | 0 | 0
8358 | 674.56 | 0 | 14.4 | 0 | 0 | 0 | 0 | 0.03739 | 0.03739 | 0 | 0 | 0 | 74.3912 | 674.5974 | 0 | 0.05921 | 3.8228 | 0 | 0 | 0 | 0 | off_peak | 674.56 | 0 | 100 | 0 | 0 | 100 | 0 | 0
8359 | 689.82 | 0 | 14.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3912 | 689.82 | 0 | 0.088511 | 3.3584 | 0 | 0 | 0 | 0 | on_peak | 689.82 |  |  | 0 | 0 | 100 | 0 | 0
8360 | 761.01 | 53.6779 | 14.7 | 11.2728 | 11.2728 | 0 | 0 | 0 | 0 | 62.6277 | 62.6277 | 0 | 7.4394 | 687.1094 | 0 | 0.088511 | 3.0568 | 0 | 0 | 0 | 11.2728 | on_peak | 687.1094 |  |  | 1.48 | 8.23 | 90.29 | 34.4584 | 0
8361 | 817.3 | 225.739 | 15.3 | 47.3084 | 47.3084 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 769.9916 | 0 | 0.088511 | 2.8939 | 0 | 0 | 0 | 47.3084 | on_peak | 769.9916 |  |  | 5.79 | 0 | 94.21 | 136.9036 | 0
8362 | 829.55 | 387.186 | 15.9 | 80.9737 | 80.9737 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 748.5763 | 0 | 0.088511 | 2.8405 | 0 | 0 | 0 | 80.9737 | on_peak | 748.5763 |  |  | 9.76 | 0 | 90.24 | 230.0025 | 0
8363 | 756.07 | 437.843 | 16.7 | 91.3125 | 78.9135 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 0 | 19.0375 | 677.1565 | 0 | 0.05921 | 2.9343 | 0 | 0 | 11.5981 | 78.9135 | off_peak | 677.1565 | 100 | 0 | 10.44 | 0 | 89.56 | 231.5596 | 0
8364 | 822.64 | 538.053 | 17.4 | 111.9368 | 99.5378 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 0 | 30.6357 | 723.1022 | 0 | 0.05921 | 3.2532 | 0 | 0 | 23.1963 | 99.5378 | off_peak | 723.1022 | 100 | 0 | 12.1 | 0 | 87.9 | 323.8147 | 0
8365 | 744.93 | 390.191 | 17.9 | 81.0333 | 68.6343 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 0 | 42.2338 | 676.2957 | 0 | 0.05921 | 3.8753 | 0 | 0 | 34.7944 | 68.6343 | off_peak | 676.2957 | 100 | 0 | 9.21 | 0 | 90.79 | 265.9766 | 0
8366 | 819.6 | 335.062 | 18.3 | 69.4866 | 57.0877 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 0 | 53.832 | 762.5123 | 0 | 0.05921 | 4.2774 | 0 | 0 | 46.3926 | 57.0877 | off_peak | 762.5123 | 100 | 0 | 6.97 | 0 | 93.03 | 244.1856 | 0
8367 | 816.47 | 371.646 | 18.4 | 77.0465 | 77.0465 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 65.4301 | 751.8225 | 0 | 0.05921 | 4.2432 | 0 | 0 | 46.3926 | 77.0465 | off_peak | 739.4235 | 0 | 100 | 9.44 | 0 | 90.56 | 326.9203 | 0
8368 | 774.77 | 195.684 | 18.4 | 40.5675 | 31.604 | 0 | 8.9635 | 8.9635 | 0 | 0 | 0 | 0 | 73.8147 | 743.166 | 0 | 0.05921 | 4.2527 | 0 | 0 | 54.7772 | 31.604 | off_peak | 743.166 | 100 | 0 | 4.08 | 0 | 95.92 | 134.4014 | 0
8369 | 755.28 | 97.2478 | 17.9 | 20.196 | 20.196 | 0 | 0 | 0.57892 | 0.57892 | 0 | 0 | 0 | 74.3563 | 735.6629 | 0 | 0.05921 | 4.1558 | 0 | 0 | 54.7772 | 20.196 | off_peak | 735.084 | 0 | 100 | 2.67 | 0 | 97.33 | 83.931 | 0
8370 | 756.61 | 4.75 | 17.4 | 0.98819 | 0.9508 | 0 | 0.03739 | 0.03739 | 0 | 0 | 0 | 0 | 74.3912 | 755.6592 | 0 | 0.05921 | 4.1515 | 0 | 0 | 54.8122 | 0.9508 | off_peak | 755.6592 | 100 | 0 | 0.13 | 0 | 99.87 | 3.9473 | 0
8371 | 712.98 | 0 | 17.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3912 | 712.98 | 0 | 0.088511 | 4.0649 | 0 | 0 | 54.8122 | 0 | on_peak | 712.98 |  |  | 0 | 0 | 100 | 0 | 0
8372 | 750.85 | 0 | 16.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3912 | 750.85 | 0 | 0.088511 | 4.1298 | 0 | 0 | 54.8122 | 0 | on_peak | 750.85 |  |  | 0 | 0 | 100 | 0 | 0
8373 | 749.8 | 0 | 16.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3912 | 749.8 | 0 | 0.088511 | 4.2624 | 0 | 0 | 54.8122 | 0 | on_peak | 749.8 |  |  | 0 | 0 | 100 | 0 | 0
8374 | 711.23 | 0 | 15.8 | 0 | 0 | 0 | 0 | 0 | 0 | 62.6277 | 62.6277 | 0 | 7.4394 | 648.6023 | 0 | 0.088511 | 4.4759 | 0 | 0 | 54.8122 | 0 | on_peak | 648.6023 |  |  | 0 | 8.81 | 91.19 | 0 | 0
8375 | 728.28 | 0 | 15.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 728.28 | 0 | 0.05921 | 4.7451 | 0 | 0 | 54.8122 | 0 | off_peak | 728.28 |  |  | 0 | 0 | 100 | 0 | 0
8376 | 692.84 | 0 | 15.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 692.84 | 0 | 0.05921 | 5.0187 | 0 | 0 | 54.8122 | 0 | off_peak | 692.84 |  |  | 0 | 0 | 100 | 0 | 0
8377 | 683.56 | 0 | 14.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 683.56 | 0 | 0.05921 | 5.1279 | 0 | 0 | 54.8122 | 0 | off_peak | 683.56 |  |  | 0 | 0 | 100 | 0 | 0
8378 | 632.78 | 0 | 14.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 632.78 | 0 | 0.05921 | 4.9563 | 0 | 0 | 54.8122 | 0 | off_peak | 632.78 |  |  | 0 | 0 | 100 | 0 | 0
8379 | 562.46 | 0 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 562.46 | 0 | 0.05921 | 4.7858 | 0 | 0 | 54.8122 | 0 | off_peak | 562.46 |  |  | 0 | 0 | 100 | 0 | 0
8380 | 600.33 | 0 | 13.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 600.33 | 0 | 0.05921 | 4.5518 | 0 | 0 | 54.8122 | 0 | off_peak | 600.33 |  |  | 0 | 0 | 100 | 0 | 0
8381 | 590.29 | 0 | 13.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 590.29 | 0 | 0.05921 | 4.2674 | 0 | 0 | 54.8122 | 0 | off_peak | 590.29 |  |  | 0 | 0 | 100 | 0 | 0
8382 | 623.26 | 0 | 13.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 623.26 | 0 | 0.05921 | 3.8989 | 0 | 0 | 54.8122 | 0 | off_peak | 623.26 |  |  | 0 | 0 | 100 | 0 | 0
8383 | 735.78 | 0 | 13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 735.78 | 0 | 0.05921 | 3.5102 | 0 | 0 | 54.8122 | 0 | off_peak | 735.78 |  |  | 0 | 0 | 100 | 0 | 0
8384 | 679.38 | 15.2 | 13.4 | 3.2065 | 0 | 0 | 3.2065 | 3.2065 | 0 | 0 | 0 | 0 | 10.4388 | 679.38 | 0 | 0.05921 | 3.2111 | 0 | 0 | 57.8116 | 0 | off_peak | 679.38 | 100 | 0 | 0 | 0 | 100 | 0 | 0
8385 | 737.33 | 113.605 | 14 | 23.916 | 23.916 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10.4388 | 713.414 | 0 | 0.05921 | 3.0595 | 0 | 0 | 57.8116 | 23.916 | off_peak | 713.414 |  |  | 3.24 | 0 | 96.76 | 73.1717 | 0
8386 | 726.76 | 209.342 | 14.7 | 43.9636 | 31.5647 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 0 | 22.037 | 695.1953 | 0 | 0.05921 | 2.9819 | 0 | 0 | 69.4098 | 31.5647 | off_peak | 695.1953 | 100 | 0 | 4.34 | 0 | 95.66 | 94.1228 | 0
8387 | 694.68 | 254.976 | 15.8 | 53.3427 | 53.3427 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22.037 | 641.3373 | 0 | 0.05921 | 2.984 | 0 | 0 | 69.4098 | 53.3427 | off_peak | 641.3373 |  |  | 7.68 | 0 | 92.32 | 159.1772 | 0
8388 | 763.71 | 460.629 | 16.8 | 96.0309 | 96.0309 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22.037 | 667.6791 | 0 | 0.05921 | 3.0885 | 0 | 0 | 69.4098 | 96.0309 | off_peak | 667.6791 |  |  | 12.57 | 0 | 87.43 | 296.5905 | 0
8389 | 711.61 | 513.031 | 17.6 | 106.6564 | 106.6564 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22.037 | 604.9536 | 0 | 0.05921 | 3.3331 | 0 | 0 | 69.4098 | 106.6564 | off_peak | 604.9536 |  |  | 14.99 | 0 | 85.01 | 355.495 | 0
8390 | 696.84 | 432.912 | 18.2 | 89.8107 | 89.8107 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22.037 | 607.0293 | 0 | 0.05921 | 3.647 | 0 | 0 | 69.4098 | 89.8107 | off_peak | 607.0293 |  |  | 12.89 | 0 | 87.11 | 327.5415 | 0
8391 | 696.19 | 124.943 | 18.6 | 25.8839 | 25.8839 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22.037 | 670.3061 | 0 | 0.05921 | 4.1351 | 0 | 0 | 69.4098 | 25.8839 | off_peak | 670.3061 |  |  | 3.72 | 0 | 96.28 | 107.0334 | 0
8392 | 683.49 | 277.798 | 18.6 | 57.5502 | 57.5502 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22.037 | 625.9398 | 0 | 0.05921 | 4.6472 | 0 | 0 | 69.4098 | 57.5502 | off_peak | 625.9398 |  |  | 8.42 | 0 | 91.58 | 267.4464 | 0
8393 | 658.46 | 77.9281 | 17.9 | 16.1838 | 3.7848 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 0 | 33.6351 | 654.6752 | 0 | 0.05921 | 4.8953 | 0 | 0 | 81.0079 | 3.7848 | off_peak | 654.6752 | 100 | 0 | 0.57 | 0 | 99.43 | 18.5278 | 0
8394 | 611.87 | 2.85 | 17.1 | 0.59354 | 0 | 0 | 0.59354 | 12.3989 | 11.8054 | 0 | 0 | 0 | 45.2332 | 623.6754 | 0 | 0.05921 | 5.037 | 0 | 0 | 81.5631 | 0 | off_peak | 611.87 | 4.79 | 95.21 | 0 | 0 | 100 | 0 | 0
8395 | 563.65 | 0 | 16.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 45.2332 | 563.65 | 0 | 0.05921 | 5.041 | 0 | 0 | 81.5631 | 0 | off_peak | 563.65 |  |  | 0 | 0 | 100 | 0 | 0
8396 | 547.9 | 0 | 16.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 45.2332 | 547.9 | 0 | 0.05921 | 5.0183 | 0 | 0 | 81.5631 | 0 | off_peak | 547.9 |  |  | 0 | 0 | 100 | 0 | 0
8397 | 570.22 | 0 | 16.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 45.2332 | 570.22 | 0 | 0.05921 | 5.0586 | 0 | 0 | 81.5631 | 0 | off_peak | 570.22 |  |  | 0 | 0 | 100 | 0 | 0
8398 | 534.69 | 0 | 16.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 45.2332 | 534.69 | 0 | 0.05921 | 5.0257 | 0 | 0 | 81.5631 | 0 | off_peak | 534.69 |  |  | 0 | 0 | 100 | 0 | 0
8399 | 555.37 | 0 | 16.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 45.2332 | 555.37 | 0 | 0.05921 | 5.0983 | 0 | 0 | 81.5631 | 0 | off_peak | 555.37 |  |  | 0 | 0 | 100 | 0 | 0
8400 | 479.63 | 0 | 15.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 45.2332 | 479.63 | 0 | 0.05921 | 5.3404 | 0 | 0 | 81.5631 | 0 | off_peak | 479.63 |  |  | 0 | 0 | 100 | 0 | 0
8401 | 460.51 | 0 | 15.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 45.2332 | 460.51 | 0 | 0.05921 | 5.3964 | 0 | 0 | 81.5631 | 0 | off_peak | 460.51 |  |  | 0 | 0 | 100 | 0 | 0
8402 | 498.96 | 0 | 15.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 45.2332 | 498.96 | 0 | 0.05921 | 5.2015 | 0 | 0 | 81.5631 | 0 | off_peak | 498.96 |  |  | 0 | 0 | 100 | 0 | 0
8403 | 457.74 | 0 | 15.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 45.2332 | 457.74 | 0 | 0.05921 | 4.964 | 0 | 0 | 81.5631 | 0 | off_peak | 457.74 |  |  | 0 | 0 | 100 | 0 | 0
8404 | 467.45 | 0 | 15.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 45.2332 | 467.45 | 0 | 0.05921 | 4.753 | 0 | 0 | 81.5631 | 0 | off_peak | 467.45 |  |  | 0 | 0 | 100 | 0 | 0
8405 | 511.16 | 0 | 15.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 45.2332 | 511.16 | 0 | 0.05921 | 4.4203 | 0 | 0 | 81.5631 | 0 | off_peak | 511.16 |  |  | 0 | 0 | 100 | 0 | 0
8406 | 541.7 | 0 | 15.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 45.2332 | 541.7 | 0 | 0.05921 | 4.0889 | 0 | 0 | 81.5631 | 0 | off_peak | 541.7 |  |  | 0 | 0 | 100 | 0 | 0
8407 | 658.6 | 0 | 15.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 45.2332 | 658.6 | 0 | 0.05921 | 3.7426 | 0 | 0 | 81.5631 | 0 | off_peak | 658.6 |  |  | 0 | 0 | 100 | 0 | 0
8408 | 727.97 | 42.7343 | 16.4 | 8.9216 | 8.9216 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 45.2332 | 719.0484 | 0 | 0.05921 | 3.4489 | 0 | 0 | 81.5631 | 8.9216 | off_peak | 719.0484 |  |  | 1.23 | 0 | 98.77 | 30.7701 | 0
8409 | 703.23 | 76.1904 | 17.6 | 15.8396 | 3.4406 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 0 | 56.8314 | 699.7894 | 0 | 0.05921 | 3.288 | 0 | 0 | 93.1613 | 3.4406 | off_peak | 699.7894 | 100 | 0 | 0.49 | 0 | 99.51 | 11.3129 | 0
8410 | 701.9 | 122.863 | 18.8 | 25.4351 | 25.4351 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 68.4295 | 688.8639 | 0 | 0.05921 | 3.2113 | 0 | 0 | 93.1613 | 25.4351 | off_peak | 676.4649 | 0 | 100 | 3.62 | 0 | 96.38 | 81.6798 | 0
8411 | 687.18 | 188.468 | 19.9 | 38.8655 | 38.8655 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 68.4295 | 648.3145 | 0 | 0.05921 | 3.1535 | 0 | 0 | 93.1613 | 38.8655 | off_peak | 648.3145 |  |  | 5.66 | 0 | 94.34 | 122.5637 | 0
8412 | 697.4 | 325.807 | 20.9 | 66.9497 | 66.9497 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 68.4295 | 630.4503 | 0 | 0.05921 | 3.2206 | 0 | 0 | 93.1613 | 66.9497 | off_peak | 630.4503 |  |  | 9.6 | 0 | 90.4 | 215.6202 | 0
8413 | 677.19 | 196.526 | 21.6 | 40.2836 | 40.2836 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 68.4295 | 636.9064 | 0 | 0.05921 | 3.3921 | 0 | 0 | 93.1613 | 40.2836 | off_peak | 636.9064 |  |  | 5.95 | 0 | 94.05 | 136.6478 | 0
8414 | 707.63 | 249.042 | 22 | 50.9757 | 50.9757 | 0 | 0 | 5.3321 | 5.3321 | 0 | 0 | 0 | 73.4172 | 661.9864 | 0 | 0.05921 | 3.6733 | 0 | 0 | 93.1613 | 50.9757 | off_peak | 656.6543 | 0 | 100 | 7.2 | 0 | 92.8 | 187.251 | 0
8415 | 665.53 | 446.164 | 22.1 | 91.2914 | 91.2914 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 73.4172 | 574.2386 | 0 | 0.05921 | 4.1215 | 0 | 0 | 93.1613 | 91.2914 | off_peak | 574.2386 |  |  | 13.72 | 0 | 86.28 | 376.2573 | 0
8416 | 671.68 | 226.539 | 21.9 | 46.3861 | 46.3861 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 73.4172 | 625.2939 | 0 | 0.05921 | 4.3917 | 0 | 0 | 93.1613 | 46.3861 | off_peak | 625.2939 |  |  | 6.91 | 0 | 93.09 | 203.7127 | 0
8417 | 640.08 | 50.7331 | 21.3 | 10.4103 | 10.4103 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 73.4172 | 629.6697 | 0 | 0.05921 | 4.5255 | 0 | 0 | 93.1613 | 10.4103 | off_peak | 629.6697 |  |  | 1.63 | 0 | 98.37 | 47.1118 | 0
8418 | 619.38 | 4.75 | 20.8 | 0.97642 | 0 | 0 | 0.97642 | 0.97642 | 0 | 0 | 0 | 0 | 74.3306 | 619.38 | 0 | 0.05921 | 4.5521 | 0 | 0 | 94.0746 | 0 | off_peak | 619.38 | 100 | 0 | 0 | 0 | 100 | 0 | 0
8419 | 568.47 | 0 | 20.6 | 0 | 0 | 0 | 0 | 0.063063 | 0.063063 | 0 | 0 | 0 | 74.3896 | 568.5331 | 0 | 0.05921 | 4.5747 | 0 | 0 | 94.0746 | 0 | off_peak | 568.47 | 0 | 100 | 0 | 0 | 100 | 0 | 0
8420 | 572.56 | 0 | 20.5 | 0 | 0 | 0 | 0 | 0.0040729 | 0.0040729 | 0 | 0 | 0 | 74.3934 | 572.5641 | 0 | 0.05921 | 4.6679 | 0 | 0 | 94.0746 | 0 | off_peak | 572.56 | 0 | 100 | 0 | 0 | 100 | 0 | 0
8421 | 525.99 | 0 | 20.5 | 0 | 0 | 0 | 0 | 0.00026305 | 0.00026305 | 0 | 0 | 0 | 74.3936 | 525.9903 | 0 | 0.05921 | 4.7205 | 0 | 0 | 94.0746 | 0 | off_peak | 525.99 | 0 | 100 | 0 | 0 | 100 | 0 | 0
8422 | 551.2 | 0 | 20.6 | 0 | 0 | 0 | 0 | 1.8163e-05 | 1.8163e-05 | 0 | 0 | 0 | 74.3936 | 551.2 | 0 | 0.05921 | 4.6885 | 0 | 0 | 94.0746 | 0 | off_peak | 551.2 | 0 | 100 | 0 | 0 | 100 | 0 | 0
8423 | 577.32 | 0 | 20.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 577.32 | 0 | 0.05921 | 4.984 | 0 | 0 | 94.0746 | 0 | off_peak | 577.32 |  |  | 0 | 0 | 100 | 0 | 0
8424 | 557.82 | 0 | 20.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 557.82 | 0 | 0.05921 | 5.2526 | 0 | 0 | 94.0746 | 0 | off_peak | 557.82 |  |  | 0 | 0 | 100 | 0 | 0
8425 | 555.85 | 0 | 20.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 555.85 | 0 | 0.05921 | 5.4112 | 0 | 0 | 94.0746 | 0 | off_peak | 555.85 |  |  | 0 | 0 | 100 | 0 | 0
8426 | 560.46 | 0 | 20.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 560.46 | 0 | 0.05921 | 5.2169 | 0 | 0 | 94.0746 | 0 | off_peak | 560.46 |  |  | 0 | 0 | 100 | 0 | 0
8427 | 553.81 | 0 | 20.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 553.81 | 0 | 0.05921 | 4.965 | 0 | 0 | 94.0746 | 0 | off_peak | 553.81 |  |  | 0 | 0 | 100 | 0 | 0
8428 | 547.67 | 0 | 20.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 547.67 | 0 | 0.05921 | 4.6357 | 0 | 0 | 94.0746 | 0 | off_peak | 547.67 |  |  | 0 | 0 | 100 | 0 | 0
8429 | 578.83 | 0 | 20.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 578.83 | 0 | 0.05921 | 4.1766 | 0 | 0 | 94.0746 | 0 | off_peak | 578.83 |  |  | 0 | 0 | 100 | 0 | 0
8430 | 637.75 | 0 | 20.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 637.75 | 0 | 0.05921 | 3.7136 | 0 | 0 | 94.0746 | 0 | off_peak | 637.75 |  |  | 0 | 0 | 100 | 0 | 0
8431 | 703.01 | 0 | 20.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 703.01 | 0 | 0.088511 | 3.2776 | 0 | 0 | 94.0746 | 0 | on_peak | 703.01 |  |  | 0 | 0 | 100 | 0 | 0
8432 | 756.26 | 29.1507 | 21.1 | 5.9859 | 5.9859 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 750.2741 | 0 | 0.088511 | 3.0055 | 0 | 0 | 94.0746 | 5.9859 | on_peak | 750.2741 |  |  | 0.79 | 0 | 99.21 | 17.9906 | 0
8433 | 766.82 | 125.562 | 21.7 | 25.7284 | 25.7284 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 741.0916 | 0 | 0.088511 | 2.8718 | 0 | 0 | 94.0746 | 25.7284 | on_peak | 741.0916 |  |  | 3.36 | 0 | 96.64 | 73.8879 | 0
8434 | 847.06 | 292.628 | 22.3 | 59.8331 | 59.8331 | 0 | 0 | 0 | 0 | 62.63 | 62.63 | 0 | 7.4394 | 724.5969 | 0 | 0.088511 | 2.8202 | 0 | 0 | 94.0746 | 59.8331 | on_peak | 724.5969 |  |  | 7.06 | 7.39 | 85.54 | 168.7419 | 0
8435 | 761.06 | 118.616 | 23 | 24.1927 | 11.7937 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 0 | 19.0375 | 749.2663 | 0 | 0.05921 | 2.9165 | 0 | 0 | 105.6728 | 11.7937 | off_peak | 749.2663 | 100 | 0 | 1.55 | 0 | 98.45 | 34.3967 | 0
8436 | 784.87 | 554.461 | 23.3 | 112.9655 | 100.5666 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 0 | 30.6357 | 684.3034 | 0 | 0.05921 | 3.2202 | 0 | 0 | 117.2709 | 100.5666 | off_peak | 684.3034 | 100 | 0 | 12.81 | 0 | 87.19 | 323.8457 | 0
8437 | 758.87 | 531.763 | 23.6 | 108.2247 | 108.2247 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 42.2338 | 663.0442 | 0 | 0.05921 | 3.7877 | 0 | 0 | 117.2709 | 108.2247 | off_peak | 650.6453 | 0 | 100 | 14.26 | 0 | 85.74 | 409.918 | 0
8438 | 750.53 | 561.06 | 23.7 | 114.1464 | 114.1464 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 53.832 | 648.7826 | 0 | 0.05921 | 4.1861 | 0 | 0 | 117.2709 | 114.1464 | off_peak | 636.3836 | 0 | 100 | 15.21 | 0 | 84.79 | 477.8265 | 0
8439 | 734.4 | 405.587 | 23.7 | 82.5157 | 82.5157 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 65.4301 | 664.2832 | 0 | 0.05921 | 3.9304 | 0 | 0 | 117.2709 | 82.5157 | off_peak | 651.8843 | 0 | 100 | 11.24 | 0 | 88.76 | 324.3236 | 0
8440 | 697.33 | 94.05 | 23.5 | 19.148 | 10.1844 | 0 | 8.9635 | 8.9635 | 0 | 0 | 0 | 0 | 73.8147 | 687.1456 | 0 | 0.05921 | 3.4992 | 0 | 0 | 125.6556 | 10.1844 | off_peak | 687.1456 | 100 | 0 | 1.46 | 0 | 98.54 | 35.6372 | 0
8441 | 718.71 | 30.7856 | 22.8 | 6.2835 | 5.7045 | 0 | 0.57892 | 0.57892 | 0 | 0 | 0 | 0 | 74.3563 | 713.0055 | 0 | 0.05921 | 3.2565 | 0 | 0 | 126.1971 | 5.7045 | off_peak | 713.0055 | 100 | 0 | 0.79 | 0 | 99.21 | 18.5766 | 0
8442 | 738.61 | 4.75 | 22.2 | 0.97157 | 0.97157 | 0 | 0 | 0.03739 | 0.03739 | 0 | 0 | 0 | 74.3912 | 737.6758 | 0 | 0.05921 | 3.1423 | 0 | 0 | 126.1971 | 0.97157 | off_peak | 737.6384 | 0 | 100 | 0.13 | 0 | 99.87 | 3.053 | 0
8443 | 710.11 | 0 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 62.6277 | 62.6277 | 0 | 7.4394 | 647.4823 | 0 | 0.088511 | 3.1184 | 62.6277 | 0 | 59.2452 | 62.6277 | on_peak | 647.4823 |  |  | 0 | 8.82 | 91.18 | 195.3014 | 0
8444 | 692.11 | 0 | 21.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 692.11 | 0 | 0.088511 | 3.1258 | 0 | 0 | 59.2452 | 0 | on_peak | 692.11 |  |  | 0 | 0 | 100 | 0 | 0
8445 | 708.56 | 0 | 21.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 708.56 | 0 | 0.088511 | 3.2522 | 0 | 0 | 59.2452 | 0 | on_peak | 708.56 |  |  | 0 | 0 | 100 | 0 | 0
8446 | 676.22 | 0 | 21.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 676.22 | 0 | 0.088511 | 3.6097 | 0 | 0 | 59.2452 | 0 | on_peak | 676.22 |  |  | 0 | 0 | 100 | 0 | 0
8447 | 688.03 | 0 | 21.5 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 19.0375 | 700.4289 | 0 | 0.05921 | 4.3571 | 0 | 0 | 59.2452 | 0 | off_peak | 688.03 | 0 | 100 | 0 | 0 | 100 | 0 | 0
8448 | 678.1 | 0 | 21.5 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 30.6357 | 690.4989 | 0 | 0.05921 | 5.0464 | 0 | 0 | 59.2452 | 0 | off_peak | 678.1 | 0 | 100 | 0 | 0 | 100 | 0 | 0
8449 | 641.75 | 0 | 21.4 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 42.2338 | 654.1489 | 0 | 0.05921 | 5.4034 | 0 | 0 | 59.2452 | 0 | off_peak | 641.75 | 0 | 100 | 0 | 0 | 100 | 0 | 0
8450 | 616.63 | 0 | 21.3 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 53.832 | 629.0289 | 0 | 0.05921 | 5.2989 | 0 | 0 | 59.2452 | 0 | off_peak | 616.63 | 0 | 100 | 0 | 0 | 100 | 0 | 0
8451 | 586.26 | 0 | 21.3 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 65.4301 | 598.6589 | 0 | 0.05921 | 5.0984 | 0 | 0 | 59.2452 | 0 | off_peak | 586.26 | 0 | 100 | 0 | 0 | 100 | 0 | 0
8452 | 565.17 | 0 | 21.2 | 0 | 0 | 0 | 0 | 8.9635 | 8.9635 | 0 | 0 | 0 | 73.8147 | 574.1335 | 0 | 0.05921 | 4.7482 | 0 | 0 | 59.2452 | 0 | off_peak | 565.17 | 0 | 100 | 0 | 0 | 100 | 0 | 0
8453 | 585.32 | 0 | 21.2 | 0 | 0 | 0 | 0 | 0.57892 | 0.57892 | 0 | 0 | 0 | 74.3563 | 585.8989 | 0 | 0.05921 | 4.3293 | 0 | 0 | 59.2452 | 0 | off_peak | 585.32 | 0 | 100 | 0 | 0 | 100 | 0 | 0
8454 | 606.71 | 0 | 21.2 | 0 | 0 | 0 | 0 | 0.03739 | 0.03739 | 0 | 0 | 0 | 74.3912 | 606.7474 | 0 | 0.05921 | 3.7686 | 0 | 0 | 59.2452 | 0 | off_peak | 606.71 | 0 | 100 | 0 | 0 | 100 | 0 | 0
8455 | 669.52 | 0 | 21.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3912 | 669.52 | 0 | 0.088511 | 3.5635 | 0 | 0 | 59.2452 | 0 | on_peak | 669.52 |  |  | 0 | 0 | 100 | 0 | 0
8456 | 715.55 | 46.0945 | 22.2 | 9.4282 | 9.4282 | 0 | 0 | 0 | 0 | 62.6277 | 62.6277 | 0 | 7.4394 | 643.494 | 0 | 0.088511 | 3.3719 | 0 | 0 | 59.2452 | 9.4282 | on_peak | 643.494 |  |  | 1.32 | 8.75 | 89.93 | 31.7913 | 0
8457 | 691.16 | 212.727 | 23.1 | 43.3719 | 43.3719 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 647.7881 | 0 | 0.088511 | 3.3841 | 0 | 0 | 59.2452 | 43.3719 | on_peak | 647.7881 |  |  | 6.28 | 0 | 93.72 | 146.7759 | 0
8458 | 770.49 | 386.796 | 23.6 | 78.721 | 78.721 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 691.769 | 0 | 0.088511 | 3.3923 | 0 | 0 | 59.2452 | 78.721 | on_peak | 691.769 |  |  | 10.22 | 0 | 89.78 | 267.0446 | 0
8459 | 711.67 | 525.141 | 24 | 106.7239 | 106.7239 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 19.0375 | 617.3451 | 0 | 0.05921 | 3.533 | 0 | 0 | 59.2452 | 106.7239 | off_peak | 604.9461 | 0 | 100 | 15 | 0 | 85 | 377.0589 | 0
8460 | 733.97 | 606.763 | 24.3 | 123.1791 | 123.1791 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 30.6357 | 623.1898 | 0 | 0.05921 | 3.8841 | 0 | 0 | 59.2452 | 123.1791 | off_peak | 610.7909 | 0 | 100 | 16.78 | 0 | 83.22 | 478.4354 | 0
8461 | 739.75 | 627.15 | 24.4 | 127.2722 | 127.2722 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 42.2338 | 624.8768 | 0 | 0.05921 | 4.5846 | 0 | 0 | 59.2452 | 127.2722 | off_peak | 612.4778 | 0 | 100 | 17.2 | 0 | 82.8 | 583.4911 | 0
8462 | 786.95 | 582.395 | 24.5 | 118.1473 | 105.7483 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 0 | 53.832 | 681.2017 | 0 | 0.05921 | 5.1554 | 0 | 0 | 70.8434 | 105.7483 | off_peak | 681.2017 | 100 | 0 | 13.44 | 0 | 86.56 | 545.1697 | 0
8463 | 784.54 | 478.005 | 24.5 | 96.9702 | 84.5713 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 0 | 65.4301 | 699.9687 | 0 | 0.05921 | 4.8253 | 0 | 0 | 82.4415 | 84.5713 | off_peak | 699.9687 | 100 | 0 | 10.78 | 0 | 89.22 | 408.0846 | 0
8464 | 753.58 | 326.23 | 24.3 | 66.2281 | 57.2645 | 0 | 8.9635 | 8.9635 | 0 | 0 | 0 | 0 | 73.8147 | 696.3155 | 0 | 0.05921 | 4.1605 | 0 | 0 | 90.8261 | 57.2645 | off_peak | 696.3155 | 100 | 0 | 7.6 | 0 | 92.4 | 238.2517 | 0
8465 | 766.25 | 147.982 | 23.8 | 30.0958 | 29.5169 | 0 | 0.57892 | 0.57892 | 0 | 0 | 0 | 0 | 74.3563 | 736.7331 | 0 | 0.05921 | 3.6538 | 0 | 0 | 91.3677 | 29.5169 | off_peak | 736.7331 | 100 | 0 | 3.85 | 0 | 96.15 | 107.8493 | 0
8466 | 772.55 | 8.8304 | 23.2 | 1.7997 | 1.7623 | 0 | 0.03739 | 0.03739 | 0 | 0 | 0 | 0 | 74.3912 | 770.7877 | 0 | 0.05921 | 3.396 | 0 | 0 | 91.4026 | 1.7623 | off_peak | 770.7877 | 100 | 0 | 0.23 | 0 | 99.77 | 5.9849 | 0
8467 | 721.2 | 0 | 23 | 0 | 0 | 0 | 0 | 0 | 0 | 62.6277 | 62.6277 | 0 | 7.4394 | 658.5723 | 0 | 0.088511 | 3.2807 | 0 | 0 | 91.4026 | 0 | on_peak | 658.5723 |  |  | 0 | 8.68 | 91.32 | 0 | 0
8468 | 750.52 | 0 | 22.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 750.52 | 0 | 0.088511 | 3.2724 | 0 | 0 | 91.4026 | 0 | on_peak | 750.52 |  |  | 0 | 0 | 100 | 0 | 0
8469 | 718.88 | 0 | 22.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 718.88 | 0 | 0.088511 | 3.3994 | 0 | 0 | 91.4026 | 0 | on_peak | 718.88 |  |  | 0 | 0 | 100 | 0 | 0
8470 | 699.4 | 0 | 22.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 699.4 | 0 | 0.088511 | 3.8113 | 0 | 0 | 91.4026 | 0 | on_peak | 699.4 |  |  | 0 | 0 | 100 | 0 | 0
8471 | 731.41 | 0 | 22.8 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 19.0375 | 743.8089 | 0 | 0.05921 | 4.5738 | 0 | 0 | 91.4026 | 0 | off_peak | 731.41 | 0 | 100 | 0 | 0 | 100 | 0 | 0
8472 | 693.87 | 0 | 22.8 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 30.6357 | 706.2689 | 0 | 0.05921 | 5.3115 | 0 | 0 | 91.4026 | 0 | off_peak | 693.87 | 0 | 100 | 0 | 0 | 100 | 0 | 0
8473 | 681.97 | 0 | 22.9 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 42.2338 | 694.3689 | 0 | 0.05921 | 5.6636 | 0 | 0 | 91.4026 | 0 | off_peak | 681.97 | 0 | 100 | 0 | 0 | 100 | 0 | 0
8474 | 616.5 | 0 | 22.9 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 53.832 | 628.8989 | 0 | 0.05921 | 5.6345 | 0 | 0 | 91.4026 | 0 | off_peak | 616.5 | 0 | 100 | 0 | 0 | 100 | 0 | 0
8475 | 587.47 | 0 | 22.9 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 65.4301 | 599.8689 | 0 | 0.05921 | 5.5644 | 0 | 0 | 91.4026 | 0 | off_peak | 587.47 | 0 | 100 | 0 | 0 | 100 | 0 | 0
8476 | 576.59 | 0 | 23 | 0 | 0 | 0 | 0 | 8.9635 | 8.9635 | 0 | 0 | 0 | 73.8147 | 585.5535 | 0 | 0.05921 | 5.1995 | 0 | 0 | 91.4026 | 0 | off_peak | 576.59 | 0 | 100 | 0 | 0 | 100 | 0 | 0
8477 | 593.86 | 0 | 23 | 0 | 0 | 0 | 0 | 0.57892 | 0.57892 | 0 | 0 | 0 | 74.3563 | 594.4389 | 0 | 0.05921 | 4.6838 | 0 | 0 | 91.4026 | 0 | off_peak | 593.86 | 0 | 100 | 0 | 0 | 100 | 0 | 0
8478 | 597.67 | 0 | 23.1 | 0 | 0 | 0 | 0 | 0.03739 | 0.03739 | 0 | 0 | 0 | 74.3912 | 597.7074 | 0 | 0.05921 | 4.1158 | 0 | 0 | 91.4026 | 0 | off_peak | 597.67 | 0 | 100 | 0 | 0 | 100 | 0 | 0
8479 | 684.3 | 0 | 23.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3912 | 684.3 | 0 | 0.088511 | 3.7387 | 0 | 0 | 91.4026 | 0 | on_peak | 684.3 |  |  | 0 | 0 | 100 | 0 | 0
8480 | 712.8 | 45.9741 | 23.7 | 9.3533 | 9.3533 | 0 | 0 | 0 | 0 | 62.6277 | 62.6277 | 0 | 7.4394 | 640.8189 | 0 | 0.088511 | 3.5248 | 0 | 0 | 91.4026 | 9.3533 | on_peak | 640.8189 |  |  | 1.31 | 8.79 | 89.9 | 32.9682 | 0
8481 | 715.58 | 197.932 | 24.2 | 40.1967 | 40.1967 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 675.3833 | 0 | 0.088511 | 3.3897 | 0 | 0 | 91.4026 | 40.1967 | on_peak | 675.3833 |  |  | 5.62 | 0 | 94.38 | 136.2561 | 0
8482 | 768.15 | 388.422 | 24.7 | 78.7404 | 78.7404 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 689.4096 | 0 | 0.088511 | 3.3152 | 0 | 0 | 91.4026 | 78.7404 | on_peak | 689.4096 |  |  | 10.25 | 0 | 89.75 | 261.0376 | 0
8483 | 712.67 | 493.909 | 25.2 | 99.9446 | 99.9446 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 19.0375 | 625.1244 | 0 | 0.05921 | 3.3222 | 0 | 0 | 91.4026 | 99.9446 | off_peak | 612.7254 | 0 | 100 | 14.02 | 0 | 85.98 | 332.031 | 0
8484 | 748.16 | 403.169 | 25.5 | 81.4948 | 81.4948 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 30.6357 | 679.0642 | 0 | 0.05921 | 3.6368 | 0 | 0 | 91.4026 | 81.4948 | off_peak | 666.6652 | 0 | 100 | 10.89 | 0 | 89.11 | 296.3841 | 0
8485 | 737.23 | 345.093 | 25.6 | 69.7304 | 69.7304 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 42.2338 | 679.8986 | 0 | 0.05921 | 4.3232 | 0 | 0 | 91.4026 | 69.7304 | off_peak | 667.4996 | 0 | 100 | 9.46 | 0 | 90.54 | 301.4602 | 0
8486 | 762.13 | 346.639 | 25.5 | 70.068 | 57.6691 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 0 | 53.832 | 704.4609 | 0 | 0.05921 | 4.7585 | 0 | 0 | 103.0008 | 57.6691 | off_peak | 704.4609 | 100 | 0 | 7.57 | 0 | 92.43 | 274.4182 | 0
8487 | 771.07 | 152.202 | 25.1 | 30.8098 | 30.8098 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 65.4301 | 752.6591 | 0 | 0.05921 | 4.6184 | 0 | 0 | 103.0008 | 30.8098 | off_peak | 740.2602 | 0 | 100 | 4 | 0 | 96 | 142.2923 | 0
8488 | 766.26 | 64.3763 | 24.3 | 13.0691 | 4.1055 | 0 | 8.9635 | 8.9635 | 0 | 0 | 0 | 0 | 73.8147 | 762.1545 | 0 | 0.05921 | 4.3354 | 0 | 0 | 111.3854 | 4.1055 | off_peak | 762.1545 | 100 | 0 | 0.54 | 0 | 99.46 | 17.7991 | 0
8489 | 752.65 | 24.7 | 23 | 5.0378 | 4.4588 | 0 | 0.57892 | 0.57892 | 0 | 0 | 0 | 0 | 74.3563 | 748.1912 | 0 | 0.05921 | 4.1307 | 0 | 0 | 111.9269 | 4.4588 | off_peak | 748.1912 | 100 | 0 | 0.59 | 0 | 99.41 | 18.4182 | 0
8490 | 778.96 | 2.85 | 21.5 | 0.5844 | 0.54701 | 0 | 0.03739 | 0.03739 | 0 | 0 | 0 | 0 | 74.3912 | 778.413 | 0 | 0.05921 | 3.9385 | 0 | 0 | 111.9619 | 0.54701 | off_peak | 778.413 | 100 | 0 | 0.07 | 0 | 99.93 | 2.1544 | 0
8491 | 765.34 | 0 | 20.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3912 | 765.34 | 0 | 0.088511 | 3.8271 | 0 | 0 | 111.9619 | 0 | on_peak | 765.34 |  |  | 0 | 0 | 100 | 0 | 0
8492 | 741.92 | 0 | 19.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3912 | 741.92 | 0 | 0.088511 | 3.9046 | 0 | 0 | 111.9619 | 0 | on_peak | 741.92 |  |  | 0 | 0 | 100 | 0 | 0
8493 | 754.98 | 0 | 18.9 | 0 | 0 | 0 | 0 | 0 | 0 | 62.6277 | 62.6277 | 0 | 7.4394 | 692.3523 | 0 | 0.088511 | 4.007 | 0 | 0 | 111.9619 | 0 | on_peak | 692.3523 |  |  | 0 | 8.3 | 91.7 | 0 | 0
8494 | 727.4 | 0 | 18.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 727.4 | 0 | 0.088511 | 4.236 | 0 | 0 | 111.9619 | 0 | on_peak | 727.4 |  |  | 0 | 0 | 100 | 0 | 0
8495 | 735.14 | 0 | 17.4 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 19.0375 | 747.5389 | 0 | 0.05921 | 4.5118 | 0 | 0 | 111.9619 | 0 | off_peak | 735.14 | 0 | 100 | 0 | 0 | 100 | 0 | 0
8496 | 709.56 | 0 | 16.6 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 30.6357 | 721.9589 | 0 | 0.05921 | 4.9304 | 0 | 0 | 111.9619 | 0 | off_peak | 709.56 | 0 | 100 | 0 | 0 | 100 | 0 | 0
8497 | 698.45 | 0 | 16 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 42.2338 | 710.8489 | 0 | 0.05921 | 5.2043 | 0 | 0 | 111.9619 | 0 | off_peak | 698.45 | 0 | 100 | 0 | 0 | 100 | 0 | 0
8498 | 660.19 | 0 | 15.5 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 53.832 | 672.5889 | 0 | 0.05921 | 5.1898 | 0 | 0 | 111.9619 | 0 | off_peak | 660.19 | 0 | 100 | 0 | 0 | 100 | 0 | 0
8499 | 610.68 | 0 | 15.2 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 65.4301 | 623.0789 | 0 | 0.05921 | 5.0406 | 0 | 0 | 111.9619 | 0 | off_peak | 610.68 | 0 | 100 | 0 | 0 | 100 | 0 | 0
8500 | 590.59 | 0 | 15 | 0 | 0 | 0 | 0 | 8.9635 | 8.9635 | 0 | 0 | 0 | 73.8147 | 599.5535 | 0 | 0.05921 | 4.7584 | 0 | 0 | 111.9619 | 0 | off_peak | 590.59 | 0 | 100 | 0 | 0 | 100 | 0 | 0
8501 | 559.93 | 0 | 14.8 | 0 | 0 | 0 | 0 | 0.57892 | 0.57892 | 0 | 0 | 0 | 74.3563 | 560.5089 | 0 | 0.05921 | 4.3165 | 0 | 0 | 111.9619 | 0 | off_peak | 559.93 | 0 | 100 | 0 | 0 | 100 | 0 | 0
8502 | 662.87 | 0 | 14.7 | 0 | 0 | 0 | 0 | 0.03739 | 0.03739 | 0 | 0 | 0 | 74.3912 | 662.9074 | 0 | 0.05921 | 3.8197 | 0 | 0 | 111.9619 | 0 | off_peak | 662.87 | 0 | 100 | 0 | 0 | 100 | 0 | 0
8503 | 717.73 | 0 | 14.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3912 | 717.73 | 0 | 0.088511 | 3.3563 | 0 | 0 | 111.9619 | 0 | on_peak | 717.73 |  |  | 0 | 0 | 100 | 0 | 0
8504 | 769.99 | 38.0015 | 15.2 | 7.9668 | 7.9668 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3912 | 762.0232 | 0 | 0.088511 | 3.163 | 0 | 0 | 111.9619 | 7.9668 | on_peak | 762.0232 |  |  | 1.03 | 0 | 98.97 | 25.1993 | 0
8505 | 769.86 | 184.055 | 16.2 | 38.4519 | 38.4519 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3912 | 731.4081 | 0 | 0.088511 | 3.0482 | 0 | 0 | 111.9619 | 38.4519 | on_peak | 731.4081 |  |  | 4.99 | 0 | 95.01 | 117.2079 | 0
8506 | 741.12 | 318.316 | 17.4 | 66.2226 | 66.2226 | 0 | 0 | 0 | 0 | 62.6277 | 62.6277 | 0 | 7.4394 | 612.2697 | 0 | 0.088511 | 3.0268 | 0 | 0 | 111.9619 | 66.2226 | on_peak | 612.2697 |  |  | 8.94 | 8.45 | 82.61 | 200.4412 | 0
8507 | 729.85 | 429.223 | 18.7 | 88.8889 | 88.8889 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 19.0375 | 653.36 | 0 | 0.05921 | 3.1113 | 0 | 0 | 111.9619 | 88.8889 | off_peak | 640.9611 | 0 | 100 | 12.18 | 0 | 87.82 | 276.5595 | 0
8508 | 827.35 | 416.319 | 19.7 | 85.9131 | 85.9131 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 30.6357 | 753.8358 | 0 | 0.05921 | 3.4409 | 0 | 0 | 111.9619 | 85.9131 | off_peak | 741.4369 | 0 | 100 | 10.38 | 0 | 89.62 | 295.6163 | 0
8509 | 741.28 | 338.611 | 20.5 | 69.6795 | 57.2806 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 0 | 42.2338 | 683.9994 | 0 | 0.05921 | 4.0517 | 0 | 0 | 123.5601 | 57.2806 | off_peak | 683.9994 | 100 | 0 | 7.73 | 0 | 92.27 | 232.0814 | 0
8510 | 784.86 | 316.959 | 21 | 65.1084 | 65.1084 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 53.832 | 732.1505 | 0 | 0.05921 | 4.396 | 0 | 0 | 123.5601 | 65.1084 | off_peak | 719.7516 | 0 | 100 | 8.3 | 0 | 91.7 | 286.2162 | 0
8511 | 817.06 | 204.575 | 21.3 | 41.9782 | 41.9782 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 65.4301 | 787.4807 | 0 | 0.05921 | 4.2758 | 0 | 0 | 123.5601 | 41.9782 | off_peak | 775.0818 | 0 | 100 | 5.14 | 0 | 94.86 | 179.489 | 0
8512 | 790.12 | 208.2 | 21.3 | 42.7221 | 33.7585 | 0 | 8.9635 | 8.9635 | 0 | 0 | 0 | 0 | 73.8147 | 756.3615 | 0 | 0.05921 | 3.8994 | 0 | 0 | 131.9447 | 33.7585 | off_peak | 756.3615 | 100 | 0 | 4.27 | 0 | 95.73 | 131.6388 | 0
8513 | 748.89 | 68.5046 | 20.8 | 14.0819 | 13.503 | 0 | 0.57892 | 0.57892 | 0 | 0 | 0 | 0 | 74.3563 | 735.387 | 0 | 0.05921 | 3.6156 | 0 | 0 | 132.4862 | 13.503 | off_peak | 735.387 | 100 | 0 | 1.8 | 0 | 98.2 | 48.822 | 0
8514 | 749.02 | 6.65 | 20.1 | 1.3704 | 1.3704 | 0 | 0 | 0.03739 | 0.03739 | 0 | 0 | 0 | 74.3912 | 747.687 | 0 | 0.05921 | 3.3977 | 0 | 0 | 132.4862 | 1.3704 | off_peak | 747.6496 | 0 | 100 | 0.18 | 0 | 99.82 | 4.6561 | 0
8515 | 751.85 | 0 | 19.9 | 0 | 0 | 0 | 0 | 0 | 0 | 62.6277 | 62.6277 | 0 | 7.4394 | 689.2223 | 0 | 0.088511 | 3.3677 | 0 | 0 | 132.4862 | 0 | on_peak | 689.2223 |  |  | 0 | 8.33 | 91.67 | 0 | 0
8516 | 729.48 | 0 | 19.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 729.48 | 0 | 0.088511 | 3.3428 | 0 | 0 | 132.4862 | 0 | on_peak | 729.48 |  |  | 0 | 0 | 100 | 0 | 0
8517 | 726.04 | 0 | 19.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 726.04 | 0 | 0.088511 | 3.4781 | 0 | 0 | 132.4862 | 0 | on_peak | 726.04 |  |  | 0 | 0 | 100 | 0 | 0
8518 | 683.02 | 0 | 19.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 683.02 | 0 | 0.088511 | 3.8289 | 0 | 0 | 132.4862 | 0 | on_peak | 683.02 |  |  | 0 | 0 | 100 | 0 | 0
8519 | 677.5 | 0 | 19.7 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 19.0375 | 689.8989 | 0 | 0.05921 | 4.3679 | 0 | 0 | 132.4862 | 0 | off_peak | 677.5 | 0 | 100 | 0 | 0 | 100 | 0 | 0
8520 | 685.72 | 0 | 19.7 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 30.6357 | 698.1189 | 0 | 0.05921 | 4.8364 | 0 | 0 | 132.4862 | 0 | off_peak | 685.72 | 0 | 100 | 0 | 0 | 100 | 0 | 0
8521 | 658.15 | 0 | 19.7 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 42.2338 | 670.5489 | 0 | 0.05921 | 5.0764 | 0 | 0 | 132.4862 | 0 | off_peak | 658.15 | 0 | 100 | 0 | 0 | 100 | 0 | 0
8522 | 621.43 | 0 | 19.7 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 53.832 | 633.8289 | 0 | 0.05921 | 4.9542 | 0 | 0 | 132.4862 | 0 | off_peak | 621.43 | 0 | 100 | 0 | 0 | 100 | 0 | 0
8523 | 574.6 | 0 | 19.8 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 65.4301 | 586.9989 | 0 | 0.05921 | 4.7953 | 0 | 0 | 132.4862 | 0 | off_peak | 574.6 | 0 | 100 | 0 | 0 | 100 | 0 | 0
8524 | 566.01 | 0 | 19.8 | 0 | 0 | 0 | 0 | 8.9635 | 8.9635 | 0 | 0 | 0 | 73.8147 | 574.9735 | 0 | 0.05921 | 4.5127 | 0 | 0 | 132.4862 | 0 | off_peak | 566.01 | 0 | 100 | 0 | 0 | 100 | 0 | 0
8525 | 581.15 | 0 | 19.8 | 0 | 0 | 0 | 0 | 0.57892 | 0.57892 | 0 | 0 | 0 | 74.3563 | 581.7289 | 0 | 0.05921 | 4.1446 | 0 | 0 | 132.4862 | 0 | off_peak | 581.15 | 0 | 100 | 0 | 0 | 100 | 0 | 0
8526 | 664.17 | 0 | 19.8 | 0 | 0 | 0 | 0 | 0.03739 | 0.03739 | 0 | 0 | 0 | 74.3912 | 664.2074 | 0 | 0.05921 | 3.6803 | 0 | 0 | 132.4862 | 0 | off_peak | 664.17 | 0 | 100 | 0 | 0 | 100 | 0 | 0
8527 | 791.26 | 0 | 19.7 | 0 | 0 | 0 | 0 | 0 | 0 | 62.6277 | 62.6277 | 0 | 7.4394 | 728.6323 | 0 | 0.088511 | 3.2402 | 0 | 0 | 132.4862 | 0 | on_peak | 728.6323 |  |  | 0 | 7.91 | 92.09 | 0 | 0
8528 | 767.19 | 45.6645 | 20 | 9.4135 | 9.4135 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 757.7765 | 0 | 0.088511 | 3.0015 | 0 | 0 | 132.4862 | 9.4135 | on_peak | 757.7765 |  |  | 1.23 | 0 | 98.77 | 28.2544 | 0
8529 | 778.33 | 207.846 | 20.6 | 42.7555 | 42.7555 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 735.5745 | 0 | 0.088511 | 2.8568 | 0 | 0 | 132.4862 | 42.7555 | on_peak | 735.5745 |  |  | 5.49 | 0 | 94.51 | 122.1457 | 0
8530 | 730.38 | 276.923 | 21.3 | 56.8239 | 56.8239 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 673.5561 | 0 | 0.088511 | 2.8208 | 0 | 0 | 132.4862 | 56.8239 | on_peak | 673.5561 |  |  | 7.78 | 0 | 92.22 | 160.2868 | 0
8531 | 749.63 | 516.74 | 22 | 105.77 | 93.371 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 0 | 19.0375 | 656.259 | 0 | 0.05921 | 2.8869 | 0 | 0 | 144.0844 | 93.371 | off_peak | 656.259 | 100 | 0 | 12.46 | 0 | 87.54 | 269.5556 | 0
8532 | 772.78 | 599.927 | 22.4 | 122.6223 | 122.6223 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 30.6357 | 662.5566 | 0 | 0.05921 | 3.1635 | 0 | 0 | 144.0844 | 122.6223 | off_peak | 650.1577 | 0 | 100 | 15.87 | 0 | 84.13 | 387.9213 | 0
8533 | 799.37 | 493.484 | 22.7 | 100.7579 | 88.359 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 0 | 42.2338 | 711.011 | 0 | 0.05921 | 3.5907 | 0 | 0 | 155.6825 | 88.359 | off_peak | 711.011 | 100 | 0 | 11.05 | 0 | 88.95 | 317.2732 | 0
8534 | 721.3 | 429.983 | 22.9 | 87.7298 | 87.7298 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 53.832 | 645.9691 | 0 | 0.05921 | 4.0108 | 0 | 0 | 155.6825 | 87.7298 | off_peak | 633.5702 | 0 | 100 | 12.16 | 0 | 87.84 | 351.8645 | 0
8535 | 719.63 | 441.895 | 22.9 | 90.1602 | 90.1602 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 65.4301 | 641.8687 | 0 | 0.05921 | 4.2209 | 0 | 0 | 155.6825 | 90.1602 | off_peak | 629.4698 | 0 | 100 | 12.53 | 0 | 87.47 | 380.5578 | 0
8536 | 666.62 | 290.513 | 22.8 | 59.2948 | 59.2948 | 0 | 0 | 8.9635 | 8.9635 | 0 | 0 | 0 | 73.8147 | 616.2887 | 0 | 0.05921 | 4.1194 | 0 | 0 | 155.6825 | 59.2948 | off_peak | 607.3252 | 0 | 100 | 8.89 | 0 | 91.11 | 244.2613 | 0
8537 | 665.64 | 85.3157 | 22.3 | 17.4444 | 16.8654 | 0 | 0.57892 | 0.57892 | 0 | 0 | 0 | 0 | 74.3563 | 648.7746 | 0 | 0.05921 | 3.9867 | 0 | 0 | 156.224 | 16.8654 | off_peak | 648.7746 | 100 | 0 | 2.53 | 0 | 97.47 | 67.2369 | 0
8538 | 642.95 | 6.65 | 21.6 | 1.3631 | 1.3631 | 0 | 0 | 0.03739 | 0.03739 | 0 | 0 | 0 | 74.3912 | 641.6243 | 0 | 0.05921 | 3.7653 | 0 | 0 | 156.224 | 1.3631 | off_peak | 641.5869 | 0 | 100 | 0.21 | 0 | 99.79 | 5.1324 | 0
8539 | 599.02 | 0 | 21.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3912 | 599.02 | 0 | 0.088511 | 3.6184 | 0 | 0 | 156.224 | 0 | on_peak | 599.02 |  |  | 0 | 0 | 100 | 0 | 0
8540 | 606.31 | 0 | 21.1 | 0 | 0 | 0 | 0 | 0 | 0 | 62.6277 | 62.6277 | 0 | 7.4394 | 543.6823 | 0 | 0.088511 | 3.7236 | 62.6277 | 0 | 89.2722 | 62.6277 | on_peak | 543.6823 |  |  | 0 | 10.33 | 89.67 | 233.2027 | 0
8541 | 568.33 | 0 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 568.33 | 0 | 0.088511 | 3.9149 | 0 | 0 | 89.2722 | 0 | on_peak | 568.33 |  |  | 0 | 0 | 100 | 0 | 0
8542 | 601.42 | 0 | 20.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 601.42 | 0 | 0.088511 | 4.0034 | 0 | 0 | 89.2722 | 0 | on_peak | 601.42 |  |  | 0 | 0 | 100 | 0 | 0
8543 | 594.09 | 0 | 20.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 594.09 | 0 | 0.05921 | 4.2138 | 0 | 0 | 89.2722 | 0 | off_peak | 594.09 |  |  | 0 | 0 | 100 | 0 | 0
8544 | 593.75 | 0 | 20.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 593.75 | 0 | 0.05921 | 4.7114 | 0 | 0 | 89.2722 | 0 | off_peak | 593.75 |  |  | 0 | 0 | 100 | 0 | 0
8545 | 594.81 | 0 | 20.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 594.81 | 0 | 0.05921 | 4.8951 | 0 | 0 | 89.2722 | 0 | off_peak | 594.81 |  |  | 0 | 0 | 100 | 0 | 0
8546 | 554.61 | 0 | 20.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 554.61 | 0 | 0.05921 | 4.6992 | 0 | 0 | 89.2722 | 0 | off_peak | 554.61 |  |  | 0 | 0 | 100 | 0 | 0
8547 | 567.3 | 0 | 20.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 567.3 | 0 | 0.05921 | 4.5358 | 0 | 0 | 89.2722 | 0 | off_peak | 567.3 |  |  | 0 | 0 | 100 | 0 | 0
8548 | 611.83 | 0 | 20.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 611.83 | 0 | 0.05921 | 4.2694 | 0 | 0 | 89.2722 | 0 | off_peak | 611.83 |  |  | 0 | 0 | 100 | 0 | 0
8549 | 587.22 | 0 | 20.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 587.22 | 0 | 0.05921 | 3.9652 | 0 | 0 | 89.2722 | 0 | off_peak | 587.22 |  |  | 0 | 0 | 100 | 0 | 0
8550 | 699.87 | 0 | 20.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 699.87 | 0 | 0.05921 | 3.5827 | 0 | 0 | 89.2722 | 0 | off_peak | 699.87 |  |  | 0 | 0 | 100 | 0 | 0
8551 | 781.15 | 0 | 20.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 781.15 | 0 | 0.05921 | 3.122 | 0 | 0 | 89.2722 | 0 | off_peak | 781.15 |  |  | 0 | 0 | 100 | 0 | 0
8552 | 775.11 | 12.35 | 21.3 | 2.5342 | 0 | 0 | 2.5342 | 2.5342 | 0 | 0 | 0 | 0 | 9.8099 | 775.11 | 0 | 0.05921 | 2.8103 | 0 | 0 | 91.6427 | 0 | off_peak | 775.11 | 100 | 0 | 0 | 0 | 100 | 0 | 0
8553 | 759.25 | 14.25 | 22.2 | 2.9147 | 0 | 0 | 2.9147 | 2.9147 | 0 | 0 | 0 | 0 | 12.5363 | 759.25 | 0 | 0.05921 | 2.6416 | 0 | 0 | 94.3692 | 0 | off_peak | 759.25 | 100 | 0 | 0 | 0 | 100 | 0 | 0
8554 | 792.12 | 159.27 | 22.8 | 32.5076 | 32.5076 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 24.1345 | 772.0113 | 0 | 0.05921 | 2.5647 | 0 | 0 | 94.3692 | 32.5076 | off_peak | 759.6124 | 0 | 100 | 4.1 | 0 | 95.9 | 83.3709 | 0
8555 | 724.31 | 185.979 | 23.3 | 37.8912 | 37.8912 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 24.1345 | 686.4188 | 0 | 0.05921 | 2.5786 | 0 | 0 | 94.3692 | 37.8912 | off_peak | 686.4188 |  |  | 5.23 | 0 | 94.77 | 97.7056 | 0
8556 | 758.92 | 252.07 | 23.7 | 51.2831 | 51.2831 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 24.1345 | 707.6369 | 0 | 0.05921 | 2.6985 | 0 | 0 | 94.3692 | 51.2831 | off_peak | 707.6369 |  |  | 6.76 | 0 | 93.24 | 138.3869 | 0
8557 | 731.25 | 558.873 | 23.9 | 113.6199 | 113.6199 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 24.1345 | 617.6301 | 0 | 0.05921 | 2.9679 | 0 | 0 | 94.3692 | 113.6199 | off_peak | 617.6301 |  |  | 15.54 | 0 | 84.46 | 337.2093 | 0
8558 | 700.77 | 559.217 | 24 | 113.6491 | 113.6491 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 35.7326 | 599.5198 | 0 | 0.05921 | 3.3168 | 0 | 0 | 94.3692 | 113.6491 | off_peak | 587.1209 | 0 | 100 | 16.22 | 0 | 83.78 | 376.9526 | 0
8559 | 700.98 | 415.303 | 23.9 | 84.4319 | 84.4319 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 35.7326 | 616.5481 | 0 | 0.05921 | 3.521 | 0 | 0 | 94.3692 | 84.4319 | off_peak | 616.5481 |  |  | 12.04 | 0 | 87.96 | 297.2872 | 0
8560 | 705.85 | 213.722 | 23.7 | 43.4812 | 43.4812 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 35.7326 | 662.3688 | 0 | 0.05921 | 3.2892 | 0 | 0 | 94.3692 | 43.4812 | off_peak | 662.3688 |  |  | 6.16 | 0 | 93.84 | 143.0206 | 0
8561 | 671.6 | 138.793 | 23.2 | 28.2877 | 28.2877 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 35.7326 | 643.3123 | 0 | 0.05921 | 3.1578 | 0 | 0 | 94.3692 | 28.2877 | off_peak | 643.3123 |  |  | 4.21 | 0 | 95.79 | 89.327 | 0
8562 | 631.77 | 9.1175 | 22.7 | 1.8616 | 0 | 0 | 1.8616 | 1.8616 | 0 | 0 | 0 | 0 | 37.474 | 631.77 | 0 | 0.05921 | 3.2053 | 0 | 0 | 96.1105 | 0 | off_peak | 631.77 | 100 | 0 | 0 | 0 | 100 | 0 | 0
8563 | 589.46 | 0 | 22.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 37.474 | 589.46 | 0 | 0.05921 | 3.2738 | 0 | 0 | 96.1105 | 0 | off_peak | 589.46 |  |  | 0 | 0 | 100 | 0 | 0
8564 | 569 | 0 | 22.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 37.474 | 569 | 0 | 0.05921 | 3.3146 | 0 | 0 | 96.1105 | 0 | off_peak | 569 |  |  | 0 | 0 | 100 | 0 | 0
8565 | 574.76 | 0 | 22.8 | 0 | 0 | 0 | 0 | 6.7893 | 6.7893 | 0 | 0 | 0 | 43.8248 | 581.5493 | 0 | 0.05921 | 3.4839 | 0 | 0 | 96.1105 | 0 | off_peak | 574.76 | 0 | 100 | 0 | 0 | 100 | 0 | 0
8566 | 576.89 | 0 | 22.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 43.8248 | 576.89 | 0 | 0.05921 | 3.703 | 0 | 0 | 96.1105 | 0 | off_peak | 576.89 |  |  | 0 | 0 | 100 | 0 | 0
8567 | 561.28 | 0 | 23.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 43.8248 | 561.28 | 0 | 0.05921 | 4.137 | 0 | 0 | 96.1105 | 0 | off_peak | 561.28 |  |  | 0 | 0 | 100 | 0 | 0
8568 | 561.49 | 0 | 23.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 43.8248 | 561.49 | 0 | 0.05921 | 4.6009 | 0 | 0 | 96.1105 | 0 | off_peak | 561.49 |  |  | 0 | 0 | 100 | 0 | 0
8569 | 584.61 | 0 | 23.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 43.8248 | 584.61 | 0 | 0.05921 | 4.7682 | 0 | 0 | 96.1105 | 0 | off_peak | 584.61 |  |  | 0 | 0 | 100 | 0 | 0
8570 | 563.91 | 0 | 23.3 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 55.423 | 576.3089 | 0 | 0.05921 | 4.6031 | 0 | 0 | 96.1105 | 0 | off_peak | 563.91 | 0 | 100 | 0 | 0 | 100 | 0 | 0
8571 | 538.03 | 0 | 23.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 55.423 | 538.03 | 0 | 0.05921 | 4.3972 | 0 | 0 | 96.1105 | 0 | off_peak | 538.03 |  |  | 0 | 0 | 100 | 0 | 0
8572 | 567.86 | 0 | 23.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 55.423 | 567.86 | 0 | 0.05921 | 4.1831 | 0 | 0 | 96.1105 | 0 | off_peak | 567.86 |  |  | 0 | 0 | 100 | 0 | 0
8573 | 572.18 | 0 | 23.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 55.423 | 572.18 | 0 | 0.05921 | 3.9079 | 0 | 0 | 96.1105 | 0 | off_peak | 572.18 |  |  | 0 | 0 | 100 | 0 | 0
8574 | 650.64 | 0 | 23.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 55.423 | 650.64 | 0 | 0.05921 | 3.4771 | 0 | 0 | 96.1105 | 0 | off_peak | 650.64 |  |  | 0 | 0 | 100 | 0 | 0
8575 | 659.36 | 0 | 23.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 55.423 | 659.36 | 0 | 0.05921 | 3.0981 | 0 | 0 | 96.1105 | 0 | off_peak | 659.36 |  |  | 0 | 0 | 100 | 0 | 0
8576 | 642.03 | 24.68 | 24 | 5.0157 | 0 | 0 | 5.0157 | 5.0157 | 0 | 0 | 0 | 0 | 60.1147 | 642.03 | 0 | 0.05921 | 2.8157 | 0 | 0 | 100.8022 | 0 | off_peak | 642.03 | 100 | 0 | 0 | 0 | 100 | 0 | 0
8577 | 651.96 | 131.018 | 24.3 | 26.598 | 26.598 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60.1147 | 625.362 | 0 | 0.05921 | 2.6187 | 0 | 0 | 100.8022 | 26.598 | off_peak | 625.362 |  |  | 4.08 | 0 | 95.92 | 69.6523 | 0
8578 | 679.77 | 198.027 | 24.6 | 40.1582 | 40.1582 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60.1147 | 639.6118 | 0 | 0.05921 | 2.5028 | 0 | 0 | 100.8022 | 40.1582 | off_peak | 639.6118 |  |  | 5.91 | 0 | 94.09 | 100.5071 | 0
8579 | 638.82 | 258.034 | 24.9 | 52.2707 | 52.2707 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60.1147 | 586.5493 | 0 | 0.05921 | 2.4699 | 0 | 0 | 100.8022 | 52.2707 | off_peak | 586.5493 |  |  | 8.18 | 0 | 91.82 | 129.102 | 0
8580 | 680.05 | 36.1 | 25.3 | 7.3024 | 0 | 0 | 7.3024 | 7.3024 | 0 | 0 | 0 | 0 | 66.9454 | 680.05 | 0 | 0.05921 | 2.5409 | 0 | 0 | 107.633 | 0 | off_peak | 680.05 | 100 | 0 | 0 | 0 | 100 | 0 | 0
8581 | 642.5 | 185.665 | 25.6 | 37.516 | 37.516 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 66.9454 | 604.984 | 0 | 0.05921 | 2.7586 | 0 | 0 | 107.633 | 37.516 | off_peak | 604.984 |  |  | 5.84 | 0 | 94.16 | 103.49 | 0
8582 | 649.36 | 119.19 | 25.8 | 24.0665 | 24.0665 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 66.9454 | 625.2935 | 0 | 0.05921 | 3.1186 | 0 | 0 | 107.633 | 24.0665 | off_peak | 625.2935 |  |  | 3.71 | 0 | 96.29 | 75.0528 | 0
8583 | 649.89 | 123.146 | 25.7 | 24.8742 | 24.8742 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 66.9454 | 625.0158 | 0 | 0.05921 | 3.5491 | 0 | 0 | 107.633 | 24.8742 | off_peak | 625.0158 |  |  | 3.83 | 0 | 96.17 | 88.2815 | 0
8584 | 653.49 | 174.461 | 25.5 | 35.2648 | 35.2648 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 66.9454 | 618.2252 | 0 | 0.05921 | 3.7196 | 0 | 0 | 107.633 | 35.2648 | off_peak | 618.2252 |  |  | 5.4 | 0 | 94.6 | 131.1694 | 0
8585 | 655.99 | 26.6 | 25 | 5.3865 | 0 | 0 | 5.3865 | 5.3865 | 0 | 0 | 0 | 0 | 71.984 | 655.99 | 0 | 0.05921 | 3.8756 | 0 | 0 | 112.6716 | 0 | off_peak | 655.99 | 100 | 0 | 0 | 0 | 100 | 0 | 0
8586 | 581.24 | 3.8 | 24.5 | 0.77089 | 0.77089 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 71.984 | 580.4691 | 0 | 0.05921 | 4.084 | 0 | 0 | 112.6716 | 0.77089 | off_peak | 580.4691 |  |  | 0.13 | 0 | 99.87 | 3.1483 | 0
8587 | 574.35 | 0 | 24.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 71.984 | 574.35 | 0 | 0.05921 | 4.1689 | 0 | 0 | 112.6716 | 0 | off_peak | 574.35 |  |  | 0 | 0 | 100 | 0 | 0
8588 | 550.61 | 0 | 24.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 71.984 | 550.61 | 0 | 0.05921 | 4.2855 | 0 | 0 | 112.6716 | 0 | off_peak | 550.61 |  |  | 0 | 0 | 100 | 0 | 0
8589 | 543.32 | 0 | 24.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 71.984 | 543.32 | 0 | 0.05921 | 4.4956 | 0 | 0 | 112.6716 | 0 | off_peak | 543.32 |  |  | 0 | 0 | 100 | 0 | 0
8590 | 557.24 | 0 | 24.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 71.984 | 557.24 | 0 | 0.05921 | 4.6316 | 0 | 0 | 112.6716 | 0 | off_peak | 557.24 |  |  | 0 | 0 | 100 | 0 | 0
8591 | 541.81 | 0 | 24.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 71.984 | 541.81 | 0 | 0.05921 | 4.7886 | 0 | 0 | 112.6716 | 0 | off_peak | 541.81 |  |  | 0 | 0 | 100 | 0 | 0
8592 | 529.56 | 0 | 24.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 71.984 | 529.56 | 0 | 0.05921 | 4.9272 | 0 | 0 | 112.6716 | 0 | off_peak | 529.56 |  |  | 0 | 0 | 100 | 0 | 0
8593 | 558.34 | 0 | 24.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 71.984 | 558.34 | 0 | 0.05921 | 4.9579 | 0 | 0 | 112.6716 | 0 | off_peak | 558.34 |  |  | 0 | 0 | 100 | 0 | 0
8594 | 540.44 | 0 | 24.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 71.984 | 540.44 | 0 | 0.05921 | 4.6036 | 0 | 0 | 112.6716 | 0 | off_peak | 540.44 |  |  | 0 | 0 | 100 | 0 | 0
8595 | 539.47 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 71.984 | 539.47 | 0 | 0.05921 | 4.3126 | 0 | 0 | 112.6716 | 0 | off_peak | 539.47 |  |  | 0 | 0 | 100 | 0 | 0
8596 | 545.72 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 71.984 | 545.72 | 0 | 0.05921 | 4.0839 | 0 | 0 | 112.6716 | 0 | off_peak | 545.72 |  |  | 0 | 0 | 100 | 0 | 0
8597 | 571.34 | 0 | 23.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 71.984 | 571.34 | 0 | 0.05921 | 3.8551 | 0 | 0 | 112.6716 | 0 | off_peak | 571.34 |  |  | 0 | 0 | 100 | 0 | 0
8598 | 683.67 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 71.984 | 683.67 | 0 | 0.05921 | 3.5646 | 0 | 0 | 112.6716 | 0 | off_peak | 683.67 |  |  | 0 | 0 | 100 | 0 | 0
8599 | 695.35 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 71.984 | 695.35 | 0 | 0.05921 | 3.1836 | 0 | 0 | 112.6716 | 0 | on_peak | 695.35 |  |  | 0 | 0 | 100 | 0 | 0
8600 | 724.26 | 8.55 | 23.9 | 1.7382 | 0 | 0 | 1.7382 | 1.7382 | 0 | 0 | 0 | 0 | 73.61 | 724.26 | 0 | 0.05921 | 2.9261 | 0 | 0 | 114.2975 | 0 | on_peak | 724.26 | 100 | 0 | 0 | 0 | 100 | 0 | 0
8601 | 695.4 | 31.8589 | 23.3 | 6.4909 | 6.4909 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 73.61 | 688.9091 | 0 | 0.05921 | 2.7222 | 0 | 0 | 114.2975 | 6.4909 | on_peak | 688.9091 |  |  | 0.93 | 0 | 99.07 | 17.6693 | 0
8602 | 687.38 | 27.55 | 22.7 | 5.6251 | 5.6251 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 73.61 | 681.7549 | 0 | 0.05921 | 2.5839 | 0 | 0 | 114.2975 | 5.6251 | on_peak | 681.7549 |  |  | 0.82 | 0 | 99.18 | 14.5344 | 0
8603 | 699.2 | 66.1897 | 22.5 | 13.524 | 13.524 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 73.61 | 685.676 | 0 | 0.05921 | 2.5416 | 0 | 0 | 114.2975 | 13.524 | off_peak | 685.676 |  |  | 1.93 | 0 | 98.07 | 34.3724 | 0
8604 | 654.2 | 88.001 | 22.6 | 17.9742 | 17.9742 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 73.61 | 636.2258 | 0 | 0.05921 | 2.5866 | 0 | 0 | 114.2975 | 17.9742 | off_peak | 636.2258 |  |  | 2.75 | 0 | 97.25 | 46.492 | 0
8605 | 680.55 | 168.941 | 22.6 | 34.5061 | 34.5061 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 73.61 | 646.0439 | 0 | 0.05921 | 2.7514 | 0 | 0 | 114.2975 | 34.5061 | off_peak | 646.0439 |  |  | 5.07 | 0 | 94.93 | 94.94 | 0
8606 | 661.68 | 68.4 | 22.5 | 13.9757 | 13.9757 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 73.61 | 647.7043 | 0 | 0.05921 | 3.0244 | 0 | 0 | 114.2975 | 13.9757 | off_peak | 647.7043 |  |  | 2.11 | 0 | 97.89 | 42.2685 | 0
8607 | 642.63 | 133.153 | 22.2 | 27.2353 | 27.2353 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 73.61 | 615.3947 | 0 | 0.05921 | 3.5534 | 0 | 0 | 114.2975 | 27.2353 | off_peak | 615.3947 |  |  | 4.24 | 0 | 95.76 | 96.7787 | 0
8608 | 580.32 | 64.3114 | 21.8 | 13.1731 | 13.1731 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 73.61 | 567.1469 | 0 | 0.05921 | 4.105 | 0 | 0 | 114.2975 | 13.1731 | off_peak | 567.1469 |  |  | 2.27 | 0 | 97.73 | 54.0761 | 0
8609 | 531.83 | 42.4814 | 20.9 | 8.7295 | 8.7295 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 73.61 | 523.1005 | 0 | 0.05921 | 4.4232 | 0 | 0 | 114.2975 | 8.7295 | off_peak | 523.1005 |  |  | 1.64 | 0 | 98.36 | 38.612 | 0
8610 | 537.75 | 3.8 | 19.9 | 0.78363 | 0 | 0 | 0.78363 | 0.78363 | 0 | 0 | 0 | 0 | 74.343 | 537.75 | 0 | 0.05921 | 4.5253 | 0 | 0 | 115.0306 | 0 | off_peak | 537.75 | 100 | 0 | 0 | 0 | 100 | 0 | 0
8611 | 537.85 | 0 | 19.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.343 | 537.85 | 0 | 0.05921 | 4.5839 | 0 | 0 | 115.0306 | 0 | on_peak | 537.85 |  |  | 0 | 0 | 100 | 0 | 0
8612 | 539.32 | 0 | 18.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.343 | 539.32 | 0 | 0.05921 | 4.5749 | 0 | 0 | 115.0306 | 0 | on_peak | 539.32 |  |  | 0 | 0 | 100 | 0 | 0
8613 | 546.84 | 0 | 17.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.343 | 546.84 | 0 | 0.05921 | 4.4956 | 0 | 0 | 115.0306 | 0 | on_peak | 546.84 |  |  | 0 | 0 | 100 | 0 | 0
8614 | 525.27 | 0 | 17.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.343 | 525.27 | 0 | 0.05921 | 4.3641 | 0 | 0 | 115.0306 | 0 | on_peak | 525.27 |  |  | 0 | 0 | 100 | 0 | 0
8615 | 530.31 | 0 | 16.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.343 | 530.31 | 0 | 0.05921 | 4.4293 | 0 | 0 | 115.0306 | 0 | off_peak | 530.31 |  |  | 0 | 0 | 100 | 0 | 0
8616 | 548.28 | 0 | 15.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.343 | 548.28 | 0 | 0.05921 | 4.6348 | 0 | 0 | 115.0306 | 0 | off_peak | 548.28 |  |  | 0 | 0 | 100 | 0 | 0
8617 | 539.53 | 0 | 15.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.343 | 539.53 | 0 | 0.05921 | 4.6381 | 0 | 0 | 115.0306 | 0 | off_peak | 539.53 |  |  | 0 | 0 | 100 | 0 | 0
8618 | 526.54 | 0 | 14.7 | 0 | 0 | 0 | 0 | 0.050611 | 0.050611 | 0 | 0 | 0 | 74.3904 | 526.5906 | 0 | 0.05921 | 4.4809 | 0 | 0 | 115.0306 | 0 | off_peak | 526.54 | 0 | 100 | 0 | 0 | 100 | 0 | 0
8619 | 537.87 | 0 | 14.3 | 0 | 0 | 0 | 0 | 0.0032688 | 0.0032688 | 0 | 0 | 0 | 74.3934 | 537.8733 | 0 | 0.05921 | 4.3593 | 0 | 0 | 115.0306 | 0 | off_peak | 537.87 | 0 | 100 | 0 | 0 | 100 | 0 | 0
8620 | 531.85 | 0 | 14 | 0 | 0 | 0 | 0 | 0.00021111 | 0.00021111 | 0 | 0 | 0 | 74.3936 | 531.8502 | 0 | 0.05921 | 4.1348 | 0 | 0 | 115.0306 | 0 | off_peak | 531.85 | 0 | 100 | 0 | 0 | 100 | 0 | 0
8621 | 554.17 | 0 | 13.7 | 0 | 0 | 0 | 0 | 1.3635e-05 | 1.3635e-05 | 0 | 0 | 0 | 74.3936 | 554.17 | 0 | 0.05921 | 3.8935 | 0 | 0 | 115.0306 | 0 | off_peak | 554.17 | 0 | 100 | 0 | 0 | 100 | 0 | 0
8622 | 647.67 | 0 | 13.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 647.67 | 0 | 0.05921 | 3.5234 | 0 | 0 | 115.0306 | 0 | off_peak | 647.67 |  |  | 0 | 0 | 100 | 0 | 0
8623 | 710.17 | 0 | 13.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 710.17 | 0 | 0.088511 | 3.1583 | 0 | 0 | 115.0306 | 0 | on_peak | 710.17 |  |  | 0 | 0 | 100 | 0 | 0
8624 | 688.27 | 5.7 | 13.9 | 1.2004 | 1.2004 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 687.0696 | 0 | 0.088511 | 2.8415 | 0 | 0 | 115.0306 | 1.2004 | on_peak | 687.0696 |  |  | 0.17 | 0 | 99.83 | 3.4109 | 0
8625 | 786.33 | 16.15 | 14.8 | 3.3905 | 3.3905 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3936 | 782.9395 | 0 | 0.088511 | 2.6591 | 0 | 0 | 115.0306 | 3.3905 | on_peak | 782.9395 |  |  | 0.43 | 0 | 99.57 | 9.0155 | 0
8626 | 771.22 | 14.25 | 15.8 | 2.9812 | 2.9812 | 0 | 0 | 0 | 0 | 62.63 | 62.63 | 0 | 7.4394 | 705.6088 | 0 | 0.088511 | 2.5641 | 0 | 0 | 115.0306 | 2.9812 | on_peak | 705.6088 |  |  | 0.39 | 8.12 | 91.49 | 7.6441 | 0
8627 | 758.34 | 62.7 | 17.1 | 13.0578 | 0.65891 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 0 | 19.0375 | 757.6811 | 0 | 0.05921 | 2.5655 | 0 | 0 | 126.6287 | 0.65891 | off_peak | 757.6811 | 100 | 0 | 0.09 | 0 | 99.91 | 1.6904 | 0
8628 | 831.17 | 68.4 | 18.2 | 14.1901 | 1.7911 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 0 | 30.6357 | 829.3789 | 0 | 0.05921 | 2.7317 | 0 | 0 | 138.2269 | 1.7911 | off_peak | 829.3789 | 100 | 0 | 0.22 | 0 | 99.78 | 4.8929 | 0
8629 | 746.07 | 60.4705 | 19 | 12.5098 | 12.5098 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 42.2338 | 745.9592 | 0 | 0.05921 | 3.0266 | 0 | 0 | 138.2269 | 12.5098 | off_peak | 733.5602 | 0 | 100 | 1.68 | 0 | 98.32 | 37.8615 | 0
8630 | 770.92 | 112.77 | 19.7 | 23.2716 | 23.2716 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 53.832 | 760.0473 | 0 | 0.05921 | 3.364 | 0 | 0 | 138.2269 | 23.2716 | off_peak | 747.6484 | 0 | 100 | 3.02 | 0 | 96.98 | 78.2855 | 0
8631 | 819.8 | 50.35 | 20 | 10.3794 | 0 | 0 | 10.3794 | 12.3989 | 2.0195 | 0 | 0 | 0 | 65.4301 | 821.8195 | 0 | 0.05921 | 3.7634 | 0 | 0 | 147.9359 | 0 | off_peak | 819.8 | 83.71 | 16.29 | 0 | 0 | 100 | 0 | 0
8632 | 774.96 | 42.1716 | 20 | 8.6935 | 0 | 0 | 8.6935 | 8.9635 | 0.27008 | 0 | 0 | 0 | 73.8147 | 775.2301 | 0 | 0.05921 | 4.134 | 0 | 0 | 156.0679 | 0 | off_peak | 774.96 | 96.99 | 3.01 | 0 | 0 | 100 | 0 | 0
8633 | 719.64 | 21.85 | 19.3 | 4.5154 | 3.9365 | 0 | 0.57892 | 0.57892 | 0 | 0 | 0 | 0 | 74.3563 | 715.7035 | 0 | 0.05921 | 4.4081 | 0 | 0 | 156.6094 | 3.9365 | off_peak | 715.7035 | 100 | 0 | 0.55 | 0 | 99.45 | 17.3524 | 0
8634 | 769.69 | 2.85 | 18.6 | 0.59042 | 0.55303 | 0 | 0.03739 | 0.03739 | 0 | 0 | 0 | 0 | 74.3912 | 769.137 | 0 | 0.05921 | 4.5518 | 0 | 0 | 156.6444 | 0.55303 | off_peak | 769.137 | 100 | 0 | 0.07 | 0 | 99.93 | 2.5173 | 0
8635 | 764.14 | 0 | 18.3 | 0 | 0 | 0 | 0 | 0 | 0 | 62.6277 | 62.6277 | 0 | 7.4394 | 701.5123 | 0 | 0.088511 | 4.6933 | 0 | 0 | 156.6444 | 0 | on_peak | 701.5123 |  |  | 0 | 8.2 | 91.8 | 0 | 0
8636 | 746.25 | 0 | 17.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 746.25 | 0 | 0.088511 | 4.7665 | 0 | 0 | 156.6444 | 0 | on_peak | 746.25 |  |  | 0 | 0 | 100 | 0 | 0
8637 | 715.83 | 0 | 17.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 715.83 | 0 | 0.088511 | 4.8333 | 0 | 0 | 156.6444 | 0 | on_peak | 715.83 |  |  | 0 | 0 | 100 | 0 | 0
8638 | 715.7 | 0 | 17.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 715.7 | 0 | 0.088511 | 5.085 | 0 | 0 | 156.6444 | 0 | on_peak | 715.7 |  |  | 0 | 0 | 100 | 0 | 0
8639 | 693.3 | 0 | 17.4 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 19.0375 | 705.6989 | 0 | 0.05921 | 5.3582 | 0 | 0 | 156.6444 | 0 | off_peak | 693.3 | 0 | 100 | 0 | 0 | 100 | 0 | 0
8640 | 687.27 | 0 | 17.4 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 30.6357 | 699.6689 | 0 | 0.05921 | 5.5237 | 0 | 0 | 156.6444 | 0 | off_peak | 687.27 | 0 | 100 | 0 | 0 | 100 | 0 | 0
8641 | 678.13 | 0 | 17.3 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 42.2338 | 690.5289 | 0 | 0.05921 | 5.6336 | 0 | 0 | 156.6444 | 0 | off_peak | 678.13 | 0 | 100 | 0 | 0 | 100 | 0 | 0
8642 | 603.51 | 0 | 17.3 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 53.832 | 615.9089 | 0 | 0.05921 | 5.3211 | 0 | 0 | 156.6444 | 0 | off_peak | 603.51 | 0 | 100 | 0 | 0 | 100 | 0 | 0
8643 | 583.59 | 0 | 17.2 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 65.4301 | 595.9889 | 0 | 0.05921 | 4.9667 | 0 | 0 | 156.6444 | 0 | off_peak | 583.59 | 0 | 100 | 0 | 0 | 100 | 0 | 0
8644 | 636.27 | 0 | 17.1 | 0 | 0 | 0 | 0 | 8.9635 | 8.9635 | 0 | 0 | 0 | 73.8147 | 645.2335 | 0 | 0.05921 | 4.594 | 0 | 0 | 156.6444 | 0 | off_peak | 636.27 | 0 | 100 | 0 | 0 | 100 | 0 | 0
8645 | 579.19 | 0 | 17 | 0 | 0 | 0 | 0 | 0.57892 | 0.57892 | 0 | 0 | 0 | 74.3563 | 579.7689 | 0 | 0.05921 | 4.1814 | 0 | 0 | 156.6444 | 0 | off_peak | 579.19 | 0 | 100 | 0 | 0 | 100 | 0 | 0
8646 | 647.89 | 0 | 17 | 0 | 0 | 0 | 0 | 0.03739 | 0.03739 | 0 | 0 | 0 | 74.3912 | 647.9274 | 0 | 0.05921 | 3.6591 | 0 | 0 | 156.6444 | 0 | off_peak | 647.89 | 0 | 100 | 0 | 0 | 100 | 0 | 0
8647 | 715.26 | 0 | 17.1 | 0 | 0 | 0 | 0 | 0 | 0 | 62.6277 | 62.6277 | 0 | 7.4394 | 652.6323 | 0 | 0.088511 | 3.1794 | 62.6277 | 0 | 89.6925 | 62.6277 | on_peak | 652.6323 |  |  | 0 | 8.76 | 91.24 | 199.1166 | 0
8648 | 730.65 | 8.55 | 17.7 | 1.7769 | 1.7769 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 728.8731 | 0 | 0.088511 | 2.8302 | 0 | 0 | 89.6925 | 1.7769 | on_peak | 728.8731 |  |  | 0.24 | 0 | 99.76 | 5.0289 | 0
8649 | 762.51 | 67.3003 | 18.6 | 13.9423 | 13.9423 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 748.5677 | 0 | 0.088511 | 2.6105 | 0 | 0 | 89.6925 | 13.9423 | on_peak | 748.5677 |  |  | 1.83 | 0 | 98.17 | 36.3966 | 0
8650 | 736.23 | 69.0906 | 19.5 | 14.2679 | 14.2679 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 721.9621 | 0 | 0.088511 | 2.5236 | 0 | 0 | 89.6925 | 14.2679 | on_peak | 721.9621 |  |  | 1.94 | 0 | 98.06 | 36.0058 | 0
8651 | 695.04 | 163.642 | 20.6 | 33.6624 | 33.6624 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 19.0375 | 673.7765 | 0 | 0.05921 | 2.5766 | 0 | 0 | 89.6925 | 33.6624 | off_peak | 661.3776 | 0 | 100 | 4.84 | 0 | 95.16 | 86.7337 | 0
8652 | 800.36 | 185.428 | 21.4 | 38.0358 | 38.0358 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 30.6357 | 774.7231 | 0 | 0.05921 | 2.7715 | 0 | 0 | 89.6925 | 38.0358 | off_peak | 762.3242 | 0 | 100 | 4.75 | 0 | 95.25 | 105.4153 | 0
8653 | 743.14 | 107.313 | 21.8 | 21.9812 | 21.9812 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 42.2338 | 733.5577 | 0 | 0.05921 | 3.0929 | 0 | 0 | 89.6925 | 21.9812 | off_peak | 721.1588 | 0 | 100 | 2.96 | 0 | 97.04 | 67.9854 | 0
8654 | 738.01 | 234.738 | 22 | 48.0478 | 48.0478 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 53.832 | 702.3611 | 0 | 0.05921 | 3.4148 | 0 | 0 | 89.6925 | 48.0478 | off_peak | 689.9622 | 0 | 100 | 6.51 | 0 | 93.49 | 164.0754 | 0
8655 | 791.48 | 450.586 | 22 | 92.2291 | 79.8302 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 0 | 65.4301 | 711.6498 | 0 | 0.05921 | 3.6761 | 0 | 0 | 101.2907 | 79.8302 | off_peak | 711.6498 | 100 | 0 | 10.09 | 0 | 89.91 | 293.4664 | 0
8656 | 776.43 | 346.104 | 21.9 | 70.8682 | 70.8682 | 0 | 0 | 8.9635 | 8.9635 | 0 | 0 | 0 | 73.8147 | 714.5253 | 0 | 0.05921 | 3.6575 | 0 | 0 | 101.2907 | 70.8682 | off_peak | 705.5618 | 0 | 100 | 9.13 | 0 | 90.87 | 259.199 | 0
8657 | 751.45 | 168.697 | 21.3 | 34.6162 | 34.0373 | 0 | 0.57892 | 0.57892 | 0 | 0 | 0 | 0 | 74.3563 | 717.4127 | 0 | 0.05921 | 3.5188 | 0 | 0 | 101.8322 | 34.0373 | off_peak | 717.4127 | 100 | 0 | 4.53 | 0 | 95.47 | 119.7714 | 0
8658 | 764.03 | 15.284 | 20.7 | 3.1429 | 3.1055 | 0 | 0.03739 | 0.03739 | 0 | 0 | 0 | 0 | 74.3912 | 760.9245 | 0 | 0.05921 | 3.4698 | 0 | 0 | 101.8672 | 3.1055 | off_peak | 760.9245 | 100 | 0 | 0.41 | 0 | 99.59 | 10.7754 | 0
8659 | 710.47 | 0 | 20.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3912 | 710.47 | 0 | 0.088511 | 3.5255 | 0 | 0 | 101.8672 | 0 | on_peak | 710.47 |  |  | 0 | 0 | 100 | 0 | 0
8660 | 719.39 | 0 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3912 | 719.39 | 0 | 0.088511 | 3.7379 | 0 | 0 | 101.8672 | 0 | on_peak | 719.39 |  |  | 0 | 0 | 100 | 0 | 0
8661 | 735.04 | 0 | 19.5 | 0 | 0 | 0 | 0 | 0 | 0 | 62.6277 | 62.6277 | 0 | 7.4394 | 672.4123 | 0 | 0.088511 | 4.0818 | 0 | 0 | 101.8672 | 0 | on_peak | 672.4123 |  |  | 0 | 8.52 | 91.48 | 0 | 0
8662 | 709.88 | 0 | 18.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 709.88 | 0 | 0.088511 | 4.4639 | 0 | 0 | 101.8672 | 0 | on_peak | 709.88 |  |  | 0 | 0 | 100 | 0 | 0
8663 | 712.44 | 0 | 18.4 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 19.0375 | 724.8389 | 0 | 0.05921 | 4.932 | 0 | 0 | 101.8672 | 0 | off_peak | 712.44 | 0 | 100 | 0 | 0 | 100 | 0 | 0
8664 | 718.62 | 0 | 18 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 30.6357 | 731.0189 | 0 | 0.05921 | 5.133 | 0 | 0 | 101.8672 | 0 | off_peak | 718.62 | 0 | 100 | 0 | 0 | 100 | 0 | 0
8665 | 677.34 | 0 | 17.6 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 42.2338 | 689.7389 | 0 | 0.05921 | 5.2956 | 0 | 0 | 101.8672 | 0 | off_peak | 677.34 | 0 | 100 | 0 | 0 | 100 | 0 | 0
8666 | 618.4 | 0 | 17.1 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 53.832 | 630.7989 | 0 | 0.05921 | 4.9943 | 0 | 0 | 101.8672 | 0 | off_peak | 618.4 | 0 | 100 | 0 | 0 | 100 | 0 | 0
8667 | 583.5 | 0 | 16.5 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 65.4301 | 595.8989 | 0 | 0.05921 | 4.6925 | 0 | 0 | 101.8672 | 0 | off_peak | 583.5 | 0 | 100 | 0 | 0 | 100 | 0 | 0
8668 | 558.37 | 0 | 15.9 | 0 | 0 | 0 | 0 | 8.9635 | 8.9635 | 0 | 0 | 0 | 73.8147 | 567.3335 | 0 | 0.05921 | 4.3559 | 0 | 0 | 101.8672 | 0 | off_peak | 558.37 | 0 | 100 | 0 | 0 | 100 | 0 | 0
8669 | 566.42 | 0 | 15.5 | 0 | 0 | 0 | 0 | 0.57892 | 0.57892 | 0 | 0 | 0 | 74.3563 | 566.9989 | 0 | 0.05921 | 3.9731 | 0 | 0 | 101.8672 | 0 | off_peak | 566.42 | 0 | 100 | 0 | 0 | 100 | 0 | 0
8670 | 653.74 | 0 | 15.2 | 0 | 0 | 0 | 0 | 0.03739 | 0.03739 | 0 | 0 | 0 | 74.3912 | 653.7774 | 0 | 0.05921 | 3.4651 | 0 | 0 | 101.8672 | 0 | off_peak | 653.74 | 0 | 100 | 0 | 0 | 100 | 0 | 0
8671 | 704.34 | 0 | 15.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3912 | 704.34 | 0 | 0.088511 | 3.0437 | 0 | 0 | 101.8672 | 0 | on_peak | 704.34 |  |  | 0 | 0 | 100 | 0 | 0
8672 | 717.14 | 42.8682 | 15.2 | 8.9871 | 8.9871 | 0 | 0 | 0 | 0 | 62.6277 | 62.6277 | 0 | 7.4394 | 645.5252 | 0 | 0.088511 | 2.7198 | 0 | 0 | 101.8672 | 8.9871 | on_peak | 645.5252 |  |  | 1.25 | 8.73 | 90.01 | 24.4433 | 0
8673 | 730.69 | 219.692 | 15.6 | 45.9931 | 45.9931 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 684.6969 | 0 | 0.088511 | 2.5609 | 0 | 0 | 101.8672 | 45.9931 | on_peak | 684.6969 |  |  | 6.29 | 0 | 93.71 | 117.7844 | 0
8674 | 745.69 | 398.979 | 16.2 | 83.3528 | 83.3528 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 662.3372 | 0 | 0.088511 | 2.4882 | 0 | 0 | 101.8672 | 83.3528 | on_peak | 662.3372 |  |  | 11.18 | 0 | 88.82 | 207.3948 | 0
8675 | 707.05 | 541.584 | 16.9 | 112.8688 | 112.8688 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 19.0375 | 606.5802 | 0 | 0.05921 | 2.5444 | 0 | 0 | 101.8672 | 112.8688 | off_peak | 594.1812 | 0 | 100 | 15.96 | 0 | 84.04 | 287.1814 | 0
8676 | 751.1 | 555.611 | 17.6 | 115.5085 | 115.5085 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 30.6357 | 647.9904 | 0 | 0.05921 | 2.7831 | 0 | 0 | 101.8672 | 115.5085 | off_peak | 635.5915 | 0 | 100 | 15.38 | 0 | 84.62 | 321.4763 | 0
8677 | 740.23 | 578.132 | 18.3 | 119.8955 | 119.8955 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 42.2338 | 632.7334 | 0 | 0.05921 | 3.1621 | 0 | 0 | 101.8672 | 119.8955 | off_peak | 620.3345 | 0 | 100 | 16.2 | 0 | 83.8 | 379.1275 | 0
8678 | 752.86 | 538.85 | 18.7 | 111.5919 | 111.5919 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 53.832 | 653.667 | 0 | 0.05921 | 3.6235 | 0 | 0 | 101.8672 | 111.5919 | off_peak | 641.2681 | 0 | 100 | 14.82 | 0 | 85.18 | 404.3557 | 0
8679 | 763.81 | 435.224 | 18.8 | 90.1 | 90.1 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 65.4301 | 686.109 | 0 | 0.05921 | 4.042 | 0 | 0 | 101.8672 | 90.1 | off_peak | 673.71 | 0 | 100 | 11.8 | 0 | 88.2 | 364.1878 | 0
8680 | 693.08 | 358.797 | 18.7 | 74.3042 | 74.3042 | 0 | 0 | 8.9635 | 8.9635 | 0 | 0 | 0 | 73.8147 | 627.7393 | 0 | 0.05921 | 4.2681 | 0 | 0 | 101.8672 | 74.3042 | off_peak | 618.7758 | 0 | 100 | 10.72 | 0 | 89.28 | 317.1397 | 0
8681 | 742.68 | 174.154 | 17.9 | 36.1676 | 35.5887 | 0 | 0.57892 | 0.57892 | 0 | 0 | 0 | 0 | 74.3563 | 707.0913 | 0 | 0.05921 | 4.303 | 0 | 0 | 102.4087 | 35.5887 | off_peak | 707.0913 | 100 | 0 | 4.79 | 0 | 95.21 | 153.1386 | 0
8682 | 724.61 | 16.4097 | 17.1 | 3.4175 | 3.3801 | 0 | 0.03739 | 0.03739 | 0 | 0 | 0 | 0 | 74.3912 | 721.2299 | 0 | 0.05921 | 4.3271 | 0 | 0 | 102.4437 | 3.3801 | off_peak | 721.2299 | 100 | 0 | 0.47 | 0 | 99.53 | 14.6259 | 0
8683 | 719.28 | 0 | 16.8 | 0 | 0 | 0 | 0 | 0 | 0 | 62.6277 | 62.6277 | 0 | 7.4394 | 656.6523 | 0 | 0.088511 | 4.2035 | 0 | 0 | 102.4437 | 0 | on_peak | 656.6523 |  |  | 0 | 8.71 | 91.29 | 0 | 0
8684 | 730.21 | 0 | 16.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 730.21 | 0 | 0.088511 | 3.8683 | 0 | 0 | 102.4437 | 0 | on_peak | 730.21 |  |  | 0 | 0 | 100 | 0 | 0
8685 | 698.44 | 0 | 16.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 698.44 | 0 | 0.088511 | 3.5264 | 0 | 0 | 102.4437 | 0 | on_peak | 698.44 |  |  | 0 | 0 | 100 | 0 | 0
8686 | 708.44 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 708.44 | 0 | 0.088511 | 3.3539 | 0 | 0 | 102.4437 | 0 | on_peak | 708.44 |  |  | 0 | 0 | 100 | 0 | 0
8687 | 692.54 | 0 | 15.8 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 19.0375 | 704.9389 | 0 | 0.05921 | 3.7848 | 0 | 0 | 102.4437 | 0 | off_peak | 692.54 | 0 | 100 | 0 | 0 | 100 | 0 | 0
8688 | 657.56 | 0 | 15.7 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 30.6357 | 669.9589 | 0 | 0.05921 | 4.5259 | 0 | 0 | 102.4437 | 0 | off_peak | 657.56 | 0 | 100 | 0 | 0 | 100 | 0 | 0
8689 | 634.19 | 0 | 15.6 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 42.2338 | 646.5889 | 0 | 0.05921 | 4.8938 | 0 | 0 | 102.4437 | 0 | off_peak | 634.19 | 0 | 100 | 0 | 0 | 100 | 0 | 0
8690 | 602.15 | 0 | 15.5 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 53.832 | 614.5489 | 0 | 0.05921 | 4.7585 | 0 | 0 | 102.4437 | 0 | off_peak | 602.15 | 0 | 100 | 0 | 0 | 100 | 0 | 0
8691 | 585.92 | 0 | 15.4 | 0 | 0 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 65.4301 | 598.3189 | 0 | 0.05921 | 4.5308 | 0 | 0 | 102.4437 | 0 | off_peak | 585.92 | 0 | 100 | 0 | 0 | 100 | 0 | 0
8692 | 546.16 | 0 | 15.2 | 0 | 0 | 0 | 0 | 8.9635 | 8.9635 | 0 | 0 | 0 | 73.8147 | 555.1235 | 0 | 0.05921 | 4.258 | 0 | 0 | 102.4437 | 0 | off_peak | 546.16 | 0 | 100 | 0 | 0 | 100 | 0 | 0
8693 | 563.06 | 0 | 15 | 0 | 0 | 0 | 0 | 0.57892 | 0.57892 | 0 | 0 | 0 | 74.3563 | 563.6389 | 0 | 0.05921 | 3.8566 | 0 | 0 | 102.4437 | 0 | off_peak | 563.06 | 0 | 100 | 0 | 0 | 100 | 0 | 0
8694 | 602.35 | 0 | 14.8 | 0 | 0 | 0 | 0 | 0.03739 | 0.03739 | 0 | 0 | 0 | 74.3912 | 602.3874 | 0 | 0.05921 | 3.3591 | 0 | 0 | 102.4437 | 0 | off_peak | 602.35 | 0 | 100 | 0 | 0 | 100 | 0 | 0
8695 | 617.04 | 0 | 14.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3912 | 617.04 | 0 | 0.088511 | 2.9742 | 0 | 0 | 102.4437 | 0 | on_peak | 617.04 |  |  | 0 | 0 | 100 | 0 | 0
8696 | 683.71 | 35.3961 | 15.3 | 7.418 | 7.418 | 0 | 0 | 0 | 0 | 62.6277 | 62.6277 | 0 | 7.4394 | 613.6643 | 0 | 0.088511 | 2.7398 | 0 | 0 | 102.4437 | 7.418 | on_peak | 613.6643 |  |  | 1.08 | 9.16 | 89.76 | 20.3238 | 0
8697 | 676.76 | 204.091 | 16.2 | 42.6377 | 42.6377 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 634.1223 | 0 | 0.088511 | 2.6086 | 0 | 0 | 102.4437 | 42.6377 | on_peak | 634.1223 |  |  | 6.3 | 0 | 93.7 | 111.2255 | 0
8698 | 688.87 | 377.915 | 17.4 | 78.6216 | 78.6216 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 610.2484 | 0 | 0.088511 | 2.5722 | 0 | 0 | 102.4437 | 78.6216 | on_peak | 610.2484 |  |  | 11.41 | 0 | 88.59 | 202.2303 | 0
8699 | 697.28 | 483.258 | 18.6 | 100.1144 | 100.1144 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 19.0375 | 609.5645 | 0 | 0.05921 | 2.6774 | 0 | 0 | 102.4437 | 100.1144 | off_peak | 597.1656 | 0 | 100 | 14.36 | 0 | 85.64 | 268.0437 | 0
8700 | 739.08 | 271.926 | 19.6 | 56.1355 | 56.1355 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 30.6357 | 695.3435 | 0 | 0.05921 | 2.9836 | 0 | 0 | 102.4437 | 56.1355 | off_peak | 682.9445 | 0 | 100 | 7.6 | 0 | 92.4 | 167.4843 | 0
8701 | 663.47 | 438.856 | 20.2 | 90.404 | 90.404 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 42.2338 | 585.465 | 0 | 0.05921 | 3.3754 | 0 | 0 | 102.4437 | 90.404 | off_peak | 573.066 | 0 | 100 | 13.63 | 0 | 86.37 | 305.1475 | 0
8702 | 742.08 | 585.573 | 20.6 | 120.4568 | 120.4568 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 53.832 | 634.0221 | 0 | 0.05921 | 3.8163 | 0 | 0 | 102.4437 | 120.4568 | off_peak | 621.6232 | 0 | 100 | 16.23 | 0 | 83.77 | 459.7004 | 0
8703 | 677.52 | 485.434 | 20.8 | 99.7867 | 87.3877 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 0 | 65.4301 | 590.1323 | 0 | 0.05921 | 3.7734 | 0 | 0 | 114.0418 | 87.3877 | off_peak | 590.1323 | 100 | 0 | 12.9 | 0 | 87.1 | 329.7524 | 0
8704 | 684.37 | 338.395 | 20.6 | 69.6104 | 69.6104 | 0 | 0 | 8.9635 | 8.9635 | 0 | 0 | 0 | 73.8147 | 623.7231 | 0 | 0.05921 | 3.4821 | 0 | 0 | 114.0418 | 69.6104 | off_peak | 614.7596 | 0 | 100 | 10.17 | 0 | 89.83 | 242.3896 | 0
8705 | 700.48 | 153.211 | 19.9 | 31.5949 | 31.5949 | 0 | 0 | 0.57892 | 0.57892 | 0 | 0 | 0 | 74.3563 | 669.4641 | 0 | 0.05921 | 3.2712 | 0 | 0 | 114.0418 | 31.5949 | off_peak | 668.8851 | 0 | 100 | 4.51 | 0 | 95.49 | 103.3524 | 0
8706 | 649.31 | 14.8438 | 19 | 3.0708 | 3.0708 | 0 | 0 | 0.03739 | 0.03739 | 0 | 0 | 0 | 74.3912 | 646.2766 | 0 | 0.05921 | 3.0914 | 0 | 0 | 114.0418 | 3.0708 | off_peak | 646.2392 | 0 | 100 | 0.47 | 0 | 99.53 | 9.493 | 0
8707 | 636.94 | 0 | 18.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3912 | 636.94 | 0 | 0.088511 | 2.9989 | 0 | 0 | 114.0418 | 0 | on_peak | 636.94 |  |  | 0 | 0 | 100 | 0 | 0
8708 | 644.65 | 0 | 18.3 | 0 | 0 | 0 | 0 | 0 | 0 | 62.6277 | 62.6277 | 0 | 7.4394 | 582.0223 | 0 | 0.088511 | 2.9127 | 0 | 0 | 114.0418 | 0 | on_peak | 582.0223 |  |  | 0 | 9.71 | 90.29 | 0 | 0
8709 | 633.46 | 0 | 18.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 633.46 | 0 | 0.088511 | 3.0115 | 0 | 0 | 114.0418 | 0 | on_peak | 633.46 |  |  | 0 | 0 | 100 | 0 | 0
8710 | 608.6 | 0 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 608.6 | 0 | 0.088511 | 3.3154 | 0 | 0 | 114.0418 | 0 | on_peak | 608.6 |  |  | 0 | 0 | 100 | 0 | 0
8711 | 593.73 | 0 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 593.73 | 0 | 0.05921 | 3.9068 | 0 | 0 | 114.0418 | 0 | off_peak | 593.73 |  |  | 0 | 0 | 100 | 0 | 0
8712 | 598.17 | 0 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 598.17 | 0 | 0.05921 | 4.6093 | 0 | 0 | 114.0418 | 0 | off_peak | 598.17 |  |  | 0 | 0 | 100 | 0 | 0
8713 | 587.35 | 0 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 587.35 | 0 | 0.05921 | 4.9048 | 0 | 0 | 114.0418 | 0 | off_peak | 587.35 |  |  | 0 | 0 | 100 | 0 | 0
8714 | 515.41 | 0 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 515.41 | 0 | 0.05921 | 4.7663 | 0 | 0 | 114.0418 | 0 | off_peak | 515.41 |  |  | 0 | 0 | 100 | 0 | 0
8715 | 469.67 | 0 | 17.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 469.67 | 0 | 0.05921 | 4.5975 | 0 | 0 | 114.0418 | 0 | off_peak | 469.67 |  |  | 0 | 0 | 100 | 0 | 0
8716 | 505.86 | 0 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 505.86 | 0 | 0.05921 | 4.3263 | 0 | 0 | 114.0418 | 0 | off_peak | 505.86 |  |  | 0 | 0 | 100 | 0 | 0
8717 | 517.52 | 0 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 517.52 | 0 | 0.05921 | 4.0415 | 0 | 0 | 114.0418 | 0 | off_peak | 517.52 |  |  | 0 | 0 | 100 | 0 | 0
8718 | 561.55 | 0 | 18.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 561.55 | 0 | 0.05921 | 3.6322 | 0 | 0 | 114.0418 | 0 | off_peak | 561.55 |  |  | 0 | 0 | 100 | 0 | 0
8719 | 597.76 | 0 | 18.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4394 | 597.76 | 0 | 0.05921 | 3.3429 | 0 | 0 | 114.0418 | 0 | off_peak | 597.76 |  |  | 0 | 0 | 100 | 0 | 0
8720 | 619.33 | 24.6159 | 19.5 | 5.0834 | 0 | 0 | 5.0834 | 5.0834 | 0 | 0 | 0 | 0 | 12.1945 | 619.33 | 0 | 0.05921 | 3.1505 | 0 | 0 | 118.7969 | 0 | off_peak | 619.33 | 100 | 0 | 0 | 0 | 100 | 0 | 0
8721 | 623.26 | 204.954 | 20.7 | 42.1457 | 42.1457 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1945 | 581.1143 | 0 | 0.05921 | 3.0365 | 0 | 0 | 118.7969 | 42.1457 | off_peak | 581.1143 |  |  | 6.76 | 0 | 93.24 | 127.9763 | 0
8722 | 617.8 | 380.083 | 21.5 | 77.9366 | 77.9366 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1945 | 539.8634 | 0 | 0.05921 | 3.0167 | 0 | 0 | 118.7969 | 77.9366 | off_peak | 539.8634 |  |  | 12.62 | 0 | 87.38 | 235.1128 | 0
8723 | 646.29 | 517.855 | 22 | 105.9982 | 105.9982 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1945 | 540.2918 | 0 | 0.05921 | 3.0559 | 0 | 0 | 118.7969 | 105.9982 | off_peak | 540.2918 |  |  | 16.4 | 0 | 83.6 | 323.9183 | 0
8724 | 642.83 | 605 | 22.2 | 123.7474 | 123.7474 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1945 | 519.0826 | 0 | 0.05921 | 3.1986 | 0 | 0 | 118.7969 | 123.7474 | off_peak | 519.0826 |  |  | 19.25 | 0 | 80.75 | 395.8186 | 0
8725 | 581.05 | 631.164 | 22.4 | 129.007 | 129.007 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1945 | 452.043 | 0 | 0.05921 | 3.4742 | 0 | 0 | 118.7969 | 129.007 | off_peak | 452.043 |  |  | 22.2 | 0 | 77.8 | 448.1944 | 0
8726 | 576.39 | 592.454 | 22.5 | 121.0517 | 121.0517 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1945 | 455.3383 | 0 | 0.05921 | 3.9529 | 0 | 0 | 118.7969 | 121.0517 | off_peak | 455.3383 |  |  | 21 | 0 | 79 | 478.5026 | 0
8727 | 562.3 | 384.363 | 22.4 | 78.562 | 78.562 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1945 | 483.738 | 0 | 0.05921 | 4.1322 | 0 | 0 | 118.7969 | 78.562 | off_peak | 483.738 |  |  | 13.97 | 0 | 86.03 | 324.6302 | 0
8728 | 563.75 | 301.867 | 22.3 | 61.7222 | 61.7222 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1945 | 502.0278 | 0 | 0.05921 | 3.761 | 0 | 0 | 118.7969 | 61.7222 | off_peak | 502.0278 |  |  | 10.95 | 0 | 89.05 | 232.1377 | 0
8729 | 542.96 | 156.416 | 21.8 | 32.0391 | 32.0391 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1945 | 510.9209 | 0 | 0.05921 | 3.6444 | 0 | 0 | 118.7969 | 32.0391 | off_peak | 510.9209 |  |  | 5.9 | 0 | 94.1 | 116.7636 | 0
8730 | 491.36 | 15.8776 | 21.4 | 3.2569 | 3.2569 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1945 | 488.1031 | 0 | 0.05921 | 3.5954 | 0 | 0 | 118.7969 | 3.2569 | off_peak | 488.1031 |  |  | 0.66 | 0 | 99.34 | 11.7097 | 0
8731 | 463.88 | 0 | 21.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1945 | 463.88 | 0 | 0.05921 | 3.3833 | 0 | 0 | 118.7969 | 0 | off_peak | 463.88 |  |  | 0 | 0 | 100 | 0 | 0
8732 | 470.01 | 0 | 21.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1945 | 470.01 | 0 | 0.05921 | 3.2255 | 0 | 0 | 118.7969 | 0 | off_peak | 470.01 |  |  | 0 | 0 | 100 | 0 | 0
8733 | 431.11 | 0 | 21.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1945 | 431.11 | 0 | 0.05921 | 3.2826 | 0 | 0 | 118.7969 | 0 | off_peak | 431.11 |  |  | 0 | 0 | 100 | 0 | 0
8734 | 473.61 | 0 | 21.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1945 | 473.61 | 0 | 0.05921 | 3.2381 | 0 | 0 | 118.7969 | 0 | off_peak | 473.61 |  |  | 0 | 0 | 100 | 0 | 0
8735 | 462.3 | 0 | 21.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1945 | 462.3 | 0 | 0.05921 | 3.6435 | 0 | 0 | 118.7969 | 0 | off_peak | 462.3 |  |  | 0 | 0 | 100 | 0 | 0
8736 | 454.16 | 0 | 21.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1945 | 454.16 | 0 | 0.05921 | 4.3877 | 0 | 0 | 118.7969 | 0 | off_peak | 454.16 |  |  | 0 | 0 | 100 | 0 | 0
8737 | 485.75 | 0 | 21.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1945 | 485.75 | 0 | 0.05921 | 4.7875 | 0 | 0 | 118.7969 | 0 | off_peak | 485.75 |  |  | 0 | 0 | 100 | 0 | 0
8738 | 444.21 | 0 | 21.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1945 | 444.21 | 0 | 0.05921 | 3.6985 | 0 | 0 | 118.7969 | 0 | off_peak | 444.21 |  |  | 0 | 0 | 100 | 0 | 0
8739 | 460.23 | 0 | 21.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1945 | 460.23 | 0 | 0.05921 | 3.7078 | 0 | 0 | 118.7969 | 0 | off_peak | 460.23 |  |  | 0 | 0 | 100 | 0 | 0
8740 | 455.35 | 0 | 21.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1945 | 455.35 | 0 | 0.05921 | 3.6977 | 0 | 0 | 118.7969 | 0 | off_peak | 455.35 |  |  | 0 | 0 | 100 | 0 | 0
8741 | 459.2 | 0 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1945 | 459.2 | 0 | 0.05921 | 3.6816 | 0 | 0 | 118.7969 | 0 | off_peak | 459.2 |  |  | 0 | 0 | 100 | 0 | 0
8742 | 554.35 | 0 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1945 | 554.35 | 0 | 0.05921 | 3.6627 | 0 | 0 | 118.7969 | 0 | off_peak | 554.35 |  |  | 0 | 0 | 100 | 0 | 0
8743 | 554.81 | 0 | 22.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1945 | 554.81 | 0 | 0.05921 | 3.6414 | 0 | 0 | 118.7969 | 0 | off_peak | 554.81 |  |  | 0 | 0 | 100 | 0 | 0
8744 | 577.89 | 40.8613 | 22.5 | 8.3489 | 8.3489 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1945 | 569.5411 | 0 | 0.05921 | 3.6239 | 0 | 0 | 118.7969 | 8.3489 | off_peak | 569.5411 |  |  | 1.44 | 0 | 98.56 | 30.2557 | 0
8745 | 593.38 | 212.732 | 23 | 43.3884 | 43.3884 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 23.7926 | 562.3905 | 0 | 0.05921 | 3.6101 | 0 | 0 | 118.7969 | 43.3884 | off_peak | 549.9916 | 0 | 100 | 7.31 | 0 | 92.69 | 156.6363 | 0
8746 | 588.05 | 388.965 | 23.4 | 79.2191 | 79.2191 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 23.7926 | 508.8309 | 0 | 0.05921 | 3.6005 | 0 | 0 | 118.7969 | 79.2191 | off_peak | 508.8309 |  |  | 13.47 | 0 | 86.53 | 285.2257 | 0
8747 | 578.61 | 526.706 | 23.7 | 107.1571 | 107.1571 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 23.7926 | 471.4529 | 0 | 0.05921 | 3.5957 | 0 | 0 | 118.7969 | 107.1571 | off_peak | 471.4529 |  |  | 18.52 | 0 | 81.48 | 385.3038 | 0
8748 | 580.28 | 614.288 | 24 | 124.8411 | 124.8411 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 23.7926 | 455.4389 | 0 | 0.05921 | 3.5975 | 0 | 0 | 118.7969 | 124.8411 | off_peak | 455.4389 |  |  | 21.51 | 0 | 78.49 | 449.1124 | 0
8749 | 559.15 | 638.82 | 24.2 | 129.7336 | 129.7336 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 23.7926 | 429.4164 | 0 | 0.05921 | 3.6047 | 0 | 0 | 118.7969 | 129.7336 | off_peak | 429.4164 |  |  | 23.2 | 0 | 76.8 | 467.6552 | 0
8750 | 522.18 | 597.871 | 24.3 | 121.374 | 121.374 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 23.7926 | 400.806 | 0 | 0.05921 | 3.6163 | 0 | 0 | 118.7969 | 121.374 | off_peak | 400.806 |  |  | 23.24 | 0 | 76.76 | 438.9225 | 0
8751 | 539.15 | 499.502 | 24.2 | 101.4405 | 101.4405 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 23.7926 | 437.7095 | 0 | 0.05921 | 3.63 | 0 | 0 | 118.7969 | 101.4405 | off_peak | 437.7095 |  |  | 18.81 | 0 | 81.19 | 368.2306 | 0
8752 | 518.95 | 351.671 | 24.1 | 71.4441 | 71.4441 | 0 | 0 | 1.9308 | 1.9308 | 0 | 0 | 0 | 25.5987 | 449.4367 | 0 | 0.05921 | 3.6449 | 0 | 0 | 118.7969 | 71.4441 | off_peak | 447.5059 | 0 | 100 | 13.77 | 0 | 86.23 | 260.4038 | 0
8753 | 525.15 | 173.152 | 23.8 | 35.2148 | 35.2148 | 0 | 0 | 12.3989 | 12.3989 | 0 | 0 | 0 | 37.1968 | 502.3342 | 0 | 0.05921 | 3.6591 | 0 | 0 | 118.7969 | 35.2148 | off_peak | 489.9352 | 0 | 100 | 6.71 | 0 | 93.29 | 128.8559 | 0
8754 | 502.86 | 17.167 | 23.5 | 3.4951 | 3.4951 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 37.1968 | 499.3649 | 0 | 0.05921 | 3.6705 | 0 | 0 | 118.7969 | 3.4951 | off_peak | 499.3649 |  |  | 0.7 | 0 | 99.3 | 12.8287 | 0
8755 | 438.03 | 0 | 23.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 37.1968 | 438.03 | 0 | 0.05921 | 3.677 | 0 | 0 | 118.7969 | 0 | off_peak | 438.03 |  |  | 0 | 0 | 100 | 0 | 0
8756 | 450.97 | 0 | 23.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 37.1968 | 450.97 | 0 | 0.05921 | 3.6776 | 0 | 0 | 118.7969 | 0 | off_peak | 450.97 |  |  | 0 | 0 | 100 | 0 | 0
8757 | 446.82 | 0 | 23.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 37.1968 | 446.82 | 0 | 0.05921 | 3.6728 | 0 | 0 | 118.7969 | 0 | off_peak | 446.82 |  |  | 0 | 0 | 100 | 0 | 0
8758 | 448.82 | 0 | 23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 37.1968 | 448.82 | 0 | 0.05921 | 3.6651 | 0 | 0 | 118.7969 | 0 | off_peak | 448.82 |  |  | 0 | 0 | 100 | 0 | 0
8759 | 444.15 | 0 | 22.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 37.1968 | 444.15 | 0 | 0.05921 | 3.6568 | 0 | 0 | 118.7969 | 0 | off_peak | 444.15 |  |  | 0 | 0 | 100 | 0 | 0
8760 | 432.71 | 0 | 22.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 37.1968 | 432.71 | 0 | 0.05921 | 3.6481 | 0 | 0 | 118.7969 | 0 | off_peak | 432.71 |  |  | 0 | 0 | 100 | 0 | 0

## Summary
Run_ID | Configuration | itc_PV | itc_Bat | Utility Limit Applied? | Enable Sell Flag | Installed PV Size Limit (kW) | Max PV Array Area | Total Cost ($) | Number of Panels | Installed Area (m^2) | PV Capacity (kW) | Battery Energy Capacity (kWh) | Battery Power (kW) | Battery E/P Ratio (hrs) | PV Type | Battery Type | Switch Count | PV Cost ($/kW) | Battery Cost E ($/kWh) | Battery Cost P ($/kW) | Annualized PV Cost | Annualized Battery Cost E | Annualized Battery Cost P | Installed PV Cost | Installed Battery Energy Cost | Installed Battery Power Cost | Installed Battery Total Cost | Annual PV Generation (kWh) | Annual Grid Import (kWh) | Annual Grid Export (kWh) | Yearly Import Cost ($) | Off-Peak Import Cost ($) | On-Peak Import Cost ($) | Demand Charge ($) | Max Demand Charge ($) | Total Sale Revenue | Offset Price ($/tCO2) | Total Emissions Offset | Gross Emissions | Net Emissions | Abatement Credit ($)
Sweep_A2000 | Mono Bifacial_Li-ion LFP_ITC0.00_ITC0.30_Lim1.00_Sell1.00 | 0 | 0.3 | 1 | 1 | 1010.988 | 2000 | 633568.1845 | 625 | 1000 | 225 | 74.3936 | 12.3989 | 6 | Mono Bifacial | Li-ion LFP | 106 | 1230 | 487 | 530 | 116.22 | 55.39 | 49.23 | 26149.5 | 4120.6639 | 610.3998 | 4731.0637 | 361777.4954 | 6124429.338 | 0 | 411676.7656 | 261968.5235 | 149708.2422 | 156913.3215 | 33026.4136 | 0 | 0 | 1536410.0336 | 31648108.4134 | 30111698.3797 | 0

## M_A2000_Mono_BF_Li-io_Sweep_A20
Month | OffPeak_Energy | OffPeak_Cost | OnPeak_Energy | OnPeak_Cost | Total_Energy_Cost | OnPeak_Max | Overall_Max | Demand_Charge | Max_Demand_Charge | Fixed_Charge | Total_Demand_Charges | Total_Monthly_Cost | Gross_Emissions | Abatement_Energy_KWh | Abated_Emissions | Net_Emissions | Abatement_Credit_$
1 | 370759.1545 | 21952.6495 | 129400.7054 | 11453.4117 | 33406.0613 | 819.3258 | 885.6468 | 12453.7528 | 2745.5051 | 89.26 | 15288.5179 | 48694.5792 | 2021895.7518 | 21850.8403 | 78422.6649 | 1943473.0869 | 0
2 | 358387.5246 | 21220.1253 | 125464.2148 | 11104.9882 | 32325.1135 | 877.8141 | 909.5577 | 13342.7741 | 2819.6288 | 89.26 | 16251.6629 | 48576.7765 | 2116829.4513 | 25131.6531 | 88741.7253 | 2028087.726 | 0
3 | 398051.7606 | 23568.6447 | 143470.6255 | 12698.7572 | 36267.402 | 866.6016 | 912.6071 | 13172.3448 | 2829.0819 | 89.26 | 16090.6867 | 52358.0887 | 2445048.8863 | 33991.9289 | 122096.2059 | 2322952.6804 | 0
4 | 352504.5222 | 20871.7928 | 134250.0629 | 11882.6342 | 32754.4269 | 884.74 | 910.764 | 13448.048 | 2823.3684 | 89.26 | 16360.6764 | 49115.1033 | 2412300.0456 | 36786.3888 | 144535.6602 | 2267764.3854 | 0
5 | 366541.8014 | 21702.9401 | 158670.6888 | 13863.1798 | 35566.1198 | 842.788 | 864.524 | 12810.3774 | 2680.0245 | 89.26 | 15579.6619 | 51145.7817 | 2731105.6257 | 42117.0893 | 170182.4463 | 2560923.1794 | 0
6 | 358502.3603 | 21226.9248 | 156240.9309 | 13829.0723 | 35055.997 | 876.57 | 899.91 | 13323.8643 | 2789.721 | 89.26 | 16202.8453 | 51258.8424 | 2986017.9645 | 33525.0296 | 152741.3605 | 2833276.6041 | 0
7 | 389174.1285 | 23043.0001 | 151142.4029 | 13236.9236 | 36279.9238 | 943.5482 | 943.5482 | 14341.9329 | 2924.9995 | 89.26 | 17356.1924 | 53636.1161 | 3414364.4332 | 36323.1026 | 186877.8078 | 3227486.6254 | 0
8 | 375302.6385 | 22221.6692 | 161063.6656 | 14255.9383 | 36477.6075 | 898.2431 | 898.2431 | 13653.2944 | 2784.5535 | 89.26 | 16527.1079 | 53004.7155 | 3462015.3347 | 35288.7238 | 189492.0138 | 3272523.321 | 0
9 | 364910.0161 | 21606.3221 | 144233.1867 | 12622.6345 | 34228.9566 | 848.5132 | 893.1344 | 12897.4013 | 2768.7167 | 89.26 | 15755.378 | 49984.3346 | 3100510.4912 | 29092.9464 | 141073.322 | 2959437.1692 | 0
10 | 360741.569 | 21359.5083 | 151146.1167 | 13378.1242 | 34737.6325 | 831.6211 | 842.1617 | 12640.6406 | 2610.7014 | 89.26 | 15340.602 | 50078.2345 | 2771808.0928 | 26473.994 | 115971.1413 | 2655836.9515 | 0
11 | 361761.8112 | 21419.9168 | 127384.2233 | 11121.4141 | 32541.3309 | 825.2441 | 852.8274 | 12543.7101 | 2643.765 | 89.26 | 15276.7351 | 47818.066 | 2228729.3963 | 21040.0752 | 77209.2786 | 2151520.1177 | 0
12 | 367759.3261 | 21775.0297 | 117565.9013 | 10261.1641 | 32036.1938 | 808.2356 | 840.7574 | 12285.1806 | 2606.3479 | 89.26 | 14980.7885 | 47016.9824 | 1957482.94 | 19599.8939 | 69066.4072 | 1888416.5327 | 0