## Initial
PV_types | STC_eff | temp_coeff | pv_cost | O_M | kW_stc
Mono Bifacial | 0.225 | -0.0036 | 1230 | 20 | 0.36
Battery Data
BATTERY_TYPES | B_rt_eff | B_dod | B_cost_e | B_cost_p | B_power_rating | B_O_M | Energy_Life | Power_Life | Replacement_Fraction_E | Replacement_Fraction_P
Li-ion LFP | 0.875 | 0.9 | 487 | 530 | 1 | 9 | 10 | 10 | 0.85 | 0.8
Sweep Parameters
itc_pv | itc_bat | enable_sell | enforce_limit_flag | A_tot | offset_price | insolation_mult | sweep_file
0 | 0.3 | 1 | 1 | 800 | 0 | 1 | src\microgrid\Launch_files\sweep_1_itc_area.csv
PV Sizing Limits
Metric | Value
Final Allowed System Size (kW) | 1010.988

## H_A800_Mono_BF_Li-io_Sweep_A800
Installed PV Size Limit (kW) | Max PV Array Area | Total Cost ($) | Switch Count | Number of Panels | Installed Area (m^2) | PV Capacity (kW) | Battery Energy Capacity (kWh) | Battery Power (kW) | Annual PV Generation (kWh) | Annual Grid Import (kWh) | Annual Grid Export (kWh) | Annual % Load from PV | Annual % Load from Battery | Annual % Load from Grid | Annual % Batt Charge from PV | Annual % Batt Charge from Grid
1010.988 | 800 | 633789.8672 | 118 | 500 | 800 | 180 | 74.1743 | 12.3624 | 289421.9963 | 6196774.1149 | 0 | 4.46 | 0.35 | 95.19 | 0.87 | 99.13
Hour | Consumption | Insolation | Temperature | Total PV Generation | PV to Load | PV to Grid | PV to Battery | Total Battery Charge | Charge from Grid | Total Battery Discharge | Battery to Load | Battery to Grid | SOC | Grid Import | Grid Export | Grid Price | EF_grid | PV_Charged_Discharge_to_Load | PV_Charged_Discharge_to_Grid | SOC_renew | Abatement_Energy_kWh | On_peak/Off_peak | Grid to Load | %Batt_Charge_from_PV | %Batt_Charge_from_Grid | %Load_from_PV | %Load_from_Battery | %Load_from_Grid | Abated_Emissions | Abatement_Value_$
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 37.0871 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | off_peak | 0 | [5 empty] | 0 | 0
1 | 531.38 | 0 | 22.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 37.0871 | 531.38 | 0 | 0.05921 | 5.9568 | 0 | 0 | 0 | 0 | off_peak | 531.38 |  |  | 0 | 0 | 100 | 0 | 0
2 | 524.77 | 0 | 22.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 37.0871 | 524.77 | 0 | 0.05921 | 5.5568 | 0 | 0 | 0 | 0 | off_peak | 524.77 |  |  | 0 | 0 | 100 | 0 | 0
3 | 563.46 | 0 | 22.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 37.0871 | 563.46 | 0 | 0.05921 | 4.9807 | 0 | 0 | 0 | 0 | off_peak | 563.46 |  |  | 0 | 0 | 100 | 0 | 0
4 | 506.28 | 0 | 22.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 37.0871 | 506.28 | 0 | 0.05921 | 4.5051 | 0 | 0 | 0 | 0 | off_peak | 506.28 |  |  | 0 | 0 | 100 | 0 | 0
5 | 542.58 | 0 | 22.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 37.0871 | 542.58 | 0 | 0.05921 | 4.0751 | 0 | 0 | 0 | 0 | off_peak | 542.58 |  |  | 0 | 0 | 100 | 0 | 0
6 | 588.2 | 0 | 22.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 37.0871 | 588.2 | 0 | 0.05921 | 3.8681 | 0 | 0 | 0 | 0 | off_peak | 588.2 |  |  | 0 | 0 | 100 | 0 | 0
7 | 603.97 | 0 | 23.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 37.0871 | 603.97 | 0 | 0.05921 | 3.4937 | 0 | 0 | 0 | 0 | off_peak | 603.97 |  |  | 0 | 0 | 100 | 0 | 0
8 | 633.99 | 33.2315 | 23.5 | 5.4126 | 5.4126 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 37.0871 | 628.5774 | 0 | 0.05921 | 3.2911 | 0 | 0 | 0 | 5.4126 | off_peak | 628.5774 |  |  | 0.85 | 0 | 99.15 | 17.8133 | 0
9 | 608.88 | 202.289 | 24.2 | 32.8652 | 32.8652 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 37.0871 | 576.0148 | 0 | 0.05921 | 3.0059 | 0 | 0 | 0 | 32.8652 | off_peak | 576.0148 |  |  | 5.4 | 0 | 94.6 | 98.7889 | 0
10 | 620.18 | 377.901 | 24.8 | 61.264 | 61.264 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 37.0871 | 558.916 | 0 | 0.05921 | 2.7361 | 0 | 0 | 0 | 61.264 | off_peak | 558.916 |  |  | 9.88 | 0 | 90.12 | 167.6271 | 0
11 | 617.58 | 124.45 | 25.3 | 20.1391 | 20.1391 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 37.0871 | 597.4409 | 0 | 0.05921 | 2.6008 | 0 | 0 | 0 | 20.1391 | off_peak | 597.4409 |  |  | 3.26 | 0 | 96.74 | 52.3776 | 0
12 | 623.52 | 475.2 | 25.6 | 76.8161 | 76.8161 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 37.0871 | 546.7039 | 0 | 0.05921 | 2.5747 | 0 | 0 | 0 | 76.8161 | off_peak | 546.7039 |  |  | 12.32 | 0 | 87.68 | 197.781 | 0
13 | 553.4 | 369.042 | 25.7 | 59.6341 | 59.6341 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 37.0871 | 493.7659 | 0 | 0.05921 | 2.6772 | 0 | 0 | 0 | 59.6341 | off_peak | 493.7659 |  |  | 10.78 | 0 | 89.22 | 159.6519 | 0
14 | 523.02 | 193.445 | 25.7 | 31.2591 | 31.2591 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 37.0871 | 491.7609 | 0 | 0.05921 | 2.8145 | 0 | 0 | 0 | 31.2591 | off_peak | 491.7609 |  |  | 5.98 | 0 | 94.02 | 87.9792 | 0
15 | 525.29 | 165.812 | 25.5 | 26.8132 | 26.8132 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 37.0871 | 498.4768 | 0 | 0.05921 | 3.1865 | 0 | 0 | 0 | 26.8132 | off_peak | 498.4768 |  |  | 5.1 | 0 | 94.9 | 85.4401 | 0
16 | 529.7 | 83.6 | 25.3 | 13.5286 | 13.5286 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 37.0871 | 516.1714 | 0 | 0.05921 | 3.6633 | 0 | 0 | 0 | 13.5286 | off_peak | 516.1714 |  |  | 2.55 | 0 | 97.45 | 49.5595 | 0
17 | 511.5 | 172.225 | 24.9 | 27.9105 | 27.9105 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 37.0871 | 483.5895 | 0 | 0.05921 | 3.9222 | 0 | 0 | 0 | 27.9105 | off_peak | 483.5895 |  |  | 5.46 | 0 | 94.54 | 109.4703 | 0
18 | 516.63 | 17.4465 | 24.5 | 2.8314 | 2.8314 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 37.0871 | 513.7986 | 0 | 0.05921 | 4.1203 | 0 | 0 | 0 | 2.8314 | off_peak | 513.7986 |  |  | 0.55 | 0 | 99.45 | 11.6663 | 0
19 | 511.42 | 0 | 24.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 37.0871 | 511.42 | 0 | 0.05921 | 4.4428 | 0 | 0 | 0 | 0 | off_peak | 511.42 |  |  | 0 | 0 | 100 | 0 | 0
20 | 500.8 | 0 | 24.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 37.0871 | 500.8 | 0 | 0.05921 | 4.7239 | 0 | 0 | 0 | 0 | off_peak | 500.8 |  |  | 0 | 0 | 100 | 0 | 0
21 | 503.63 | 0 | 24.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 37.0871 | 503.63 | 0 | 0.05921 | 4.9839 | 0 | 0 | 0 | 0 | off_peak | 503.63 |  |  | 0 | 0 | 100 | 0 | 0
22 | 494.11 | 0 | 24.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 37.0871 | 494.11 | 0 | 0.05921 | 5.1804 | 0 | 0 | 0 | 0 | off_peak | 494.11 |  |  | 0 | 0 | 100 | 0 | 0
23 | 502.97 | 0 | 24.1 | 0 | 0 | 0 | 0 | 1.7071 | 1.7071 | 0 | 0 | 0 | 38.684 | 504.6771 | 0 | 0.05921 | 5.3914 | 0 | 0 | 0 | 0 | off_peak | 502.97 | 0 | 100 | 0 | 0 | 100 | 0 | 0
24 | 488.34 | 0 | 24 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 50.2479 | 500.7024 | 0 | 0.05921 | 5.4856 | 0 | 0 | 0 | 0 | off_peak | 488.34 | 0 | 100 | 0 | 0 | 100 | 0 | 0
25 | 497.81 | 0 | 24 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 61.8119 | 510.1724 | 0 | 0.05921 | 5.4744 | 0 | 0 | 0 | 0 | off_peak | 497.81 | 0 | 100 | 0 | 0 | 100 | 0 | 0
26 | 532.79 | 0 | 23.9 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 73.3758 | 545.1524 | 0 | 0.05921 | 5.1948 | 0 | 0 | 0 | 0 | off_peak | 532.79 | 0 | 100 | 0 | 0 | 100 | 0 | 0
27 | 501.31 | 0 | 23.9 | 0 | 0 | 0 | 0 | 0.79843 | 0.79843 | 0 | 0 | 0 | 74.1227 | 502.1084 | 0 | 0.05921 | 4.8676 | 0 | 0 | 0 | 0 | off_peak | 501.31 | 0 | 100 | 0 | 0 | 100 | 0 | 0
28 | 529.55 | 0 | 23.8 | 0 | 0 | 0 | 0 | 0.051567 | 0.051567 | 0 | 0 | 0 | 74.1709 | 529.6016 | 0 | 0.05921 | 4.4899 | 0 | 0 | 0 | 0 | off_peak | 529.55 | 0 | 100 | 0 | 0 | 100 | 0 | 0
29 | 523.1 | 0 | 23.7 | 0 | 0 | 0 | 0 | 0.0033305 | 0.0033305 | 0 | 0 | 0 | 74.174 | 523.1033 | 0 | 0.05921 | 4.1419 | 0 | 0 | 0 | 0 | off_peak | 523.1 | 0 | 100 | 0 | 0 | 100 | 0 | 0
30 | 675.53 | 0 | 23.6 | 0 | 0 | 0 | 0 | 0.0002151 | 0.0002151 | 0 | 0 | 0 | 74.1742 | 675.5302 | 0 | 0.05921 | 3.6568 | 0 | 0 | 0 | 0 | off_peak | 675.53 | 0 | 100 | 0 | 0 | 100 | 0 | 0
31 | 686.99 | 0 | 23.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1742 | 686.99 | 0 | 0.088511 | 3.2669 | 0 | 0 | 0 | 0 | on_peak | 686.99 |  |  | 0 | 0 | 100 | 0 | 0
32 | 684.66 | 34.1904 | 24.3 | 5.5528 | 5.5528 | 0 | 0 | 0 | 0 | 62.4453 | 62.4453 | 0 | 7.4174 | 616.6619 | 0 | 0.088511 | 2.9109 | 0 | 0 | 0 | 5.5528 | on_peak | 616.6619 |  |  | 0.81 | 9.12 | 90.07 | 16.1636 | 0
33 | 686.98 | 205.065 | 25 | 33.2205 | 33.2205 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 653.7595 | 0 | 0.088511 | 2.69 | 0 | 0 | 0 | 33.2205 | on_peak | 653.7595 |  |  | 4.84 | 0 | 95.16 | 89.3641 | 0
34 | 668.24 | 380.134 | 25.5 | 61.4709 | 61.4709 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 606.7691 | 0 | 0.088511 | 2.5729 | 0 | 0 | 0 | 61.4709 | on_peak | 606.7691 |  |  | 9.2 | 0 | 90.8 | 158.1577 | 0
35 | 686.54 | 519.82 | 26 | 83.9077 | 83.9077 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 18.9814 | 614.9947 | 0 | 0.05921 | 2.5438 | 0 | 0 | 0 | 83.9077 | off_peak | 602.6323 | 0 | 100 | 12.22 | 0 | 87.78 | 213.4469 | 0
36 | 718.85 | 422.547 | 26.2 | 68.1569 | 68.1569 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 30.5453 | 663.0555 | 0 | 0.05921 | 2.6441 | 0 | 0 | 0 | 68.1569 | off_peak | 650.6931 | 0 | 100 | 9.48 | 0 | 90.52 | 180.2126 | 0
37 | 622.47 | 207.727 | 26.4 | 33.4822 | 33.4822 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 42.1093 | 601.3502 | 0 | 0.05921 | 2.829 | 0 | 0 | 0 | 33.4822 | off_peak | 588.9878 | 0 | 100 | 5.38 | 0 | 94.62 | 94.7214 | 0
38 | 623.76 | 193.446 | 26.4 | 31.1803 | 31.1803 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 53.6732 | 604.9421 | 0 | 0.05921 | 3.0786 | 0 | 0 | 0 | 31.1803 | off_peak | 592.5797 | 0 | 100 | 5 | 0 | 95 | 95.9915 | 0
39 | 613.75 | 296.891 | 26.3 | 47.8713 | 47.8713 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 65.2371 | 578.2411 | 0 | 0.05921 | 3.3996 | 0 | 0 | 0 | 47.8713 | off_peak | 565.8787 | 0 | 100 | 7.8 | 0 | 92.2 | 162.7428 | 0
40 | 577.73 | 347.366 | 26 | 56.0707 | 56.0707 | 0 | 0 | 8.9371 | 8.9371 | 0 | 0 | 0 | 73.597 | 530.5964 | 0 | 0.05921 | 3.7017 | 0 | 0 | 0 | 56.0707 | off_peak | 521.6593 | 0 | 100 | 9.71 | 0 | 90.29 | 207.5588 | 0
41 | 572.7 | 117.757 | 25.5 | 19.0423 | 19.0423 | 0 | 0 | 0.57721 | 0.57721 | 0 | 0 | 0 | 74.137 | 554.2349 | 0 | 0.05921 | 4.02 | 0 | 0 | 0 | 19.0423 | off_peak | 553.6577 | 0 | 100 | 3.33 | 0 | 96.67 | 76.5499 | 0
42 | 522.44 | 17.2992 | 25 | 2.8025 | 2.8025 | 0 | 0 | 0.037279 | 0.037279 | 0 | 0 | 0 | 74.1718 | 519.6748 | 0 | 0.05921 | 4.3091 | 0 | 0 | 0 | 2.8025 | off_peak | 519.6375 | 0 | 100 | 0.54 | 0 | 99.46 | 12.0762 | 0
43 | 537.46 | 0 | 24.7 | 0 | 0 | 0 | 0 | 0 | 0 | 62.443 | 62.443 | 0 | 7.4174 | 475.017 | 0 | 0.088511 | 4.5774 | 0 | 0 | 0 | 0 | on_peak | 475.017 |  |  | 0 | 11.62 | 88.38 | 0 | 0
44 | 523.26 | 0 | 24.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 523.26 | 0 | 0.088511 | 4.7446 | 0 | 0 | 0 | 0 | on_peak | 523.26 |  |  | 0 | 0 | 100 | 0 | 0
45 | 508.2 | 0 | 24.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 508.2 | 0 | 0.088511 | 4.9584 | 0 | 0 | 0 | 0 | on_peak | 508.2 |  |  | 0 | 0 | 100 | 0 | 0
46 | 517.42 | 0 | 24.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 517.42 | 0 | 0.088511 | 5.2563 | 0 | 0 | 0 | 0 | on_peak | 517.42 |  |  | 0 | 0 | 100 | 0 | 0
47 | 498.13 | 0 | 24.3 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 18.9814 | 510.4924 | 0 | 0.05921 | 5.5907 | 0 | 0 | 0 | 0 | off_peak | 498.13 | 0 | 100 | 0 | 0 | 100 | 0 | 0
48 | 528.69 | 0 | 24.3 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 30.5453 | 541.0524 | 0 | 0.05921 | 5.81 | 0 | 0 | 0 | 0 | off_peak | 528.69 | 0 | 100 | 0 | 0 | 100 | 0 | 0
49 | 512.65 | 0 | 24.3 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 42.1093 | 525.0124 | 0 | 0.05921 | 5.9242 | 0 | 0 | 0 | 0 | off_peak | 512.65 | 0 | 100 | 0 | 0 | 100 | 0 | 0
50 | 515.23 | 0 | 24.2 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 53.6732 | 527.5924 | 0 | 0.05921 | 5.5488 | 0 | 0 | 0 | 0 | off_peak | 515.23 | 0 | 100 | 0 | 0 | 100 | 0 | 0
51 | 552.16 | 0 | 24.2 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 65.2371 | 564.5224 | 0 | 0.05921 | 5.1595 | 0 | 0 | 0 | 0 | off_peak | 552.16 | 0 | 100 | 0 | 0 | 100 | 0 | 0
52 | 516.52 | 0 | 24.2 | 0 | 0 | 0 | 0 | 8.9371 | 8.9371 | 0 | 0 | 0 | 73.597 | 525.4571 | 0 | 0.05921 | 4.7666 | 0 | 0 | 0 | 0 | off_peak | 516.52 | 0 | 100 | 0 | 0 | 100 | 0 | 0
53 | 589.27 | 0 | 24.2 | 0 | 0 | 0 | 0 | 0.57721 | 0.57721 | 0 | 0 | 0 | 74.137 | 589.8472 | 0 | 0.05921 | 4.3901 | 0 | 0 | 0 | 0 | off_peak | 589.27 | 0 | 100 | 0 | 0 | 100 | 0 | 0
54 | 643.08 | 0 | 24.3 | 0 | 0 | 0 | 0 | 0.037279 | 0.037279 | 0 | 0 | 0 | 74.1718 | 643.1173 | 0 | 0.05921 | 3.9311 | 0 | 0 | 0 | 0 | off_peak | 643.08 | 0 | 100 | 0 | 0 | 100 | 0 | 0
55 | 763.27 | 0 | 24.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1718 | 763.27 | 0 | 0.088511 | 3.4383 | 0 | 0 | 0 | 0 | on_peak | 763.27 |  |  | 0 | 0 | 100 | 0 | 0
56 | 780.24 | 32.8003 | 25.1 | 5.3117 | 5.3117 | 0 | 0 | 0 | 0 | 62.443 | 62.443 | 0 | 7.4174 | 712.4852 | 0 | 0.088511 | 3.0499 | 0 | 0 | 0 | 5.3117 | on_peak | 712.4852 |  |  | 0.68 | 8 | 91.32 | 16.2003 | 0
57 | 764.81 | 203.018 | 25.7 | 32.806 | 32.806 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 732.004 | 0 | 0.088511 | 2.839 | 0 | 0 | 0 | 32.806 | on_peak | 732.004 |  |  | 4.29 | 0 | 95.71 | 93.1359 | 0
58 | 813.52 | 114.95 | 26 | 18.5549 | 18.5549 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 794.9651 | 0 | 0.088511 | 2.7457 | 0 | 0 | 0 | 18.5549 | on_peak | 794.9651 |  |  | 2.28 | 0 | 97.72 | 50.9463 | 0
59 | 764.84 | 250.162 | 26.3 | 40.3366 | 40.3366 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 18.9814 | 736.8658 | 0 | 0.05921 | 2.7378 | 0 | 0 | 0 | 40.3366 | off_peak | 724.5034 | 0 | 100 | 5.27 | 0 | 94.73 | 110.4342 | 0
60 | 777.85 | 614.3 | 26.4 | 99.015 | 99.015 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 30.5453 | 691.1973 | 0 | 0.05921 | 2.9708 | 0 | 0 | 0 | 99.015 | off_peak | 678.835 | 0 | 100 | 12.73 | 0 | 87.27 | 294.1518 | 0
61 | 789.22 | 462.441 | 26.5 | 74.5109 | 74.5109 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 42.1093 | 727.0715 | 0 | 0.05921 | 3.3636 | 0 | 0 | 0 | 74.5109 | off_peak | 714.7091 | 0 | 100 | 9.44 | 0 | 90.56 | 250.6266 | 0
62 | 790.34 | 527.2 | 26.6 | 84.9145 | 84.9145 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 53.6732 | 717.7879 | 0 | 0.05921 | 3.6886 | 0 | 0 | 0 | 84.9145 | off_peak | 705.4255 | 0 | 100 | 10.74 | 0 | 89.26 | 313.2175 | 0
63 | 820.57 | 425.885 | 26.5 | 68.6208 | 68.6208 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 65.2371 | 764.3116 | 0 | 0.05921 | 3.8339 | 0 | 0 | 0 | 68.6208 | off_peak | 751.9492 | 0 | 100 | 8.36 | 0 | 91.64 | 263.0841 | 0
64 | 773.29 | 359.692 | 26.3 | 57.9974 | 57.9974 | 0 | 0 | 8.9371 | 8.9371 | 0 | 0 | 0 | 73.597 | 724.2297 | 0 | 0.05921 | 3.9307 | 0 | 0 | 0 | 57.9974 | off_peak | 715.2926 | 0 | 100 | 7.5 | 0 | 92.5 | 227.972 | 0
65 | 735.37 | 101.03 | 26 | 16.3079 | 16.3079 | 0 | 0 | 0.57721 | 0.57721 | 0 | 0 | 0 | 74.137 | 719.6393 | 0 | 0.05921 | 4.2528 | 0 | 0 | 0 | 16.3079 | off_peak | 719.0621 | 0 | 100 | 2.22 | 0 | 97.78 | 69.3538 | 0
66 | 744.16 | 13.3 | 25.7 | 2.1492 | 2.1119 | 0 | 0.037279 | 0.037279 | 0 | 0 | 0 | 0 | 74.1718 | 742.0481 | 0 | 0.05921 | 4.5647 | 0 | 0 | 0.034872 | 2.1119 | off_peak | 742.0481 | 100 | 0 | 0.28 | 0 | 99.72 | 9.6402 | 0
67 | 723.25 | 0 | 25.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1718 | 723.25 | 0 | 0.088511 | 4.9942 | 0 | 0 | 0.034872 | 0 | on_peak | 723.25 |  |  | 0 | 0 | 100 | 0 | 0
68 | 719.4 | 0 | 25.5 | 0 | 0 | 0 | 0 | 0 | 0 | 62.443 | 62.443 | 0 | 7.4174 | 656.957 | 0 | 0.088511 | 5.2412 | 0 | 0 | 0.034872 | 0 | on_peak | 656.957 |  |  | 0 | 8.68 | 91.32 | 0 | 0
69 | 668.31 | 0 | 25.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 668.31 | 0 | 0.088511 | 5.4172 | 0 | 0 | 0.034872 | 0 | on_peak | 668.31 |  |  | 0 | 0 | 100 | 0 | 0
70 | 668.49 | 0 | 25.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 668.49 | 0 | 0.088511 | 5.6047 | 0 | 0 | 0.034872 | 0 | on_peak | 668.49 |  |  | 0 | 0 | 100 | 0 | 0
71 | 689.14 | 0 | 25.3 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 18.9814 | 701.5024 | 0 | 0.05921 | 5.8983 | 0 | 0 | 0.034872 | 0 | off_peak | 689.14 | 0 | 100 | 0 | 0 | 100 | 0 | 0
72 | 655.37 | 0 | 25.2 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 30.5453 | 667.7324 | 0 | 0.05921 | 6.0439 | 0 | 0 | 0.034872 | 0 | off_peak | 655.37 | 0 | 100 | 0 | 0 | 100 | 0 | 0
73 | 623.33 | 0 | 25.2 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 42.1093 | 635.6924 | 0 | 0.05921 | 6.1816 | 0 | 0 | 0.034872 | 0 | off_peak | 623.33 | 0 | 100 | 0 | 0 | 100 | 0 | 0
74 | 565.79 | 0 | 25.1 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 53.6732 | 578.1524 | 0 | 0.05921 | 5.9388 | 0 | 0 | 0.034872 | 0 | off_peak | 565.79 | 0 | 100 | 0 | 0 | 100 | 0 | 0
75 | 499.28 | 0 | 25 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 65.2371 | 511.6424 | 0 | 0.05921 | 5.5251 | 0 | 0 | 0.034872 | 0 | off_peak | 499.28 | 0 | 100 | 0 | 0 | 100 | 0 | 0
76 | 523.2 | 0 | 24.9 | 0 | 0 | 0 | 0 | 8.9371 | 8.9371 | 0 | 0 | 0 | 73.597 | 532.1371 | 0 | 0.05921 | 5.1591 | 0 | 0 | 0.034872 | 0 | off_peak | 523.2 | 0 | 100 | 0 | 0 | 100 | 0 | 0
77 | 516.74 | 0 | 24.8 | 0 | 0 | 0 | 0 | 0.57721 | 0.57721 | 0 | 0 | 0 | 74.137 | 517.3172 | 0 | 0.05921 | 4.7625 | 0 | 0 | 0.034872 | 0 | off_peak | 516.74 | 0 | 100 | 0 | 0 | 100 | 0 | 0
78 | 620.7 | 0 | 24.7 | 0 | 0 | 0 | 0 | 0.037279 | 0.037279 | 0 | 0 | 0 | 74.1718 | 620.7373 | 0 | 0.05921 | 4.2547 | 0 | 0 | 0.034872 | 0 | off_peak | 620.7 | 0 | 100 | 0 | 0 | 100 | 0 | 0
79 | 656.92 | 0 | 24.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1718 | 656.92 | 0 | 0.088511 | 3.685 | 0 | 0 | 0.034872 | 0 | on_peak | 656.92 |  |  | 0 | 0 | 100 | 0 | 0
80 | 706.33 | 18.0175 | 25.2 | 2.9167 | 2.9167 | 0 | 0 | 0 | 0 | 62.443 | 62.443 | 0 | 7.4174 | 640.9702 | 0 | 0.088511 | 3.3035 | 0.032619 | 0 | 0 | 2.9494 | on_peak | 640.9702 |  |  | 0.41 | 8.84 | 90.75 | 9.7432 | 0
81 | 753.64 | 106.684 | 25.7 | 17.2393 | 17.2393 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 736.4007 | 0 | 0.088511 | 3.0402 | 0 | 0 | 0 | 17.2393 | on_peak | 736.4007 |  |  | 2.29 | 0 | 97.71 | 52.4105 | 0
82 | 740.72 | 283.869 | 26 | 45.8212 | 45.8212 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 694.8988 | 0 | 0.088511 | 2.9359 | 0 | 0 | 0 | 45.8212 | on_peak | 694.8988 |  |  | 6.19 | 0 | 93.81 | 134.5282 | 0
83 | 751.48 | 241.811 | 26.3 | 38.9901 | 38.9901 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 18.9814 | 724.8523 | 0 | 0.05921 | 2.9293 | 0 | 0 | 0 | 38.9901 | off_peak | 712.4899 | 0 | 100 | 5.19 | 0 | 94.81 | 114.2138 | 0
84 | 765.02 | 530.559 | 26.5 | 85.4864 | 85.4864 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 30.5453 | 691.896 | 0 | 0.05921 | 3.1481 | 0 | 0 | 0 | 85.4864 | off_peak | 679.5336 | 0 | 100 | 11.17 | 0 | 88.83 | 269.1178 | 0
85 | 697.64 | 175.75 | 26.6 | 28.3075 | 28.3075 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 42.1093 | 681.6949 | 0 | 0.05921 | 3.5463 | 0 | 0 | 0 | 28.3075 | off_peak | 669.3325 | 0 | 100 | 4.06 | 0 | 95.94 | 100.3868 | 0
86 | 724.8 | 389.078 | 26.7 | 62.6449 | 62.6449 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 53.6732 | 674.5175 | 0 | 0.05921 | 3.8548 | 0 | 0 | 0 | 62.6449 | off_peak | 662.1551 | 0 | 100 | 8.64 | 0 | 91.36 | 241.4811 | 0
87 | 797.16 | 327.919 | 26.6 | 52.8169 | 52.8169 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 65.2371 | 756.7055 | 0 | 0.05921 | 4.1389 | 0 | 0 | 0 | 52.8169 | off_peak | 744.3431 | 0 | 100 | 6.63 | 0 | 93.37 | 218.6057 | 0
88 | 779.42 | 288.153 | 26.4 | 46.4455 | 46.4455 | 0 | 0 | 8.9371 | 8.9371 | 0 | 0 | 0 | 73.597 | 741.9116 | 0 | 0.05921 | 4.417 | 0 | 0 | 0 | 46.4455 | off_peak | 732.9745 | 0 | 100 | 5.96 | 0 | 94.04 | 205.1504 | 0
89 | 787.46 | 134.381 | 26 | 21.6914 | 21.6914 | 0 | 0 | 0.57721 | 0.57721 | 0 | 0 | 0 | 74.137 | 766.3459 | 0 | 0.05921 | 4.6371 | 0 | 0 | 0 | 21.6914 | off_peak | 765.7686 | 0 | 100 | 2.75 | 0 | 97.25 | 100.5848 | 0
90 | 749.12 | 14.25 | 25.4 | 2.3052 | 2.3052 | 0 | 0 | 0.037279 | 0.037279 | 0 | 0 | 0 | 74.1718 | 746.8521 | 0 | 0.05921 | 4.9059 | 0 | 0 | 0 | 2.3052 | off_peak | 746.8148 | 0 | 100 | 0.31 | 0 | 99.69 | 11.309 | 0
91 | 731.12 | 0 | 25.2 | 0 | 0 | 0 | 0 | 0 | 0 | 62.443 | 62.443 | 0 | 7.4174 | 668.677 | 0 | 0.088511 | 5.2836 | 0 | 0 | 0 | 0 | on_peak | 668.677 |  |  | 0 | 8.54 | 91.46 | 0 | 0
92 | 746.91 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 746.91 | 0 | 0.088511 | 5.553 | 0 | 0 | 0 | 0 | on_peak | 746.91 |  |  | 0 | 0 | 100 | 0 | 0
93 | 722.82 | 0 | 24.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 722.82 | 0 | 0.088511 | 5.7665 | 0 | 0 | 0 | 0 | on_peak | 722.82 |  |  | 0 | 0 | 100 | 0 | 0
94 | 697.04 | 0 | 24.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 697.04 | 0 | 0.088511 | 6.0912 | 0 | 0 | 0 | 0 | on_peak | 697.04 |  |  | 0 | 0 | 100 | 0 | 0
95 | 721.9 | 0 | 24.6 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 18.9814 | 734.2624 | 0 | 0.05921 | 6.2512 | 0 | 0 | 0 | 0 | off_peak | 721.9 | 0 | 100 | 0 | 0 | 100 | 0 | 0
96 | 698.97 | 0 | 24.6 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 30.5453 | 711.3324 | 0 | 0.05921 | 6.3175 | 0 | 0 | 0 | 0 | off_peak | 698.97 | 0 | 100 | 0 | 0 | 100 | 0 | 0
97 | 655.92 | 0 | 24.5 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 42.1093 | 668.2824 | 0 | 0.05921 | 6.3825 | 0 | 0 | 0 | 0 | off_peak | 655.92 | 0 | 100 | 0 | 0 | 100 | 0 | 0
98 | 636.36 | 0 | 24.5 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 53.6732 | 648.7224 | 0 | 0.05921 | 6.1937 | 0 | 0 | 0 | 0 | off_peak | 636.36 | 0 | 100 | 0 | 0 | 100 | 0 | 0
99 | 575.58 | 0 | 24.4 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 65.2371 | 587.9424 | 0 | 0.05921 | 5.7264 | 0 | 0 | 0 | 0 | off_peak | 575.58 | 0 | 100 | 0 | 0 | 100 | 0 | 0
100 | 576.47 | 0 | 24.3 | 0 | 0 | 0 | 0 | 8.9371 | 8.9371 | 0 | 0 | 0 | 73.597 | 585.4071 | 0 | 0.05921 | 5.2621 | 0 | 0 | 0 | 0 | off_peak | 576.47 | 0 | 100 | 0 | 0 | 100 | 0 | 0
101 | 580.04 | 0 | 24.2 | 0 | 0 | 0 | 0 | 0.57721 | 0.57721 | 0 | 0 | 0 | 74.137 | 580.6172 | 0 | 0.05921 | 4.7501 | 0 | 0 | 0 | 0 | off_peak | 580.04 | 0 | 100 | 0 | 0 | 100 | 0 | 0
102 | 665.06 | 0 | 24.1 | 0 | 0 | 0 | 0 | 0.037279 | 0.037279 | 0 | 0 | 0 | 74.1718 | 665.0973 | 0 | 0.05921 | 4.1765 | 0 | 0 | 0 | 0 | off_peak | 665.06 | 0 | 100 | 0 | 0 | 100 | 0 | 0
103 | 748.44 | 0 | 24.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1718 | 748.44 | 0 | 0.088511 | 3.7369 | 0 | 0 | 0 | 0 | on_peak | 748.44 |  |  | 0 | 0 | 100 | 0 | 0
104 | 725.21 | 34.8872 | 24.7 | 5.6578 | 5.6578 | 0 | 0 | 0 | 0 | 62.443 | 62.443 | 0 | 7.4174 | 657.1091 | 0 | 0.088511 | 3.3266 | 0 | 0 | 0 | 5.6578 | on_peak | 657.1091 |  |  | 0.78 | 8.61 | 90.61 | 18.8213 | 0
105 | 750.66 | 170.267 | 25.3 | 27.5535 | 27.5535 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 723.1065 | 0 | 0.088511 | 3.118 | 0 | 0 | 0 | 27.5535 | on_peak | 723.1065 |  |  | 3.67 | 0 | 96.33 | 85.9117 | 0
106 | 777.58 | 393.45 | 25.8 | 63.5553 | 63.5553 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 714.0247 | 0 | 0.088511 | 2.9697 | 0 | 0 | 0 | 63.5553 | on_peak | 714.0247 |  |  | 8.17 | 0 | 91.83 | 188.7425 | 0
107 | 794.41 | 470.036 | 26.3 | 75.7895 | 75.7895 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 18.9814 | 730.9829 | 0 | 0.05921 | 2.9508 | 0 | 0 | 0 | 75.7895 | off_peak | 718.6205 | 0 | 100 | 9.54 | 0 | 90.46 | 223.6381 | 0
108 | 911.97 | 629.254 | 26.7 | 101.3153 | 101.3153 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 30.5453 | 823.0171 | 0 | 0.05921 | 3.1531 | 0 | 0 | 0 | 101.3153 | off_peak | 810.6547 | 0 | 100 | 11.11 | 0 | 88.89 | 319.4605 | 0
109 | 829.64 | 655.571 | 27 | 105.4378 | 105.4378 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 42.1093 | 736.5645 | 0 | 0.05921 | 3.5627 | 0 | 0 | 0 | 105.4378 | off_peak | 724.2022 | 0 | 100 | 12.71 | 0 | 87.29 | 375.6467 | 0
110 | 883.77 | 628.744 | 27.1 | 101.0865 | 101.0865 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 53.6732 | 795.0459 | 0 | 0.05921 | 3.9229 | 0 | 0 | 0 | 101.0865 | off_peak | 782.6835 | 0 | 100 | 11.44 | 0 | 88.56 | 396.5482 | 0
111 | 911.51 | 527.951 | 27.1 | 84.8815 | 84.8815 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 65.2371 | 838.9909 | 0 | 0.05921 | 4.1771 | 0 | 0 | 0 | 84.8815 | off_peak | 826.6285 | 0 | 100 | 9.31 | 0 | 90.69 | 354.557 | 0
112 | 891.73 | 376.425 | 26.8 | 60.5857 | 60.5857 | 0 | 0 | 8.9371 | 8.9371 | 0 | 0 | 0 | 73.597 | 840.0814 | 0 | 0.05921 | 4.286 | 0 | 0 | 0 | 60.5857 | off_peak | 831.1443 | 0 | 100 | 6.79 | 0 | 93.21 | 259.6708 | 0
113 | 868.67 | 191.859 | 26 | 30.9693 | 30.9693 | 0 | 0 | 0.57721 | 0.57721 | 0 | 0 | 0 | 74.137 | 838.2779 | 0 | 0.05921 | 4.3698 | 0 | 0 | 0 | 30.9693 | off_peak | 837.7007 | 0 | 100 | 3.57 | 0 | 96.43 | 135.3295 | 0
114 | 872.17 | 23.2185 | 25.2 | 3.7587 | 3.7214 | 0 | 0.037279 | 0.037279 | 0 | 0 | 0 | 0 | 74.1718 | 868.4486 | 0 | 0.05921 | 4.6662 | 0 | 0 | 0.034872 | 3.7214 | off_peak | 868.4486 | 100 | 0 | 0.43 | 0 | 99.57 | 17.3647 | 0
115 | 794.27 | 0 | 24.8 | 0 | 0 | 0 | 0 | 0 | 0 | 39.3622 | 39.3622 | 0 | 32.0919 | 754.9078 | 0 | 0.088511 | 4.9803 | 0 | 0 | 0.034872 | 0 | on_peak | 754.9078 |  |  | 0 | 4.96 | 95.04 | 0 | 0
116 | 846.67 | 0 | 24.1 | 0 | 0 | 0 | 0 | 0 | 0 | 23.0809 | 23.0809 | 0 | 7.4174 | 823.5891 | 0 | 0.088511 | 5.438 | 0.032619 | 0 | 0 | 0.032619 | on_peak | 823.5891 |  |  | 0 | 2.73 | 97.27 | 0.17738 | 0
117 | 805.5 | 0 | 23.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 805.5 | 0 | 0.088511 | 5.5995 | 0 | 0 | 0 | 0 | on_peak | 805.5 |  |  | 0 | 0 | 100 | 0 | 0
118 | 789.04 | 0 | 23.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 789.04 | 0 | 0.088511 | 5.7008 | 0 | 0 | 0 | 0 | on_peak | 789.04 |  |  | 0 | 0 | 100 | 0 | 0
119 | 783.91 | 0 | 23.7 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 18.9814 | 796.2724 | 0 | 0.05921 | 5.8055 | 0 | 0 | 0 | 0 | off_peak | 783.91 | 0 | 100 | 0 | 0 | 100 | 0 | 0
120 | 755.57 | 0 | 23.7 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 30.5453 | 767.9324 | 0 | 0.05921 | 6.0091 | 0 | 0 | 0 | 0 | off_peak | 755.57 | 0 | 100 | 0 | 0 | 100 | 0 | 0
121 | 735.54 | 0 | 23.7 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 42.1093 | 747.9024 | 0 | 0.05921 | 6.1559 | 0 | 0 | 0 | 0 | off_peak | 735.54 | 0 | 100 | 0 | 0 | 100 | 0 | 0
122 | 656.71 | 0 | 23.6 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 53.6732 | 669.0724 | 0 | 0.05921 | 5.9015 | 0 | 0 | 0 | 0 | off_peak | 656.71 | 0 | 100 | 0 | 0 | 100 | 0 | 0
123 | 635.01 | 0 | 23.5 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 65.2371 | 647.3724 | 0 | 0.05921 | 5.5042 | 0 | 0 | 0 | 0 | off_peak | 635.01 | 0 | 100 | 0 | 0 | 100 | 0 | 0
124 | 622.1 | 0 | 23.4 | 0 | 0 | 0 | 0 | 8.9371 | 8.9371 | 0 | 0 | 0 | 73.597 | 631.0371 | 0 | 0.05921 | 4.9625 | 0 | 0 | 0 | 0 | off_peak | 622.1 | 0 | 100 | 0 | 0 | 100 | 0 | 0
125 | 635.59 | 0 | 23.3 | 0 | 0 | 0 | 0 | 0.57721 | 0.57721 | 0 | 0 | 0 | 74.137 | 636.1672 | 0 | 0.05921 | 4.4999 | 0 | 0 | 0 | 0 | off_peak | 635.59 | 0 | 100 | 0 | 0 | 100 | 0 | 0
126 | 703.08 | 0 | 23.3 | 0 | 0 | 0 | 0 | 0.037279 | 0.037279 | 0 | 0 | 0 | 74.1718 | 703.1173 | 0 | 0.05921 | 3.8718 | 0 | 0 | 0 | 0 | off_peak | 703.08 | 0 | 100 | 0 | 0 | 100 | 0 | 0
127 | 767.76 | 0 | 23.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1718 | 767.76 | 0 | 0.088511 | 3.4465 | 0 | 0 | 0 | 0 | on_peak | 767.76 |  |  | 0 | 0 | 100 | 0 | 0
128 | 760.34 | 32.8886 | 24.1 | 5.3452 | 5.3452 | 0 | 0 | 0 | 0 | 62.443 | 62.443 | 0 | 7.4174 | 692.5517 | 0 | 0.088511 | 3.0586 | 0 | 0 | 0 | 5.3452 | on_peak | 692.5517 |  |  | 0.7 | 8.21 | 91.08 | 16.3491 | 0
129 | 772.37 | 204.107 | 24.9 | 33.0772 | 33.0772 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 739.2928 | 0 | 0.088511 | 2.8492 | 0 | 0 | 0 | 33.0772 | on_peak | 739.2928 |  |  | 4.28 | 0 | 95.72 | 94.2441 | 0
130 | 746.33 | 381.111 | 25.4 | 61.6511 | 61.6511 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 684.6789 | 0 | 0.088511 | 2.7526 | 0 | 0 | 0 | 61.6511 | on_peak | 684.6789 |  |  | 8.26 | 0 | 91.74 | 169.6984 | 0
131 | 737.21 | 522.043 | 25.9 | 84.297 | 84.297 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 18.9814 | 665.2754 | 0 | 0.05921 | 2.7477 | 0 | 0 | 0 | 84.297 | off_peak | 652.913 | 0 | 100 | 11.43 | 0 | 88.57 | 231.6232 | 0
132 | 807.64 | 608.572 | 26.3 | 98.1273 | 98.1273 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 30.5453 | 721.8751 | 0 | 0.05921 | 3.0043 | 0 | 0 | 0 | 98.1273 | off_peak | 709.5127 | 0 | 100 | 12.15 | 0 | 87.85 | 294.8029 | 0
133 | 746.33 | 633.456 | 26.5 | 102.0657 | 102.0657 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 42.1093 | 656.6267 | 0 | 0.05921 | 3.4763 | 0 | 0 | 0 | 102.0657 | off_peak | 644.2643 | 0 | 100 | 13.68 | 0 | 86.32 | 354.8124 | 0
134 | 784.07 | 573.928 | 26.6 | 92.4408 | 92.4408 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 53.6732 | 703.9916 | 0 | 0.05921 | 3.8971 | 0 | 0 | 0 | 92.4408 | off_peak | 691.6292 | 0 | 100 | 11.79 | 0 | 88.21 | 360.2546 | 0
135 | 800.58 | 262.623 | 26.6 | 42.2999 | 42.2999 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 65.2371 | 770.6425 | 0 | 0.05921 | 3.9327 | 0 | 0 | 0 | 42.2999 | off_peak | 758.2801 | 0 | 100 | 5.28 | 0 | 94.72 | 166.3519 | 0
136 | 813.37 | 213.97 | 26.4 | 34.4884 | 34.4884 | 0 | 0 | 8.9371 | 8.9371 | 0 | 0 | 0 | 73.597 | 787.8187 | 0 | 0.05921 | 3.624 | 0 | 0 | 0 | 34.4884 | off_peak | 778.8816 | 0 | 100 | 4.24 | 0 | 95.76 | 124.9864 | 0
137 | 753.32 | 173.916 | 26 | 28.073 | 28.073 | 0 | 0 | 0.57721 | 0.57721 | 0 | 0 | 0 | 74.137 | 725.8242 | 0 | 0.05921 | 3.5748 | 0 | 0 | 0 | 28.073 | off_peak | 725.247 | 0 | 100 | 3.73 | 0 | 96.27 | 100.3559 | 0
138 | 770.19 | 11.4 | 25.5 | 1.8435 | 1.8435 | 0 | 0 | 0.037279 | 0.037279 | 0 | 0 | 0 | 74.1718 | 768.3838 | 0 | 0.05921 | 3.4823 | 0 | 0 | 0 | 1.8435 | off_peak | 768.3465 | 0 | 100 | 0.24 | 0 | 99.76 | 6.4196 | 0
139 | 756.83 | 0 | 25.3 | 0 | 0 | 0 | 0 | 0 | 0 | 62.443 | 62.443 | 0 | 7.4174 | 694.387 | 0 | 0.088511 | 3.4996 | 0 | 0 | 0 | 0 | on_peak | 694.387 |  |  | 0 | 8.25 | 91.75 | 0 | 0
140 | 747.62 | 0 | 24.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 747.62 | 0 | 0.088511 | 3.5914 | 0 | 0 | 0 | 0 | on_peak | 747.62 |  |  | 0 | 0 | 100 | 0 | 0
141 | 712.58 | 0 | 24.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 712.58 | 0 | 0.088511 | 3.7058 | 0 | 0 | 0 | 0 | on_peak | 712.58 |  |  | 0 | 0 | 100 | 0 | 0
142 | 703.91 | 0 | 24.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 703.91 | 0 | 0.088511 | 3.9865 | 0 | 0 | 0 | 0 | on_peak | 703.91 |  |  | 0 | 0 | 100 | 0 | 0
143 | 689.9 | 0 | 24.1 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 18.9814 | 702.2624 | 0 | 0.05921 | 4.516 | 0 | 0 | 0 | 0 | off_peak | 689.9 | 0 | 100 | 0 | 0 | 100 | 0 | 0
144 | 730.97 | 0 | 23.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18.9814 | 730.97 | 0 | 0.05921 | 4.9681 | 0 | 0 | 0 | 0 | off_peak | 730.97 |  |  | 0 | 0 | 100 | 0 | 0
145 | 645.57 | 0 | 23.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18.9814 | 645.57 | 0 | 0.05921 | 5.1383 | 0 | 0 | 0 | 0 | off_peak | 645.57 |  |  | 0 | 0 | 100 | 0 | 0
146 | 619.36 | 0 | 23.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18.9814 | 619.36 | 0 | 0.05921 | 4.957 | 0 | 0 | 0 | 0 | off_peak | 619.36 |  |  | 0 | 0 | 100 | 0 | 0
147 | 570.98 | 0 | 23.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18.9814 | 570.98 | 0 | 0.05921 | 4.6814 | 0 | 0 | 0 | 0 | off_peak | 570.98 |  |  | 0 | 0 | 100 | 0 | 0
148 | 570.47 | 0 | 23.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18.9814 | 570.47 | 0 | 0.05921 | 4.4219 | 0 | 0 | 0 | 0 | off_peak | 570.47 |  |  | 0 | 0 | 100 | 0 | 0
149 | 582.47 | 0 | 23.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18.9814 | 582.47 | 0 | 0.05921 | 4.0417 | 0 | 0 | 0 | 0 | off_peak | 582.47 |  |  | 0 | 0 | 100 | 0 | 0
150 | 659.41 | 0 | 22.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18.9814 | 659.41 | 0 | 0.05921 | 3.6094 | 0 | 0 | 0 | 0 | off_peak | 659.41 |  |  | 0 | 0 | 100 | 0 | 0
151 | 668.43 | 0 | 22.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18.9814 | 668.43 | 0 | 0.05921 | 3.363 | 0 | 0 | 0 | 0 | off_peak | 668.43 |  |  | 0 | 0 | 100 | 0 | 0
152 | 680.52 | 28.1777 | 22.6 | 4.6042 | 4.6042 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18.9814 | 675.9158 | 0 | 0.05921 | 3.0777 | 0 | 0 | 0 | 4.6042 | off_peak | 675.9158 |  |  | 0.68 | 0 | 99.32 | 14.1704 | 0
153 | 725.4 | 194.003 | 22.7 | 31.6887 | 31.6887 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18.9814 | 693.7113 | 0 | 0.05921 | 2.921 | 0 | 0 | 0 | 31.6887 | off_peak | 693.7113 |  |  | 4.37 | 0 | 95.63 | 92.5624 | 0
154 | 701.32 | 370.695 | 23.1 | 60.4633 | 60.4633 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18.9814 | 640.8567 | 0 | 0.05921 | 2.8836 | 0 | 0 | 0 | 60.4633 | off_peak | 640.8567 |  |  | 8.62 | 0 | 91.38 | 174.3536 | 0
155 | 721.82 | 515.763 | 23.8 | 83.9146 | 83.9146 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18.9814 | 637.9054 | 0 | 0.05921 | 2.8993 | 0 | 0 | 0 | 83.9146 | off_peak | 637.9054 |  |  | 11.63 | 0 | 88.37 | 243.2923 | 0
156 | 721.35 | 606.311 | 24.4 | 98.4345 | 98.4345 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18.9814 | 622.9155 | 0 | 0.05921 | 3.0398 | 0 | 0 | 0 | 98.4345 | off_peak | 622.9155 |  |  | 13.65 | 0 | 86.35 | 299.2261 | 0
157 | 695.28 | 466.087 | 24.9 | 75.5333 | 75.5333 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18.9814 | 619.7467 | 0 | 0.05921 | 3.3813 | 0 | 0 | 0 | 75.5333 | off_peak | 619.7467 |  |  | 10.86 | 0 | 89.14 | 255.3984 | 0
158 | 660.79 | 117.455 | 25.2 | 19.014 | 19.014 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18.9814 | 641.776 | 0 | 0.05921 | 3.9272 | 0 | 0 | 0 | 19.014 | off_peak | 641.776 |  |  | 2.88 | 0 | 97.12 | 74.6717 | 0
159 | 625.65 | 254.162 | 25.4 | 41.115 | 41.115 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18.9814 | 584.535 | 0 | 0.05921 | 3.9496 | 0 | 0 | 0 | 41.115 | off_peak | 584.535 |  |  | 6.57 | 0 | 93.43 | 162.3868 | 0
160 | 627.58 | 35.15 | 25.4 | 5.6861 | 5.6861 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18.9814 | 621.8939 | 0 | 0.05921 | 3.6729 | 0 | 0 | 0 | 5.6861 | off_peak | 621.8939 |  |  | 0.91 | 0 | 99.09 | 20.8847 | 0
161 | 602.92 | 85.7155 | 25 | 13.8859 | 13.8859 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18.9814 | 589.0341 | 0 | 0.05921 | 3.4665 | 0 | 0 | 0 | 13.8859 | off_peak | 589.0341 |  |  | 2.3 | 0 | 97.7 | 48.1352 | 0
162 | 570.45 | 4.75 | 24.3 | 0.77144 | 0.77144 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18.9814 | 569.6786 | 0 | 0.05921 | 3.2594 | 0 | 0 | 0 | 0.77144 | off_peak | 569.6786 |  |  | 0.14 | 0 | 99.86 | 2.5145 | 0
163 | 549.28 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18.9814 | 549.28 | 0 | 0.05921 | 3.263 | 0 | 0 | 0 | 0 | off_peak | 549.28 |  |  | 0 | 0 | 100 | 0 | 0
164 | 505.18 | 0 | 22.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18.9814 | 505.18 | 0 | 0.05921 | 3.3097 | 0 | 0 | 0 | 0 | off_peak | 505.18 |  |  | 0 | 0 | 100 | 0 | 0
165 | 534.63 | 0 | 21.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18.9814 | 534.63 | 0 | 0.05921 | 3.4478 | 0 | 0 | 0 | 0 | off_peak | 534.63 |  |  | 0 | 0 | 100 | 0 | 0
166 | 504.31 | 0 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18.9814 | 504.31 | 0 | 0.05921 | 3.7534 | 0 | 0 | 0 | 0 | off_peak | 504.31 |  |  | 0 | 0 | 100 | 0 | 0
167 | 520.65 | 0 | 20.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18.9814 | 520.65 | 0 | 0.05921 | 4.2573 | 0 | 0 | 0 | 0 | off_peak | 520.65 |  |  | 0 | 0 | 100 | 0 | 0
168 | 528.55 | 0 | 19.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18.9814 | 528.55 | 0 | 0.05921 | 4.6642 | 0 | 0 | 0 | 0 | off_peak | 528.55 |  |  | 0 | 0 | 100 | 0 | 0
169 | 499.41 | 0 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18.9814 | 499.41 | 0 | 0.05921 | 4.8552 | 0 | 0 | 0 | 0 | off_peak | 499.41 |  |  | 0 | 0 | 100 | 0 | 0
170 | 554 | 0 | 18.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18.9814 | 554 | 0 | 0.05921 | 4.6595 | 0 | 0 | 0 | 0 | off_peak | 554 |  |  | 0 | 0 | 100 | 0 | 0
171 | 552.65 | 0 | 17.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18.9814 | 552.65 | 0 | 0.05921 | 4.4161 | 0 | 0 | 0 | 0 | off_peak | 552.65 |  |  | 0 | 0 | 100 | 0 | 0
172 | 525.44 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18.9814 | 525.44 | 0 | 0.05921 | 4.1597 | 0 | 0 | 0 | 0 | off_peak | 525.44 |  |  | 0 | 0 | 100 | 0 | 0
173 | 526.94 | 0 | 16.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18.9814 | 526.94 | 0 | 0.05921 | 3.8636 | 0 | 0 | 0 | 0 | off_peak | 526.94 |  |  | 0 | 0 | 100 | 0 | 0
174 | 560.98 | 0 | 16.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18.9814 | 560.98 | 0 | 0.05921 | 3.507 | 0 | 0 | 0 | 0 | off_peak | 560.98 |  |  | 0 | 0 | 100 | 0 | 0
175 | 649.14 | 0 | 15.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18.9814 | 649.14 | 0 | 0.05921 | 3.2173 | 0 | 0 | 0 | 0 | off_peak | 649.14 |  |  | 0 | 0 | 100 | 0 | 0
176 | 640.05 | 32.242 | 16.2 | 5.3887 | 5.3887 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18.9814 | 634.6613 | 0 | 0.05921 | 2.9434 | 0 | 0 | 0 | 5.3887 | off_peak | 634.6613 |  |  | 0.84 | 0 | 99.16 | 15.8611 | 0
177 | 637.43 | 210.867 | 17 | 35.1443 | 35.1443 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18.9814 | 602.2857 | 0 | 0.05921 | 2.8066 | 0 | 0 | 0 | 35.1443 | off_peak | 602.2857 |  |  | 5.51 | 0 | 94.49 | 98.6345 | 0
178 | 674.87 | 400.005 | 18.3 | 66.3638 | 66.3638 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18.9814 | 608.5062 | 0 | 0.05921 | 2.7508 | 0 | 0 | 0 | 66.3638 | off_peak | 608.5062 |  |  | 9.83 | 0 | 90.17 | 182.5568 | 0
179 | 618.45 | 553.776 | 19.5 | 91.488 | 91.488 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18.9814 | 526.962 | 0 | 0.05921 | 2.755 | 0 | 0 | 0 | 91.488 | off_peak | 526.962 |  |  | 14.79 | 0 | 85.21 | 252.0528 | 0
180 | 642.16 | 652.689 | 20.3 | 107.5247 | 107.5247 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18.9814 | 534.6353 | 0 | 0.05921 | 2.891 | 0 | 0 | 0 | 107.5247 | off_peak | 534.6353 |  |  | 16.74 | 0 | 83.26 | 310.853 | 0
181 | 621.77 | 682.59 | 20.9 | 112.2117 | 112.2117 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18.9814 | 509.5583 | 0 | 0.05921 | 3.1352 | 0 | 0 | 0 | 112.2117 | off_peak | 509.5583 |  |  | 18.05 | 0 | 81.95 | 351.8113 | 0
182 | 594.91 | 646.219 | 21.2 | 106.1196 | 106.1196 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18.9814 | 488.7904 | 0 | 0.05921 | 3.5512 | 0 | 0 | 0 | 106.1196 | off_peak | 488.7904 |  |  | 17.84 | 0 | 82.16 | 376.854 | 0
183 | 617.49 | 547.594 | 21.2 | 89.9238 | 89.9238 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18.9814 | 527.5662 | 0 | 0.05921 | 3.752 | 0 | 0 | 0 | 89.9238 | off_peak | 527.5662 |  |  | 14.56 | 0 | 85.44 | 337.3925 | 0
184 | 587.52 | 391.283 | 21.1 | 64.2778 | 64.2778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18.9814 | 523.2422 | 0 | 0.05921 | 3.5786 | 0 | 0 | 0 | 64.2778 | off_peak | 523.2422 |  |  | 10.94 | 0 | 89.06 | 230.0258 | 0
185 | 617.31 | 200.857 | 20.9 | 33.0191 | 33.0191 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18.9814 | 584.2909 | 0 | 0.05921 | 3.4652 | 0 | 0 | 0 | 33.0191 | off_peak | 584.2909 |  |  | 5.35 | 0 | 94.65 | 114.4188 | 0
186 | 555.24 | 24.6514 | 20.8 | 4.0539 | 4.0539 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18.9814 | 551.1861 | 0 | 0.05921 | 3.6129 | 0 | 0 | 0 | 4.0539 | off_peak | 551.1861 |  |  | 0.73 | 0 | 99.27 | 14.6464 | 0
187 | 557.43 | 0 | 20.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18.9814 | 557.43 | 0 | 0.05921 | 3.739 | 0 | 0 | 0 | 0 | off_peak | 557.43 |  |  | 0 | 0 | 100 | 0 | 0
188 | 529.05 | 0 | 20.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18.9814 | 529.05 | 0 | 0.05921 | 3.8649 | 0 | 0 | 0 | 0 | off_peak | 529.05 |  |  | 0 | 0 | 100 | 0 | 0
189 | 508.7 | 0 | 20.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18.9814 | 508.7 | 0 | 0.05921 | 4.0754 | 0 | 0 | 0 | 0 | off_peak | 508.7 |  |  | 0 | 0 | 100 | 0 | 0
190 | 506.93 | 0 | 20.9 | 0 | 0 | 0 | 0 | 8.7006 | 8.7006 | 0 | 0 | 0 | 27.12 | 515.6306 | 0 | 0.05921 | 4.3274 | 0 | 0 | 0 | 0 | off_peak | 506.93 | 0 | 100 | 0 | 0 | 100 | 0 | 0
191 | 507.89 | 0 | 20.9 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 38.684 | 520.2524 | 0 | 0.05921 | 4.6948 | 0 | 0 | 0 | 0 | off_peak | 507.89 | 0 | 100 | 0 | 0 | 100 | 0 | 0
192 | 494.64 | 0 | 20.9 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 50.2479 | 507.0024 | 0 | 0.05921 | 5.0539 | 0 | 0 | 0 | 0 | off_peak | 494.64 | 0 | 100 | 0 | 0 | 100 | 0 | 0
193 | 518.56 | 0 | 20.9 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 61.8119 | 530.9224 | 0 | 0.05921 | 5.2595 | 0 | 0 | 0 | 0 | off_peak | 518.56 | 0 | 100 | 0 | 0 | 100 | 0 | 0
194 | 504.72 | 0 | 20.9 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 73.3758 | 517.0824 | 0 | 0.05921 | 5.0554 | 0 | 0 | 0 | 0 | off_peak | 504.72 | 0 | 100 | 0 | 0 | 100 | 0 | 0
195 | 507.78 | 0 | 20.9 | 0 | 0 | 0 | 0 | 0.79843 | 0.79843 | 0 | 0 | 0 | 74.1227 | 508.5784 | 0 | 0.05921 | 4.7467 | 0 | 0 | 0 | 0 | off_peak | 507.78 | 0 | 100 | 0 | 0 | 100 | 0 | 0
196 | 518.91 | 0 | 20.9 | 0 | 0 | 0 | 0 | 0.051567 | 0.051567 | 0 | 0 | 0 | 74.1709 | 518.9616 | 0 | 0.05921 | 4.3693 | 0 | 0 | 0 | 0 | off_peak | 518.91 | 0 | 100 | 0 | 0 | 100 | 0 | 0
197 | 535.62 | 0 | 21 | 0 | 0 | 0 | 0 | 0.0033305 | 0.0033305 | 0 | 0 | 0 | 74.174 | 535.6233 | 0 | 0.05921 | 3.924 | 0 | 0 | 0 | 0 | off_peak | 535.62 | 0 | 100 | 0 | 0 | 100 | 0 | 0
198 | 634.83 | 0 | 21.1 | 0 | 0 | 0 | 0 | 0.0002151 | 0.0002151 | 0 | 0 | 0 | 74.1742 | 634.8302 | 0 | 0.05921 | 3.4127 | 0 | 0 | 0 | 0 | off_peak | 634.83 | 0 | 100 | 0 | 0 | 100 | 0 | 0
199 | 719.73 | 0 | 21.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1742 | 719.73 | 0 | 0.088511 | 2.9105 | 0 | 0 | 0 | 0 | on_peak | 719.73 |  |  | 0 | 0 | 100 | 0 | 0
200 | 777.71 | 32.075 | 21.9 | 5.2541 | 5.2541 | 0 | 0 | 0 | 0 | 62.4453 | 62.4453 | 0 | 7.4174 | 710.0106 | 0 | 0.088511 | 2.6501 | 0 | 0 | 0 | 5.2541 | on_peak | 710.0106 |  |  | 0.68 | 8.03 | 91.3 | 13.924 | 0
201 | 770.3 | 207.483 | 22.7 | 33.8906 | 33.8906 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 736.4094 | 0 | 0.088511 | 2.5161 | 0 | 0 | 0 | 33.8906 | on_peak | 736.4094 |  |  | 4.4 | 0 | 95.6 | 85.2731 | 0
202 | 836.04 | 392.781 | 23.2 | 64.0428 | 64.0428 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 771.9972 | 0 | 0.088511 | 2.469 | 0 | 0 | 0 | 64.0428 | on_peak | 771.9972 |  |  | 7.66 | 0 | 92.34 | 158.1219 | 0
203 | 819.64 | 299.003 | 23.5 | 48.7001 | 48.7001 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 18.9814 | 783.3023 | 0 | 0.05921 | 2.5525 | 0 | 0 | 0 | 48.7001 | off_peak | 770.9399 | 0 | 100 | 5.94 | 0 | 94.06 | 124.3081 | 0
204 | 874.27 | 470.348 | 23.7 | 76.553 | 76.553 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 30.5453 | 810.0794 | 0 | 0.05921 | 2.9107 | 0 | 0 | 0 | 76.553 | off_peak | 797.717 | 0 | 100 | 8.76 | 0 | 91.24 | 222.8233 | 0
205 | 833.95 | 679.811 | 23.7 | 110.6448 | 110.6448 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 42.1093 | 735.6676 | 0 | 0.05921 | 3.4778 | 0 | 0 | 0 | 110.6448 | off_peak | 723.3052 | 0 | 100 | 13.27 | 0 | 86.73 | 384.7984 | 0
206 | 871.71 | 652.608 | 23.7 | 106.2173 | 106.2173 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 53.6732 | 777.8551 | 0 | 0.05921 | 3.8323 | 0 | 0 | 0 | 106.2173 | off_peak | 765.4927 | 0 | 100 | 12.18 | 0 | 87.82 | 407.0549 | 0
207 | 831.8 | 553.051 | 23.6 | 90.0458 | 90.0458 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 65.2371 | 754.1166 | 0 | 0.05921 | 3.7913 | 0 | 0 | 0 | 90.0458 | off_peak | 741.7542 | 0 | 100 | 10.83 | 0 | 89.17 | 341.3946 | 0
208 | 839.46 | 398.344 | 23.5 | 64.8802 | 64.8802 | 0 | 0 | 8.9371 | 8.9371 | 0 | 0 | 0 | 73.597 | 783.5169 | 0 | 0.05921 | 3.5663 | 0 | 0 | 0 | 64.8802 | off_peak | 774.5798 | 0 | 100 | 7.73 | 0 | 92.27 | 231.383 | 0
209 | 798.72 | 42.75 | 23.3 | 6.9679 | 6.3907 | 0 | 0.57721 | 0.57721 | 0 | 0 | 0 | 0 | 74.137 | 792.3293 | 0 | 0.05921 | 3.4135 | 0 | 0 | 0.53993 | 6.3907 | off_peak | 792.3293 | 100 | 0 | 0.8 | 0 | 99.2 | 21.8148 | 0
210 | 808.72 | 28.4621 | 23.1 | 4.6424 | 4.6051 | 0 | 0.037279 | 0.037279 | 0 | 0 | 0 | 0 | 74.1718 | 804.1149 | 0 | 0.05921 | 3.4302 | 0 | 0 | 0.5748 | 4.6051 | off_peak | 804.1149 | 100 | 0 | 0.57 | 0 | 99.43 | 15.7966 | 0
211 | 778.28 | 0 | 23 | 0 | 0 | 0 | 0 | 0 | 0 | 62.443 | 62.443 | 0 | 7.4174 | 715.837 | 0 | 0.088511 | 3.5255 | 0.53768 | 0 | 0 | 0.53768 | on_peak | 715.837 |  |  | 0 | 8.02 | 91.98 | 1.8956 | 0
212 | 808.23 | 0 | 22.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 808.23 | 0 | 0.088511 | 3.6586 | 0 | 0 | 0 | 0 | on_peak | 808.23 |  |  | 0 | 0 | 100 | 0 | 0
213 | 746.54 | 0 | 22.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 746.54 | 0 | 0.088511 | 3.8765 | 0 | 0 | 0 | 0 | on_peak | 746.54 |  |  | 0 | 0 | 100 | 0 | 0
214 | 708.99 | 0 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 708.99 | 0 | 0.088511 | 4.2085 | 0 | 0 | 0 | 0 | on_peak | 708.99 |  |  | 0 | 0 | 100 | 0 | 0
215 | 745.9 | 0 | 21.4 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 18.9814 | 758.2624 | 0 | 0.05921 | 4.7418 | 0 | 0 | 0 | 0 | off_peak | 745.9 | 0 | 100 | 0 | 0 | 100 | 0 | 0
216 | 705.86 | 0 | 20.8 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 30.5453 | 718.2224 | 0 | 0.05921 | 5.1884 | 0 | 0 | 0 | 0 | off_peak | 705.86 | 0 | 100 | 0 | 0 | 100 | 0 | 0
217 | 661.04 | 0 | 20.2 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 42.1093 | 673.4024 | 0 | 0.05921 | 5.3396 | 0 | 0 | 0 | 0 | off_peak | 661.04 | 0 | 100 | 0 | 0 | 100 | 0 | 0
218 | 567.56 | 0 | 19.6 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 53.6732 | 579.9224 | 0 | 0.05921 | 5.2182 | 0 | 0 | 0 | 0 | off_peak | 567.56 | 0 | 100 | 0 | 0 | 100 | 0 | 0
219 | 590.04 | 0 | 19 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 65.2371 | 602.4024 | 0 | 0.05921 | 4.8625 | 0 | 0 | 0 | 0 | off_peak | 590.04 | 0 | 100 | 0 | 0 | 100 | 0 | 0
220 | 559.7 | 0 | 18.5 | 0 | 0 | 0 | 0 | 8.9371 | 8.9371 | 0 | 0 | 0 | 73.597 | 568.6371 | 0 | 0.05921 | 4.4499 | 0 | 0 | 0 | 0 | off_peak | 559.7 | 0 | 100 | 0 | 0 | 100 | 0 | 0
221 | 593.9 | 0 | 18.1 | 0 | 0 | 0 | 0 | 0.57721 | 0.57721 | 0 | 0 | 0 | 74.137 | 594.4772 | 0 | 0.05921 | 4.0293 | 0 | 0 | 0 | 0 | off_peak | 593.9 | 0 | 100 | 0 | 0 | 100 | 0 | 0
222 | 702.82 | 0 | 17.9 | 0 | 0 | 0 | 0 | 0.037279 | 0.037279 | 0 | 0 | 0 | 74.1718 | 702.8573 | 0 | 0.05921 | 3.4953 | 0 | 0 | 0 | 0 | off_peak | 702.82 | 0 | 100 | 0 | 0 | 100 | 0 | 0
223 | 753.69 | 0 | 17.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1718 | 753.69 | 0 | 0.088511 | 3.0781 | 0 | 0 | 0 | 0 | on_peak | 753.69 |  |  | 0 | 0 | 100 | 0 | 0
224 | 769.8 | 14.25 | 17.9 | 2.3675 | 2.3675 | 0 | 0 | 0 | 0 | 62.443 | 62.443 | 0 | 7.4174 | 704.9895 | 0 | 0.088511 | 2.7894 | 0 | 0 | 0 | 2.3675 | on_peak | 704.9895 |  |  | 0.31 | 8.11 | 91.58 | 6.604 | 0
225 | 753.4 | 48.45 | 18.5 | 8.0326 | 8.0326 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 745.3674 | 0 | 0.088511 | 2.6614 | 0 | 0 | 0 | 8.0326 | on_peak | 745.3674 |  |  | 1.07 | 0 | 98.93 | 21.3775 | 0
226 | 813.74 | 170.2 | 19.7 | 28.0985 | 28.0985 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 785.6415 | 0 | 0.088511 | 2.6343 | 0 | 0 | 0 | 28.0985 | on_peak | 785.6415 |  |  | 3.45 | 0 | 96.55 | 74.0185 | 0
227 | 759.56 | 389.136 | 21.1 | 63.9251 | 63.9251 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 18.9814 | 707.9973 | 0 | 0.05921 | 2.7296 | 0 | 0 | 0 | 63.9251 | off_peak | 695.6349 | 0 | 100 | 8.42 | 0 | 91.58 | 174.4902 | 0
228 | 828.64 | 646.118 | 22.4 | 105.6508 | 105.6508 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 30.5453 | 735.3515 | 0 | 0.05921 | 3.1254 | 0 | 0 | 0 | 105.6508 | off_peak | 722.9892 | 0 | 100 | 12.75 | 0 | 87.25 | 330.2053 | 0
229 | 780.57 | 677.308 | 23.3 | 110.3954 | 110.3954 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 42.1093 | 682.537 | 0 | 0.05921 | 3.7444 | 0 | 0 | 0 | 110.3954 | off_peak | 670.1746 | 0 | 100 | 14.14 | 0 | 85.86 | 413.3678 | 0
230 | 808.3 | 144.4 | 23.8 | 23.4939 | 23.4939 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 53.6732 | 797.1685 | 0 | 0.05921 | 4.1098 | 0 | 0 | 0 | 23.4939 | off_peak | 784.8061 | 0 | 100 | 2.91 | 0 | 97.09 | 96.556 | 0
231 | 857.22 | 368.807 | 24 | 59.9618 | 59.9618 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 65.2371 | 809.6206 | 0 | 0.05921 | 4.1144 | 0 | 0 | 0 | 59.9618 | off_peak | 797.2582 | 0 | 100 | 6.99 | 0 | 93.01 | 246.7043 | 0
232 | 799.58 | 104.5 | 23.9 | 16.996 | 16.996 | 0 | 0 | 8.9371 | 8.9371 | 0 | 0 | 0 | 73.597 | 791.5211 | 0 | 0.05921 | 3.7979 | 0 | 0 | 0 | 16.996 | off_peak | 782.584 | 0 | 100 | 2.13 | 0 | 97.87 | 64.5499 | 0
233 | 821.27 | 75.2909 | 23.5 | 12.263 | 11.6858 | 0 | 0.57721 | 0.57721 | 0 | 0 | 0 | 0 | 74.137 | 809.5842 | 0 | 0.05921 | 3.5793 | 0 | 0 | 0.53993 | 11.6858 | off_peak | 809.5842 | 100 | 0 | 1.42 | 0 | 98.58 | 41.8274 | 0
234 | 794.64 | 11.4 | 23 | 1.8601 | 1.8228 | 0 | 0.037279 | 0.037279 | 0 | 0 | 0 | 0 | 74.1718 | 792.8172 | 0 | 0.05921 | 3.3467 | 0 | 0 | 0.5748 | 1.8228 | off_peak | 792.8172 | 100 | 0 | 0.23 | 0 | 99.77 | 6.1005 | 0
235 | 768.02 | 0 | 22.8 | 0 | 0 | 0 | 0 | 0 | 0 | 62.443 | 62.443 | 0 | 7.4174 | 705.577 | 0 | 0.088511 | 3.3139 | 0 | 0 | 0.5748 | 0 | on_peak | 705.577 |  |  | 0 | 8.13 | 91.87 | 0 | 0
236 | 782.16 | 0 | 22.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 782.16 | 0 | 0.088511 | 3.3528 | 0 | 0 | 0.5748 | 0 | on_peak | 782.16 |  |  | 0 | 0 | 100 | 0 | 0
237 | 773.31 | 0 | 22.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 773.31 | 0 | 0.088511 | 3.4464 | 0 | 0 | 0.5748 | 0 | on_peak | 773.31 |  |  | 0 | 0 | 100 | 0 | 0
238 | 725.41 | 0 | 22.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 725.41 | 0 | 0.088511 | 3.7718 | 0 | 0 | 0.5748 | 0 | on_peak | 725.41 |  |  | 0 | 0 | 100 | 0 | 0
239 | 726.85 | 0 | 22.3 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 18.9814 | 739.2124 | 0 | 0.05921 | 4.3543 | 0 | 0 | 0.5748 | 0 | off_peak | 726.85 | 0 | 100 | 0 | 0 | 100 | 0 | 0
240 | 736.16 | 0 | 22.2 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 30.5453 | 748.5224 | 0 | 0.05921 | 4.868 | 0 | 0 | 0.5748 | 0 | off_peak | 736.16 | 0 | 100 | 0 | 0 | 100 | 0 | 0
241 | 656.04 | 0 | 22.3 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 42.1093 | 668.4024 | 0 | 0.05921 | 5.1044 | 0 | 0 | 0.5748 | 0 | off_peak | 656.04 | 0 | 100 | 0 | 0 | 100 | 0 | 0
242 | 589.97 | 0 | 22.3 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 53.6732 | 602.3324 | 0 | 0.05921 | 5.0042 | 0 | 0 | 0.5748 | 0 | off_peak | 589.97 | 0 | 100 | 0 | 0 | 100 | 0 | 0
243 | 586.37 | 0 | 22.3 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 65.2371 | 598.7324 | 0 | 0.05921 | 4.7263 | 0 | 0 | 0.5748 | 0 | off_peak | 586.37 | 0 | 100 | 0 | 0 | 100 | 0 | 0
244 | 573.97 | 0 | 22.3 | 0 | 0 | 0 | 0 | 8.9371 | 8.9371 | 0 | 0 | 0 | 73.597 | 582.9071 | 0 | 0.05921 | 4.335 | 0 | 0 | 0.5748 | 0 | off_peak | 573.97 | 0 | 100 | 0 | 0 | 100 | 0 | 0
245 | 593.67 | 0 | 22.3 | 0 | 0 | 0 | 0 | 0.57721 | 0.57721 | 0 | 0 | 0 | 74.137 | 594.2472 | 0 | 0.05921 | 3.878 | 0 | 0 | 0.5748 | 0 | off_peak | 593.67 | 0 | 100 | 0 | 0 | 100 | 0 | 0
246 | 688.61 | 0 | 22.4 | 0 | 0 | 0 | 0 | 0.037279 | 0.037279 | 0 | 0 | 0 | 74.1718 | 688.6473 | 0 | 0.05921 | 3.4184 | 0 | 0 | 0.5748 | 0 | off_peak | 688.61 | 0 | 100 | 0 | 0 | 100 | 0 | 0
247 | 767.66 | 0 | 22.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1718 | 767.66 | 0 | 0.088511 | 3.0758 | 0 | 0 | 0.5748 | 0 | on_peak | 767.66 |  |  | 0 | 0 | 100 | 0 | 0
248 | 778.82 | 16.15 | 23.2 | 2.6333 | 2.6333 | 0 | 0 | 0 | 0 | 62.443 | 62.443 | 0 | 7.4174 | 713.7437 | 0 | 0.088511 | 2.8636 | 0.53768 | 0 | 0 | 3.1709 | on_peak | 713.7437 |  |  | 0.34 | 8.02 | 91.64 | 9.0803 | 0
249 | 804.75 | 205.12 | 23.9 | 33.361 | 33.361 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 771.389 | 0 | 0.088511 | 2.7779 | 0 | 0 | 0 | 33.361 | on_peak | 771.389 |  |  | 4.15 | 0 | 95.85 | 92.6727 | 0
250 | 850.28 | 295.185 | 24.4 | 47.9233 | 47.9233 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 802.3567 | 0 | 0.088511 | 2.753 | 0 | 0 | 0 | 47.9233 | on_peak | 802.3567 |  |  | 5.64 | 0 | 94.36 | 131.9304 | 0
251 | 832.02 | 544.191 | 24.7 | 88.2542 | 88.2542 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 18.9814 | 756.1282 | 0 | 0.05921 | 2.8938 | 0 | 0 | 0 | 88.2542 | off_peak | 743.7658 | 0 | 100 | 10.61 | 0 | 89.39 | 255.392 | 0
252 | 861.5 | 250.13 | 24.8 | 40.5502 | 40.5502 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 30.5453 | 833.3121 | 0 | 0.05921 | 3.2984 | 0 | 0 | 0 | 40.5502 | off_peak | 820.9498 | 0 | 100 | 4.71 | 0 | 95.29 | 133.7498 | 0
253 | 818.26 | 396.151 | 24.8 | 64.2227 | 64.2227 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 42.1093 | 766.3997 | 0 | 0.05921 | 4.0526 | 0 | 0 | 0 | 64.2227 | off_peak | 754.0373 | 0 | 100 | 7.85 | 0 | 92.15 | 260.2688 | 0
254 | 813.74 | 637.968 | 24.7 | 103.4624 | 103.4624 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 53.6732 | 722.6399 | 0 | 0.05921 | 4.5429 | 0 | 0 | 0 | 103.4624 | off_peak | 710.2776 | 0 | 100 | 12.71 | 0 | 87.29 | 470.0144 | 0
255 | 877.08 | 540.6 | 24.4 | 87.7664 | 87.7664 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 65.2371 | 801.676 | 0 | 0.05921 | 4.3206 | 0 | 0 | 0 | 87.7664 | off_peak | 789.3136 | 0 | 100 | 10.01 | 0 | 89.99 | 379.2031 | 0
256 | 857.84 | 205.349 | 24.3 | 33.3504 | 33.3504 | 0 | 0 | 8.9371 | 8.9371 | 0 | 0 | 0 | 73.597 | 833.4267 | 0 | 0.05921 | 3.7531 | 0 | 0 | 0 | 33.3504 | off_peak | 824.4896 | 0 | 100 | 3.89 | 0 | 96.11 | 125.1671 | 0
257 | 803.01 | 137.432 | 24.1 | 22.3361 | 22.3361 | 0 | 0 | 0.57721 | 0.57721 | 0 | 0 | 0 | 74.137 | 781.2511 | 0 | 0.05921 | 3.3861 | 0 | 0 | 0 | 22.3361 | off_peak | 780.6739 | 0 | 100 | 2.78 | 0 | 97.22 | 75.6332 | 0
258 | 800.8 | 17.0512 | 24 | 2.7722 | 2.7722 | 0 | 0 | 0.037279 | 0.037279 | 0 | 0 | 0 | 74.1718 | 798.065 | 0 | 0.05921 | 3.1141 | 0 | 0 | 0 | 2.7722 | off_peak | 798.0278 | 0 | 100 | 0.35 | 0 | 99.65 | 8.6331 | 0
259 | 807.38 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 62.443 | 62.443 | 0 | 7.4174 | 744.937 | 0 | 0.088511 | 3.0959 | 0 | 0 | 0 | 0 | on_peak | 744.937 |  |  | 0 | 7.73 | 92.27 | 0 | 0
260 | 805.92 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 805.92 | 0 | 0.088511 | 3.1666 | 0 | 0 | 0 | 0 | on_peak | 805.92 |  |  | 0 | 0 | 100 | 0 | 0
261 | 796.23 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 796.23 | 0 | 0.088511 | 3.1437 | 0 | 0 | 0 | 0 | on_peak | 796.23 |  |  | 0 | 0 | 100 | 0 | 0
262 | 743.38 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 743.38 | 0 | 0.088511 | 3.4301 | 0 | 0 | 0 | 0 | on_peak | 743.38 |  |  | 0 | 0 | 100 | 0 | 0
263 | 840.76 | 0 | 23.9 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 18.9814 | 853.1224 | 0 | 0.05921 | 4.1446 | 0 | 0 | 0 | 0 | off_peak | 840.76 | 0 | 100 | 0 | 0 | 100 | 0 | 0
264 | 738.4 | 0 | 23.8 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 30.5453 | 750.7624 | 0 | 0.05921 | 4.637 | 0 | 0 | 0 | 0 | off_peak | 738.4 | 0 | 100 | 0 | 0 | 100 | 0 | 0
265 | 700.86 | 0 | 23.7 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 42.1093 | 713.2224 | 0 | 0.05921 | 4.9734 | 0 | 0 | 0 | 0 | off_peak | 700.86 | 0 | 100 | 0 | 0 | 100 | 0 | 0
266 | 651.61 | 0 | 23.7 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 53.6732 | 663.9724 | 0 | 0.05921 | 4.855 | 0 | 0 | 0 | 0 | off_peak | 651.61 | 0 | 100 | 0 | 0 | 100 | 0 | 0
267 | 569.62 | 0 | 23.7 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 65.2371 | 581.9824 | 0 | 0.05921 | 4.6415 | 0 | 0 | 0 | 0 | off_peak | 569.62 | 0 | 100 | 0 | 0 | 100 | 0 | 0
268 | 601.2 | 0 | 23.6 | 0 | 0 | 0 | 0 | 8.9371 | 8.9371 | 0 | 0 | 0 | 73.597 | 610.1371 | 0 | 0.05921 | 4.2793 | 0 | 0 | 0 | 0 | off_peak | 601.2 | 0 | 100 | 0 | 0 | 100 | 0 | 0
269 | 589.54 | 0 | 23.7 | 0 | 0 | 0 | 0 | 0.57721 | 0.57721 | 0 | 0 | 0 | 74.137 | 590.1172 | 0 | 0.05921 | 3.8496 | 0 | 0 | 0 | 0 | off_peak | 589.54 | 0 | 100 | 0 | 0 | 100 | 0 | 0
270 | 686.6 | 0 | 23.7 | 0 | 0 | 0 | 0 | 0.037279 | 0.037279 | 0 | 0 | 0 | 74.1718 | 686.6373 | 0 | 0.05921 | 3.4138 | 0 | 0 | 0 | 0 | off_peak | 686.6 | 0 | 100 | 0 | 0 | 100 | 0 | 0
271 | 787.76 | 0 | 23.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1718 | 787.76 | 0 | 0.088511 | 2.9946 | 0 | 0 | 0 | 0 | on_peak | 787.76 |  |  | 0 | 0 | 100 | 0 | 0
272 | 766.39 | 19.8274 | 24 | 3.2236 | 3.2236 | 0 | 0 | 0 | 0 | 33.1958 | 33.1958 | 0 | 38.684 | 729.9706 | 0 | 0.088511 | 2.7736 | 0 | 0 | 0 | 3.2236 | on_peak | 729.9706 |  |  | 0.42 | 4.33 | 95.25 | 8.9411 | 0
273 | 815.53 | 211.175 | 24.3 | 34.2966 | 34.2966 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 38.684 | 781.2334 | 0 | 0.088511 | 2.6886 | 0 | 0 | 0 | 34.2966 | on_peak | 781.2334 |  |  | 4.21 | 0 | 95.79 | 92.2107 | 0
274 | 813.34 | 91.2 | 24.5 | 14.801 | 14.801 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 38.684 | 798.539 | 0 | 0.088511 | 2.6729 | 0 | 0 | 0 | 14.801 | on_peak | 798.539 |  |  | 1.82 | 0 | 98.18 | 39.5618 | 0
275 | 773.33 | 152.95 | 24.7 | 24.8047 | 24.8047 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 50.2479 | 760.8877 | 0 | 0.05921 | 2.7925 | 0 | 0 | 0 | 24.8047 | off_peak | 748.5253 | 0 | 100 | 3.21 | 0 | 96.79 | 69.2663 | 0
276 | 894.05 | 501.159 | 24.7 | 81.2754 | 81.2754 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 61.8119 | 825.1369 | 0 | 0.05921 | 3.1544 | 0 | 0 | 0 | 81.2754 | off_peak | 812.7746 | 0 | 100 | 9.09 | 0 | 90.91 | 256.3743 | 0
277 | 845.08 | 516.349 | 24.6 | 83.769 | 83.769 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 73.3758 | 773.6734 | 0 | 0.05921 | 3.8055 | 0 | 0 | 0 | 83.769 | off_peak | 761.311 | 0 | 100 | 9.91 | 0 | 90.09 | 318.7818 | 0
278 | 845.29 | 405.303 | 24.5 | 65.7773 | 65.7773 | 0 | 0 | 0.79843 | 0.79843 | 0 | 0 | 0 | 74.1227 | 780.3112 | 0 | 0.05921 | 4.2694 | 0 | 0 | 0 | 65.7773 | off_peak | 779.5127 | 0 | 100 | 7.78 | 0 | 92.22 | 280.8279 | 0
279 | 927.72 | 244.355 | 24.4 | 39.671 | 39.671 | 0 | 0 | 0.051567 | 0.051567 | 0 | 0 | 0 | 74.1709 | 888.1006 | 0 | 0.05921 | 4.0443 | 0 | 0 | 0 | 39.671 | off_peak | 888.049 | 0 | 100 | 4.28 | 0 | 95.72 | 160.4399 | 0
280 | 959.8 | 57 | 24.3 | 9.2573 | 9.2573 | 0 | 0 | 0 | 0 | 62.4422 | 62.4422 | 0 | 7.4174 | 888.1006 | 0 | 0.05921 | 3.5482 | 0 | 0 | 0 | 9.2573 | off_peak | 888.1006 |  |  | 0.96 | 6.51 | 92.53 | 32.8466 | 0
281 | 897.02 | 212.794 | 24 | 34.5967 | 34.5967 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 18.9814 | 874.7856 | 0 | 0.05921 | 3.3189 | 0 | 0 | 0 | 34.5967 | off_peak | 862.4233 | 0 | 100 | 3.86 | 0 | 96.14 | 114.8245 | 0
282 | 841.26 | 33.4928 | 23.8 | 5.4493 | 0 | 0 | 5.4493 | 12.3624 | 6.9131 | 0 | 0 | 0 | 30.5453 | 848.1731 | 0 | 0.05921 | 3.2554 | 0 | 0 | 5.0973 | 0 | off_peak | 841.26 | 44.08 | 55.92 | 0 | 0 | 100 | 0 | 0
283 | 796.09 | 0 | 23.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30.5453 | 796.09 | 0 | 0.088511 | 3.3158 | 0 | 0 | 5.0973 | 0 | on_peak | 796.09 |  |  | 0 | 0 | 100 | 0 | 0
284 | 791.66 | 0 | 23.8 | 0 | 0 | 0 | 0 | 0 | 0 | 16.866 | 16.866 | 0 | 12.5148 | 774.794 | 0 | 0.088511 | 3.468 | 0 | 0 | 5.0973 | 0 | on_peak | 774.794 |  |  | 0 | 2.13 | 97.87 | 0 | 0
285 | 798.05 | 0 | 23.8 | 0 | 0 | 0 | 0 | 0 | 0 | 4.7681 | 4.7681 | 0 | 7.4174 | 793.2819 | 0 | 0.088511 | 3.6069 | 4.7681 | 0 | 0 | 4.7681 | on_peak | 793.2819 |  |  | 0 | 0.6 | 99.4 | 17.198 | 0
286 | 762.21 | 0 | 23.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 762.21 | 0 | 0.088511 | 3.9853 | 0 | 0 | 0 | 0 | on_peak | 762.21 |  |  | 0 | 0 | 100 | 0 | 0
287 | 775.92 | 0 | 23.6 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 18.9814 | 788.2824 | 0 | 0.05921 | 4.5606 | 0 | 0 | 0 | 0 | off_peak | 775.92 | 0 | 100 | 0 | 0 | 100 | 0 | 0
288 | 755.66 | 0 | 23.5 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 30.5453 | 768.0224 | 0 | 0.05921 | 4.9878 | 0 | 0 | 0 | 0 | off_peak | 755.66 | 0 | 100 | 0 | 0 | 100 | 0 | 0
289 | 715.4 | 0 | 23.5 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 42.1093 | 727.7624 | 0 | 0.05921 | 5.2524 | 0 | 0 | 0 | 0 | off_peak | 715.4 | 0 | 100 | 0 | 0 | 100 | 0 | 0
290 | 623.93 | 0 | 23.4 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 53.6732 | 636.2924 | 0 | 0.05921 | 5.0409 | 0 | 0 | 0 | 0 | off_peak | 623.93 | 0 | 100 | 0 | 0 | 100 | 0 | 0
291 | 638.65 | 0 | 23.4 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 65.2371 | 651.0124 | 0 | 0.05921 | 4.679 | 0 | 0 | 0 | 0 | off_peak | 638.65 | 0 | 100 | 0 | 0 | 100 | 0 | 0
292 | 606.03 | 0 | 23.3 | 0 | 0 | 0 | 0 | 8.9371 | 8.9371 | 0 | 0 | 0 | 73.597 | 614.9671 | 0 | 0.05921 | 4.2856 | 0 | 0 | 0 | 0 | off_peak | 606.03 | 0 | 100 | 0 | 0 | 100 | 0 | 0
293 | 619.17 | 0 | 23.1 | 0 | 0 | 0 | 0 | 0.57721 | 0.57721 | 0 | 0 | 0 | 74.137 | 619.7472 | 0 | 0.05921 | 3.835 | 0 | 0 | 0 | 0 | off_peak | 619.17 | 0 | 100 | 0 | 0 | 100 | 0 | 0
294 | 673.42 | 0 | 22.9 | 0 | 0 | 0 | 0 | 0.037279 | 0.037279 | 0 | 0 | 0 | 74.1718 | 673.4573 | 0 | 0.05921 | 3.3298 | 0 | 0 | 0 | 0 | off_peak | 673.42 | 0 | 100 | 0 | 0 | 100 | 0 | 0
295 | 815.47 | 0 | 22.8 | 0 | 0 | 0 | 0 | 0.0024077 | 0.0024077 | 0 | 0 | 0 | 74.1741 | 815.4724 | 0 | 0.088511 | 2.9017 | 0 | 0 | 0 | 0 | on_peak | 815.47 | 0 | 100 | 0 | 0 | 100 | 0 | 0
296 | 888.72 | 33.1652 | 23 | 5.4114 | 5.4114 | 0 | 0 | 0 | 0 | 59.7194 | 59.7194 | 0 | 10.3313 | 823.5891 | 0 | 0.088511 | 2.6281 | 0 | 0 | 0 | 5.4114 | on_peak | 823.5891 |  |  | 0.61 | 6.72 | 92.67 | 14.2221 | 0
297 | 798.04 | 149.858 | 23.4 | 24.4168 | 24.4168 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 21.8953 | 785.9855 | 0 | 0.088511 | 2.5063 | 0 | 0 | 0 | 24.4168 | on_peak | 773.6232 | 0 | 100 | 3.06 | 0 | 96.94 | 61.197 | 0
298 | 864.96 | 171.162 | 24 | 27.8281 | 27.8281 | 0 | 0 | 0 | 0 | 13.5428 | 13.5428 | 0 | 7.4174 | 823.5891 | 0 | 0.088511 | 2.4587 | 0 | 0 | 0 | 27.8281 | on_peak | 823.5891 |  |  | 3.22 | 1.57 | 95.22 | 68.4213 | 0
299 | 840.1 | 548.844 | 24.5 | 89.0728 | 89.0728 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 18.9814 | 763.3896 | 0 | 0.05921 | 2.5067 | 0 | 0 | 0 | 89.0728 | off_peak | 751.0272 | 0 | 100 | 10.6 | 0 | 89.4 | 223.276 | 0
300 | 914.96 | 644.958 | 24.8 | 104.5584 | 104.5584 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 30.5453 | 822.764 | 0 | 0.05921 | 2.7709 | 0 | 0 | 0 | 104.5584 | off_peak | 810.4016 | 0 | 100 | 11.43 | 0 | 88.57 | 289.719 | 0
301 | 812.68 | 506.626 | 25 | 82.0734 | 82.0734 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 42.1093 | 742.969 | 0 | 0.05921 | 3.3281 | 0 | 0 | 0 | 82.0734 | off_peak | 730.6066 | 0 | 100 | 10.1 | 0 | 89.9 | 273.1512 | 0
302 | 831.34 | 648.771 | 25 | 105.1009 | 105.1009 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 53.6732 | 738.6015 | 0 | 0.05921 | 3.7587 | 0 | 0 | 0 | 105.1009 | off_peak | 726.2391 | 0 | 100 | 12.64 | 0 | 87.36 | 395.0428 | 0
303 | 869.04 | 552.695 | 24.9 | 89.5688 | 89.5688 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 65.2371 | 791.8336 | 0 | 0.05921 | 4.0113 | 0 | 0 | 0 | 89.5688 | off_peak | 779.4712 | 0 | 100 | 10.31 | 0 | 89.69 | 359.2857 | 0
304 | 796.76 | 400.792 | 24.8 | 64.9751 | 64.9751 | 0 | 0 | 8.9371 | 8.9371 | 0 | 0 | 0 | 73.597 | 740.7221 | 0 | 0.05921 | 4.1716 | 0 | 0 | 0 | 64.9751 | off_peak | 731.7849 | 0 | 100 | 8.15 | 0 | 91.85 | 271.0497 | 0
305 | 813.25 | 111.445 | 24.5 | 18.0866 | 18.0866 | 0 | 0 | 0.57721 | 0.57721 | 0 | 0 | 0 | 74.137 | 795.7406 | 0 | 0.05921 | 4.2586 | 0 | 0 | 0 | 18.0866 | off_peak | 795.1634 | 0 | 100 | 2.22 | 0 | 97.78 | 77.0228 | 0
306 | 831.49 | 34.2194 | 24.2 | 5.5595 | 5.5595 | 0 | 0 | 0.037279 | 0.037279 | 0 | 0 | 0 | 74.1718 | 825.9678 | 0 | 0.05921 | 4.2851 | 0 | 0 | 0 | 5.5595 | off_peak | 825.9305 | 0 | 100 | 0.67 | 0 | 99.33 | 23.8228 | 0
307 | 737.41 | 0 | 24.1 | 0 | 0 | 0 | 0 | 0 | 0 | 62.443 | 62.443 | 0 | 7.4174 | 674.967 | 0 | 0.088511 | 4.1948 | 0 | 0 | 0 | 0 | on_peak | 674.967 |  |  | 0 | 8.47 | 91.53 | 0 | 0
308 | 775.9 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 775.9 | 0 | 0.088511 | 4.0306 | 0 | 0 | 0 | 0 | on_peak | 775.9 |  |  | 0 | 0 | 100 | 0 | 0
309 | 717.86 | 0 | 23.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 717.86 | 0 | 0.088511 | 3.7773 | 0 | 0 | 0 | 0 | on_peak | 717.86 |  |  | 0 | 0 | 100 | 0 | 0
310 | 716.65 | 0 | 23.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 716.65 | 0 | 0.088511 | 3.8896 | 0 | 0 | 0 | 0 | on_peak | 716.65 |  |  | 0 | 0 | 100 | 0 | 0
311 | 747.66 | 0 | 23.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 747.66 | 0 | 0.05921 | 4.1519 | 0 | 0 | 0 | 0 | off_peak | 747.66 |  |  | 0 | 0 | 100 | 0 | 0
312 | 750.31 | 0 | 22.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 750.31 | 0 | 0.05921 | 4.6388 | 0 | 0 | 0 | 0 | off_peak | 750.31 |  |  | 0 | 0 | 100 | 0 | 0
313 | 710.89 | 0 | 22.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 710.89 | 0 | 0.05921 | 4.9531 | 0 | 0 | 0 | 0 | off_peak | 710.89 |  |  | 0 | 0 | 100 | 0 | 0
314 | 631.28 | 0 | 22.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 631.28 | 0 | 0.05921 | 4.8503 | 0 | 0 | 0 | 0 | off_peak | 631.28 |  |  | 0 | 0 | 100 | 0 | 0
315 | 549.97 | 0 | 22.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 549.97 | 0 | 0.05921 | 4.6462 | 0 | 0 | 0 | 0 | off_peak | 549.97 |  |  | 0 | 0 | 100 | 0 | 0
316 | 626.56 | 0 | 22.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 626.56 | 0 | 0.05921 | 4.4229 | 0 | 0 | 0 | 0 | off_peak | 626.56 |  |  | 0 | 0 | 100 | 0 | 0
317 | 566.72 | 0 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 566.72 | 0 | 0.05921 | 4.0798 | 0 | 0 | 0 | 0 | off_peak | 566.72 |  |  | 0 | 0 | 100 | 0 | 0
318 | 679.61 | 0 | 21.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 679.61 | 0 | 0.05921 | 3.7042 | 0 | 0 | 0 | 0 | off_peak | 679.61 |  |  | 0 | 0 | 100 | 0 | 0
319 | 719.11 | 0 | 21.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 719.11 | 0 | 0.05921 | 3.5591 | 0 | 0 | 0 | 0 | off_peak | 719.11 |  |  | 0 | 0 | 100 | 0 | 0
320 | 786.81 | 12.35 | 22 | 2.0223 | 2.0223 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 784.7877 | 0 | 0.05921 | 3.4435 | 0 | 0 | 0 | 2.0223 | off_peak | 784.7877 |  |  | 0.26 | 0 | 99.74 | 6.9638 | 0
321 | 782.98 | 212.315 | 22.5 | 34.7046 | 34.7046 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 748.2754 | 0 | 0.05921 | 3.4188 | 0 | 0 | 0 | 34.7046 | off_peak | 748.2754 |  |  | 4.43 | 0 | 95.57 | 118.6481 | 0
322 | 777.37 | 287.233 | 23.2 | 46.8333 | 46.8333 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 730.5367 | 0 | 0.05921 | 3.4966 | 0 | 0 | 0 | 46.8333 | off_peak | 730.5367 |  |  | 6.02 | 0 | 93.98 | 163.7576 | 0
323 | 706.16 | 549.73 | 23.9 | 89.4089 | 89.4089 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 616.7511 | 0 | 0.05921 | 3.6497 | 0 | 0 | 0 | 89.4089 | off_peak | 616.7511 |  |  | 12.66 | 0 | 87.34 | 326.3135 | 0
324 | 723.3 | 164.35 | 24.3 | 26.6918 | 26.6918 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 696.6082 | 0 | 0.05921 | 3.9832 | 0 | 0 | 0 | 26.6918 | off_peak | 696.6082 |  |  | 3.69 | 0 | 96.31 | 106.3193 | 0
325 | 759.09 | 379.792 | 24.7 | 61.5928 | 61.5928 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 697.4972 | 0 | 0.05921 | 4.4031 | 0 | 0 | 0 | 61.5928 | off_peak | 697.4972 |  |  | 8.11 | 0 | 91.89 | 271.196 | 0
326 | 668.88 | 419.247 | 24.9 | 67.9425 | 67.9425 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 600.9375 | 0 | 0.05921 | 4.9416 | 0 | 0 | 0 | 67.9425 | off_peak | 600.9375 |  |  | 10.16 | 0 | 89.84 | 335.7475 | 0
327 | 669.76 | 111.15 | 24.9 | 18.0128 | 18.0128 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 651.7472 | 0 | 0.05921 | 5.0578 | 0 | 0 | 0 | 18.0128 | off_peak | 651.7472 |  |  | 2.69 | 0 | 97.31 | 91.1044 | 0
328 | 625.25 | 186.56 | 24.8 | 30.2445 | 30.2445 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 595.0055 | 0 | 0.05921 | 4.7576 | 0 | 0 | 0 | 30.2445 | off_peak | 595.0055 |  |  | 4.84 | 0 | 95.16 | 143.8915 | 0
329 | 612.39 | 159.285 | 24.3 | 25.8692 | 25.8692 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 586.5208 | 0 | 0.05921 | 4.3356 | 0 | 0 | 0 | 25.8692 | off_peak | 586.5208 |  |  | 4.22 | 0 | 95.78 | 112.1591 | 0
330 | 620.02 | 37.3402 | 23.7 | 6.0774 | 6.0774 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 613.9426 | 0 | 0.05921 | 4.0427 | 0 | 0 | 0 | 6.0774 | off_peak | 613.9426 |  |  | 0.98 | 0 | 99.02 | 24.5695 | 0
331 | 642.95 | 0 | 23.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 642.95 | 0 | 0.05921 | 3.7694 | 0 | 0 | 0 | 0 | off_peak | 642.95 |  |  | 0 | 0 | 100 | 0 | 0
332 | 605.32 | 0 | 22.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 605.32 | 0 | 0.05921 | 3.5335 | 0 | 0 | 0 | 0 | off_peak | 605.32 |  |  | 0 | 0 | 100 | 0 | 0
333 | 647.25 | 0 | 22.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 647.25 | 0 | 0.05921 | 3.3099 | 0 | 0 | 0 | 0 | off_peak | 647.25 |  |  | 0 | 0 | 100 | 0 | 0
334 | 584.85 | 0 | 21.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 584.85 | 0 | 0.05921 | 3.3893 | 0 | 0 | 0 | 0 | off_peak | 584.85 |  |  | 0 | 0 | 100 | 0 | 0
335 | 559.46 | 0 | 21.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 559.46 | 0 | 0.05921 | 4.0581 | 0 | 0 | 0 | 0 | off_peak | 559.46 |  |  | 0 | 0 | 100 | 0 | 0
336 | 578.14 | 0 | 21.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 578.14 | 0 | 0.05921 | 4.992 | 0 | 0 | 0 | 0 | off_peak | 578.14 |  |  | 0 | 0 | 100 | 0 | 0
337 | 537.06 | 0 | 21.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 537.06 | 0 | 0.05921 | 5.642 | 0 | 0 | 0 | 0 | off_peak | 537.06 |  |  | 0 | 0 | 100 | 0 | 0
338 | 575.88 | 0 | 20.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 575.88 | 0 | 0.05921 | 5.6421 | 0 | 0 | 0 | 0 | off_peak | 575.88 |  |  | 0 | 0 | 100 | 0 | 0
339 | 603.95 | 0 | 20.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 603.95 | 0 | 0.05921 | 5.5936 | 0 | 0 | 0 | 0 | off_peak | 603.95 |  |  | 0 | 0 | 100 | 0 | 0
340 | 568.87 | 0 | 20.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 568.87 | 0 | 0.05921 | 5.5335 | 0 | 0 | 0 | 0 | off_peak | 568.87 |  |  | 0 | 0 | 100 | 0 | 0
341 | 600.89 | 0 | 20.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 600.89 | 0 | 0.05921 | 5.3072 | 0 | 0 | 0 | 0 | off_peak | 600.89 |  |  | 0 | 0 | 100 | 0 | 0
342 | 715.55 | 0 | 19.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 715.55 | 0 | 0.05921 | 5.1251 | 0 | 0 | 0 | 0 | off_peak | 715.55 |  |  | 0 | 0 | 100 | 0 | 0
343 | 678.03 | 0 | 19.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 678.03 | 0 | 0.05921 | 5.0568 | 0 | 0 | 0 | 0 | off_peak | 678.03 |  |  | 0 | 0 | 100 | 0 | 0
344 | 735.55 | 11.4 | 20.2 | 1.8787 | 1.8787 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 733.6713 | 0 | 0.05921 | 5.0867 | 0 | 0 | 0 | 1.8787 | off_peak | 733.6713 |  |  | 0.26 | 0 | 99.74 | 9.5564 | 0
345 | 719.06 | 71.25 | 21 | 11.7087 | 11.7087 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 707.3513 | 0 | 0.05921 | 5.1649 | 0 | 0 | 0 | 11.7087 | off_peak | 707.3513 |  |  | 1.63 | 0 | 98.37 | 60.4743 | 0
346 | 712.99 | 114.95 | 22.1 | 18.8163 | 18.8163 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 694.1737 | 0 | 0.05921 | 5.2763 | 0 | 0 | 0 | 18.8163 | off_peak | 694.1737 |  |  | 2.64 | 0 | 97.36 | 99.2809 | 0
347 | 640.3 | 141.55 | 23 | 23.0962 | 23.0962 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 617.2038 | 0 | 0.05921 | 5.4521 | 0 | 0 | 0 | 23.0962 | off_peak | 617.2038 |  |  | 3.61 | 0 | 96.39 | 125.9228 | 0
348 | 685.31 | 155.8 | 23.6 | 25.3668 | 25.3668 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 659.9432 | 0 | 0.05921 | 5.6092 | 0 | 0 | 0 | 25.3668 | off_peak | 659.9432 |  |  | 3.7 | 0 | 96.3 | 142.2871 | 0
349 | 640 | 490.213 | 24 | 79.7004 | 79.7004 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 560.2996 | 0 | 0.05921 | 6.0858 | 0 | 0 | 0 | 79.7004 | off_peak | 560.2996 |  |  | 12.45 | 0 | 87.55 | 485.0441 | 0
350 | 640.52 | 440.538 | 24.1 | 71.5984 | 71.5984 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 568.9216 | 0 | 0.05921 | 6.6211 | 0 | 0 | 0 | 71.5984 | off_peak | 568.9216 |  |  | 11.18 | 0 | 88.82 | 474.0597 | 0
351 | 632.68 | 416.489 | 24.1 | 67.6898 | 67.6898 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 564.9902 | 0 | 0.05921 | 6.5084 | 0 | 0 | 0 | 67.6898 | off_peak | 564.9902 |  |  | 10.7 | 0 | 89.3 | 440.5537 | 0
352 | 585.91 | 202.289 | 24.1 | 32.877 | 32.877 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 553.033 | 0 | 0.05921 | 5.9185 | 0 | 0 | 0 | 32.877 | off_peak | 553.033 |  |  | 5.61 | 0 | 94.39 | 194.5815 | 0
353 | 570.87 | 61.75 | 23.8 | 10.0467 | 10.0467 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 560.8233 | 0 | 0.05921 | 5.0662 | 0 | 0 | 0 | 10.0467 | off_peak | 560.8233 |  |  | 1.76 | 0 | 98.24 | 50.899 | 0
354 | 550.73 | 36.5592 | 23.5 | 5.9546 | 5.9546 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 544.7754 | 0 | 0.05921 | 4.3793 | 0 | 0 | 0 | 5.9546 | off_peak | 544.7754 |  |  | 1.08 | 0 | 98.92 | 26.0767 | 0
355 | 498.49 | 0 | 23.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 498.49 | 0 | 0.05921 | 3.894 | 0 | 0 | 0 | 0 | off_peak | 498.49 |  |  | 0 | 0 | 100 | 0 | 0
356 | 540.44 | 0 | 23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 540.44 | 0 | 0.05921 | 3.5032 | 0 | 0 | 0 | 0 | off_peak | 540.44 |  |  | 0 | 0 | 100 | 0 | 0
357 | 518.54 | 0 | 22.7 | 0 | 0 | 0 | 0 | 8.7006 | 8.7006 | 0 | 0 | 0 | 15.5561 | 527.2406 | 0 | 0.05921 | 3.2129 | 0 | 0 | 0 | 0 | off_peak | 518.54 | 0 | 100 | 0 | 0 | 100 | 0 | 0
358 | 534.09 | 0 | 22.3 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 27.12 | 546.4524 | 0 | 0.05921 | 3.2445 | 0 | 0 | 0 | 0 | off_peak | 534.09 | 0 | 100 | 0 | 0 | 100 | 0 | 0
359 | 554.7 | 0 | 21.9 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 38.684 | 567.0624 | 0 | 0.05921 | 3.7981 | 0 | 0 | 0 | 0 | off_peak | 554.7 | 0 | 100 | 0 | 0 | 100 | 0 | 0
360 | 504.31 | 0 | 21.4 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 50.2479 | 516.6724 | 0 | 0.05921 | 4.7358 | 0 | 0 | 0 | 0 | off_peak | 504.31 | 0 | 100 | 0 | 0 | 100 | 0 | 0
361 | 554.9 | 0 | 21.1 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 61.8119 | 567.2624 | 0 | 0.05921 | 5.3865 | 0 | 0 | 0 | 0 | off_peak | 554.9 | 0 | 100 | 0 | 0 | 100 | 0 | 0
362 | 540.94 | 0 | 20.8 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 73.3758 | 553.3024 | 0 | 0.05921 | 5.4488 | 0 | 0 | 0 | 0 | off_peak | 540.94 | 0 | 100 | 0 | 0 | 100 | 0 | 0
363 | 524.67 | 0 | 20.4 | 0 | 0 | 0 | 0 | 0.79843 | 0.79843 | 0 | 0 | 0 | 74.1227 | 525.4684 | 0 | 0.05921 | 5.5146 | 0 | 0 | 0 | 0 | off_peak | 524.67 | 0 | 100 | 0 | 0 | 100 | 0 | 0
364 | 526.44 | 0 | 20.1 | 0 | 0 | 0 | 0 | 0.051567 | 0.051567 | 0 | 0 | 0 | 74.1709 | 526.4916 | 0 | 0.05921 | 5.4363 | 0 | 0 | 0 | 0 | off_peak | 526.44 | 0 | 100 | 0 | 0 | 100 | 0 | 0
365 | 548.05 | 0 | 19.7 | 0 | 0 | 0 | 0 | 0.0033305 | 0.0033305 | 0 | 0 | 0 | 74.174 | 548.0533 | 0 | 0.05921 | 5.3168 | 0 | 0 | 0 | 0 | off_peak | 548.05 | 0 | 100 | 0 | 0 | 100 | 0 | 0
366 | 679.56 | 0 | 19.4 | 0 | 0 | 0 | 0 | 0.0002151 | 0.0002151 | 0 | 0 | 0 | 74.1742 | 679.5602 | 0 | 0.05921 | 5.1902 | 0 | 0 | 0 | 0 | off_peak | 679.56 | 0 | 100 | 0 | 0 | 100 | 0 | 0
367 | 703.4 | 0 | 19.2 | 0 | 0 | 0 | 0 | 0 | 0 | 62.4453 | 62.4453 | 0 | 7.4174 | 640.9547 | 0 | 0.088511 | 4.947 | 0 | 0 | 0 | 0 | on_peak | 640.9547 |  |  | 0 | 8.88 | 91.12 | 0 | 0
368 | 770.06 | 34.1113 | 19.2 | 5.6414 | 5.6414 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 764.4186 | 0 | 0.088511 | 4.9498 | 0 | 0 | 0 | 5.6414 | on_peak | 764.4186 |  |  | 0.73 | 0 | 99.27 | 27.9237 | 0
369 | 799.54 | 213.225 | 19.4 | 35.2388 | 35.2388 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 764.3012 | 0 | 0.088511 | 4.981 | 0 | 0 | 0 | 35.2388 | on_peak | 764.3012 |  |  | 4.41 | 0 | 95.59 | 175.5261 | 0
370 | 734.93 | 336.312 | 19.9 | 55.4828 | 55.4828 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 679.4472 | 0 | 0.088511 | 5.1095 | 0 | 0 | 0 | 55.4828 | on_peak | 679.4472 |  |  | 7.55 | 0 | 92.45 | 283.4895 | 0
371 | 689.69 | 431.638 | 20.6 | 71.033 | 71.033 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 18.9814 | 631.0194 | 0 | 0.05921 | 5.382 | 0 | 0 | 0 | 71.033 | off_peak | 618.657 | 0 | 100 | 10.3 | 0 | 89.7 | 382.2965 | 0
372 | 824.81 | 345.897 | 21.4 | 56.7615 | 56.7615 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 30.5453 | 780.4108 | 0 | 0.05921 | 5.7823 | 0 | 0 | 0 | 56.7615 | off_peak | 768.0485 | 0 | 100 | 6.88 | 0 | 93.12 | 328.2123 | 0
373 | 679.39 | 117.8 | 21.8 | 19.3034 | 19.3034 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 42.1093 | 672.4489 | 0 | 0.05921 | 6.2745 | 0 | 0 | 0 | 19.3034 | off_peak | 660.0866 | 0 | 100 | 2.84 | 0 | 97.16 | 121.1202 | 0
374 | 666.4 | 652.732 | 21.9 | 106.9227 | 106.9227 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 53.6732 | 571.8397 | 0 | 0.05921 | 6.903 | 0 | 0 | 0 | 106.9227 | off_peak | 559.4773 | 0 | 100 | 16.04 | 0 | 83.96 | 738.0888 | 0
375 | 603.24 | 392.065 | 21.8 | 64.2462 | 64.2462 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 65.2371 | 551.3562 | 0 | 0.05921 | 6.6918 | 0 | 0 | 0 | 64.2462 | off_peak | 538.9938 | 0 | 100 | 10.65 | 0 | 89.35 | 429.9238 | 0
376 | 641.49 | 79.8 | 21.5 | 13.0905 | 13.0905 | 0 | 0 | 8.9371 | 8.9371 | 0 | 0 | 0 | 73.597 | 637.3366 | 0 | 0.05921 | 5.5791 | 0 | 0 | 0 | 13.0905 | off_peak | 628.3995 | 0 | 100 | 2.04 | 0 | 97.96 | 73.0327 | 0
377 | 601.67 | 150.894 | 21.1 | 24.788 | 24.788 | 0 | 0 | 0.57721 | 0.57721 | 0 | 0 | 0 | 74.137 | 577.4592 | 0 | 0.05921 | 4.7298 | 0 | 0 | 0 | 24.788 | off_peak | 576.882 | 0 | 100 | 4.12 | 0 | 95.88 | 117.2422 | 0
378 | 578.56 | 39.8723 | 20.7 | 6.5593 | 6.5593 | 0 | 0 | 0.037279 | 0.037279 | 0 | 0 | 0 | 74.1718 | 572.038 | 0 | 0.05921 | 3.9607 | 0 | 0 | 0 | 6.5593 | off_peak | 572.0007 | 0 | 100 | 1.13 | 0 | 98.87 | 25.9793 | 0
379 | 569.14 | 0 | 20.5 | 0 | 0 | 0 | 0 | 0 | 0 | 62.443 | 62.443 | 0 | 7.4174 | 506.697 | 0 | 0.088511 | 3.5115 | 0 | 0 | 0 | 0 | on_peak | 506.697 |  |  | 0 | 10.97 | 89.03 | 0 | 0
380 | 612.94 | 0 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 612.94 | 0 | 0.088511 | 3.2211 | 0 | 0 | 0 | 0 | on_peak | 612.94 |  |  | 0 | 0 | 100 | 0 | 0
381 | 629.33 | 0 | 19.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 629.33 | 0 | 0.088511 | 3.0634 | 0 | 0 | 0 | 0 | on_peak | 629.33 |  |  | 0 | 0 | 100 | 0 | 0
382 | 607.73 | 0 | 19.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 607.73 | 0 | 0.088511 | 3.2101 | 0 | 0 | 0 | 0 | on_peak | 607.73 |  |  | 0 | 0 | 100 | 0 | 0
383 | 558.52 | 0 | 19 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 18.9814 | 570.8824 | 0 | 0.05921 | 3.7904 | 0 | 0 | 0 | 0 | off_peak | 558.52 | 0 | 100 | 0 | 0 | 100 | 0 | 0
384 | 570.69 | 0 | 18.6 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 30.5453 | 583.0524 | 0 | 0.05921 | 4.4994 | 0 | 0 | 0 | 0 | off_peak | 570.69 | 0 | 100 | 0 | 0 | 100 | 0 | 0
385 | 539.4 | 0 | 18.3 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 42.1093 | 551.7624 | 0 | 0.05921 | 5.1739 | 0 | 0 | 0 | 0 | off_peak | 539.4 | 0 | 100 | 0 | 0 | 100 | 0 | 0
386 | 563.08 | 0 | 18.2 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 53.6732 | 575.4424 | 0 | 0.05921 | 5.1869 | 0 | 0 | 0 | 0 | off_peak | 563.08 | 0 | 100 | 0 | 0 | 100 | 0 | 0
387 | 552.34 | 0 | 18.1 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 65.2371 | 564.7024 | 0 | 0.05921 | 5.054 | 0 | 0 | 0 | 0 | off_peak | 552.34 | 0 | 100 | 0 | 0 | 100 | 0 | 0
388 | 549.09 | 0 | 18 | 0 | 0 | 0 | 0 | 8.9371 | 8.9371 | 0 | 0 | 0 | 73.597 | 558.0271 | 0 | 0.05921 | 4.8046 | 0 | 0 | 0 | 0 | off_peak | 549.09 | 0 | 100 | 0 | 0 | 100 | 0 | 0
389 | 584.62 | 0 | 17.9 | 0 | 0 | 0 | 0 | 0.57721 | 0.57721 | 0 | 0 | 0 | 74.137 | 585.1972 | 0 | 0.05921 | 4.4033 | 0 | 0 | 0 | 0 | off_peak | 584.62 | 0 | 100 | 0 | 0 | 100 | 0 | 0
390 | 652.9 | 0 | 17.9 | 0 | 0 | 0 | 0 | 0.037279 | 0.037279 | 0 | 0 | 0 | 74.1718 | 652.9373 | 0 | 0.05921 | 4.2053 | 0 | 0 | 0 | 0 | off_peak | 652.9 | 0 | 100 | 0 | 0 | 100 | 0 | 0
391 | 715.63 | 0 | 18.2 | 0 | 0 | 0 | 0 | 0 | 0 | 62.443 | 62.443 | 0 | 7.4174 | 653.187 | 0 | 0.088511 | 3.6733 | 0 | 0 | 0 | 0 | on_peak | 653.187 |  |  | 0 | 8.73 | 91.27 | 0 | 0
392 | 785.95 | 35.6211 | 19 | 5.8953 | 5.8953 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 780.0547 | 0 | 0.088511 | 3.632 | 0 | 0 | 0 | 5.8953 | on_peak | 780.0547 |  |  | 0.75 | 0 | 99.25 | 21.4118 | 0
393 | 829.83 | 218.826 | 20.2 | 36.0624 | 36.0624 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 793.7676 | 0 | 0.088511 | 3.6178 | 0 | 0 | 0 | 36.0624 | on_peak | 793.7676 |  |  | 4.35 | 0 | 95.65 | 130.4659 | 0
394 | 778.31 | 406.446 | 21.4 | 66.6976 | 66.6976 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 711.6124 | 0 | 0.088511 | 3.742 | 0 | 0 | 0 | 66.6976 | on_peak | 711.6124 |  |  | 8.57 | 0 | 91.43 | 249.5804 | 0
395 | 737.55 | 560.613 | 22.3 | 91.7021 | 91.7021 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 18.9814 | 658.2103 | 0 | 0.05921 | 3.9636 | 0 | 0 | 0 | 91.7021 | off_peak | 645.8479 | 0 | 100 | 12.43 | 0 | 87.57 | 363.4691 | 0
396 | 831.8 | 406.232 | 22.8 | 66.3308 | 66.3308 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 30.5453 | 777.8316 | 0 | 0.05921 | 4.5744 | 0 | 0 | 0 | 66.3308 | off_peak | 765.4692 | 0 | 100 | 7.97 | 0 | 92.03 | 303.4239 | 0
397 | 832.97 | 694.498 | 23.1 | 113.2782 | 113.2782 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 42.1093 | 732.0541 | 0 | 0.05921 | 5.4082 | 0 | 0 | 0 | 113.2782 | off_peak | 719.6918 | 0 | 100 | 13.6 | 0 | 86.4 | 612.6369 | 0
398 | 768.84 | 530.936 | 23.2 | 86.569 | 86.569 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 53.6732 | 694.6334 | 0 | 0.05921 | 6.0951 | 0 | 0 | 0 | 86.569 | off_peak | 682.271 | 0 | 100 | 11.26 | 0 | 88.74 | 527.6463 | 0
399 | 864.73 | 500.411 | 23.2 | 81.5919 | 81.5919 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 65.2371 | 795.5005 | 0 | 0.05921 | 5.4626 | 0 | 0 | 0 | 81.5919 | off_peak | 783.1381 | 0 | 100 | 9.44 | 0 | 90.56 | 445.7061 | 0
400 | 825.61 | 243.695 | 23 | 39.7628 | 39.7628 | 0 | 0 | 8.9371 | 8.9371 | 0 | 0 | 0 | 73.597 | 794.7843 | 0 | 0.05921 | 4.3485 | 0 | 0 | 0 | 39.7628 | off_peak | 785.8472 | 0 | 100 | 4.82 | 0 | 95.18 | 172.91 | 0
401 | 755.05 | 168.839 | 22.4 | 27.6079 | 27.6079 | 0 | 0 | 0.57721 | 0.57721 | 0 | 0 | 0 | 74.137 | 728.0193 | 0 | 0.05921 | 3.5366 | 0 | 0 | 0 | 27.6079 | off_peak | 727.4421 | 0 | 100 | 3.66 | 0 | 96.34 | 97.6394 | 0
402 | 782.73 | 43.9821 | 21.8 | 7.2072 | 7.2072 | 0 | 0 | 0.037279 | 0.037279 | 0 | 0 | 0 | 74.1718 | 775.5601 | 0 | 0.05921 | 3.0687 | 0 | 0 | 0 | 7.2072 | off_peak | 775.5228 | 0 | 100 | 0.92 | 0 | 99.08 | 22.1169 | 0
403 | 751.17 | 0 | 21.6 | 0 | 0 | 0 | 0 | 0 | 0 | 62.443 | 62.443 | 0 | 7.4174 | 688.727 | 0 | 0.088511 | 2.9363 | 0 | 0 | 0 | 0 | on_peak | 688.727 |  |  | 0 | 8.31 | 91.69 | 0 | 0
404 | 760.65 | 0 | 21.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 760.65 | 0 | 0.088511 | 2.8969 | 0 | 0 | 0 | 0 | on_peak | 760.65 |  |  | 0 | 0 | 100 | 0 | 0
405 | 744.26 | 0 | 21.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 744.26 | 0 | 0.088511 | 2.9636 | 0 | 0 | 0 | 0 | on_peak | 744.26 |  |  | 0 | 0 | 100 | 0 | 0
406 | 709.84 | 0 | 21.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 709.84 | 0 | 0.088511 | 3.1851 | 0 | 0 | 0 | 0 | on_peak | 709.84 |  |  | 0 | 0 | 100 | 0 | 0
407 | 780.96 | 0 | 21.5 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 18.9814 | 793.3224 | 0 | 0.05921 | 3.7943 | 0 | 0 | 0 | 0 | off_peak | 780.96 | 0 | 100 | 0 | 0 | 100 | 0 | 0
408 | 710.79 | 0 | 21.5 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 30.5453 | 723.1524 | 0 | 0.05921 | 4.3731 | 0 | 0 | 0 | 0 | off_peak | 710.79 | 0 | 100 | 0 | 0 | 100 | 0 | 0
409 | 693.35 | 0 | 21.6 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 42.1093 | 705.7124 | 0 | 0.05921 | 4.7753 | 0 | 0 | 0 | 0 | off_peak | 693.35 | 0 | 100 | 0 | 0 | 100 | 0 | 0
410 | 609.33 | 0 | 21.6 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 53.6732 | 621.6924 | 0 | 0.05921 | 4.6619 | 0 | 0 | 0 | 0 | off_peak | 609.33 | 0 | 100 | 0 | 0 | 100 | 0 | 0
411 | 597.22 | 0 | 21.7 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 65.2371 | 609.5824 | 0 | 0.05921 | 4.4022 | 0 | 0 | 0 | 0 | off_peak | 597.22 | 0 | 100 | 0 | 0 | 100 | 0 | 0
412 | 564.93 | 0 | 21.7 | 0 | 0 | 0 | 0 | 8.9371 | 8.9371 | 0 | 0 | 0 | 73.597 | 573.8671 | 0 | 0.05921 | 4.0747 | 0 | 0 | 0 | 0 | off_peak | 564.93 | 0 | 100 | 0 | 0 | 100 | 0 | 0
413 | 594.41 | 0 | 21.6 | 0 | 0 | 0 | 0 | 0.57721 | 0.57721 | 0 | 0 | 0 | 74.137 | 594.9872 | 0 | 0.05921 | 3.7799 | 0 | 0 | 0 | 0 | off_peak | 594.41 | 0 | 100 | 0 | 0 | 100 | 0 | 0
414 | 682.07 | 0 | 21.4 | 0 | 0 | 0 | 0 | 0.037279 | 0.037279 | 0 | 0 | 0 | 74.1718 | 682.1073 | 0 | 0.05921 | 3.355 | 0 | 0 | 0 | 0 | off_peak | 682.07 | 0 | 100 | 0 | 0 | 100 | 0 | 0
415 | 806.66 | 0 | 21.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1718 | 806.66 | 0 | 0.088511 | 2.7662 | 0 | 0 | 0 | 0 | on_peak | 806.66 |  |  | 0 | 0 | 100 | 0 | 0
416 | 808.26 | 37.5822 | 21.6 | 6.1628 | 6.1628 | 0 | 0 | 0 | 0 | 62.443 | 62.443 | 0 | 7.4174 | 739.6541 | 0 | 0.088511 | 2.576 | 0 | 0 | 0 | 6.1628 | on_peak | 739.6541 |  |  | 0.76 | 7.73 | 91.51 | 15.8755 | 0
417 | 822.59 | 224.836 | 22.2 | 36.7906 | 36.7906 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 785.7994 | 0 | 0.088511 | 2.4922 | 0 | 0 | 0 | 36.7906 | on_peak | 785.7994 |  |  | 4.47 | 0 | 95.53 | 91.6882 | 0
418 | 804.33 | 413.99 | 22.8 | 67.5975 | 67.5975 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 736.7325 | 0 | 0.088511 | 2.4957 | 0 | 0 | 0 | 67.5975 | on_peak | 736.7325 |  |  | 8.4 | 0 | 91.6 | 168.704 | 0
419 | 773.18 | 568.43 | 23.3 | 92.6492 | 92.6492 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 18.9814 | 692.8932 | 0 | 0.05921 | 2.6496 | 0 | 0 | 0 | 92.6492 | off_peak | 680.5308 | 0 | 100 | 11.98 | 0 | 88.02 | 245.4795 | 0
420 | 769.75 | 486.59 | 23.6 | 79.2249 | 79.2249 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 30.5453 | 702.8875 | 0 | 0.05921 | 3.062 | 0 | 0 | 0 | 79.2249 | off_peak | 690.5251 | 0 | 100 | 10.29 | 0 | 89.71 | 242.5853 | 0
421 | 788.04 | 631.721 | 23.8 | 102.7809 | 102.7809 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 42.1093 | 697.6215 | 0 | 0.05921 | 3.85 | 0 | 0 | 0 | 102.7809 | off_peak | 685.2591 | 0 | 100 | 13.04 | 0 | 86.96 | 395.7114 | 0
422 | 845.46 | 518.669 | 24 | 84.3269 | 84.3269 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 53.6732 | 773.4955 | 0 | 0.05921 | 4.2645 | 0 | 0 | 0 | 84.3269 | off_peak | 761.1331 | 0 | 100 | 9.97 | 0 | 90.03 | 359.615 | 0
423 | 820.64 | 361.646 | 24.1 | 58.7765 | 58.7765 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 65.2371 | 774.2259 | 0 | 0.05921 | 4.0172 | 0 | 0 | 0 | 58.7765 | off_peak | 761.8635 | 0 | 100 | 7.16 | 0 | 92.84 | 236.1187 | 0
424 | 835.52 | 261.252 | 24 | 42.4752 | 42.4752 | 0 | 0 | 8.9371 | 8.9371 | 0 | 0 | 0 | 73.597 | 801.9819 | 0 | 0.05921 | 3.5124 | 0 | 0 | 0 | 42.4752 | off_peak | 793.0448 | 0 | 100 | 5.08 | 0 | 94.92 | 149.1901 | 0
425 | 803.26 | 154.659 | 23.5 | 25.1901 | 25.1901 | 0 | 0 | 0.57721 | 0.57721 | 0 | 0 | 0 | 74.137 | 778.6472 | 0 | 0.05921 | 3.2077 | 0 | 0 | 0 | 25.1901 | off_peak | 778.0699 | 0 | 100 | 3.14 | 0 | 96.86 | 80.8033 | 0
426 | 837.8 | 31.1809 | 22.7 | 5.0931 | 5.0931 | 0 | 0 | 0.037279 | 0.037279 | 0 | 0 | 0 | 74.1718 | 832.7441 | 0 | 0.05921 | 3.1034 | 0 | 0 | 0 | 5.0931 | off_peak | 832.7069 | 0 | 100 | 0.61 | 0 | 99.39 | 15.8058 | 0
427 | 791.06 | 0 | 22.4 | 0 | 0 | 0 | 0 | 0 | 0 | 62.443 | 62.443 | 0 | 7.4174 | 728.617 | 0 | 0.088511 | 3.1216 | 0 | 0 | 0 | 0 | on_peak | 728.617 |  |  | 0 | 7.89 | 92.11 | 0 | 0
428 | 773.77 | 0 | 21.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 773.77 | 0 | 0.088511 | 3.2448 | 0 | 0 | 0 | 0 | on_peak | 773.77 |  |  | 0 | 0 | 100 | 0 | 0
429 | 763.19 | 0 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 763.19 | 0 | 0.088511 | 3.436 | 0 | 0 | 0 | 0 | on_peak | 763.19 |  |  | 0 | 0 | 100 | 0 | 0
430 | 714.1 | 0 | 20.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 714.1 | 0 | 0.088511 | 3.7611 | 0 | 0 | 0 | 0 | on_peak | 714.1 |  |  | 0 | 0 | 100 | 0 | 0
431 | 713.9 | 0 | 20 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 18.9814 | 726.2624 | 0 | 0.05921 | 4.1629 | 0 | 0 | 0 | 0 | off_peak | 713.9 | 0 | 100 | 0 | 0 | 100 | 0 | 0
432 | 757.41 | 0 | 19.5 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 30.5453 | 769.7724 | 0 | 0.05921 | 4.6517 | 0 | 0 | 0 | 0 | off_peak | 757.41 | 0 | 100 | 0 | 0 | 100 | 0 | 0
433 | 697.95 | 0 | 19.1 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 42.1093 | 710.3124 | 0 | 0.05921 | 5.0038 | 0 | 0 | 0 | 0 | off_peak | 697.95 | 0 | 100 | 0 | 0 | 100 | 0 | 0
434 | 623.26 | 0 | 18.6 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 53.6732 | 635.6224 | 0 | 0.05921 | 4.8857 | 0 | 0 | 0 | 0 | off_peak | 623.26 | 0 | 100 | 0 | 0 | 100 | 0 | 0
435 | 571.64 | 0 | 18.2 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 65.2371 | 584.0024 | 0 | 0.05921 | 4.5895 | 0 | 0 | 0 | 0 | off_peak | 571.64 | 0 | 100 | 0 | 0 | 100 | 0 | 0
436 | 559.23 | 0 | 17.7 | 0 | 0 | 0 | 0 | 8.9371 | 8.9371 | 0 | 0 | 0 | 73.597 | 568.1671 | 0 | 0.05921 | 4.2 | 0 | 0 | 0 | 0 | off_peak | 559.23 | 0 | 100 | 0 | 0 | 100 | 0 | 0
437 | 561.92 | 0 | 17.3 | 0 | 0 | 0 | 0 | 0.57721 | 0.57721 | 0 | 0 | 0 | 74.137 | 562.4972 | 0 | 0.05921 | 3.7272 | 0 | 0 | 0 | 0 | off_peak | 561.92 | 0 | 100 | 0 | 0 | 100 | 0 | 0
438 | 684.3 | 0 | 17.1 | 0 | 0 | 0 | 0 | 0.037279 | 0.037279 | 0 | 0 | 0 | 74.1718 | 684.3373 | 0 | 0.05921 | 3.2194 | 0 | 0 | 0 | 0 | off_peak | 684.3 | 0 | 100 | 0 | 0 | 100 | 0 | 0
439 | 706.06 | 0 | 17.1 | 0 | 0 | 0 | 0 | 0 | 0 | 62.443 | 62.443 | 0 | 7.4174 | 643.617 | 0 | 0.088511 | 2.7714 | 0 | 0 | 0 | 0 | on_peak | 643.617 |  |  | 0 | 8.84 | 91.16 | 0 | 0
440 | 775.99 | 33.9932 | 17.6 | 5.6536 | 5.6536 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 770.3364 | 0 | 0.088511 | 2.5123 | 0 | 0 | 0 | 5.6536 | on_peak | 770.3364 |  |  | 0.73 | 0 | 99.27 | 14.2037 | 0
441 | 791.87 | 214.823 | 18.6 | 35.6031 | 35.6031 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 756.2669 | 0 | 0.088511 | 2.3733 | 0 | 0 | 0 | 35.6031 | on_peak | 756.2669 |  |  | 4.5 | 0 | 95.5 | 84.4986 | 0
442 | 795.86 | 402.273 | 19.5 | 66.4586 | 66.4586 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 729.4014 | 0 | 0.088511 | 2.3192 | 0 | 0 | 0 | 66.4586 | on_peak | 729.4014 |  |  | 8.35 | 0 | 91.65 | 154.1306 | 0
443 | 773.91 | 555.011 | 20.4 | 91.4007 | 91.4007 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 18.9814 | 694.8717 | 0 | 0.05921 | 2.3578 | 0 | 0 | 0 | 91.4007 | off_peak | 682.5093 | 0 | 100 | 11.81 | 0 | 88.19 | 215.5052 | 0
444 | 875.88 | 653.653 | 21.2 | 107.3404 | 107.3404 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 30.5453 | 780.902 | 0 | 0.05921 | 2.7124 | 0 | 0 | 0 | 107.3404 | off_peak | 768.5396 | 0 | 100 | 12.26 | 0 | 87.74 | 291.1467 | 0
445 | 817.75 | 689.946 | 21.7 | 113.0991 | 113.0991 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 42.1093 | 717.0133 | 0 | 0.05921 | 3.3541 | 0 | 0 | 0 | 113.0991 | off_peak | 704.6509 | 0 | 100 | 13.83 | 0 | 86.17 | 379.3456 | 0
446 | 833.89 | 663.098 | 22.1 | 108.5434 | 108.5434 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 53.6732 | 737.709 | 0 | 0.05921 | 3.7257 | 0 | 0 | 0 | 108.5434 | off_peak | 725.3466 | 0 | 100 | 13.02 | 0 | 86.98 | 404.3961 | 0
447 | 864.96 | 425.434 | 22.3 | 69.5902 | 69.5902 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 65.2371 | 807.7322 | 0 | 0.05921 | 3.6098 | 0 | 0 | 0 | 69.5902 | off_peak | 795.3698 | 0 | 100 | 8.05 | 0 | 91.95 | 251.2047 | 0
448 | 818.4 | 418.077 | 22.2 | 68.4112 | 68.4112 | 0 | 0 | 8.9371 | 8.9371 | 0 | 0 | 0 | 73.597 | 758.9259 | 0 | 0.05921 | 3.3897 | 0 | 0 | 0 | 68.4112 | off_peak | 749.9888 | 0 | 100 | 8.36 | 0 | 91.64 | 231.891 | 0
449 | 822.73 | 230.666 | 21.7 | 37.8118 | 37.8118 | 0 | 0 | 0.57721 | 0.57721 | 0 | 0 | 0 | 74.137 | 785.4954 | 0 | 0.05921 | 3.2906 | 0 | 0 | 0 | 37.8118 | off_peak | 784.9182 | 0 | 100 | 4.6 | 0 | 95.4 | 124.4224 | 0
450 | 812.72 | 46.5514 | 21.2 | 7.6445 | 7.6445 | 0 | 0 | 0.037279 | 0.037279 | 0 | 0 | 0 | 74.1718 | 805.1128 | 0 | 0.05921 | 3.3243 | 0 | 0 | 0 | 7.6445 | off_peak | 805.0755 | 0 | 100 | 0.94 | 0 | 99.06 | 25.4125 | 0
451 | 799.45 | 0 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 40.9922 | 40.9922 | 0 | 30.3494 | 758.4578 | 0 | 0.088511 | 3.5372 | 0 | 0 | 0 | 0 | on_peak | 758.4578 |  |  | 0 | 5.13 | 94.87 | 0 | 0
452 | 845.04 | 0 | 20.9 | 0 | 0 | 0 | 0 | 0 | 0 | 21.4509 | 21.4509 | 0 | 7.4174 | 823.5891 | 0 | 0.088511 | 3.8695 | 0 | 0 | 0 | 0 | on_peak | 823.5891 |  |  | 0 | 2.54 | 97.46 | 0 | 0
453 | 813.7 | 0 | 20.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 813.7 | 0 | 0.088511 | 4.3749 | 0 | 0 | 0 | 0 | on_peak | 813.7 |  |  | 0 | 0 | 100 | 0 | 0
454 | 753.93 | 0 | 20.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 753.93 | 0 | 0.088511 | 4.7001 | 0 | 0 | 0 | 0 | on_peak | 753.93 |  |  | 0 | 0 | 100 | 0 | 0
455 | 832.1 | 0 | 20.8 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 18.9814 | 844.4624 | 0 | 0.05921 | 5.0309 | 0 | 0 | 0 | 0 | off_peak | 832.1 | 0 | 100 | 0 | 0 | 100 | 0 | 0
456 | 747.77 | 0 | 20.7 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 30.5453 | 760.1324 | 0 | 0.05921 | 5.2812 | 0 | 0 | 0 | 0 | off_peak | 747.77 | 0 | 100 | 0 | 0 | 100 | 0 | 0
457 | 712.83 | 0 | 20.7 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 42.1093 | 725.1924 | 0 | 0.05921 | 5.4514 | 0 | 0 | 0 | 0 | off_peak | 712.83 | 0 | 100 | 0 | 0 | 100 | 0 | 0
458 | 646.22 | 0 | 20.7 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 53.6732 | 658.5824 | 0 | 0.05921 | 5.3439 | 0 | 0 | 0 | 0 | off_peak | 646.22 | 0 | 100 | 0 | 0 | 100 | 0 | 0
459 | 571.03 | 0 | 20.7 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 65.2371 | 583.3924 | 0 | 0.05921 | 5.0187 | 0 | 0 | 0 | 0 | off_peak | 571.03 | 0 | 100 | 0 | 0 | 100 | 0 | 0
460 | 585.33 | 0 | 20.7 | 0 | 0 | 0 | 0 | 8.9371 | 8.9371 | 0 | 0 | 0 | 73.597 | 594.2671 | 0 | 0.05921 | 4.6466 | 0 | 0 | 0 | 0 | off_peak | 585.33 | 0 | 100 | 0 | 0 | 100 | 0 | 0
461 | 587.41 | 0 | 20.7 | 0 | 0 | 0 | 0 | 0.57721 | 0.57721 | 0 | 0 | 0 | 74.137 | 587.9872 | 0 | 0.05921 | 4.1662 | 0 | 0 | 0 | 0 | off_peak | 587.41 | 0 | 100 | 0 | 0 | 100 | 0 | 0
462 | 704.7 | 0 | 20.8 | 0 | 0 | 0 | 0 | 0.037279 | 0.037279 | 0 | 0 | 0 | 74.1718 | 704.7373 | 0 | 0.05921 | 3.6547 | 0 | 0 | 0 | 0 | off_peak | 704.7 | 0 | 100 | 0 | 0 | 100 | 0 | 0
463 | 770.92 | 0 | 20.9 | 0 | 0 | 0 | 0 | 0 | 0 | 62.443 | 62.443 | 0 | 7.4174 | 708.477 | 0 | 0.088511 | 3.0622 | 0 | 0 | 0 | 0 | on_peak | 708.477 |  |  | 0 | 8.1 | 91.9 | 0 | 0
464 | 807.22 | 27.431 | 21.4 | 4.5014 | 4.5014 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 802.7186 | 0 | 0.088511 | 2.6624 | 0 | 0 | 0 | 4.5014 | on_peak | 802.7186 |  |  | 0.56 | 0 | 99.44 | 11.9844 | 0
465 | 776.44 | 172.436 | 22 | 28.2363 | 28.2363 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 748.2037 | 0 | 0.088511 | 2.5018 | 0 | 0 | 0 | 28.2363 | on_peak | 748.2037 |  |  | 3.64 | 0 | 96.36 | 70.6425 | 0
466 | 822.45 | 410.637 | 22.4 | 67.1459 | 67.1459 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 755.3041 | 0 | 0.088511 | 2.42 | 0 | 0 | 0 | 67.1459 | on_peak | 755.3041 |  |  | 8.16 | 0 | 91.84 | 162.4904 | 0
467 | 793.54 | 563.153 | 22.7 | 91.9862 | 91.9862 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 18.9814 | 713.9162 | 0 | 0.05921 | 2.4599 | 0 | 0 | 0 | 91.9862 | off_peak | 701.5538 | 0 | 100 | 11.59 | 0 | 88.41 | 226.273 | 0
468 | 848.52 | 527.379 | 22.8 | 86.112 | 86.112 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 30.5453 | 774.7703 | 0 | 0.05921 | 2.734 | 0 | 0 | 0 | 86.112 | off_peak | 762.408 | 0 | 100 | 10.15 | 0 | 89.85 | 235.4335 | 0
469 | 826.33 | 693.845 | 22.9 | 113.2527 | 113.2527 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 42.1093 | 725.4397 | 0 | 0.05921 | 3.3165 | 0 | 0 | 0 | 113.2527 | off_peak | 713.0773 | 0 | 100 | 13.71 | 0 | 86.29 | 375.5991 | 0
470 | 891.83 | 661.463 | 22.8 | 108.0057 | 108.0057 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 53.6732 | 796.1867 | 0 | 0.05921 | 3.7053 | 0 | 0 | 0 | 108.0057 | off_peak | 783.8243 | 0 | 100 | 12.11 | 0 | 87.89 | 400.1918 | 0
471 | 869.43 | 378.861 | 22.8 | 61.8616 | 61.8616 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 65.2371 | 819.9308 | 0 | 0.05921 | 3.7776 | 0 | 0 | 0 | 61.8616 | off_peak | 807.5684 | 0 | 100 | 7.12 | 0 | 92.88 | 233.6903 | 0
472 | 863.55 | 161.417 | 22.7 | 26.3661 | 26.3661 | 0 | 0 | 8.9371 | 8.9371 | 0 | 0 | 0 | 73.597 | 846.121 | 0 | 0.05921 | 3.7977 | 0 | 0 | 0 | 26.3661 | off_peak | 837.1839 | 0 | 100 | 3.05 | 0 | 96.95 | 100.1311 | 0
473 | 852.99 | 185.124 | 22.3 | 30.2816 | 30.2816 | 0 | 0 | 0.57721 | 0.57721 | 0 | 0 | 0 | 74.137 | 823.2856 | 0 | 0.05921 | 3.8821 | 0 | 0 | 0 | 30.2816 | off_peak | 822.7084 | 0 | 100 | 3.55 | 0 | 96.45 | 117.557 | 0
474 | 847.33 | 46.3127 | 22 | 7.5837 | 7.5837 | 0 | 0 | 0.037279 | 0.037279 | 0 | 0 | 0 | 74.1718 | 839.7836 | 0 | 0.05921 | 3.8969 | 0 | 0 | 0 | 7.5837 | off_peak | 839.7463 | 0 | 100 | 0.9 | 0 | 99.1 | 29.5526 | 0
475 | 795.02 | 0 | 21.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1718 | 795.02 | 0 | 0.088511 | 4.1488 | 0 | 0 | 0 | 0 | on_peak | 795.02 |  |  | 0 | 0 | 100 | 0 | 0
476 | 766.07 | 0 | 21.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1718 | 766.07 | 0 | 0.088511 | 4.2491 | 0 | 0 | 0 | 0 | on_peak | 766.07 |  |  | 0 | 0 | 100 | 0 | 0
477 | 772.07 | 0 | 21.9 | 0 | 0 | 0 | 0 | 0 | 0 | 62.443 | 62.443 | 0 | 7.4174 | 709.627 | 0 | 0.088511 | 4.385 | 0 | 0 | 0 | 0 | on_peak | 709.627 |  |  | 0 | 8.09 | 91.91 | 0 | 0
478 | 756.99 | 0 | 21.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 756.99 | 0 | 0.088511 | 4.639 | 0 | 0 | 0 | 0 | on_peak | 756.99 |  |  | 0 | 0 | 100 | 0 | 0
479 | 768.71 | 0 | 21.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 768.71 | 0 | 0.05921 | 5.0226 | 0 | 0 | 0 | 0 | off_peak | 768.71 |  |  | 0 | 0 | 100 | 0 | 0
480 | 752.87 | 0 | 21.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 752.87 | 0 | 0.05921 | 5.2759 | 0 | 0 | 0 | 0 | off_peak | 752.87 |  |  | 0 | 0 | 100 | 0 | 0
481 | 673.18 | 0 | 21.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 673.18 | 0 | 0.05921 | 5.4388 | 0 | 0 | 0 | 0 | off_peak | 673.18 |  |  | 0 | 0 | 100 | 0 | 0
482 | 645.34 | 0 | 21.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 645.34 | 0 | 0.05921 | 5.155 | 0 | 0 | 0 | 0 | off_peak | 645.34 |  |  | 0 | 0 | 100 | 0 | 0
483 | 596.95 | 0 | 21.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 596.95 | 0 | 0.05921 | 4.8314 | 0 | 0 | 0 | 0 | off_peak | 596.95 |  |  | 0 | 0 | 100 | 0 | 0
484 | 558.91 | 0 | 21.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 558.91 | 0 | 0.05921 | 4.461 | 0 | 0 | 0 | 0 | off_peak | 558.91 |  |  | 0 | 0 | 100 | 0 | 0
485 | 601.37 | 0 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 601.37 | 0 | 0.05921 | 4.1179 | 0 | 0 | 0 | 0 | off_peak | 601.37 |  |  | 0 | 0 | 100 | 0 | 0
486 | 706.9 | 0 | 21.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 706.9 | 0 | 0.05921 | 3.7248 | 0 | 0 | 0 | 0 | off_peak | 706.9 |  |  | 0 | 0 | 100 | 0 | 0
487 | 722.34 | 0 | 21.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 722.34 | 0 | 0.05921 | 3.23 | 0 | 0 | 0 | 0 | off_peak | 722.34 |  |  | 0 | 0 | 100 | 0 | 0
488 | 736.57 | 33.6792 | 21.9 | 5.5169 | 5.5169 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 731.0531 | 0 | 0.05921 | 2.9044 | 0 | 0 | 0 | 5.5169 | off_peak | 731.0531 |  |  | 0.75 | 0 | 99.25 | 16.0232 | 0
489 | 676.94 | 212.231 | 22.6 | 34.6785 | 34.6785 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 642.2615 | 0 | 0.05921 | 2.706 | 0 | 0 | 0 | 34.6785 | off_peak | 642.2615 |  |  | 5.12 | 0 | 94.88 | 93.8397 | 0
490 | 714.87 | 399.536 | 23.4 | 65.0976 | 65.0976 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 649.7724 | 0 | 0.05921 | 2.5847 | 0 | 0 | 0 | 65.0976 | off_peak | 649.7724 |  |  | 9.11 | 0 | 90.89 | 168.2562 | 0
491 | 728.84 | 551.659 | 24.1 | 89.6583 | 89.6583 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 639.1817 | 0 | 0.05921 | 2.546 | 0 | 0 | 0 | 89.6583 | off_peak | 639.1817 |  |  | 12.3 | 0 | 87.7 | 228.2687 | 0
492 | 764.43 | 489.283 | 24.6 | 79.378 | 79.378 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 685.052 | 0 | 0.05921 | 2.6887 | 0 | 0 | 0 | 79.378 | off_peak | 685.052 |  |  | 10.38 | 0 | 89.62 | 213.42 | 0
493 | 748.63 | 522.396 | 24.9 | 84.6586 | 84.6586 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 663.9714 | 0 | 0.05921 | 2.9122 | 0 | 0 | 0 | 84.6586 | off_peak | 663.9714 |  |  | 11.31 | 0 | 88.69 | 246.5403 | 0
494 | 683.93 | 405.907 | 25.1 | 65.7333 | 65.7333 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 618.1967 | 0 | 0.05921 | 3.2323 | 0 | 0 | 0 | 65.7333 | off_peak | 618.1967 |  |  | 9.61 | 0 | 90.39 | 212.4699 | 0
495 | 688.7 | 566.017 | 25.1 | 91.6617 | 91.6617 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 597.0383 | 0 | 0.05921 | 3.6504 | 0 | 0 | 0 | 91.6617 | off_peak | 597.0383 |  |  | 13.31 | 0 | 86.69 | 334.6064 | 0
496 | 680.18 | 418.48 | 24.9 | 67.8182 | 67.8182 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 612.3618 | 0 | 0.05921 | 3.9908 | 0 | 0 | 0 | 67.8182 | off_peak | 612.3618 |  |  | 9.97 | 0 | 90.03 | 270.6501 | 0
497 | 653.49 | 233.788 | 24.4 | 37.9555 | 37.9555 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 615.5345 | 0 | 0.05921 | 4.1916 | 0 | 0 | 0 | 37.9555 | off_peak | 615.5345 |  |  | 5.81 | 0 | 94.19 | 159.0937 | 0
498 | 670.86 | 50.3805 | 23.7 | 8.1998 | 8.1998 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 662.6602 | 0 | 0.05921 | 4.2983 | 0 | 0 | 0 | 8.1998 | off_peak | 662.6602 |  |  | 1.22 | 0 | 98.78 | 35.2451 | 0
499 | 654.67 | 0 | 23.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 654.67 | 0 | 0.05921 | 4.5463 | 0 | 0 | 0 | 0 | off_peak | 654.67 |  |  | 0 | 0 | 100 | 0 | 0
500 | 638.11 | 0 | 23.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 638.11 | 0 | 0.05921 | 4.8164 | 0 | 0 | 0 | 0 | off_peak | 638.11 |  |  | 0 | 0 | 100 | 0 | 0
501 | 647.83 | 0 | 23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 647.83 | 0 | 0.05921 | 5.0705 | 0 | 0 | 0 | 0 | off_peak | 647.83 |  |  | 0 | 0 | 100 | 0 | 0
502 | 568.07 | 0 | 22.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 568.07 | 0 | 0.05921 | 5.2705 | 0 | 0 | 0 | 0 | off_peak | 568.07 |  |  | 0 | 0 | 100 | 0 | 0
503 | 574.38 | 0 | 22.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 574.38 | 0 | 0.05921 | 5.3273 | 0 | 0 | 0 | 0 | off_peak | 574.38 |  |  | 0 | 0 | 100 | 0 | 0
504 | 519.33 | 0 | 22.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 519.33 | 0 | 0.05921 | 5.2583 | 0 | 0 | 0 | 0 | off_peak | 519.33 |  |  | 0 | 0 | 100 | 0 | 0
505 | 567.77 | 0 | 22.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 567.77 | 0 | 0.05921 | 5.3194 | 0 | 0 | 0 | 0 | off_peak | 567.77 |  |  | 0 | 0 | 100 | 0 | 0
506 | 536.42 | 0 | 22.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 536.42 | 0 | 0.05921 | 5.1121 | 0 | 0 | 0 | 0 | off_peak | 536.42 |  |  | 0 | 0 | 100 | 0 | 0
507 | 535.86 | 0 | 22.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 535.86 | 0 | 0.05921 | 4.791 | 0 | 0 | 0 | 0 | off_peak | 535.86 |  |  | 0 | 0 | 100 | 0 | 0
508 | 555.97 | 0 | 22.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 555.97 | 0 | 0.05921 | 4.4048 | 0 | 0 | 0 | 0 | off_peak | 555.97 |  |  | 0 | 0 | 100 | 0 | 0
509 | 563.82 | 0 | 22.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 563.82 | 0 | 0.05921 | 4.0545 | 0 | 0 | 0 | 0 | off_peak | 563.82 |  |  | 0 | 0 | 100 | 0 | 0
510 | 624.34 | 0 | 22.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 624.34 | 0 | 0.05921 | 3.7269 | 0 | 0 | 0 | 0 | off_peak | 624.34 |  |  | 0 | 0 | 100 | 0 | 0
511 | 715.2 | 0 | 22.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 715.2 | 0 | 0.05921 | 3.3351 | 0 | 0 | 0 | 0 | off_peak | 715.2 |  |  | 0 | 0 | 100 | 0 | 0
512 | 673.51 | 33.285 | 23.1 | 5.4291 | 5.4291 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 668.0809 | 0 | 0.05921 | 2.9645 | 0 | 0 | 0 | 5.4291 | off_peak | 668.0809 |  |  | 0.81 | 0 | 99.19 | 16.0943 | 0
513 | 668.22 | 208.824 | 23.9 | 33.9635 | 33.9635 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 634.2565 | 0 | 0.05921 | 2.7476 | 0 | 0 | 0 | 33.9635 | off_peak | 634.2565 |  |  | 5.08 | 0 | 94.92 | 93.3187 | 0
514 | 672.57 | 392.988 | 24.3 | 63.8245 | 63.8245 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 608.7455 | 0 | 0.05921 | 2.6296 | 0 | 0 | 0 | 63.8245 | off_peak | 608.7455 |  |  | 9.49 | 0 | 90.51 | 167.8352 | 0
515 | 660.43 | 542.807 | 24.7 | 88.0297 | 88.0297 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 572.4003 | 0 | 0.05921 | 2.5947 | 0 | 0 | 0 | 88.0297 | off_peak | 572.4003 |  |  | 13.33 | 0 | 86.67 | 228.4118 | 0
516 | 669.59 | 260.312 | 24.9 | 42.1857 | 42.1857 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 627.4043 | 0 | 0.05921 | 2.6517 | 0 | 0 | 0 | 42.1857 | off_peak | 627.4043 |  |  | 6.3 | 0 | 93.7 | 111.8632 | 0
517 | 623.91 | 420.037 | 25 | 68.046 | 68.046 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 555.864 | 0 | 0.05921 | 2.8479 | 0 | 0 | 0 | 68.046 | off_peak | 555.864 |  |  | 10.91 | 0 | 89.09 | 193.786 | 0
518 | 658.82 | 338.548 | 24.9 | 54.8645 | 54.8645 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 603.9555 | 0 | 0.05921 | 3.1358 | 0 | 0 | 0 | 54.8645 | off_peak | 603.9555 |  |  | 8.33 | 0 | 91.67 | 172.0463 | 0
519 | 657.28 | 561.18 | 24.6 | 91.0421 | 91.0421 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 566.2379 | 0 | 0.05921 | 3.542 | 0 | 0 | 0 | 91.0421 | off_peak | 566.2379 |  |  | 13.85 | 0 | 86.15 | 322.4704 | 0
520 | 624.03 | 413.65 | 24.3 | 67.1802 | 67.1802 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 556.8498 | 0 | 0.05921 | 3.9365 | 0 | 0 | 0 | 67.1802 | off_peak | 556.8498 |  |  | 10.77 | 0 | 89.23 | 264.4523 | 0
521 | 601.96 | 228.506 | 23.8 | 37.1779 | 37.1779 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 564.7821 | 0 | 0.05921 | 4.1587 | 0 | 0 | 0 | 37.1779 | off_peak | 564.7821 |  |  | 6.18 | 0 | 93.82 | 154.6115 | 0
522 | 615.1 | 47.701 | 23.4 | 7.7721 | 7.7721 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 607.3279 | 0 | 0.05921 | 4.425 | 0 | 0 | 0 | 7.7721 | off_peak | 607.3279 |  |  | 1.26 | 0 | 98.74 | 34.3913 | 0
523 | 567.04 | 0 | 23.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 567.04 | 0 | 0.05921 | 4.6585 | 0 | 0 | 0 | 0 | off_peak | 567.04 |  |  | 0 | 0 | 100 | 0 | 0
524 | 612.7 | 0 | 23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 612.7 | 0 | 0.05921 | 4.8911 | 0 | 0 | 0 | 0 | off_peak | 612.7 |  |  | 0 | 0 | 100 | 0 | 0
525 | 571.54 | 0 | 22.9 | 0 | 0 | 0 | 0 | 8.7006 | 8.7006 | 0 | 0 | 0 | 15.5561 | 580.2406 | 0 | 0.05921 | 5.0096 | 0 | 0 | 0 | 0 | off_peak | 571.54 | 0 | 100 | 0 | 0 | 100 | 0 | 0
526 | 601.66 | 0 | 22.8 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 27.12 | 614.0224 | 0 | 0.05921 | 5.2319 | 0 | 0 | 0 | 0 | off_peak | 601.66 | 0 | 100 | 0 | 0 | 100 | 0 | 0
527 | 545.01 | 0 | 22.7 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 38.684 | 557.3724 | 0 | 0.05921 | 5.4259 | 0 | 0 | 0 | 0 | off_peak | 545.01 | 0 | 100 | 0 | 0 | 100 | 0 | 0
528 | 538.46 | 0 | 22.6 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 50.2479 | 550.8224 | 0 | 0.05921 | 5.6984 | 0 | 0 | 0 | 0 | off_peak | 538.46 | 0 | 100 | 0 | 0 | 100 | 0 | 0
529 | 494.26 | 0 | 22.5 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 61.8119 | 506.6224 | 0 | 0.05921 | 5.7551 | 0 | 0 | 0 | 0 | off_peak | 494.26 | 0 | 100 | 0 | 0 | 100 | 0 | 0
530 | 479.95 | 0 | 22.4 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 73.3758 | 492.3124 | 0 | 0.05921 | 5.5712 | 0 | 0 | 0 | 0 | off_peak | 479.95 | 0 | 100 | 0 | 0 | 100 | 0 | 0
531 | 535.86 | 0 | 22.3 | 0 | 0 | 0 | 0 | 0.79843 | 0.79843 | 0 | 0 | 0 | 74.1227 | 536.6584 | 0 | 0.05921 | 5.2204 | 0 | 0 | 0 | 0 | off_peak | 535.86 | 0 | 100 | 0 | 0 | 100 | 0 | 0
532 | 504.7 | 0 | 22.2 | 0 | 0 | 0 | 0 | 0.051567 | 0.051567 | 0 | 0 | 0 | 74.1709 | 504.7516 | 0 | 0.05921 | 4.8216 | 0 | 0 | 0 | 0 | off_peak | 504.7 | 0 | 100 | 0 | 0 | 100 | 0 | 0
533 | 527.08 | 0 | 22.1 | 0 | 0 | 0 | 0 | 0.0033305 | 0.0033305 | 0 | 0 | 0 | 74.174 | 527.0833 | 0 | 0.05921 | 4.3589 | 0 | 0 | 0 | 0 | off_peak | 527.08 | 0 | 100 | 0 | 0 | 100 | 0 | 0
534 | 661.96 | 0 | 22.1 | 0 | 0 | 0 | 0 | 0.0002151 | 0.0002151 | 0 | 0 | 0 | 74.1742 | 661.9602 | 0 | 0.05921 | 3.7793 | 0 | 0 | 0 | 0 | off_peak | 661.96 | 0 | 100 | 0 | 0 | 100 | 0 | 0
535 | 733.26 | 0 | 22.3 | 0 | 0 | 0 | 0 | 0 | 0 | 62.4453 | 62.4453 | 0 | 7.4174 | 670.8147 | 0 | 0.088511 | 3.2505 | 0 | 0 | 0 | 0 | on_peak | 670.8147 |  |  | 0 | 8.52 | 91.48 | 0 | 0
536 | 803.54 | 20.8166 | 22.9 | 3.3978 | 3.3978 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 800.1422 | 0 | 0.088511 | 2.9349 | 0 | 0 | 0 | 3.3978 | on_peak | 800.1422 |  |  | 0.42 | 0 | 99.58 | 9.972 | 0
537 | 842.15 | 201.259 | 23.6 | 32.7683 | 32.7683 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 809.3817 | 0 | 0.088511 | 2.783 | 0 | 0 | 0 | 32.7683 | on_peak | 809.3817 |  |  | 3.89 | 0 | 96.11 | 91.1927 | 0
538 | 834.53 | 83.6 | 24 | 13.592 | 13.592 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 820.938 | 0 | 0.088511 | 2.7074 | 0 | 0 | 0 | 13.592 | on_peak | 820.938 |  |  | 1.63 | 0 | 98.37 | 36.7982 | 0
539 | 836.39 | 234.027 | 24.3 | 38.0079 | 38.0079 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 18.9814 | 810.7445 | 0 | 0.05921 | 2.7601 | 0 | 0 | 0 | 38.0079 | off_peak | 798.3821 | 0 | 100 | 4.54 | 0 | 95.46 | 104.907 | 0
540 | 808.24 | 330.779 | 24.5 | 53.6827 | 53.6827 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 30.5453 | 766.9197 | 0 | 0.05921 | 3.1499 | 0 | 0 | 0 | 53.6827 | off_peak | 754.5573 | 0 | 100 | 6.64 | 0 | 93.36 | 169.0954 | 0
541 | 804.67 | 682.141 | 24.4 | 110.7455 | 110.7455 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 42.1093 | 706.2868 | 0 | 0.05921 | 3.6802 | 0 | 0 | 0 | 110.7455 | off_peak | 693.9245 | 0 | 100 | 13.76 | 0 | 86.24 | 407.563 | 0
542 | 828.01 | 453.602 | 24.2 | 73.6952 | 73.6952 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 53.6732 | 766.6772 | 0 | 0.05921 | 4.0442 | 0 | 0 | 0 | 73.6952 | off_peak | 754.3148 | 0 | 100 | 8.9 | 0 | 91.1 | 298.036 | 0
543 | 842.81 | 561.265 | 24.1 | 91.2195 | 91.2195 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 65.2371 | 763.9528 | 0 | 0.05921 | 4.2792 | 0 | 0 | 0 | 91.2195 | off_peak | 751.5905 | 0 | 100 | 10.82 | 0 | 89.18 | 390.3485 | 0
544 | 833.87 | 287.611 | 24.1 | 46.7439 | 46.7439 | 0 | 0 | 8.9371 | 8.9371 | 0 | 0 | 0 | 73.597 | 796.0632 | 0 | 0.05921 | 4.3251 | 0 | 0 | 0 | 46.7439 | off_peak | 787.1261 | 0 | 100 | 5.61 | 0 | 94.39 | 202.1711 | 0
545 | 806.79 | 149.238 | 23.8 | 24.281 | 24.281 | 0 | 0 | 0.57721 | 0.57721 | 0 | 0 | 0 | 74.137 | 783.0862 | 0 | 0.05921 | 4.3614 | 0 | 0 | 0 | 24.281 | off_peak | 782.509 | 0 | 100 | 3.01 | 0 | 96.99 | 105.8984 | 0
546 | 814.35 | 50.1184 | 23.5 | 8.163 | 8.1257 | 0 | 0.037279 | 0.037279 | 0 | 0 | 0 | 0 | 74.1718 | 806.2243 | 0 | 0.05921 | 4.4974 | 0 | 0 | 0.034872 | 8.1257 | off_peak | 806.2243 | 100 | 0 | 1 | 0 | 99 | 36.5448 | 0
547 | 802.74 | 0 | 23.3 | 0 | 0 | 0 | 0 | 0 | 0 | 62.443 | 62.443 | 0 | 7.4174 | 740.297 | 0 | 0.088511 | 4.4271 | 0.032619 | 0 | 0 | 0.032619 | on_peak | 740.297 |  |  | 0 | 7.78 | 92.22 | 0.14441 | 0
548 | 787.24 | 0 | 23.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 787.24 | 0 | 0.088511 | 4.3725 | 0 | 0 | 0 | 0 | on_peak | 787.24 |  |  | 0 | 0 | 100 | 0 | 0
549 | 793.41 | 0 | 23.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 793.41 | 0 | 0.088511 | 4.3908 | 0 | 0 | 0 | 0 | on_peak | 793.41 |  |  | 0 | 0 | 100 | 0 | 0
550 | 721.55 | 0 | 23.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 721.55 | 0 | 0.088511 | 4.5128 | 0 | 0 | 0 | 0 | on_peak | 721.55 |  |  | 0 | 0 | 100 | 0 | 0
551 | 774.75 | 0 | 23.3 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 18.9814 | 787.1124 | 0 | 0.05921 | 4.8025 | 0 | 0 | 0 | 0 | off_peak | 774.75 | 0 | 100 | 0 | 0 | 100 | 0 | 0
552 | 752.31 | 0 | 23.4 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 30.5453 | 764.6724 | 0 | 0.05921 | 5.1003 | 0 | 0 | 0 | 0 | off_peak | 752.31 | 0 | 100 | 0 | 0 | 100 | 0 | 0
553 | 661.1 | 0 | 23.4 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 42.1093 | 673.4624 | 0 | 0.05921 | 5.4834 | 0 | 0 | 0 | 0 | off_peak | 661.1 | 0 | 100 | 0 | 0 | 100 | 0 | 0
554 | 631.79 | 0 | 23.5 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 53.6732 | 644.1524 | 0 | 0.05921 | 5.453 | 0 | 0 | 0 | 0 | off_peak | 631.79 | 0 | 100 | 0 | 0 | 100 | 0 | 0
555 | 550.74 | 0 | 23.5 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 65.2371 | 563.1024 | 0 | 0.05921 | 5.1419 | 0 | 0 | 0 | 0 | off_peak | 550.74 | 0 | 100 | 0 | 0 | 100 | 0 | 0
556 | 567.51 | 0 | 23.5 | 0 | 0 | 0 | 0 | 8.9371 | 8.9371 | 0 | 0 | 0 | 73.597 | 576.4471 | 0 | 0.05921 | 4.671 | 0 | 0 | 0 | 0 | off_peak | 567.51 | 0 | 100 | 0 | 0 | 100 | 0 | 0
557 | 587.18 | 0 | 23.5 | 0 | 0 | 0 | 0 | 0.57721 | 0.57721 | 0 | 0 | 0 | 74.137 | 587.7572 | 0 | 0.05921 | 4.2276 | 0 | 0 | 0 | 0 | off_peak | 587.18 | 0 | 100 | 0 | 0 | 100 | 0 | 0
558 | 666.89 | 0 | 23.6 | 0 | 0 | 0 | 0 | 0.037279 | 0.037279 | 0 | 0 | 0 | 74.1718 | 666.9273 | 0 | 0.05921 | 3.6415 | 0 | 0 | 0 | 0 | off_peak | 666.89 | 0 | 100 | 0 | 0 | 100 | 0 | 0
559 | 759.83 | 0 | 23.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1718 | 759.83 | 0 | 0.088511 | 3.3091 | 0 | 0 | 0 | 0 | on_peak | 759.83 |  |  | 0 | 0 | 100 | 0 | 0
560 | 758.76 | 40.917 | 23.9 | 6.6548 | 6.6548 | 0 | 0 | 0 | 0 | 62.443 | 62.443 | 0 | 7.4174 | 689.6622 | 0 | 0.088511 | 3.116 | 0 | 0 | 0 | 6.6548 | on_peak | 689.6622 |  |  | 0.88 | 8.23 | 90.89 | 20.736 | 0
561 | 759.64 | 234.158 | 24.2 | 38.0428 | 38.0428 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 721.5972 | 0 | 0.088511 | 3.0168 | 0 | 0 | 0 | 38.0428 | on_peak | 721.5972 |  |  | 5.01 | 0 | 94.99 | 114.7683 | 0
562 | 784.14 | 432.679 | 24.6 | 70.1949 | 70.1949 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 713.9451 | 0 | 0.088511 | 2.98 | 0 | 0 | 0 | 70.1949 | on_peak | 713.9451 |  |  | 8.95 | 0 | 91.05 | 209.1832 | 0
563 | 781.87 | 589.579 | 24.7 | 95.615 | 95.615 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 18.9814 | 698.6174 | 0 | 0.05921 | 3.0663 | 0 | 0 | 0 | 95.615 | off_peak | 686.255 | 0 | 100 | 12.23 | 0 | 87.77 | 293.1873 | 0
564 | 820.46 | 690.989 | 24.3 | 112.2223 | 112.2223 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 30.5453 | 720.6001 | 0 | 0.05921 | 3.4232 | 0 | 0 | 0 | 112.2223 | off_peak | 708.2377 | 0 | 100 | 13.68 | 0 | 86.32 | 384.1572 | 0
565 | 790.73 | 722.667 | 23.5 | 117.7042 | 117.7042 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 42.1093 | 685.3881 | 0 | 0.05921 | 4.1594 | 0 | 0 | 0 | 117.7042 | off_peak | 673.0258 | 0 | 100 | 14.89 | 0 | 85.11 | 489.5733 | 0
566 | 803.54 | 689.176 | 22.6 | 112.6111 | 112.6111 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 53.6732 | 703.2912 | 0 | 0.05921 | 4.4733 | 0 | 0 | 0 | 112.6111 | off_peak | 690.9289 | 0 | 100 | 14.01 | 0 | 85.99 | 503.7402 | 0
567 | 867.64 | 588.798 | 21.9 | 96.4498 | 96.4498 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 65.2371 | 783.5526 | 0 | 0.05921 | 4.3459 | 0 | 0 | 0 | 96.4498 | off_peak | 771.1902 | 0 | 100 | 11.12 | 0 | 88.88 | 419.1576 | 0
568 | 839.61 | 431.904 | 21.5 | 70.8501 | 70.8501 | 0 | 0 | 8.9371 | 8.9371 | 0 | 0 | 0 | 73.597 | 777.6971 | 0 | 0.05921 | 3.9733 | 0 | 0 | 0 | 70.8501 | off_peak | 768.7599 | 0 | 100 | 8.44 | 0 | 91.56 | 281.5112 | 0
569 | 829.13 | 239.803 | 21.2 | 39.3795 | 39.3795 | 0 | 0 | 0.57721 | 0.57721 | 0 | 0 | 0 | 74.137 | 790.3277 | 0 | 0.05921 | 3.6681 | 0 | 0 | 0 | 39.3795 | off_peak | 789.7505 | 0 | 100 | 4.75 | 0 | 95.25 | 144.4479 | 0
570 | 832.12 | 52.2428 | 20.8 | 8.5913 | 8.5913 | 0 | 0 | 0.037279 | 0.037279 | 0 | 0 | 0 | 74.1718 | 823.566 | 0 | 0.05921 | 3.5247 | 0 | 0 | 0 | 8.5913 | off_peak | 823.5287 | 0 | 100 | 1.03 | 0 | 98.97 | 30.2821 | 0
571 | 774.5 | 0 | 20.6 | 0 | 0 | 0 | 0 | 0 | 0 | 62.443 | 62.443 | 0 | 7.4174 | 712.057 | 0 | 0.088511 | 3.6078 | 0 | 0 | 0 | 0 | on_peak | 712.057 |  |  | 0 | 8.06 | 91.94 | 0 | 0
572 | 782.72 | 0 | 19.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 782.72 | 0 | 0.088511 | 3.7253 | 0 | 0 | 0 | 0 | on_peak | 782.72 |  |  | 0 | 0 | 100 | 0 | 0
573 | 779.41 | 0 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 779.41 | 0 | 0.088511 | 3.9635 | 0 | 0 | 0 | 0 | on_peak | 779.41 |  |  | 0 | 0 | 100 | 0 | 0
574 | 726.06 | 0 | 18.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 726.06 | 0 | 0.088511 | 4.2182 | 0 | 0 | 0 | 0 | on_peak | 726.06 |  |  | 0 | 0 | 100 | 0 | 0
575 | 770.23 | 0 | 17.3 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 18.9814 | 782.5924 | 0 | 0.05921 | 4.6331 | 0 | 0 | 0 | 0 | off_peak | 770.23 | 0 | 100 | 0 | 0 | 100 | 0 | 0
576 | 759.4 | 0 | 16.5 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 30.5453 | 771.7624 | 0 | 0.05921 | 5.0767 | 0 | 0 | 0 | 0 | off_peak | 759.4 | 0 | 100 | 0 | 0 | 100 | 0 | 0
577 | 712.7 | 0 | 15.9 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 42.1093 | 725.0624 | 0 | 0.05921 | 5.3998 | 0 | 0 | 0 | 0 | off_peak | 712.7 | 0 | 100 | 0 | 0 | 100 | 0 | 0
578 | 661.23 | 0 | 15.3 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 53.6732 | 673.5924 | 0 | 0.05921 | 5.3907 | 0 | 0 | 0 | 0 | off_peak | 661.23 | 0 | 100 | 0 | 0 | 100 | 0 | 0
579 | 565.69 | 0 | 14.9 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 65.2371 | 578.0524 | 0 | 0.05921 | 5.1099 | 0 | 0 | 0 | 0 | off_peak | 565.69 | 0 | 100 | 0 | 0 | 100 | 0 | 0
580 | 593.78 | 0 | 14.4 | 0 | 0 | 0 | 0 | 8.9371 | 8.9371 | 0 | 0 | 0 | 73.597 | 602.7171 | 0 | 0.05921 | 4.7086 | 0 | 0 | 0 | 0 | off_peak | 593.78 | 0 | 100 | 0 | 0 | 100 | 0 | 0
581 | 581.74 | 0 | 14 | 0 | 0 | 0 | 0 | 0.57721 | 0.57721 | 0 | 0 | 0 | 74.137 | 582.3172 | 0 | 0.05921 | 4.2593 | 0 | 0 | 0 | 0 | off_peak | 581.74 | 0 | 100 | 0 | 0 | 100 | 0 | 0
582 | 710.05 | 0 | 13.6 | 0 | 0 | 0 | 0 | 0.037279 | 0.037279 | 0 | 0 | 0 | 74.1718 | 710.0873 | 0 | 0.05921 | 3.7441 | 0 | 0 | 0 | 0 | off_peak | 710.05 | 0 | 100 | 0 | 0 | 100 | 0 | 0
583 | 794.34 | 0 | 13.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1718 | 794.34 | 0 | 0.088511 | 3.3127 | 0 | 0 | 0 | 0 | on_peak | 794.34 |  |  | 0 | 0 | 100 | 0 | 0
584 | 788.53 | 43.7419 | 13.7 | 7.3745 | 7.3745 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1718 | 781.1555 | 0 | 0.088511 | 3.0132 | 0 | 0 | 0 | 7.3745 | on_peak | 781.1555 |  |  | 0.94 | 0 | 99.06 | 22.221 | 0
585 | 793.05 | 240.725 | 14.3 | 40.4996 | 40.4996 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1718 | 752.5504 | 0 | 0.088511 | 2.8175 | 0 | 0 | 0 | 40.4996 | on_peak | 752.5504 |  |  | 5.11 | 0 | 94.89 | 114.1096 | 0
586 | 838.8 | 439.114 | 15.1 | 73.6718 | 73.6718 | 0 | 0 | 0 | 0 | 62.443 | 62.443 | 0 | 7.4174 | 702.6852 | 0 | 0.088511 | 2.757 | 0 | 0 | 0 | 73.6718 | on_peak | 702.6852 |  |  | 8.78 | 7.44 | 83.77 | 203.1156 | 0
587 | 805.24 | 597.452 | 16.1 | 99.8883 | 99.8883 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 18.9814 | 717.7141 | 0 | 0.05921 | 2.7693 | 0 | 0 | 0 | 99.8883 | off_peak | 705.3517 | 0 | 100 | 12.4 | 0 | 87.6 | 276.6165 | 0
588 | 864.71 | 702.232 | 17 | 117.0379 | 117.0379 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 30.5453 | 760.0345 | 0 | 0.05921 | 3.0776 | 0 | 0 | 0 | 117.0379 | off_peak | 747.6721 | 0 | 100 | 13.53 | 0 | 86.47 | 360.1947 | 0
589 | 854.39 | 740.417 | 17.7 | 123.0998 | 123.0998 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 42.1093 | 743.6526 | 0 | 0.05921 | 3.6344 | 0 | 0 | 0 | 123.0998 | off_peak | 731.2902 | 0 | 100 | 14.41 | 0 | 85.59 | 447.3963 | 0
590 | 857.77 | 708.128 | 18.2 | 117.525 | 117.525 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 53.6732 | 752.6074 | 0 | 0.05921 | 3.9819 | 0 | 0 | 0 | 117.525 | off_peak | 740.245 | 0 | 100 | 13.7 | 0 | 86.3 | 467.9723 | 0
591 | 910.36 | 612.316 | 18.5 | 101.5164 | 101.5164 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 65.2371 | 821.206 | 0 | 0.05921 | 4.0261 | 0 | 0 | 0 | 101.5164 | off_peak | 808.8436 | 0 | 100 | 11.15 | 0 | 88.85 | 408.7192 | 0
592 | 868.53 | 458.672 | 18.5 | 76.0436 | 76.0436 | 0 | 0 | 8.9371 | 8.9371 | 0 | 0 | 0 | 73.597 | 801.4235 | 0 | 0.05921 | 4.0629 | 0 | 0 | 0 | 76.0436 | off_peak | 792.4864 | 0 | 100 | 8.76 | 0 | 91.24 | 308.9581 | 0
593 | 897.16 | 264.387 | 18.3 | 43.8638 | 43.8638 | 0 | 0 | 0.57721 | 0.57721 | 0 | 0 | 0 | 74.137 | 853.8734 | 0 | 0.05921 | 4.2257 | 0 | 0 | 0 | 43.8638 | off_peak | 853.2962 | 0 | 100 | 4.89 | 0 | 95.11 | 185.3563 | 0
594 | 885.22 | 64.8251 | 18 | 10.7663 | 10.7663 | 0 | 0 | 0.037279 | 0.037279 | 0 | 0 | 0 | 74.1718 | 874.491 | 0 | 0.05921 | 4.4941 | 0 | 0 | 0 | 10.7663 | off_peak | 874.4537 | 0 | 100 | 1.22 | 0 | 98.78 | 48.3853 | 0
595 | 842.38 | 0 | 17.8 | 0 | 0 | 0 | 0 | 0 | 0 | 62.443 | 62.443 | 0 | 7.4174 | 779.937 | 0 | 0.088511 | 4.6785 | 0 | 0 | 0 | 0 | on_peak | 779.937 |  |  | 0 | 7.41 | 92.59 | 0 | 0
596 | 765.62 | 0 | 17.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 765.62 | 0 | 0.088511 | 4.8335 | 0 | 0 | 0 | 0 | on_peak | 765.62 |  |  | 0 | 0 | 100 | 0 | 0
597 | 795.78 | 0 | 17.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 795.78 | 0 | 0.088511 | 4.8934 | 0 | 0 | 0 | 0 | on_peak | 795.78 |  |  | 0 | 0 | 100 | 0 | 0
598 | 808.9 | 0 | 17.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 808.9 | 0 | 0.088511 | 5.1471 | 0 | 0 | 0 | 0 | on_peak | 808.9 |  |  | 0 | 0 | 100 | 0 | 0
599 | 789.96 | 0 | 17 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 18.9814 | 802.3224 | 0 | 0.05921 | 5.522 | 0 | 0 | 0 | 0 | off_peak | 789.96 | 0 | 100 | 0 | 0 | 100 | 0 | 0
600 | 803.59 | 0 | 16.7 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 30.5453 | 815.9524 | 0 | 0.05921 | 5.8344 | 0 | 0 | 0 | 0 | off_peak | 803.59 | 0 | 100 | 0 | 0 | 100 | 0 | 0
601 | 759.69 | 0 | 16.5 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 42.1093 | 772.0524 | 0 | 0.05921 | 5.9968 | 0 | 0 | 0 | 0 | off_peak | 759.69 | 0 | 100 | 0 | 0 | 100 | 0 | 0
602 | 667.86 | 0 | 16.4 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 53.6732 | 680.2224 | 0 | 0.05921 | 5.8994 | 0 | 0 | 0 | 0 | off_peak | 667.86 | 0 | 100 | 0 | 0 | 100 | 0 | 0
603 | 615.38 | 0 | 16.4 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 65.2371 | 627.7424 | 0 | 0.05921 | 5.5471 | 0 | 0 | 0 | 0 | off_peak | 615.38 | 0 | 100 | 0 | 0 | 100 | 0 | 0
604 | 604.84 | 0 | 16.7 | 0 | 0 | 0 | 0 | 8.9371 | 8.9371 | 0 | 0 | 0 | 73.597 | 613.7771 | 0 | 0.05921 | 5.0767 | 0 | 0 | 0 | 0 | off_peak | 604.84 | 0 | 100 | 0 | 0 | 100 | 0 | 0
605 | 620.76 | 0 | 17.3 | 0 | 0 | 0 | 0 | 0.57721 | 0.57721 | 0 | 0 | 0 | 74.137 | 621.3372 | 0 | 0.05921 | 4.5427 | 0 | 0 | 0 | 0 | off_peak | 620.76 | 0 | 100 | 0 | 0 | 100 | 0 | 0
606 | 746.73 | 0 | 18 | 0 | 0 | 0 | 0 | 0.037279 | 0.037279 | 0 | 0 | 0 | 74.1718 | 746.7673 | 0 | 0.05921 | 3.9777 | 0 | 0 | 0 | 0 | off_peak | 746.73 | 0 | 100 | 0 | 0 | 100 | 0 | 0
607 | 795.67 | 0 | 18.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1718 | 795.67 | 0 | 0.088511 | 3.4169 | 0 | 0 | 0 | 0 | on_peak | 795.67 |  |  | 0 | 0 | 100 | 0 | 0
608 | 858.89 | 40.7022 | 19.7 | 6.7196 | 6.7196 | 0 | 0 | 0 | 0 | 48.5304 | 48.5304 | 0 | 22.2906 | 803.64 | 0 | 0.088511 | 3.0673 | 0 | 0 | 0 | 6.7196 | on_peak | 803.64 |  |  | 0.78 | 5.65 | 93.57 | 20.6112 | 0
609 | 825.26 | 230.927 | 20.6 | 38.0028 | 38.0028 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22.2906 | 787.2572 | 0 | 0.088511 | 2.8843 | 0 | 0 | 0 | 38.0028 | on_peak | 787.2572 |  |  | 4.6 | 0 | 95.4 | 109.6105 | 0
610 | 868.84 | 191.039 | 21.5 | 31.3383 | 31.3383 | 0 | 0 | 0 | 0 | 13.9126 | 13.9126 | 0 | 7.4174 | 823.5891 | 0 | 0.088511 | 2.7939 | 0 | 0 | 0 | 31.3383 | on_peak | 823.5891 |  |  | 3.61 | 1.6 | 94.79 | 87.5562 | 0
611 | 800.85 | 580.841 | 22.3 | 95.0109 | 95.0109 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 18.9814 | 718.2015 | 0 | 0.05921 | 2.8154 | 0 | 0 | 0 | 95.0109 | off_peak | 705.8391 | 0 | 100 | 11.86 | 0 | 88.14 | 267.4949 | 0
612 | 807.81 | 684.273 | 22.6 | 111.81 | 111.81 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 30.5453 | 708.3624 | 0 | 0.05921 | 2.8662 | 0 | 0 | 0 | 111.81 | off_peak | 696 | 0 | 100 | 13.84 | 0 | 86.16 | 320.4694 | 0
613 | 855.3 | 719.863 | 22.8 | 117.5414 | 117.5414 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 42.1093 | 750.121 | 0 | 0.05921 | 3.7473 | 0 | 0 | 0 | 117.5414 | off_peak | 737.7586 | 0 | 100 | 13.74 | 0 | 86.26 | 440.4642 | 0
614 | 877.63 | 679.663 | 22.8 | 110.9774 | 110.9774 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 53.6732 | 779.0149 | 0 | 0.05921 | 4.1058 | 0 | 0 | 0 | 110.9774 | off_peak | 766.6526 | 0 | 100 | 12.65 | 0 | 87.35 | 455.6513 | 0
615 | 893.48 | 581.862 | 22.5 | 95.11 | 95.11 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 65.2371 | 810.7324 | 0 | 0.05921 | 4.211 | 0 | 0 | 0 | 95.11 | off_peak | 798.37 | 0 | 100 | 10.64 | 0 | 89.36 | 400.5055 | 0
616 | 828.08 | 389.92 | 21.8 | 63.8947 | 63.8947 | 0 | 0 | 8.9371 | 8.9371 | 0 | 0 | 0 | 73.597 | 773.1224 | 0 | 0.05921 | 4.0882 | 0 | 0 | 0 | 63.8947 | off_peak | 764.1853 | 0 | 100 | 7.72 | 0 | 92.28 | 261.2164 | 0
617 | 836.67 | 245.569 | 20.9 | 40.3694 | 40.3694 | 0 | 0 | 0.57721 | 0.57721 | 0 | 0 | 0 | 74.137 | 796.8778 | 0 | 0.05921 | 3.9247 | 0 | 0 | 0 | 40.3694 | off_peak | 796.3006 | 0 | 100 | 4.83 | 0 | 95.17 | 158.4368 | 0
618 | 856.24 | 46.3538 | 20.1 | 7.6418 | 7.6418 | 0 | 0 | 0.037279 | 0.037279 | 0 | 0 | 0 | 74.1718 | 848.6355 | 0 | 0.05921 | 3.8142 | 0 | 0 | 0 | 7.6418 | off_peak | 848.5982 | 0 | 100 | 0.89 | 0 | 99.11 | 29.1472 | 0
619 | 796.58 | 0 | 19.7 | 0 | 0 | 0 | 0 | 0 | 0 | 62.443 | 62.443 | 0 | 7.4174 | 734.137 | 0 | 0.088511 | 3.9099 | 0 | 0 | 0 | 0 | on_peak | 734.137 |  |  | 0 | 7.84 | 92.16 | 0 | 0
620 | 785.6 | 0 | 18.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 785.6 | 0 | 0.088511 | 3.8976 | 0 | 0 | 0 | 0 | on_peak | 785.6 |  |  | 0 | 0 | 100 | 0 | 0
621 | 795.9 | 0 | 18.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 795.9 | 0 | 0.088511 | 3.8512 | 0 | 0 | 0 | 0 | on_peak | 795.9 |  |  | 0 | 0 | 100 | 0 | 0
622 | 738.15 | 0 | 17.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 738.15 | 0 | 0.088511 | 4.0791 | 0 | 0 | 0 | 0 | on_peak | 738.15 |  |  | 0 | 0 | 100 | 0 | 0
623 | 798.94 | 0 | 17.3 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 18.9814 | 811.3024 | 0 | 0.05921 | 4.4312 | 0 | 0 | 0 | 0 | off_peak | 798.94 | 0 | 100 | 0 | 0 | 100 | 0 | 0
624 | 734.81 | 0 | 16.9 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 30.5453 | 747.1724 | 0 | 0.05921 | 4.9213 | 0 | 0 | 0 | 0 | off_peak | 734.81 | 0 | 100 | 0 | 0 | 100 | 0 | 0
625 | 717.8 | 0 | 16.5 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 42.1093 | 730.1624 | 0 | 0.05921 | 5.2996 | 0 | 0 | 0 | 0 | off_peak | 717.8 | 0 | 100 | 0 | 0 | 100 | 0 | 0
626 | 628.52 | 0 | 16.1 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 53.6732 | 640.8824 | 0 | 0.05921 | 5.2184 | 0 | 0 | 0 | 0 | off_peak | 628.52 | 0 | 100 | 0 | 0 | 100 | 0 | 0
627 | 608.31 | 0 | 15.7 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 65.2371 | 620.6724 | 0 | 0.05921 | 4.9924 | 0 | 0 | 0 | 0 | off_peak | 608.31 | 0 | 100 | 0 | 0 | 100 | 0 | 0
628 | 574.54 | 0 | 15.3 | 0 | 0 | 0 | 0 | 8.9371 | 8.9371 | 0 | 0 | 0 | 73.597 | 583.4771 | 0 | 0.05921 | 4.6506 | 0 | 0 | 0 | 0 | off_peak | 574.54 | 0 | 100 | 0 | 0 | 100 | 0 | 0
629 | 614.26 | 0 | 14.9 | 0 | 0 | 0 | 0 | 0.57721 | 0.57721 | 0 | 0 | 0 | 74.137 | 614.8372 | 0 | 0.05921 | 4.1978 | 0 | 0 | 0 | 0 | off_peak | 614.26 | 0 | 100 | 0 | 0 | 100 | 0 | 0
630 | 690.99 | 0 | 14.6 | 0 | 0 | 0 | 0 | 0.037279 | 0.037279 | 0 | 0 | 0 | 74.1718 | 691.0273 | 0 | 0.05921 | 3.6209 | 0 | 0 | 0 | 0 | off_peak | 690.99 | 0 | 100 | 0 | 0 | 100 | 0 | 0
631 | 740.32 | 0 | 14.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1718 | 740.32 | 0 | 0.088511 | 3.456 | 0 | 0 | 0 | 0 | on_peak | 740.32 |  |  | 0 | 0 | 100 | 0 | 0
632 | 777.63 | 32.1854 | 14.9 | 5.4036 | 5.4036 | 0 | 0 | 0 | 0 | 62.443 | 62.443 | 0 | 7.4174 | 709.7833 | 0 | 0.088511 | 3.2131 | 0 | 0 | 0 | 5.4036 | on_peak | 709.7833 |  |  | 0.69 | 8.03 | 91.28 | 17.3623 | 0
633 | 807.66 | 169.623 | 15.6 | 28.4088 | 28.4088 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 779.2512 | 0 | 0.088511 | 3.0986 | 0 | 0 | 0 | 28.4088 | on_peak | 779.2512 |  |  | 3.52 | 0 | 96.48 | 88.0275 | 0
634 | 816.89 | 396.991 | 16.5 | 66.2805 | 66.2805 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 750.6095 | 0 | 0.088511 | 3.1163 | 0 | 0 | 0 | 66.2805 | on_peak | 750.6095 |  |  | 8.11 | 0 | 91.89 | 206.5492 | 0
635 | 786.23 | 568.322 | 17.4 | 94.5871 | 94.5871 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 18.9814 | 704.0052 | 0 | 0.05921 | 3.2468 | 0 | 0 | 0 | 94.5871 | off_peak | 691.6429 | 0 | 100 | 12.03 | 0 | 87.97 | 307.1026 | 0
636 | 879.48 | 668.746 | 18.2 | 110.9889 | 110.9889 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 30.5453 | 780.8534 | 0 | 0.05921 | 3.6957 | 0 | 0 | 0 | 110.9889 | off_peak | 768.4911 | 0 | 100 | 12.62 | 0 | 87.38 | 410.1832 | 0
637 | 788.27 | 553.191 | 18.9 | 91.5849 | 91.5849 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 42.1093 | 709.0474 | 0 | 0.05921 | 4.5326 | 0 | 0 | 0 | 91.5849 | off_peak | 696.6851 | 0 | 100 | 11.62 | 0 | 88.38 | 415.1172 | 0
638 | 811.93 | 627.417 | 19.4 | 103.6906 | 103.6906 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 53.6732 | 720.6017 | 0 | 0.05921 | 4.9686 | 0 | 0 | 0 | 103.6906 | off_peak | 708.2394 | 0 | 100 | 12.77 | 0 | 87.23 | 515.202 | 0
639 | 811.15 | 585.898 | 19.8 | 96.6923 | 96.6923 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 65.2371 | 726.8201 | 0 | 0.05921 | 4.856 | 0 | 0 | 0 | 96.6923 | off_peak | 714.4577 | 0 | 100 | 11.92 | 0 | 88.08 | 469.5405 | 0
640 | 764.28 | 436.767 | 20 | 72.0299 | 72.0299 | 0 | 0 | 8.9371 | 8.9371 | 0 | 0 | 0 | 73.597 | 701.1872 | 0 | 0.05921 | 4.1229 | 0 | 0 | 0 | 72.0299 | off_peak | 692.2501 | 0 | 100 | 9.42 | 0 | 90.58 | 296.9695 | 0
641 | 810.57 | 191.414 | 19.6 | 31.6119 | 31.6119 | 0 | 0 | 0.57721 | 0.57721 | 0 | 0 | 0 | 74.137 | 779.5353 | 0 | 0.05921 | 3.8004 | 0 | 0 | 0 | 31.6119 | off_peak | 778.9581 | 0 | 100 | 3.9 | 0 | 96.1 | 120.1367 | 0
642 | 812.3 | 60.1287 | 19 | 9.9513 | 9.914 | 0 | 0.037279 | 0.037279 | 0 | 0 | 0 | 0 | 74.1718 | 802.386 | 0 | 0.05921 | 3.5265 | 0 | 0 | 0.034872 | 9.914 | off_peak | 802.386 | 100 | 0 | 1.22 | 0 | 98.78 | 34.9612 | 0
643 | 782.66 | 0 | 18.7 | 0 | 0 | 0 | 0 | 0 | 0 | 62.443 | 62.443 | 0 | 7.4174 | 720.217 | 0 | 0.088511 | 3.4104 | 0.032619 | 0 | 0 | 0.032619 | on_peak | 720.217 |  |  | 0 | 7.98 | 92.02 | 0.11125 | 0
644 | 770.67 | 0 | 18.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 770.67 | 0 | 0.088511 | 3.3746 | 0 | 0 | 0 | 0 | on_peak | 770.67 |  |  | 0 | 0 | 100 | 0 | 0
645 | 771.53 | 0 | 17.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 771.53 | 0 | 0.088511 | 3.3848 | 0 | 0 | 0 | 0 | on_peak | 771.53 |  |  | 0 | 0 | 100 | 0 | 0
646 | 715.3 | 0 | 17.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 715.3 | 0 | 0.088511 | 3.5262 | 0 | 0 | 0 | 0 | on_peak | 715.3 |  |  | 0 | 0 | 100 | 0 | 0
647 | 755.66 | 0 | 17.8 | 0 | 0 | 0 | 0 | 6.6603 | 6.6603 | 0 | 0 | 0 | 13.6476 | 762.3203 | 0 | 0.05921 | 3.9187 | 0 | 0 | 0 | 0 | off_peak | 755.66 | 0 | 100 | 0 | 0 | 100 | 0 | 0
648 | 724.86 | 0 | 17.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13.6476 | 724.86 | 0 | 0.05921 | 4.5437 | 0 | 0 | 0 | 0 | off_peak | 724.86 |  |  | 0 | 0 | 100 | 0 | 0
649 | 705.98 | 0 | 17.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13.6476 | 705.98 | 0 | 0.05921 | 4.936 | 0 | 0 | 0 | 0 | off_peak | 705.98 |  |  | 0 | 0 | 100 | 0 | 0
650 | 606.47 | 0 | 17.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13.6476 | 606.47 | 0 | 0.05921 | 4.8391 | 0 | 0 | 0 | 0 | off_peak | 606.47 |  |  | 0 | 0 | 100 | 0 | 0
651 | 610.94 | 0 | 17.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13.6476 | 610.94 | 0 | 0.05921 | 4.6296 | 0 | 0 | 0 | 0 | off_peak | 610.94 |  |  | 0 | 0 | 100 | 0 | 0
652 | 603.56 | 0 | 16.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13.6476 | 603.56 | 0 | 0.05921 | 4.3002 | 0 | 0 | 0 | 0 | off_peak | 603.56 |  |  | 0 | 0 | 100 | 0 | 0
653 | 592.24 | 0 | 15.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13.6476 | 592.24 | 0 | 0.05921 | 4.1246 | 0 | 0 | 0 | 0 | off_peak | 592.24 |  |  | 0 | 0 | 100 | 0 | 0
654 | 672.26 | 0 | 14.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13.6476 | 672.26 | 0 | 0.05921 | 4.0339 | 0 | 0 | 0 | 0 | off_peak | 672.26 |  |  | 0 | 0 | 100 | 0 | 0
655 | 721.78 | 0 | 14.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13.6476 | 721.78 | 0 | 0.05921 | 3.5199 | 0 | 0 | 0 | 0 | off_peak | 721.78 |  |  | 0 | 0 | 100 | 0 | 0
656 | 700.61 | 43.3107 | 14.8 | 7.274 | 7.274 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13.6476 | 693.336 | 0 | 0.05921 | 3.2258 | 0 | 0 | 0 | 7.274 | off_peak | 693.336 |  |  | 1.04 | 0 | 98.96 | 23.4647 | 0
657 | 773.28 | 235.296 | 15.6 | 39.4079 | 39.4079 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13.6476 | 733.8721 | 0 | 0.05921 | 3.1419 | 0 | 0 | 0 | 39.4079 | off_peak | 733.8721 |  |  | 5.1 | 0 | 94.9 | 123.8172 | 0
658 | 741.27 | 430.561 | 16.5 | 71.8853 | 71.8853 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13.6476 | 669.3847 | 0 | 0.05921 | 3.194 | 0 | 0 | 0 | 71.8853 | off_peak | 669.3847 |  |  | 9.7 | 0 | 90.3 | 229.6049 | 0
659 | 720.84 | 588.307 | 17.3 | 97.9476 | 97.9476 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13.6476 | 622.8924 | 0 | 0.05921 | 3.2344 | 0 | 0 | 0 | 97.9476 | off_peak | 622.8924 |  |  | 13.59 | 0 | 86.41 | 316.8028 | 0
660 | 786.61 | 692.449 | 18 | 115.0036 | 115.0036 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13.6476 | 671.6064 | 0 | 0.05921 | 3.3859 | 0 | 0 | 0 | 115.0036 | off_peak | 671.6064 |  |  | 14.62 | 0 | 85.38 | 389.3909 | 0
661 | 682.51 | 728.348 | 18.6 | 120.7109 | 120.7109 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13.6476 | 561.7991 | 0 | 0.05921 | 3.6609 | 0 | 0 | 0 | 120.7109 | off_peak | 561.7991 |  |  | 17.69 | 0 | 82.31 | 441.9095 | 0
662 | 696.83 | 691.053 | 19 | 114.3687 | 114.3687 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13.6476 | 582.4613 | 0 | 0.05921 | 4.1884 | 0 | 0 | 0 | 114.3687 | off_peak | 582.4613 |  |  | 16.41 | 0 | 83.59 | 479.0237 | 0
663 | 669.36 | 594.819 | 19.2 | 98.3727 | 98.3727 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13.6476 | 570.9873 | 0 | 0.05921 | 4.2093 | 0 | 0 | 0 | 98.3727 | off_peak | 570.9873 |  |  | 14.7 | 0 | 85.3 | 414.082 | 0
664 | 649.41 | 438.275 | 19.2 | 72.483 | 72.483 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13.6476 | 576.927 | 0 | 0.05921 | 4.1116 | 0 | 0 | 0 | 72.483 | off_peak | 576.927 |  |  | 11.16 | 0 | 88.84 | 298.024 | 0
665 | 676.91 | 247.014 | 18.6 | 40.9382 | 40.9382 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13.6476 | 635.9718 | 0 | 0.05921 | 3.8709 | 0 | 0 | 0 | 40.9382 | off_peak | 635.9718 |  |  | 6.05 | 0 | 93.95 | 158.4688 | 0
666 | 646.89 | 58.6475 | 17.7 | 9.7506 | 9.7506 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13.6476 | 637.1394 | 0 | 0.05921 | 3.9712 | 0 | 0 | 0 | 9.7506 | off_peak | 637.1394 |  |  | 1.51 | 0 | 98.49 | 38.7214 | 0
667 | 601.26 | 0 | 17.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13.6476 | 601.26 | 0 | 0.05921 | 3.8995 | 0 | 0 | 0 | 0 | off_peak | 601.26 |  |  | 0 | 0 | 100 | 0 | 0
668 | 603.47 | 0 | 16.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13.6476 | 603.47 | 0 | 0.05921 | 3.7645 | 0 | 0 | 0 | 0 | off_peak | 603.47 |  |  | 0 | 0 | 100 | 0 | 0
669 | 517.33 | 0 | 16.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13.6476 | 517.33 | 0 | 0.05921 | 3.8408 | 0 | 0 | 0 | 0 | off_peak | 517.33 |  |  | 0 | 0 | 100 | 0 | 0
670 | 555.38 | 0 | 16.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13.6476 | 555.38 | 0 | 0.05921 | 4.0046 | 0 | 0 | 0 | 0 | off_peak | 555.38 |  |  | 0 | 0 | 100 | 0 | 0
671 | 534.1 | 0 | 16.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13.6476 | 534.1 | 0 | 0.05921 | 4.1942 | 0 | 0 | 0 | 0 | off_peak | 534.1 |  |  | 0 | 0 | 100 | 0 | 0
672 | 553.8 | 0 | 16.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13.6476 | 553.8 | 0 | 0.05921 | 4.4339 | 0 | 0 | 0 | 0 | off_peak | 553.8 |  |  | 0 | 0 | 100 | 0 | 0
673 | 524.77 | 0 | 16.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13.6476 | 524.77 | 0 | 0.05921 | 4.6956 | 0 | 0 | 0 | 0 | off_peak | 524.77 |  |  | 0 | 0 | 100 | 0 | 0
674 | 513.86 | 0 | 16.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13.6476 | 513.86 | 0 | 0.05921 | 4.5978 | 0 | 0 | 0 | 0 | off_peak | 513.86 |  |  | 0 | 0 | 100 | 0 | 0
675 | 553.42 | 0 | 16.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13.6476 | 553.42 | 0 | 0.05921 | 4.4466 | 0 | 0 | 0 | 0 | off_peak | 553.42 |  |  | 0 | 0 | 100 | 0 | 0
676 | 519.17 | 0 | 16.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13.6476 | 519.17 | 0 | 0.05921 | 4.1592 | 0 | 0 | 0 | 0 | off_peak | 519.17 |  |  | 0 | 0 | 100 | 0 | 0
677 | 548.93 | 0 | 16.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13.6476 | 548.93 | 0 | 0.05921 | 3.9264 | 0 | 0 | 0 | 0 | off_peak | 548.93 |  |  | 0 | 0 | 100 | 0 | 0
678 | 609.23 | 0 | 16.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13.6476 | 609.23 | 0 | 0.05921 | 3.617 | 0 | 0 | 0 | 0 | off_peak | 609.23 |  |  | 0 | 0 | 100 | 0 | 0
679 | 644.46 | 0 | 17.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13.6476 | 644.46 | 0 | 0.05921 | 3.2934 | 0 | 0 | 0 | 0 | off_peak | 644.46 |  |  | 0 | 0 | 100 | 0 | 0
680 | 661.46 | 10.45 | 18.3 | 1.7337 | 1.7337 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13.6476 | 659.7263 | 0 | 0.05921 | 3.0167 | 0 | 0 | 0 | 1.7337 | off_peak | 659.7263 |  |  | 0.26 | 0 | 99.74 | 5.2301 | 0
681 | 667.15 | 43.7 | 19.3 | 7.2247 | 7.2247 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13.6476 | 659.9253 | 0 | 0.05921 | 2.8622 | 0 | 0 | 0 | 7.2247 | off_peak | 659.9253 |  |  | 1.08 | 0 | 98.92 | 20.6782 | 0
682 | 641.94 | 18.05 | 19.9 | 2.9778 | 2.9778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13.6476 | 638.9622 | 0 | 0.05921 | 2.7651 | 0 | 0 | 0 | 2.9778 | off_peak | 638.9622 |  |  | 0.46 | 0 | 99.54 | 8.234 | 0
683 | 649.16 | 123.692 | 20.4 | 20.3699 | 20.3699 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13.6476 | 628.7901 | 0 | 0.05921 | 2.6944 | 0 | 0 | 0 | 20.3699 | off_peak | 628.7901 |  |  | 3.14 | 0 | 96.86 | 54.8857 | 0
684 | 697.99 | 105.45 | 20.6 | 17.3535 | 17.3535 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13.6476 | 680.6365 | 0 | 0.05921 | 2.778 | 0 | 0 | 0 | 17.3535 | off_peak | 680.6365 |  |  | 2.49 | 0 | 97.51 | 48.2075 | 0
685 | 668.49 | 84.55 | 20.8 | 13.9042 | 13.9042 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13.6476 | 654.5858 | 0 | 0.05921 | 2.9584 | 0 | 0 | 0 | 13.9042 | off_peak | 654.5858 |  |  | 2.08 | 0 | 97.92 | 41.1343 | 0
686 | 640.17 | 107.35 | 20.8 | 17.6536 | 17.6536 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13.6476 | 622.5164 | 0 | 0.05921 | 3.2344 | 0 | 0 | 0 | 17.6536 | off_peak | 622.5164 |  |  | 2.76 | 0 | 97.24 | 57.099 | 0
687 | 675.72 | 26.6 | 20.8 | 4.3744 | 4.3744 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13.6476 | 671.3456 | 0 | 0.05921 | 3.5571 | 0 | 0 | 0 | 4.3744 | off_peak | 671.3456 |  |  | 0.65 | 0 | 99.35 | 15.56 | 0
688 | 712.25 | 55.1 | 20.6 | 9.0676 | 9.0676 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13.6476 | 703.1824 | 0 | 0.05921 | 3.6684 | 0 | 0 | 0 | 9.0676 | off_peak | 703.1824 |  |  | 1.27 | 0 | 98.73 | 33.2638 | 0
689 | 673.12 | 45.6 | 20.1 | 7.5175 | 7.5175 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13.6476 | 665.6025 | 0 | 0.05921 | 3.6639 | 0 | 0 | 0 | 7.5175 | off_peak | 665.6025 |  |  | 1.12 | 0 | 98.88 | 27.5436 | 0
690 | 629.43 | 12.35 | 19.5 | 2.0403 | 0 | 0 | 2.0403 | 2.0403 | 0 | 0 | 0 | 0 | 15.5561 | 629.43 | 0 | 0.05921 | 3.708 | 0 | 0 | 1.9085 | 0 | off_peak | 629.43 | 100 | 0 | 0 | 0 | 100 | 0 | 0
691 | 638.06 | 0 | 19.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15.5561 | 638.06 | 0 | 0.05921 | 3.9224 | 0 | 0 | 1.9085 | 0 | off_peak | 638.06 |  |  | 0 | 0 | 100 | 0 | 0
692 | 596.08 | 0 | 19.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15.5561 | 596.08 | 0 | 0.05921 | 4.1668 | 0 | 0 | 1.9085 | 0 | off_peak | 596.08 |  |  | 0 | 0 | 100 | 0 | 0
693 | 596.5 | 0 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15.5561 | 596.5 | 0 | 0.05921 | 4.5015 | 0 | 0 | 1.9085 | 0 | off_peak | 596.5 |  |  | 0 | 0 | 100 | 0 | 0
694 | 552.46 | 0 | 19 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 27.12 | 564.8224 | 0 | 0.05921 | 4.7891 | 0 | 0 | 1.9085 | 0 | off_peak | 552.46 | 0 | 100 | 0 | 0 | 100 | 0 | 0
695 | 548.79 | 0 | 19 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 38.684 | 561.1524 | 0 | 0.05921 | 5.1482 | 0 | 0 | 1.9085 | 0 | off_peak | 548.79 | 0 | 100 | 0 | 0 | 100 | 0 | 0
696 | 543.77 | 0 | 19 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 50.2479 | 556.1324 | 0 | 0.05921 | 5.3701 | 0 | 0 | 1.9085 | 0 | off_peak | 543.77 | 0 | 100 | 0 | 0 | 100 | 0 | 0
697 | 548.6 | 0 | 18.9 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 61.8119 | 560.9624 | 0 | 0.05921 | 5.6132 | 0 | 0 | 1.9085 | 0 | off_peak | 548.6 | 0 | 100 | 0 | 0 | 100 | 0 | 0
698 | 550 | 0 | 18.7 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 73.3758 | 562.3624 | 0 | 0.05921 | 5.4196 | 0 | 0 | 1.9085 | 0 | off_peak | 550 | 0 | 100 | 0 | 0 | 100 | 0 | 0
699 | 519.77 | 0 | 18.3 | 0 | 0 | 0 | 0 | 0.79843 | 0.79843 | 0 | 0 | 0 | 74.1227 | 520.5684 | 0 | 0.05921 | 5.1273 | 0 | 0 | 1.9085 | 0 | off_peak | 519.77 | 0 | 100 | 0 | 0 | 100 | 0 | 0
700 | 556.48 | 0 | 17.8 | 0 | 0 | 0 | 0 | 0.051567 | 0.051567 | 0 | 0 | 0 | 74.1709 | 556.5316 | 0 | 0.05921 | 4.7845 | 0 | 0 | 1.9085 | 0 | off_peak | 556.48 | 0 | 100 | 0 | 0 | 100 | 0 | 0
701 | 539.08 | 0 | 17.4 | 0 | 0 | 0 | 0 | 0.0033305 | 0.0033305 | 0 | 0 | 0 | 74.174 | 539.0833 | 0 | 0.05921 | 4.4239 | 0 | 0 | 1.9085 | 0 | off_peak | 539.08 | 0 | 100 | 0 | 0 | 100 | 0 | 0
702 | 709.57 | 0 | 17.1 | 0 | 0 | 0 | 0 | 0.0002151 | 0.0002151 | 0 | 0 | 0 | 74.1742 | 709.5702 | 0 | 0.05921 | 3.8434 | 0 | 0 | 1.9085 | 0 | off_peak | 709.57 | 0 | 100 | 0 | 0 | 100 | 0 | 0
703 | 747.3 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 1.7853 | 1.7853 | 0 | 72.2657 | 745.5147 | 0 | 0.088511 | 3.3258 | 1.7853 | 0 | 0 | 1.7853 | on_peak | 745.5147 |  |  | 0 | 0.24 | 99.76 | 5.9374 | 0
704 | 775 | 45.9622 | 17.6 | 7.6442 | 7.6442 | 0 | 0 | 0 | 0 | 60.66 | 60.66 | 0 | 7.4174 | 706.6958 | 0 | 0.088511 | 2.9905 | 0 | 0 | 0 | 7.6442 | on_peak | 706.6958 |  |  | 0.99 | 7.83 | 91.19 | 22.8602 | 0
705 | 848.23 | 238.829 | 18.7 | 39.5678 | 39.5678 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 808.6622 | 0 | 0.088511 | 2.7971 | 0 | 0 | 0 | 39.5678 | on_peak | 808.6622 |  |  | 4.66 | 0 | 95.34 | 110.6754 | 0
706 | 864.42 | 436.096 | 19.8 | 71.9701 | 71.9701 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 792.4499 | 0 | 0.088511 | 2.7 | 0 | 0 | 0 | 71.9701 | on_peak | 792.4499 |  |  | 8.33 | 0 | 91.67 | 194.3171 | 0
707 | 810.85 | 594.134 | 20.8 | 97.705 | 97.705 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 18.9814 | 725.5074 | 0 | 0.05921 | 2.744 | 0 | 0 | 0 | 97.705 | off_peak | 713.145 | 0 | 100 | 12.05 | 0 | 87.95 | 268.0978 | 0
708 | 887.87 | 698.189 | 21.2 | 114.6539 | 114.6539 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 30.5453 | 785.5785 | 0 | 0.05921 | 3.0448 | 0 | 0 | 0 | 114.6539 | off_peak | 773.2161 | 0 | 100 | 12.91 | 0 | 87.09 | 349.0925 | 0
709 | 806.66 | 735.636 | 21.5 | 120.6746 | 120.6746 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 42.1093 | 698.3478 | 0 | 0.05921 | 3.5794 | 0 | 0 | 0 | 120.6746 | off_peak | 685.9854 | 0 | 100 | 14.96 | 0 | 85.04 | 431.9401 | 0
710 | 856.41 | 711.567 | 21.7 | 116.6433 | 116.6433 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 53.6732 | 752.1291 | 0 | 0.05921 | 3.9404 | 0 | 0 | 0 | 116.6433 | off_peak | 739.7667 | 0 | 100 | 13.62 | 0 | 86.38 | 459.624 | 0
711 | 878.56 | 618.044 | 21.9 | 101.2405 | 101.2405 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 65.2371 | 789.6819 | 0 | 0.05921 | 3.9562 | 0 | 0 | 0 | 101.2405 | off_peak | 777.3195 | 0 | 100 | 11.52 | 0 | 88.48 | 400.527 | 0
712 | 848 | 465.277 | 21.9 | 76.2161 | 76.2161 | 0 | 0 | 8.9371 | 8.9371 | 0 | 0 | 0 | 73.597 | 780.7211 | 0 | 0.05921 | 3.8814 | 0 | 0 | 0 | 76.2161 | off_peak | 771.7839 | 0 | 100 | 8.99 | 0 | 91.01 | 295.8267 | 0
713 | 849.68 | 271.54 | 21.5 | 44.5437 | 44.5437 | 0 | 0 | 0.57721 | 0.57721 | 0 | 0 | 0 | 74.137 | 805.7135 | 0 | 0.05921 | 3.9975 | 0 | 0 | 0 | 44.5437 | off_peak | 805.1363 | 0 | 100 | 5.24 | 0 | 94.76 | 178.0619 | 0
714 | 833.65 | 47.7105 | 21.1 | 7.8376 | 7.8003 | 0 | 0.037279 | 0.037279 | 0 | 0 | 0 | 0 | 74.1718 | 825.8497 | 0 | 0.05921 | 4.2911 | 0 | 0 | 0.034872 | 7.8003 | off_peak | 825.8497 | 100 | 0 | 0.94 | 0 | 99.06 | 33.4717 | 0
715 | 784.09 | 0 | 20.9 | 0 | 0 | 0 | 0 | 0 | 0 | 58.0622 | 58.0622 | 0 | 12.1008 | 726.0278 | 0 | 0.088511 | 4.7131 | 0.032619 | 0 | 0 | 0.032619 | on_peak | 726.0278 |  |  | 0 | 7.41 | 92.59 | 0.15374 | 0
716 | 827.97 | 0 | 20.5 | 0 | 0 | 0 | 0 | 0 | 0 | 4.3809 | 4.3809 | 0 | 7.4174 | 823.5891 | 0 | 0.088511 | 5.0289 | 0 | 0 | 0 | 0 | on_peak | 823.5891 |  |  | 0 | 0.53 | 99.47 | 0 | 0
717 | 762.67 | 0 | 20.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 762.67 | 0 | 0.088511 | 5.4439 | 0 | 0 | 0 | 0 | on_peak | 762.67 |  |  | 0 | 0 | 100 | 0 | 0
718 | 758.9 | 0 | 19.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 758.9 | 0 | 0.088511 | 5.7363 | 0 | 0 | 0 | 0 | on_peak | 758.9 |  |  | 0 | 0 | 100 | 0 | 0
719 | 754.76 | 0 | 19.3 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 18.9814 | 767.1224 | 0 | 0.05921 | 6.0886 | 0 | 0 | 0 | 0 | off_peak | 754.76 | 0 | 100 | 0 | 0 | 100 | 0 | 0
720 | 754.25 | 0 | 18.9 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 30.5453 | 766.6124 | 0 | 0.05921 | 6.3981 | 0 | 0 | 0 | 0 | off_peak | 754.25 | 0 | 100 | 0 | 0 | 100 | 0 | 0
721 | 731.15 | 0 | 18.7 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 42.1093 | 743.5124 | 0 | 0.05921 | 6.3613 | 0 | 0 | 0 | 0 | off_peak | 731.15 | 0 | 100 | 0 | 0 | 100 | 0 | 0
722 | 665.64 | 0 | 18.6 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 53.6732 | 678.0024 | 0 | 0.05921 | 6.1868 | 0 | 0 | 0 | 0 | off_peak | 665.64 | 0 | 100 | 0 | 0 | 100 | 0 | 0
723 | 603.05 | 0 | 18.6 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 65.2371 | 615.4124 | 0 | 0.05921 | 5.6277 | 0 | 0 | 0 | 0 | off_peak | 603.05 | 0 | 100 | 0 | 0 | 100 | 0 | 0
724 | 636.06 | 0 | 18.6 | 0 | 0 | 0 | 0 | 8.9371 | 8.9371 | 0 | 0 | 0 | 73.597 | 644.9971 | 0 | 0.05921 | 5.1071 | 0 | 0 | 0 | 0 | off_peak | 636.06 | 0 | 100 | 0 | 0 | 100 | 0 | 0
725 | 575.32 | 0 | 18.4 | 0 | 0 | 0 | 0 | 0.57721 | 0.57721 | 0 | 0 | 0 | 74.137 | 575.8972 | 0 | 0.05921 | 4.6093 | 0 | 0 | 0 | 0 | off_peak | 575.32 | 0 | 100 | 0 | 0 | 100 | 0 | 0
726 | 699.23 | 0 | 18.2 | 0 | 0 | 0 | 0 | 0.037279 | 0.037279 | 0 | 0 | 0 | 74.1718 | 699.2673 | 0 | 0.05921 | 3.9939 | 0 | 0 | 0 | 0 | off_peak | 699.23 | 0 | 100 | 0 | 0 | 100 | 0 | 0
727 | 767.07 | 0 | 18.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1718 | 767.07 | 0 | 0.088511 | 3.4381 | 0 | 0 | 0 | 0 | on_peak | 767.07 |  |  | 0 | 0 | 100 | 0 | 0
728 | 789.63 | 49.0117 | 19.2 | 8.1057 | 8.1057 | 0 | 0 | 0 | 0 | 62.443 | 62.443 | 0 | 7.4174 | 719.0813 | 0 | 0.088511 | 3.0609 | 0 | 0 | 0 | 8.1057 | on_peak | 719.0813 |  |  | 1.03 | 7.91 | 91.07 | 24.8104 | 0
729 | 802.02 | 246.12 | 20.3 | 40.5461 | 40.5461 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 761.4739 | 0 | 0.088511 | 2.8201 | 0 | 0 | 0 | 40.5461 | on_peak | 761.4739 |  |  | 5.06 | 0 | 94.94 | 114.3444 | 0
730 | 832.24 | 445.514 | 21.1 | 73.1866 | 73.1866 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 759.0534 | 0 | 0.088511 | 2.6964 | 0 | 0 | 0 | 73.1866 | on_peak | 759.0534 |  |  | 8.79 | 0 | 91.21 | 197.3438 | 0
731 | 767.92 | 606.039 | 21.7 | 99.3447 | 99.3447 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 18.9814 | 680.9377 | 0 | 0.05921 | 2.7177 | 0 | 0 | 0 | 99.3447 | off_peak | 668.5753 | 0 | 100 | 12.94 | 0 | 87.06 | 269.9885 | 0
732 | 874.97 | 711.695 | 22 | 116.5398 | 116.5398 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 30.5453 | 770.7926 | 0 | 0.05921 | 2.9813 | 0 | 0 | 0 | 116.5398 | off_peak | 758.4302 | 0 | 100 | 13.32 | 0 | 86.68 | 347.4343 | 0
733 | 806.9 | 749.764 | 22.1 | 122.7298 | 122.7298 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 42.1093 | 696.5325 | 0 | 0.05921 | 3.5551 | 0 | 0 | 0 | 122.7298 | off_peak | 684.1702 | 0 | 100 | 15.21 | 0 | 84.79 | 436.3202 | 0
734 | 854.18 | 718.594 | 22.1 | 117.6276 | 117.6276 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 53.6732 | 748.9148 | 0 | 0.05921 | 3.8133 | 0 | 0 | 0 | 117.6276 | off_peak | 736.5524 | 0 | 100 | 13.77 | 0 | 86.23 | 448.545 | 0
735 | 901.73 | 622.671 | 21.9 | 101.9984 | 101.9984 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 65.2371 | 812.0939 | 0 | 0.05921 | 3.9021 | 0 | 0 | 0 | 101.9984 | off_peak | 799.7316 | 0 | 100 | 11.31 | 0 | 88.69 | 398.0118 | 0
736 | 890.06 | 470.533 | 21.5 | 77.1868 | 77.1868 | 0 | 0 | 8.9371 | 8.9371 | 0 | 0 | 0 | 73.597 | 821.8103 | 0 | 0.05921 | 4.0193 | 0 | 0 | 0 | 77.1868 | off_peak | 812.8732 | 0 | 100 | 8.67 | 0 | 91.33 | 310.2405 | 0
737 | 915.26 | 276.684 | 21 | 45.4683 | 45.4683 | 0 | 0 | 0.57721 | 0.57721 | 0 | 0 | 0 | 74.137 | 870.369 | 0 | 0.05921 | 4.1319 | 0 | 0 | 0 | 45.4683 | off_peak | 869.7917 | 0 | 100 | 4.97 | 0 | 95.03 | 187.8706 | 0
738 | 876.66 | 76.2664 | 20.5 | 12.5553 | 12.5553 | 0 | 0 | 0.037279 | 0.037279 | 0 | 0 | 0 | 74.1718 | 864.142 | 0 | 0.05921 | 4.3452 | 0 | 0 | 0 | 12.5553 | off_peak | 864.1047 | 0 | 100 | 1.43 | 0 | 98.57 | 54.5556 | 0
739 | 797.45 | 0 | 20.2 | 0 | 0 | 0 | 0 | 0 | 0 | 52.9022 | 52.9022 | 0 | 17.617 | 744.5478 | 0 | 0.088511 | 4.5515 | 0 | 0 | 0 | 0 | on_peak | 744.5478 |  |  | 0 | 6.63 | 93.37 | 0 | 0
740 | 833.13 | 0 | 20.5 | 0 | 0 | 0 | 0 | 0 | 0 | 9.5409 | 9.5409 | 0 | 7.4174 | 823.5891 | 0 | 0.088511 | 4.8609 | 0 | 0 | 0 | 0 | on_peak | 823.5891 |  |  | 0 | 1.15 | 98.85 | 0 | 0
741 | 809.69 | 0 | 20.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 809.69 | 0 | 0.088511 | 5.0328 | 0 | 0 | 0 | 0 | on_peak | 809.69 |  |  | 0 | 0 | 100 | 0 | 0
742 | 757.78 | 0 | 19.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 757.78 | 0 | 0.088511 | 5.2989 | 0 | 0 | 0 | 0 | on_peak | 757.78 |  |  | 0 | 0 | 100 | 0 | 0
743 | 756.29 | 0 | 19.5 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 18.9814 | 768.6524 | 0 | 0.05921 | 5.7331 | 0 | 0 | 0 | 0 | off_peak | 756.29 | 0 | 100 | 0 | 0 | 100 | 0 | 0
744 | 759.02 | 0 | 18.9 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 30.5453 | 771.3824 | 0 | 0.05921 | 6.0745 | 0 | 0 | 0 | 0 | off_peak | 759.02 | 0 | 100 | 0 | 0 | 100 | 0 | 0
745 | 706.88 | 0 | 18.3 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 42.1093 | 719.2424 | 0 | 0.05921 | 6.2358 | 0 | 0 | 0 | 0 | off_peak | 706.88 | 0 | 100 | 0 | 0 | 100 | 0 | 0
746 | 643.47 | 0 | 17.8 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 53.6732 | 655.8324 | 0 | 0.05921 | 6.0561 | 0 | 0 | 0 | 0 | off_peak | 643.47 | 0 | 100 | 0 | 0 | 100 | 0 | 0
747 | 642.1 | 0 | 17.2 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 65.2371 | 654.4624 | 0 | 0.05921 | 5.6381 | 0 | 0 | 0 | 0 | off_peak | 642.1 | 0 | 100 | 0 | 0 | 100 | 0 | 0
748 | 595.31 | 0 | 16.8 | 0 | 0 | 0 | 0 | 8.9371 | 8.9371 | 0 | 0 | 0 | 73.597 | 604.2471 | 0 | 0.05921 | 5.0961 | 0 | 0 | 0 | 0 | off_peak | 595.31 | 0 | 100 | 0 | 0 | 100 | 0 | 0
749 | 603.34 | 0 | 16.6 | 0 | 0 | 0 | 0 | 0.57721 | 0.57721 | 0 | 0 | 0 | 74.137 | 603.9172 | 0 | 0.05921 | 4.5552 | 0 | 0 | 0 | 0 | off_peak | 603.34 | 0 | 100 | 0 | 0 | 100 | 0 | 0
750 | 719.14 | 0 | 16.5 | 0 | 0 | 0 | 0 | 0.037279 | 0.037279 | 0 | 0 | 0 | 74.1718 | 719.1773 | 0 | 0.05921 | 4.028 | 0 | 0 | 0 | 0 | off_peak | 719.14 | 0 | 100 | 0 | 0 | 100 | 0 | 0
751 | 734.39 | 0 | 16.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1718 | 734.39 | 0 | 0.088511 | 3.4262 | 0 | 0 | 0 | 0 | on_peak | 734.39 |  |  | 0 | 0 | 100 | 0 | 0
752 | 786.83 | 51.896 | 17 | 8.6493 | 8.6493 | 0 | 0 | 0 | 0 | 62.443 | 62.443 | 0 | 7.4174 | 715.7377 | 0 | 0.088511 | 3.0407 | 0 | 0 | 0 | 8.6493 | on_peak | 715.7377 |  |  | 1.1 | 7.94 | 90.96 | 26.2997 | 0
753 | 777.86 | 245.72 | 18 | 40.8098 | 40.8098 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 737.0502 | 0 | 0.088511 | 2.7961 | 0 | 0 | 0 | 40.8098 | on_peak | 737.0502 |  |  | 5.25 | 0 | 94.75 | 114.1094 | 0
754 | 773.04 | 183.438 | 19.3 | 30.3267 | 30.3267 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 742.7133 | 0 | 0.088511 | 2.6594 | 0 | 0 | 0 | 30.3267 | on_peak | 742.7133 |  |  | 3.92 | 0 | 96.08 | 80.6513 | 0
755 | 766.94 | 448.85 | 20.5 | 73.8917 | 73.8917 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 18.9814 | 705.4107 | 0 | 0.05921 | 2.6956 | 0 | 0 | 0 | 73.8917 | off_peak | 693.0483 | 0 | 100 | 9.63 | 0 | 90.37 | 199.1806 | 0
756 | 813.69 | 401.502 | 21.3 | 65.9097 | 65.9097 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 30.5453 | 760.1427 | 0 | 0.05921 | 2.9816 | 0 | 0 | 0 | 65.9097 | off_peak | 747.7803 | 0 | 100 | 8.1 | 0 | 91.9 | 196.515 | 0
757 | 814.02 | 582.631 | 21.8 | 95.4736 | 95.4736 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 42.1093 | 730.9088 | 0 | 0.05921 | 3.5551 | 0 | 0 | 0 | 95.4736 | off_peak | 718.5464 | 0 | 100 | 11.73 | 0 | 88.27 | 339.4228 | 0
758 | 801.02 | 594.791 | 22 | 97.3968 | 97.3968 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 53.6732 | 715.9856 | 0 | 0.05921 | 3.8686 | 0 | 0 | 0 | 97.3968 | off_peak | 703.6232 | 0 | 100 | 12.16 | 0 | 87.84 | 376.7915 | 0
759 | 864.33 | 595.657 | 22 | 97.5386 | 97.5386 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 65.2371 | 779.1538 | 0 | 0.05921 | 3.8841 | 0 | 0 | 0 | 97.5386 | off_peak | 766.7914 | 0 | 100 | 11.28 | 0 | 88.72 | 378.8462 | 0
760 | 858.26 | 382.882 | 21.8 | 62.7414 | 62.7414 | 0 | 0 | 8.9371 | 8.9371 | 0 | 0 | 0 | 73.597 | 804.4557 | 0 | 0.05921 | 3.8974 | 0 | 0 | 0 | 62.7414 | off_peak | 795.5186 | 0 | 100 | 7.31 | 0 | 92.69 | 244.5283 | 0
761 | 816.78 | 270.735 | 21.2 | 44.4591 | 44.4591 | 0 | 0 | 0.57721 | 0.57721 | 0 | 0 | 0 | 74.137 | 772.8981 | 0 | 0.05921 | 4.0465 | 0 | 0 | 0 | 44.4591 | off_peak | 772.3209 | 0 | 100 | 5.44 | 0 | 94.56 | 179.9048 | 0
762 | 831.8 | 77.8842 | 20.5 | 12.8216 | 12.8216 | 0 | 0 | 0.037279 | 0.037279 | 0 | 0 | 0 | 74.1718 | 819.0156 | 0 | 0.05921 | 4.362 | 0 | 0 | 0 | 12.8216 | off_peak | 818.9784 | 0 | 100 | 1.54 | 0 | 98.46 | 55.9285 | 0
763 | 771.31 | 0 | 20.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1718 | 771.31 | 0 | 0.088511 | 4.6223 | 0 | 0 | 0 | 0 | on_peak | 771.31 |  |  | 0 | 0 | 100 | 0 | 0
764 | 782.52 | 0 | 19.8 | 0 | 0 | 0 | 0 | 0 | 0 | 62.443 | 62.443 | 0 | 7.4174 | 720.077 | 0 | 0.088511 | 4.9385 | 0 | 0 | 0 | 0 | on_peak | 720.077 |  |  | 0 | 7.98 | 92.02 | 0 | 0
765 | 799.92 | 0 | 19.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 799.92 | 0 | 0.088511 | 5.202 | 0 | 0 | 0 | 0 | on_peak | 799.92 |  |  | 0 | 0 | 100 | 0 | 0
766 | 701.57 | 0 | 19.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 701.57 | 0 | 0.088511 | 5.4827 | 0 | 0 | 0 | 0 | on_peak | 701.57 |  |  | 0 | 0 | 100 | 0 | 0
767 | 770.82 | 0 | 19.2 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 18.9814 | 783.1824 | 0 | 0.05921 | 5.9759 | 0 | 0 | 0 | 0 | off_peak | 770.82 | 0 | 100 | 0 | 0 | 100 | 0 | 0
768 | 732.78 | 0 | 19 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 30.5453 | 745.1424 | 0 | 0.05921 | 6.2184 | 0 | 0 | 0 | 0 | off_peak | 732.78 | 0 | 100 | 0 | 0 | 100 | 0 | 0
769 | 683.58 | 0 | 18.9 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 42.1093 | 695.9424 | 0 | 0.05921 | 6.3389 | 0 | 0 | 0 | 0 | off_peak | 683.58 | 0 | 100 | 0 | 0 | 100 | 0 | 0
770 | 620.71 | 0 | 18.7 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 53.6732 | 633.0724 | 0 | 0.05921 | 6.2279 | 0 | 0 | 0 | 0 | off_peak | 620.71 | 0 | 100 | 0 | 0 | 100 | 0 | 0
771 | 570.63 | 0 | 18.4 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 65.2371 | 582.9924 | 0 | 0.05921 | 5.7243 | 0 | 0 | 0 | 0 | off_peak | 570.63 | 0 | 100 | 0 | 0 | 100 | 0 | 0
772 | 583.48 | 0 | 18.2 | 0 | 0 | 0 | 0 | 8.9371 | 8.9371 | 0 | 0 | 0 | 73.597 | 592.4171 | 0 | 0.05921 | 5.2157 | 0 | 0 | 0 | 0 | off_peak | 583.48 | 0 | 100 | 0 | 0 | 100 | 0 | 0
773 | 581.35 | 0 | 17.9 | 0 | 0 | 0 | 0 | 0.57721 | 0.57721 | 0 | 0 | 0 | 74.137 | 581.9272 | 0 | 0.05921 | 4.6321 | 0 | 0 | 0 | 0 | off_peak | 581.35 | 0 | 100 | 0 | 0 | 100 | 0 | 0
774 | 677.84 | 0 | 17.8 | 0 | 0 | 0 | 0 | 0.037279 | 0.037279 | 0 | 0 | 0 | 74.1718 | 677.8773 | 0 | 0.05921 | 3.9375 | 0 | 0 | 0 | 0 | off_peak | 677.84 | 0 | 100 | 0 | 0 | 100 | 0 | 0
775 | 755.84 | 0 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1718 | 755.84 | 0 | 0.088511 | 3.4715 | 0 | 0 | 0 | 0 | on_peak | 755.84 |  |  | 0 | 0 | 100 | 0 | 0
776 | 798.77 | 50.2217 | 18.9 | 8.3146 | 8.3146 | 0 | 0 | 0 | 0 | 62.443 | 62.443 | 0 | 7.4174 | 728.0124 | 0 | 0.088511 | 3.0963 | 0 | 0 | 0 | 8.3146 | on_peak | 728.0124 |  |  | 1.04 | 7.82 | 91.14 | 25.7442 | 0
777 | 754.5 | 199.353 | 20 | 32.8765 | 32.8765 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 721.6235 | 0 | 0.088511 | 2.8684 | 0 | 0 | 0 | 32.8765 | on_peak | 721.6235 |  |  | 4.36 | 0 | 95.64 | 94.3041 | 0
778 | 787.62 | 416.852 | 20.9 | 68.5268 | 68.5268 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 719.0932 | 0 | 0.088511 | 2.7631 | 0 | 0 | 0 | 68.5268 | on_peak | 719.0932 |  |  | 8.7 | 0 | 91.3 | 189.3483 | 0
779 | 768.43 | 395.98 | 21.6 | 64.9339 | 64.9339 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 18.9814 | 715.8584 | 0 | 0.05921 | 2.7768 | 0 | 0 | 0 | 64.9339 | off_peak | 703.4961 | 0 | 100 | 8.45 | 0 | 91.55 | 180.3099 | 0
780 | 837.15 | 546.962 | 21.9 | 89.5967 | 89.5967 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 30.5453 | 759.9157 | 0 | 0.05921 | 3.0569 | 0 | 0 | 0 | 89.5967 | off_peak | 747.5533 | 0 | 100 | 10.7 | 0 | 89.3 | 273.8857 | 0
781 | 806.58 | 543.638 | 22.1 | 88.9888 | 88.9888 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 42.1093 | 729.9536 | 0 | 0.05921 | 3.5575 | 0 | 0 | 0 | 88.9888 | off_peak | 717.5912 | 0 | 100 | 11.03 | 0 | 88.97 | 316.5775 | 0
782 | 823.06 | 604.122 | 22.2 | 98.8543 | 98.8543 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 53.6732 | 736.5681 | 0 | 0.05921 | 3.9284 | 0 | 0 | 0 | 98.8543 | off_peak | 724.2057 | 0 | 100 | 12.01 | 0 | 87.99 | 388.3435 | 0
783 | 947.24 | 383.239 | 22.1 | 62.7329 | 62.7329 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 65.2371 | 896.8695 | 0 | 0.05921 | 3.9897 | 0 | 0 | 0 | 62.7329 | off_peak | 884.5071 | 0 | 100 | 6.62 | 0 | 93.38 | 250.2829 | 0
784 | 849.13 | 291.823 | 21.9 | 47.8029 | 47.8029 | 0 | 0 | 8.9371 | 8.9371 | 0 | 0 | 0 | 73.597 | 810.2642 | 0 | 0.05921 | 3.9289 | 0 | 0 | 0 | 47.8029 | off_peak | 801.3271 | 0 | 100 | 5.63 | 0 | 94.37 | 187.8123 | 0
785 | 872.44 | 189.874 | 21.4 | 31.1582 | 31.1582 | 0 | 0 | 0.57721 | 0.57721 | 0 | 0 | 0 | 74.137 | 841.859 | 0 | 0.05921 | 4.0003 | 0 | 0 | 0 | 31.1582 | off_peak | 841.2818 | 0 | 100 | 3.57 | 0 | 96.43 | 124.6432 | 0
786 | 865.97 | 68.0082 | 20.8 | 11.1839 | 11.1839 | 0 | 0 | 0.037279 | 0.037279 | 0 | 0 | 0 | 74.1718 | 854.8234 | 0 | 0.05921 | 4.2816 | 0 | 0 | 0 | 11.1839 | off_peak | 854.7861 | 0 | 100 | 1.29 | 0 | 98.71 | 47.8849 | 0
787 | 786.47 | 0 | 20.5 | 0 | 0 | 0 | 0 | 0 | 0 | 62.443 | 62.443 | 0 | 7.4174 | 724.027 | 0 | 0.088511 | 4.662 | 0 | 0 | 0 | 0 | on_peak | 724.027 |  |  | 0 | 7.94 | 92.06 | 0 | 0
788 | 861.73 | 0 | 20.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 861.73 | 0 | 0.088511 | 5.0084 | 0 | 0 | 0 | 0 | on_peak | 861.73 |  |  | 0 | 0 | 100 | 0 | 0
789 | 813.37 | 0 | 20.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 813.37 | 0 | 0.088511 | 5.2514 | 0 | 0 | 0 | 0 | on_peak | 813.37 |  |  | 0 | 0 | 100 | 0 | 0
790 | 763.94 | 0 | 20.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 763.94 | 0 | 0.088511 | 5.5529 | 0 | 0 | 0 | 0 | on_peak | 763.94 |  |  | 0 | 0 | 100 | 0 | 0
791 | 794.19 | 0 | 20.2 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 18.9814 | 806.5524 | 0 | 0.05921 | 5.999 | 0 | 0 | 0 | 0 | off_peak | 794.19 | 0 | 100 | 0 | 0 | 100 | 0 | 0
792 | 768.99 | 0 | 20.1 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 30.5453 | 781.3524 | 0 | 0.05921 | 6.3001 | 0 | 0 | 0 | 0 | off_peak | 768.99 | 0 | 100 | 0 | 0 | 100 | 0 | 0
793 | 715.39 | 0 | 20.1 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 42.1093 | 727.7524 | 0 | 0.05921 | 6.4211 | 0 | 0 | 0 | 0 | off_peak | 715.39 | 0 | 100 | 0 | 0 | 100 | 0 | 0
794 | 662.38 | 0 | 20 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 53.6732 | 674.7424 | 0 | 0.05921 | 6.2438 | 0 | 0 | 0 | 0 | off_peak | 662.38 | 0 | 100 | 0 | 0 | 100 | 0 | 0
795 | 606.7 | 0 | 19.6 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 65.2371 | 619.0624 | 0 | 0.05921 | 5.7598 | 0 | 0 | 0 | 0 | off_peak | 606.7 | 0 | 100 | 0 | 0 | 100 | 0 | 0
796 | 620.23 | 0 | 19 | 0 | 0 | 0 | 0 | 8.9371 | 8.9371 | 0 | 0 | 0 | 73.597 | 629.1671 | 0 | 0.05921 | 5.3135 | 0 | 0 | 0 | 0 | off_peak | 620.23 | 0 | 100 | 0 | 0 | 100 | 0 | 0
797 | 632.79 | 0 | 18.4 | 0 | 0 | 0 | 0 | 0.57721 | 0.57721 | 0 | 0 | 0 | 74.137 | 633.3672 | 0 | 0.05921 | 4.6988 | 0 | 0 | 0 | 0 | off_peak | 632.79 | 0 | 100 | 0 | 0 | 100 | 0 | 0
798 | 689.82 | 0 | 17.7 | 0 | 0 | 0 | 0 | 0.037279 | 0.037279 | 0 | 0 | 0 | 74.1718 | 689.8573 | 0 | 0.05921 | 3.9933 | 0 | 0 | 0 | 0 | off_peak | 689.82 | 0 | 100 | 0 | 0 | 100 | 0 | 0
799 | 719 | 0 | 17.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1718 | 719 | 0 | 0.088511 | 3.6013 | 0 | 0 | 0 | 0 | on_peak | 719 |  |  | 0 | 0 | 100 | 0 | 0
800 | 767 | 40.2803 | 17.4 | 6.7039 | 6.7039 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1718 | 760.2961 | 0 | 0.088511 | 3.2746 | 0 | 0 | 0 | 6.7039 | on_peak | 760.2961 |  |  | 0.87 | 0 | 99.13 | 21.9528 | 0
801 | 809.33 | 63.765 | 18.1 | 10.5865 | 10.5865 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1718 | 798.7435 | 0 | 0.088511 | 3.0166 | 0 | 0 | 0 | 10.5865 | on_peak | 798.7435 |  |  | 1.31 | 0 | 98.69 | 31.9356 | 0
802 | 839.23 | 33.25 | 19.3 | 5.497 | 5.497 | 0 | 0 | 0 | 0 | 62.443 | 62.443 | 0 | 7.4174 | 771.2899 | 0 | 0.088511 | 2.8956 | 0 | 0 | 0 | 5.497 | on_peak | 771.2899 |  |  | 0.66 | 7.44 | 91.9 | 15.9172 | 0
803 | 834.27 | 93.1 | 20.6 | 15.3211 | 15.3211 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 18.9814 | 831.3113 | 0 | 0.05921 | 2.9348 | 0 | 0 | 0 | 15.3211 | off_peak | 818.9489 | 0 | 100 | 1.84 | 0 | 98.16 | 44.9639 | 0
804 | 885.14 | 177.65 | 21.4 | 29.1523 | 29.1523 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 30.5453 | 868.3501 | 0 | 0.05921 | 3.2074 | 0 | 0 | 0 | 29.1523 | off_peak | 855.9877 | 0 | 100 | 3.29 | 0 | 96.71 | 93.503 | 0
805 | 812.45 | 307.601 | 21.9 | 50.3875 | 50.3875 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 42.1093 | 774.4249 | 0 | 0.05921 | 3.7498 | 0 | 0 | 0 | 50.3875 | off_peak | 762.0625 | 0 | 100 | 6.2 | 0 | 93.8 | 188.9409 | 0
806 | 783.74 | 349.778 | 22.2 | 57.2352 | 57.2352 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 53.6732 | 738.8672 | 0 | 0.05921 | 4.1002 | 0 | 0 | 0 | 57.2352 | off_peak | 726.5048 | 0 | 100 | 7.3 | 0 | 92.7 | 234.6771 | 0
807 | 821.51 | 152.95 | 22.2 | 25.0277 | 25.0277 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 65.2371 | 808.8447 | 0 | 0.05921 | 4.3541 | 0 | 0 | 0 | 25.0277 | off_peak | 796.4823 | 0 | 100 | 3.05 | 0 | 96.95 | 108.9735 | 0
808 | 795.45 | 75.05 | 22 | 12.2894 | 12.2894 | 0 | 0 | 8.9371 | 8.9371 | 0 | 0 | 0 | 73.597 | 792.0977 | 0 | 0.05921 | 4.5444 | 0 | 0 | 0 | 12.2894 | off_peak | 783.1606 | 0 | 100 | 1.54 | 0 | 98.46 | 55.8475 | 0
809 | 793.29 | 143.136 | 21.3 | 23.4969 | 23.4969 | 0 | 0 | 0.57721 | 0.57721 | 0 | 0 | 0 | 74.137 | 770.3703 | 0 | 0.05921 | 4.5263 | 0 | 0 | 0 | 23.4969 | off_peak | 769.7931 | 0 | 100 | 2.96 | 0 | 97.04 | 106.3542 | 0
810 | 768.62 | 69.4012 | 20.4 | 11.4292 | 11.4292 | 0 | 0 | 0.037279 | 0.037279 | 0 | 0 | 0 | 74.1718 | 757.2281 | 0 | 0.05921 | 4.6932 | 0 | 0 | 0 | 11.4292 | off_peak | 757.1908 | 0 | 100 | 1.49 | 0 | 98.51 | 53.6393 | 0
811 | 760.19 | 0 | 20.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1718 | 760.19 | 0 | 0.088511 | 4.8955 | 0 | 0 | 0 | 0 | on_peak | 760.19 |  |  | 0 | 0 | 100 | 0 | 0
812 | 729.21 | 0 | 19.8 | 0 | 0 | 0 | 0 | 0 | 0 | 62.443 | 62.443 | 0 | 7.4174 | 666.767 | 0 | 0.088511 | 5.0994 | 0 | 0 | 0 | 0 | on_peak | 666.767 |  |  | 0 | 8.56 | 91.44 | 0 | 0
813 | 693.72 | 0 | 19.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 693.72 | 0 | 0.088511 | 5.3727 | 0 | 0 | 0 | 0 | on_peak | 693.72 |  |  | 0 | 0 | 100 | 0 | 0
814 | 695.78 | 0 | 19.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 695.78 | 0 | 0.088511 | 5.5618 | 0 | 0 | 0 | 0 | on_peak | 695.78 |  |  | 0 | 0 | 100 | 0 | 0
815 | 724.2 | 0 | 18.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 724.2 | 0 | 0.05921 | 5.6175 | 0 | 0 | 0 | 0 | off_peak | 724.2 |  |  | 0 | 0 | 100 | 0 | 0
816 | 698.66 | 0 | 18.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 698.66 | 0 | 0.05921 | 5.8373 | 0 | 0 | 0 | 0 | off_peak | 698.66 |  |  | 0 | 0 | 100 | 0 | 0
817 | 614.29 | 0 | 17.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 614.29 | 0 | 0.05921 | 5.7661 | 0 | 0 | 0 | 0 | off_peak | 614.29 |  |  | 0 | 0 | 100 | 0 | 0
818 | 554.97 | 0 | 17.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 554.97 | 0 | 0.05921 | 5.5105 | 0 | 0 | 0 | 0 | off_peak | 554.97 |  |  | 0 | 0 | 100 | 0 | 0
819 | 555.14 | 0 | 16.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 555.14 | 0 | 0.05921 | 5.1068 | 0 | 0 | 0 | 0 | off_peak | 555.14 |  |  | 0 | 0 | 100 | 0 | 0
820 | 533.34 | 0 | 16.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 533.34 | 0 | 0.05921 | 4.8104 | 0 | 0 | 0 | 0 | off_peak | 533.34 |  |  | 0 | 0 | 100 | 0 | 0
821 | 529.5 | 0 | 15.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 529.5 | 0 | 0.05921 | 4.4784 | 0 | 0 | 0 | 0 | off_peak | 529.5 |  |  | 0 | 0 | 100 | 0 | 0
822 | 604.41 | 0 | 15.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 604.41 | 0 | 0.05921 | 4.0069 | 0 | 0 | 0 | 0 | off_peak | 604.41 |  |  | 0 | 0 | 100 | 0 | 0
823 | 681.99 | 0 | 15.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 681.99 | 0 | 0.05921 | 3.5743 | 0 | 0 | 0 | 0 | off_peak | 681.99 |  |  | 0 | 0 | 100 | 0 | 0
824 | 811.58 | 44.4295 | 16.2 | 7.4256 | 7.4256 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 804.1544 | 0 | 0.05921 | 3.3033 | 0 | 0 | 0 | 7.4256 | off_peak | 804.1544 |  |  | 0.91 | 0 | 99.09 | 24.5289 | 0
825 | 792.97 | 216.455 | 17.2 | 36.0504 | 36.0504 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 756.9196 | 0 | 0.05921 | 3.1065 | 0 | 0 | 0 | 36.0504 | off_peak | 756.9196 |  |  | 4.55 | 0 | 95.45 | 111.9899 | 0
826 | 811.91 | 431.93 | 18.4 | 71.6352 | 71.6352 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 740.2748 | 0 | 0.05921 | 3.0123 | 0 | 0 | 0 | 71.6352 | off_peak | 740.2748 |  |  | 8.82 | 0 | 91.18 | 215.7873 | 0
827 | 805.33 | 584.659 | 19.7 | 96.5219 | 96.5219 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 708.8081 | 0 | 0.05921 | 3.0395 | 0 | 0 | 0 | 96.5219 | off_peak | 708.8081 |  |  | 11.99 | 0 | 88.01 | 293.3776 | 0
828 | 811.89 | 686.857 | 20.7 | 112.9933 | 112.9933 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 698.8967 | 0 | 0.05921 | 3.1561 | 0 | 0 | 0 | 112.9933 | off_peak | 698.8967 |  |  | 13.92 | 0 | 86.08 | 356.6224 | 0
829 | 775.32 | 706.569 | 21.4 | 115.9476 | 115.9476 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 659.3724 | 0 | 0.05921 | 3.4637 | 0 | 0 | 0 | 115.9476 | off_peak | 659.3724 |  |  | 14.95 | 0 | 85.05 | 401.609 | 0
830 | 756.45 | 472.472 | 21.9 | 77.3947 | 77.3947 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 679.0553 | 0 | 0.05921 | 3.9078 | 0 | 0 | 0 | 77.3947 | off_peak | 679.0553 |  |  | 10.23 | 0 | 89.77 | 302.4467 | 0
831 | 709.99 | 464.419 | 22.1 | 76.0213 | 76.0213 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 633.9687 | 0 | 0.05921 | 3.9574 | 0 | 0 | 0 | 76.0213 | off_peak | 633.9687 |  |  | 10.71 | 0 | 89.29 | 300.8461 | 0
832 | 606.17 | 273.029 | 22.1 | 44.6925 | 44.6925 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 561.4775 | 0 | 0.05921 | 3.7826 | 0 | 0 | 0 | 44.6925 | off_peak | 561.4775 |  |  | 7.37 | 0 | 92.63 | 169.0516 | 0
833 | 623.32 | 204.135 | 21.5 | 33.4866 | 33.4866 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 589.8334 | 0 | 0.05921 | 3.6709 | 0 | 0 | 0 | 33.4866 | off_peak | 589.8334 |  |  | 5.37 | 0 | 94.63 | 122.9246 | 0
834 | 560.71 | 58.8526 | 20.8 | 9.6783 | 9.6783 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 551.0317 | 0 | 0.05921 | 3.757 | 0 | 0 | 0 | 9.6783 | off_peak | 551.0317 |  |  | 1.73 | 0 | 98.27 | 36.3615 | 0
835 | 566.52 | 0 | 20.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 566.52 | 0 | 0.05921 | 3.7244 | 0 | 0 | 0 | 0 | off_peak | 566.52 |  |  | 0 | 0 | 100 | 0 | 0
836 | 541.41 | 0 | 20.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 541.41 | 0 | 0.05921 | 3.6201 | 0 | 0 | 0 | 0 | off_peak | 541.41 |  |  | 0 | 0 | 100 | 0 | 0
837 | 507.26 | 0 | 20.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 507.26 | 0 | 0.05921 | 3.6263 | 0 | 0 | 0 | 0 | off_peak | 507.26 |  |  | 0 | 0 | 100 | 0 | 0
838 | 509.91 | 0 | 20.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 509.91 | 0 | 0.05921 | 3.7877 | 0 | 0 | 0 | 0 | off_peak | 509.91 |  |  | 0 | 0 | 100 | 0 | 0
839 | 478.19 | 0 | 20.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 478.19 | 0 | 0.05921 | 3.8821 | 0 | 0 | 0 | 0 | off_peak | 478.19 |  |  | 0 | 0 | 100 | 0 | 0
840 | 479.47 | 0 | 20.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 479.47 | 0 | 0.05921 | 4.3683 | 0 | 0 | 0 | 0 | off_peak | 479.47 |  |  | 0 | 0 | 100 | 0 | 0
841 | 483.24 | 0 | 20.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 483.24 | 0 | 0.05921 | 4.5858 | 0 | 0 | 0 | 0 | off_peak | 483.24 |  |  | 0 | 0 | 100 | 0 | 0
842 | 483.02 | 0 | 19.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 483.02 | 0 | 0.05921 | 4.5374 | 0 | 0 | 0 | 0 | off_peak | 483.02 |  |  | 0 | 0 | 100 | 0 | 0
843 | 455.08 | 0 | 19.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 455.08 | 0 | 0.05921 | 4.3521 | 0 | 0 | 0 | 0 | off_peak | 455.08 |  |  | 0 | 0 | 100 | 0 | 0
844 | 479.94 | 0 | 19.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 479.94 | 0 | 0.05921 | 4.1617 | 0 | 0 | 0 | 0 | off_peak | 479.94 |  |  | 0 | 0 | 100 | 0 | 0
845 | 509.84 | 0 | 19.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 509.84 | 0 | 0.05921 | 3.9502 | 0 | 0 | 0 | 0 | off_peak | 509.84 |  |  | 0 | 0 | 100 | 0 | 0
846 | 633.48 | 0 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 633.48 | 0 | 0.05921 | 3.6557 | 0 | 0 | 0 | 0 | off_peak | 633.48 |  |  | 0 | 0 | 100 | 0 | 0
847 | 725.53 | 0 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 725.53 | 0 | 0.05921 | 3.2936 | 0 | 0 | 0 | 0 | off_peak | 725.53 |  |  | 0 | 0 | 100 | 0 | 0
848 | 721.56 | 44.0446 | 19.7 | 7.2714 | 7.2714 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 714.2886 | 0 | 0.05921 | 3.0046 | 0 | 0 | 0 | 7.2714 | off_peak | 714.2886 |  |  | 1.01 | 0 | 98.99 | 21.8479 | 0
849 | 738.17 | 232.118 | 20.8 | 38.1717 | 38.1717 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 699.9983 | 0 | 0.05921 | 2.8157 | 0 | 0 | 0 | 38.1717 | off_peak | 699.9983 |  |  | 5.17 | 0 | 94.83 | 107.48 | 0
850 | 725.86 | 421.069 | 21.9 | 68.9744 | 68.9744 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 656.8856 | 0 | 0.05921 | 2.732 | 0 | 0 | 0 | 68.9744 | off_peak | 656.8856 |  |  | 9.5 | 0 | 90.5 | 188.4351 | 0
851 | 689.97 | 521.73 | 22.7 | 85.2201 | 85.2201 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 18.9814 | 617.1123 | 0 | 0.05921 | 2.7003 | 0 | 0 | 0 | 85.2201 | off_peak | 604.7499 | 0 | 100 | 12.35 | 0 | 87.65 | 230.1203 | 0
852 | 719.79 | 678.963 | 23.2 | 110.7048 | 110.7048 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18.9814 | 609.0852 | 0 | 0.05921 | 2.7905 | 0 | 0 | 0 | 110.7048 | off_peak | 609.0852 |  |  | 15.38 | 0 | 84.62 | 308.9241 | 0
853 | 651.77 | 679.356 | 23.5 | 110.65 | 110.65 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 30.5453 | 553.4824 | 0 | 0.05921 | 2.9782 | 0 | 0 | 0 | 110.65 | off_peak | 541.12 | 0 | 100 | 16.98 | 0 | 83.02 | 329.541 | 0
854 | 682.65 | 561.42 | 23.7 | 91.3757 | 91.3757 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30.5453 | 591.2743 | 0 | 0.05921 | 3.276 | 0 | 0 | 0 | 91.3757 | off_peak | 591.2743 |  |  | 13.39 | 0 | 86.61 | 299.3459 | 0
855 | 698.96 | 598.416 | 23.8 | 97.3622 | 97.3622 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30.5453 | 601.5978 | 0 | 0.05921 | 3.6748 | 0 | 0 | 0 | 97.3622 | off_peak | 601.5978 |  |  | 13.93 | 0 | 86.07 | 357.7849 | 0
856 | 659.02 | 451.607 | 23.8 | 73.4764 | 73.4764 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30.5453 | 585.5436 | 0 | 0.05921 | 3.9982 | 0 | 0 | 0 | 73.4764 | off_peak | 585.5436 |  |  | 11.15 | 0 | 88.85 | 293.7763 | 0
857 | 655.85 | 259.653 | 23.3 | 42.3212 | 42.3212 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30.5453 | 613.5288 | 0 | 0.05921 | 4.063 | 0 | 0 | 0 | 42.3212 | off_peak | 613.5288 |  |  | 6.45 | 0 | 93.55 | 171.9495 | 0
858 | 617 | 53.9248 | 22.6 | 8.8113 | 8.8113 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30.5453 | 608.1887 | 0 | 0.05921 | 3.9215 | 0 | 0 | 0 | 8.8113 | off_peak | 608.1887 |  |  | 1.43 | 0 | 98.57 | 34.5534 | 0
859 | 577.44 | 0 | 22.3 | 0 | 0 | 0 | 0 | 8.7006 | 8.7006 | 0 | 0 | 0 | 38.684 | 586.1406 | 0 | 0.05921 | 3.9591 | 0 | 0 | 0 | 0 | off_peak | 577.44 | 0 | 100 | 0 | 0 | 100 | 0 | 0
860 | 581.11 | 0 | 21.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 38.684 | 581.11 | 0 | 0.05921 | 4.1491 | 0 | 0 | 0 | 0 | off_peak | 581.11 |  |  | 0 | 0 | 100 | 0 | 0
861 | 549.36 | 0 | 21.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 38.684 | 549.36 | 0 | 0.05921 | 4.363 | 0 | 0 | 0 | 0 | off_peak | 549.36 |  |  | 0 | 0 | 100 | 0 | 0
862 | 539.75 | 0 | 21.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 38.684 | 539.75 | 0 | 0.05921 | 4.3536 | 0 | 0 | 0 | 0 | off_peak | 539.75 |  |  | 0 | 0 | 100 | 0 | 0
863 | 559.92 | 0 | 21.5 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 50.2479 | 572.2824 | 0 | 0.05921 | 4.5217 | 0 | 0 | 0 | 0 | off_peak | 559.92 | 0 | 100 | 0 | 0 | 100 | 0 | 0
864 | 546.53 | 0 | 21.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50.2479 | 546.53 | 0 | 0.05921 | 4.8587 | 0 | 0 | 0 | 0 | off_peak | 546.53 |  |  | 0 | 0 | 100 | 0 | 0
865 | 550.88 | 0 | 21.3 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 61.8119 | 563.2424 | 0 | 0.05921 | 5.105 | 0 | 0 | 0 | 0 | off_peak | 550.88 | 0 | 100 | 0 | 0 | 100 | 0 | 0
866 | 528.21 | 0 | 21.2 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 73.3758 | 540.5724 | 0 | 0.05921 | 5.1079 | 0 | 0 | 0 | 0 | off_peak | 528.21 | 0 | 100 | 0 | 0 | 100 | 0 | 0
867 | 538.36 | 0 | 21.1 | 0 | 0 | 0 | 0 | 0.79843 | 0.79843 | 0 | 0 | 0 | 74.1227 | 539.1584 | 0 | 0.05921 | 4.8069 | 0 | 0 | 0 | 0 | off_peak | 538.36 | 0 | 100 | 0 | 0 | 100 | 0 | 0
868 | 553.13 | 0 | 21 | 0 | 0 | 0 | 0 | 0.051567 | 0.051567 | 0 | 0 | 0 | 74.1709 | 553.1816 | 0 | 0.05921 | 4.4686 | 0 | 0 | 0 | 0 | off_peak | 553.13 | 0 | 100 | 0 | 0 | 100 | 0 | 0
869 | 556.1 | 0 | 20.9 | 0 | 0 | 0 | 0 | 0.0033305 | 0.0033305 | 0 | 0 | 0 | 74.174 | 556.1033 | 0 | 0.05921 | 3.9939 | 0 | 0 | 0 | 0 | off_peak | 556.1 | 0 | 100 | 0 | 0 | 100 | 0 | 0
870 | 670.37 | 0 | 20.7 | 0 | 0 | 0 | 0 | 0.0002151 | 0.0002151 | 0 | 0 | 0 | 74.1742 | 670.3702 | 0 | 0.05921 | 3.5001 | 0 | 0 | 0 | 0 | off_peak | 670.37 | 0 | 100 | 0 | 0 | 100 | 0 | 0
871 | 703.96 | 0 | 20.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1742 | 703.96 | 0 | 0.088511 | 3.0041 | 0 | 0 | 0 | 0 | on_peak | 703.96 |  |  | 0 | 0 | 100 | 0 | 0
872 | 780.33 | 53.396 | 21.5 | 8.7591 | 8.7591 | 0 | 0 | 0 | 0 | 62.4453 | 62.4453 | 0 | 7.4174 | 709.1256 | 0 | 0.088511 | 2.7644 | 0 | 0 | 0 | 8.7591 | on_peak | 709.1256 |  |  | 1.12 | 8 | 90.88 | 24.2138 | 0
873 | 803.24 | 238.161 | 22.5 | 38.9293 | 38.9293 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 764.3107 | 0 | 0.088511 | 2.5479 | 0 | 0 | 0 | 38.9293 | on_peak | 764.3107 |  |  | 4.85 | 0 | 95.15 | 99.1861 | 0
874 | 834.74 | 376.899 | 23.5 | 61.3873 | 61.3873 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 773.3527 | 0 | 0.088511 | 2.507 | 0 | 0 | 0 | 61.3873 | on_peak | 773.3527 |  |  | 7.35 | 0 | 92.65 | 153.8994 | 0
875 | 829.43 | 275.252 | 24 | 44.7514 | 44.7514 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 18.9814 | 797.041 | 0 | 0.05921 | 2.6187 | 0 | 0 | 0 | 44.7514 | off_peak | 784.6786 | 0 | 100 | 5.4 | 0 | 94.6 | 117.1912 | 0
876 | 872.13 | 257.242 | 24.4 | 41.7632 | 41.7632 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 30.5453 | 842.7292 | 0 | 0.05921 | 2.9885 | 0 | 0 | 0 | 41.7632 | off_peak | 830.3668 | 0 | 100 | 4.79 | 0 | 95.21 | 124.8095 | 0
877 | 837.88 | 171.95 | 24.6 | 27.896 | 27.896 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 42.1093 | 822.3464 | 0 | 0.05921 | 3.6003 | 0 | 0 | 0 | 27.896 | off_peak | 809.984 | 0 | 100 | 3.33 | 0 | 96.67 | 100.4331 | 0
878 | 870.9 | 193.712 | 24.7 | 31.4152 | 31.4152 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 53.6732 | 851.8471 | 0 | 0.05921 | 3.9983 | 0 | 0 | 0 | 31.4152 | off_peak | 839.4848 | 0 | 100 | 3.61 | 0 | 96.39 | 125.6068 | 0
879 | 865.94 | 152.95 | 24.7 | 24.8047 | 24.8047 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 65.2371 | 853.4977 | 0 | 0.05921 | 3.7826 | 0 | 0 | 0 | 24.8047 | off_peak | 841.1353 | 0 | 100 | 2.86 | 0 | 97.14 | 93.8258 | 0
880 | 868.87 | 313.392 | 24.5 | 50.8609 | 50.8609 | 0 | 0 | 8.9371 | 8.9371 | 0 | 0 | 0 | 73.597 | 826.9462 | 0 | 0.05921 | 3.431 | 0 | 0 | 0 | 50.8609 | off_peak | 818.0091 | 0 | 100 | 5.85 | 0 | 94.15 | 174.5046 | 0
881 | 862.05 | 233.182 | 24 | 37.9115 | 37.9115 | 0 | 0 | 0.57721 | 0.57721 | 0 | 0 | 0 | 74.137 | 824.7157 | 0 | 0.05921 | 3.2823 | 0 | 0 | 0 | 37.9115 | off_peak | 824.1385 | 0 | 100 | 4.4 | 0 | 95.6 | 124.4359 | 0
882 | 811 | 84.0306 | 23.3 | 13.6963 | 13.6963 | 0 | 0 | 0.037279 | 0.037279 | 0 | 0 | 0 | 74.1718 | 797.341 | 0 | 0.05921 | 3.2819 | 0 | 0 | 0 | 13.6963 | off_peak | 797.3037 | 0 | 100 | 1.69 | 0 | 98.31 | 44.9497 | 0
883 | 785.66 | 0 | 23 | 0 | 0 | 0 | 0 | 0 | 0 | 62.443 | 62.443 | 0 | 7.4174 | 723.217 | 0 | 0.088511 | 3.4289 | 0 | 0 | 0 | 0 | on_peak | 723.217 |  |  | 0 | 7.95 | 92.05 | 0 | 0
884 | 787.98 | 0 | 22.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 787.98 | 0 | 0.088511 | 3.5026 | 0 | 0 | 0 | 0 | on_peak | 787.98 |  |  | 0 | 0 | 100 | 0 | 0
885 | 770.12 | 0 | 22.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 770.12 | 0 | 0.088511 | 3.5807 | 0 | 0 | 0 | 0 | on_peak | 770.12 |  |  | 0 | 0 | 100 | 0 | 0
886 | 754.06 | 0 | 22.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 754.06 | 0 | 0.088511 | 3.93 | 0 | 0 | 0 | 0 | on_peak | 754.06 |  |  | 0 | 0 | 100 | 0 | 0
887 | 787.15 | 0 | 22.1 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 18.9814 | 799.5124 | 0 | 0.05921 | 4.4081 | 0 | 0 | 0 | 0 | off_peak | 787.15 | 0 | 100 | 0 | 0 | 100 | 0 | 0
888 | 744.47 | 0 | 21.9 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 30.5453 | 756.8324 | 0 | 0.05921 | 5.0598 | 0 | 0 | 0 | 0 | off_peak | 744.47 | 0 | 100 | 0 | 0 | 100 | 0 | 0
889 | 730.07 | 0 | 21.8 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 42.1093 | 742.4324 | 0 | 0.05921 | 5.4545 | 0 | 0 | 0 | 0 | off_peak | 730.07 | 0 | 100 | 0 | 0 | 100 | 0 | 0
890 | 627.71 | 0 | 21.8 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 53.6732 | 640.0724 | 0 | 0.05921 | 5.4065 | 0 | 0 | 0 | 0 | off_peak | 627.71 | 0 | 100 | 0 | 0 | 100 | 0 | 0
891 | 618.58 | 0 | 21.7 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 65.2371 | 630.9424 | 0 | 0.05921 | 5.0752 | 0 | 0 | 0 | 0 | off_peak | 618.58 | 0 | 100 | 0 | 0 | 100 | 0 | 0
892 | 574.87 | 0 | 21.6 | 0 | 0 | 0 | 0 | 8.9371 | 8.9371 | 0 | 0 | 0 | 73.597 | 583.8071 | 0 | 0.05921 | 4.6169 | 0 | 0 | 0 | 0 | off_peak | 574.87 | 0 | 100 | 0 | 0 | 100 | 0 | 0
893 | 602.88 | 0 | 21.6 | 0 | 0 | 0 | 0 | 0.57721 | 0.57721 | 0 | 0 | 0 | 74.137 | 603.4572 | 0 | 0.05921 | 4.1116 | 0 | 0 | 0 | 0 | off_peak | 602.88 | 0 | 100 | 0 | 0 | 100 | 0 | 0
894 | 702.73 | 0 | 21.6 | 0 | 0 | 0 | 0 | 0.037279 | 0.037279 | 0 | 0 | 0 | 74.1718 | 702.7673 | 0 | 0.05921 | 3.5113 | 0 | 0 | 0 | 0 | off_peak | 702.73 | 0 | 100 | 0 | 0 | 100 | 0 | 0
895 | 816.77 | 0 | 21.8 | 0 | 0 | 0 | 0 | 0 | 0 | 62.443 | 62.443 | 0 | 7.4174 | 754.327 | 0 | 0.088511 | 2.9714 | 0 | 0 | 0 | 0 | on_peak | 754.327 |  |  | 0 | 7.65 | 92.35 | 0 | 0
896 | 835.04 | 55.8625 | 22.6 | 9.1279 | 9.1279 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 825.9121 | 0 | 0.088511 | 2.7505 | 0 | 0 | 0 | 9.1279 | on_peak | 825.9121 |  |  | 1.09 | 0 | 98.91 | 25.1063 | 0
897 | 879.65 | 195.362 | 23.4 | 31.8309 | 31.8309 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 847.8191 | 0 | 0.088511 | 2.6141 | 0 | 0 | 0 | 31.8309 | on_peak | 847.8191 |  |  | 3.62 | 0 | 96.38 | 83.2083 | 0
898 | 886.82 | 132.377 | 23.8 | 21.5377 | 21.5377 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 865.2823 | 0 | 0.088511 | 2.5656 | 0 | 0 | 0 | 21.5377 | on_peak | 865.2823 |  |  | 2.43 | 0 | 97.57 | 55.2562 | 0
899 | 862.12 | 236.418 | 24.2 | 38.41 | 38.41 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 18.9814 | 836.0724 | 0 | 0.05921 | 2.6773 | 0 | 0 | 0 | 38.41 | off_peak | 823.71 | 0 | 100 | 4.46 | 0 | 95.54 | 102.8353 | 0
900 | 897.07 | 326.977 | 24.5 | 53.0656 | 53.0656 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 30.5453 | 856.3668 | 0 | 0.05921 | 2.9652 | 0 | 0 | 0 | 53.0656 | off_peak | 844.0044 | 0 | 100 | 5.92 | 0 | 94.08 | 157.3504 | 0
901 | 884.46 | 681.619 | 24.6 | 110.5813 | 110.5813 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 42.1093 | 786.2411 | 0 | 0.05921 | 3.587 | 0 | 0 | 0 | 110.5813 | off_peak | 773.8787 | 0 | 100 | 12.5 | 0 | 87.5 | 396.6573 | 0
902 | 861.46 | 698.791 | 24.8 | 113.2856 | 113.2856 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 53.6732 | 760.5367 | 0 | 0.05921 | 3.9318 | 0 | 0 | 0 | 113.2856 | off_peak | 748.1744 | 0 | 100 | 13.15 | 0 | 86.85 | 445.4135 | 0
903 | 893.08 | 585.146 | 24.8 | 94.8619 | 94.8619 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 65.2371 | 810.5805 | 0 | 0.05921 | 3.7767 | 0 | 0 | 0 | 94.8619 | off_peak | 798.2181 | 0 | 100 | 10.62 | 0 | 89.38 | 358.2684 | 0
904 | 831.29 | 455.589 | 24.8 | 73.8586 | 73.8586 | 0 | 0 | 8.9371 | 8.9371 | 0 | 0 | 0 | 73.597 | 766.3686 | 0 | 0.05921 | 3.2653 | 0 | 0 | 0 | 73.8586 | off_peak | 757.4314 | 0 | 100 | 8.88 | 0 | 91.12 | 241.1673 | 0
905 | 831.39 | 245.026 | 24.3 | 39.7942 | 39.7942 | 0 | 0 | 0.57721 | 0.57721 | 0 | 0 | 0 | 74.137 | 792.173 | 0 | 0.05921 | 3.1092 | 0 | 0 | 0 | 39.7942 | off_peak | 791.5958 | 0 | 100 | 4.79 | 0 | 95.21 | 123.7278 | 0
906 | 855.68 | 87.5828 | 23.7 | 14.2548 | 14.2548 | 0 | 0 | 0.037279 | 0.037279 | 0 | 0 | 0 | 74.1718 | 841.4625 | 0 | 0.05921 | 3.1025 | 0 | 0 | 0 | 14.2548 | off_peak | 841.4252 | 0 | 100 | 1.67 | 0 | 98.33 | 44.2254 | 0
907 | 783.68 | 0 | 23.3 | 0 | 0 | 0 | 0 | 0 | 0 | 62.443 | 62.443 | 0 | 7.4174 | 721.237 | 0 | 0.088511 | 3.3014 | 0 | 0 | 0 | 0 | on_peak | 721.237 |  |  | 0 | 7.97 | 92.03 | 0 | 0
908 | 798.97 | 0 | 23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 798.97 | 0 | 0.088511 | 3.455 | 0 | 0 | 0 | 0 | on_peak | 798.97 |  |  | 0 | 0 | 100 | 0 | 0
909 | 786.92 | 0 | 22.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 786.92 | 0 | 0.088511 | 3.6557 | 0 | 0 | 0 | 0 | on_peak | 786.92 |  |  | 0 | 0 | 100 | 0 | 0
910 | 741.8 | 0 | 22.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 741.8 | 0 | 0.088511 | 3.9832 | 0 | 0 | 0 | 0 | on_peak | 741.8 |  |  | 0 | 0 | 100 | 0 | 0
911 | 788.52 | 0 | 22.4 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 18.9814 | 800.8824 | 0 | 0.05921 | 4.3682 | 0 | 0 | 0 | 0 | off_peak | 788.52 | 0 | 100 | 0 | 0 | 100 | 0 | 0
912 | 777.92 | 0 | 22.3 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 30.5453 | 790.2824 | 0 | 0.05921 | 4.9268 | 0 | 0 | 0 | 0 | off_peak | 777.92 | 0 | 100 | 0 | 0 | 100 | 0 | 0
913 | 728.89 | 0 | 22.1 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 42.1093 | 741.2524 | 0 | 0.05921 | 5.1964 | 0 | 0 | 0 | 0 | off_peak | 728.89 | 0 | 100 | 0 | 0 | 100 | 0 | 0
914 | 650.92 | 0 | 22 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 53.6732 | 663.2824 | 0 | 0.05921 | 5.1512 | 0 | 0 | 0 | 0 | off_peak | 650.92 | 0 | 100 | 0 | 0 | 100 | 0 | 0
915 | 568.13 | 0 | 21.8 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 65.2371 | 580.4924 | 0 | 0.05921 | 4.9242 | 0 | 0 | 0 | 0 | off_peak | 568.13 | 0 | 100 | 0 | 0 | 100 | 0 | 0
916 | 586.59 | 0 | 21.7 | 0 | 0 | 0 | 0 | 8.9371 | 8.9371 | 0 | 0 | 0 | 73.597 | 595.5271 | 0 | 0.05921 | 4.518 | 0 | 0 | 0 | 0 | off_peak | 586.59 | 0 | 100 | 0 | 0 | 100 | 0 | 0
917 | 614.23 | 0 | 21.6 | 0 | 0 | 0 | 0 | 0.57721 | 0.57721 | 0 | 0 | 0 | 74.137 | 614.8072 | 0 | 0.05921 | 12.2935 | 0 | 0 | 0 | 0 | off_peak | 614.23 | 0 | 100 | 0 | 0 | 100 | 0 | 0
918 | 697.39 | 0 | 21.6 | 0 | 0 | 0 | 0 | 0.037279 | 0.037279 | 0 | 0 | 0 | 74.1718 | 697.4273 | 0 | 0.05921 | 11.9587 | 0 | 0 | 0 | 0 | off_peak | 697.39 | 0 | 100 | 0 | 0 | 100 | 0 | 0
919 | 755.29 | 0 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 62.443 | 62.443 | 0 | 7.4174 | 692.847 | 0 | 0.088511 | 3.0071 | 0 | 0 | 0 | 0 | on_peak | 692.847 |  |  | 0 | 8.27 | 91.73 | 0 | 0
920 | 809.44 | 61.9544 | 22.8 | 10.1161 | 10.1161 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 799.3239 | 0 | 0.088511 | 2.75 | 0 | 0 | 0 | 10.1161 | on_peak | 799.3239 |  |  | 1.25 | 0 | 98.75 | 27.8193 | 0
921 | 830.4 | 256.553 | 23.7 | 41.7561 | 41.7561 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 788.6439 | 0 | 0.088511 | 2.571 | 0 | 0 | 0 | 41.7561 | on_peak | 788.6439 |  |  | 5.03 | 0 | 94.97 | 107.3557 | 0
922 | 836.11 | 451.295 | 24.5 | 73.2414 | 73.2414 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 762.8686 | 0 | 0.088511 | 2.4885 | 0 | 0 | 0 | 73.2414 | on_peak | 762.8686 |  |  | 8.76 | 0 | 91.24 | 182.262 | 0
923 | 789.08 | 599.55 | 25.2 | 97.0572 | 97.0572 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 18.9814 | 704.3852 | 0 | 0.05921 | 2.5218 | 0 | 0 | 0 | 97.0572 | off_peak | 692.0228 | 0 | 100 | 12.3 | 0 | 87.7 | 244.7581 | 0
924 | 888.36 | 712.999 | 25.7 | 115.2148 | 115.2148 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 30.5453 | 785.5076 | 0 | 0.05921 | 2.8492 | 0 | 0 | 0 | 115.2148 | off_peak | 773.1452 | 0 | 100 | 12.97 | 0 | 87.03 | 328.2656 | 0
925 | 827.72 | 742.828 | 26 | 119.9049 | 119.9049 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 42.1093 | 720.1775 | 0 | 0.05921 | 3.401 | 0 | 0 | 0 | 119.9049 | off_peak | 707.8151 | 0 | 100 | 14.49 | 0 | 85.51 | 407.7974 | 0
926 | 870.51 | 724.495 | 26.2 | 116.8612 | 116.8612 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 53.6732 | 766.0112 | 0 | 0.05921 | 3.7096 | 0 | 0 | 0 | 116.8612 | off_peak | 753.6488 | 0 | 100 | 13.42 | 0 | 86.58 | 433.5096 | 0
927 | 889.63 | 630.582 | 26.3 | 101.6762 | 101.6762 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 65.2371 | 800.3162 | 0 | 0.05921 | 3.5506 | 0 | 0 | 0 | 101.6762 | off_peak | 787.9538 | 0 | 100 | 11.43 | 0 | 88.57 | 361.0133 | 0
928 | 871.21 | 481.144 | 26.2 | 77.6086 | 77.6086 | 0 | 0 | 8.9371 | 8.9371 | 0 | 0 | 0 | 73.597 | 802.5385 | 0 | 0.05921 | 3.2438 | 0 | 0 | 0 | 77.6086 | off_peak | 793.6014 | 0 | 100 | 8.91 | 0 | 91.09 | 251.7489 | 0
929 | 863.54 | 290.715 | 25.8 | 46.9602 | 46.9602 | 0 | 0 | 0.57721 | 0.57721 | 0 | 0 | 0 | 74.137 | 817.157 | 0 | 0.05921 | 3.2048 | 0 | 0 | 0 | 46.9602 | off_peak | 816.5798 | 0 | 100 | 5.44 | 0 | 94.56 | 150.5001 | 0
930 | 866.25 | 91.8892 | 25.1 | 14.8807 | 14.8807 | 0 | 0 | 0.037279 | 0.037279 | 0 | 0 | 0 | 74.1718 | 851.4066 | 0 | 0.05921 | 3.2975 | 0 | 0 | 0 | 14.8807 | off_peak | 851.3693 | 0 | 100 | 1.72 | 0 | 98.28 | 49.069 | 0
931 | 816.2 | 0 | 24.7 | 0 | 0 | 0 | 0 | 0 | 0 | 62.443 | 62.443 | 0 | 7.4174 | 753.757 | 0 | 0.088511 | 3.5113 | 0 | 0 | 0 | 0 | on_peak | 753.757 |  |  | 0 | 7.65 | 92.35 | 0 | 0
932 | 813.09 | 0 | 24.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 813.09 | 0 | 0.088511 | 3.7752 | 0 | 0 | 0 | 0 | on_peak | 813.09 |  |  | 0 | 0 | 100 | 0 | 0
933 | 797.7 | 0 | 23.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 797.7 | 0 | 0.088511 | 4.0737 | 0 | 0 | 0 | 0 | on_peak | 797.7 |  |  | 0 | 0 | 100 | 0 | 0
934 | 780.3 | 0 | 22.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 780.3 | 0 | 0.088511 | 4.309 | 0 | 0 | 0 | 0 | on_peak | 780.3 |  |  | 0 | 0 | 100 | 0 | 0
935 | 818.98 | 0 | 22.1 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 18.9814 | 831.3424 | 0 | 0.05921 | 4.7748 | 0 | 0 | 0 | 0 | off_peak | 818.98 | 0 | 100 | 0 | 0 | 100 | 0 | 0
936 | 776.05 | 0 | 21.5 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 30.5453 | 788.4124 | 0 | 0.05921 | 5.2197 | 0 | 0 | 0 | 0 | off_peak | 776.05 | 0 | 100 | 0 | 0 | 100 | 0 | 0
937 | 766.23 | 0 | 21 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 42.1093 | 778.5924 | 0 | 0.05921 | 5.4373 | 0 | 0 | 0 | 0 | off_peak | 766.23 | 0 | 100 | 0 | 0 | 100 | 0 | 0
938 | 689.91 | 0 | 20.7 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 53.6732 | 702.2724 | 0 | 0.05921 | 5.3795 | 0 | 0 | 0 | 0 | off_peak | 689.91 | 0 | 100 | 0 | 0 | 100 | 0 | 0
939 | 573.26 | 0 | 20.6 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 65.2371 | 585.6224 | 0 | 0.05921 | 5.0135 | 0 | 0 | 0 | 0 | off_peak | 573.26 | 0 | 100 | 0 | 0 | 100 | 0 | 0
940 | 573.41 | 0 | 20.6 | 0 | 0 | 0 | 0 | 8.9371 | 8.9371 | 0 | 0 | 0 | 73.597 | 582.3471 | 0 | 0.05921 | 4.7688 | 0 | 0 | 0 | 0 | off_peak | 573.41 | 0 | 100 | 0 | 0 | 100 | 0 | 0
941 | 607.17 | 0 | 20.8 | 0 | 0 | 0 | 0 | 0.57721 | 0.57721 | 0 | 0 | 0 | 74.137 | 607.7472 | 0 | 0.05921 | 4.2307 | 0 | 0 | 0 | 0 | off_peak | 607.17 | 0 | 100 | 0 | 0 | 100 | 0 | 0
942 | 702.58 | 0 | 21 | 0 | 0 | 0 | 0 | 0.037279 | 0.037279 | 0 | 0 | 0 | 74.1718 | 702.6173 | 0 | 0.05921 | 3.659 | 0 | 0 | 0 | 0 | off_peak | 702.58 | 0 | 100 | 0 | 0 | 100 | 0 | 0
943 | 852.41 | 0 | 21.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1718 | 852.41 | 0 | 0.088511 | 3.1136 | 0 | 0 | 0 | 0 | on_peak | 852.41 |  |  | 0 | 0 | 100 | 0 | 0
944 | 819.55 | 61.5273 | 22.3 | 10.0643 | 10.0643 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1718 | 809.4857 | 0 | 0.088511 | 2.8287 | 0 | 0 | 0 | 10.0643 | on_peak | 809.4857 |  |  | 1.23 | 0 | 98.77 | 28.4694 | 0
945 | 864.82 | 253.686 | 23.1 | 41.3782 | 41.3782 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1718 | 823.4418 | 0 | 0.088511 | 2.6465 | 0 | 0 | 0 | 41.3782 | on_peak | 823.4418 |  |  | 4.78 | 0 | 95.22 | 109.5089 | 0
946 | 837.1 | 449.08 | 23.8 | 73.0652 | 73.0652 | 0 | 0 | 0 | 0 | 62.443 | 62.443 | 0 | 7.4174 | 701.5917 | 0 | 0.088511 | 2.5624 | 0 | 0 | 0 | 73.0652 | on_peak | 701.5917 |  |  | 8.73 | 7.46 | 83.81 | 187.2198 | 0
947 | 855.69 | 595.423 | 24.4 | 96.6669 | 96.6669 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 18.9814 | 771.3855 | 0 | 0.05921 | 2.5923 | 0 | 0 | 0 | 96.6669 | off_peak | 759.0231 | 0 | 100 | 11.3 | 0 | 88.7 | 250.5872 | 0
948 | 886.27 | 632.218 | 24.7 | 102.5299 | 102.5299 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 30.5453 | 796.1024 | 0 | 0.05921 | 2.932 | 0 | 0 | 0 | 102.5299 | off_peak | 783.7401 | 0 | 100 | 11.57 | 0 | 88.43 | 300.6162 | 0
949 | 817.97 | 624.489 | 24.8 | 101.2401 | 101.2401 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 42.1093 | 729.0923 | 0 | 0.05921 | 3.4999 | 0 | 0 | 0 | 101.2401 | off_peak | 716.7299 | 0 | 100 | 12.38 | 0 | 87.62 | 354.3325 | 0
950 | 876.25 | 688.706 | 24.7 | 111.6909 | 111.6909 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 53.6732 | 776.9215 | 0 | 0.05921 | 3.8426 | 0 | 0 | 0 | 111.6909 | off_peak | 764.5591 | 0 | 100 | 12.75 | 0 | 87.25 | 429.1809 | 0
951 | 944.88 | 625.196 | 24.5 | 101.4641 | 101.4641 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 65.2371 | 855.7783 | 0 | 0.05921 | 3.7688 | 0 | 0 | 0 | 101.4641 | off_peak | 843.4159 | 0 | 100 | 10.74 | 0 | 89.26 | 382.4023 | 0
952 | 884.55 | 484.756 | 24.1 | 78.7849 | 78.7849 | 0 | 0 | 8.9371 | 8.9371 | 0 | 0 | 0 | 73.597 | 814.7022 | 0 | 0.05921 | 3.7085 | 0 | 0 | 0 | 78.7849 | off_peak | 805.7651 | 0 | 100 | 8.91 | 0 | 91.09 | 292.1768 | 0
953 | 914.41 | 276.391 | 23.6 | 45.001 | 45.001 | 0 | 0 | 0.57721 | 0.57721 | 0 | 0 | 0 | 74.137 | 869.9862 | 0 | 0.05921 | 3.7886 | 0 | 0 | 0 | 45.001 | off_peak | 869.409 | 0 | 100 | 4.92 | 0 | 95.08 | 170.4909 | 0
954 | 866.78 | 93.8254 | 23 | 15.3092 | 15.3092 | 0 | 0 | 0.037279 | 0.037279 | 0 | 0 | 0 | 74.1718 | 851.5081 | 0 | 0.05921 | 4.1058 | 0 | 0 | 0 | 15.3092 | off_peak | 851.4708 | 0 | 100 | 1.77 | 0 | 98.23 | 62.857 | 0
955 | 863.62 | 0 | 22.8 | 0 | 0 | 0 | 0 | 0 | 0 | 62.443 | 62.443 | 0 | 7.4174 | 801.177 | 0 | 0.088511 | 4.4899 | 0 | 0 | 0 | 0 | on_peak | 801.177 |  |  | 0 | 7.23 | 92.77 | 0 | 0
956 | 865.39 | 0 | 22.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 865.39 | 0 | 0.088511 | 4.7808 | 0 | 0 | 0 | 0 | on_peak | 865.39 |  |  | 0 | 0 | 100 | 0 | 0
957 | 838.14 | 0 | 22.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 838.14 | 0 | 0.088511 | 4.9776 | 0 | 0 | 0 | 0 | on_peak | 838.14 |  |  | 0 | 0 | 100 | 0 | 0
958 | 797.02 | 0 | 22.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 797.02 | 0 | 0.088511 | 5.2517 | 0 | 0 | 0 | 0 | on_peak | 797.02 |  |  | 0 | 0 | 100 | 0 | 0
959 | 839.79 | 0 | 22.1 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 18.9814 | 852.1524 | 0 | 0.05921 | 5.6845 | 0 | 0 | 0 | 0 | off_peak | 839.79 | 0 | 100 | 0 | 0 | 100 | 0 | 0
960 | 790.73 | 0 | 21.9 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 30.5453 | 803.0924 | 0 | 0.05921 | 5.8442 | 0 | 0 | 0 | 0 | off_peak | 790.73 | 0 | 100 | 0 | 0 | 100 | 0 | 0
961 | 817.45 | 0 | 21.8 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 42.1093 | 829.8124 | 0 | 0.05921 | 5.9092 | 0 | 0 | 0 | 0 | off_peak | 817.45 | 0 | 100 | 0 | 0 | 100 | 0 | 0
962 | 677 | 0 | 21.7 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 53.6732 | 689.3624 | 0 | 0.05921 | 5.8353 | 0 | 0 | 0 | 0 | off_peak | 677 | 0 | 100 | 0 | 0 | 100 | 0 | 0
963 | 610.19 | 0 | 21.6 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 65.2371 | 622.5524 | 0 | 0.05921 | 5.4627 | 0 | 0 | 0 | 0 | off_peak | 610.19 | 0 | 100 | 0 | 0 | 100 | 0 | 0
964 | 631.31 | 0 | 21.5 | 0 | 0 | 0 | 0 | 8.9371 | 8.9371 | 0 | 0 | 0 | 73.597 | 640.2471 | 0 | 0.05921 | 5.1601 | 0 | 0 | 0 | 0 | off_peak | 631.31 | 0 | 100 | 0 | 0 | 100 | 0 | 0
965 | 626.74 | 0 | 21.5 | 0 | 0 | 0 | 0 | 0.57721 | 0.57721 | 0 | 0 | 0 | 74.137 | 627.3172 | 0 | 0.05921 | 4.6295 | 0 | 0 | 0 | 0 | off_peak | 626.74 | 0 | 100 | 0 | 0 | 100 | 0 | 0
966 | 726.8 | 0 | 21.4 | 0 | 0 | 0 | 0 | 0.037279 | 0.037279 | 0 | 0 | 0 | 74.1718 | 726.8373 | 0 | 0.05921 | 3.9984 | 0 | 0 | 0 | 0 | off_peak | 726.8 | 0 | 100 | 0 | 0 | 100 | 0 | 0
967 | 779.84 | 0 | 21.7 | 0 | 0 | 0 | 0 | 0 | 0 | 62.443 | 62.443 | 0 | 7.4174 | 717.397 | 0 | 0.088511 | 3.5279 | 0 | 0 | 0 | 0 | on_peak | 717.397 |  |  | 0 | 8.01 | 91.99 | 0 | 0
968 | 814.58 | 64.452 | 22.4 | 10.539 | 10.539 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 804.041 | 0 | 0.088511 | 3.152 | 0 | 0 | 0 | 10.539 | on_peak | 804.041 |  |  | 1.29 | 0 | 98.71 | 33.2186 | 0
969 | 818 | 255.019 | 23 | 41.6105 | 41.6105 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 776.3895 | 0 | 0.088511 | 2.9032 | 0 | 0 | 0 | 41.6105 | on_peak | 776.3895 |  |  | 5.09 | 0 | 94.91 | 120.8048 | 0
970 | 845.38 | 340.053 | 23.3 | 55.4257 | 55.4257 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 789.9543 | 0 | 0.088511 | 2.7637 | 0 | 0 | 0 | 55.4257 | on_peak | 789.9543 |  |  | 6.56 | 0 | 93.44 | 153.1794 | 0
971 | 873.47 | 495.091 | 23.6 | 80.609 | 80.609 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 18.9814 | 805.2234 | 0 | 0.05921 | 2.7813 | 0 | 0 | 0 | 80.609 | off_peak | 792.861 | 0 | 100 | 9.23 | 0 | 90.77 | 224.196 | 0
972 | 916.21 | 425.917 | 23.8 | 69.2966 | 69.2966 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 30.5453 | 859.2757 | 0 | 0.05921 | 3.0369 | 0 | 0 | 0 | 69.2966 | off_peak | 846.9134 | 0 | 100 | 7.56 | 0 | 92.44 | 210.4488 | 0
973 | 886.06 | 667.568 | 23.9 | 108.5743 | 108.5743 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 42.1093 | 789.8481 | 0 | 0.05921 | 3.5568 | 0 | 0 | 0 | 108.5743 | off_peak | 777.4857 | 0 | 100 | 12.25 | 0 | 87.75 | 386.1738 | 0
974 | 939.49 | 640.695 | 23.9 | 104.2036 | 104.2036 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 53.6732 | 847.6488 | 0 | 0.05921 | 3.9014 | 0 | 0 | 0 | 104.2036 | off_peak | 835.2864 | 0 | 100 | 11.09 | 0 | 88.91 | 406.5371 | 0
975 | 956.04 | 556.813 | 23.8 | 90.5934 | 90.5934 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 65.2371 | 877.809 | 0 | 0.05921 | 3.9816 | 0 | 0 | 0 | 90.5934 | off_peak | 865.4466 | 0 | 100 | 9.48 | 0 | 90.52 | 360.7106 | 0
976 | 936.21 | 335.495 | 23.5 | 54.6437 | 54.6437 | 0 | 0 | 8.9371 | 8.9371 | 0 | 0 | 0 | 73.597 | 890.5034 | 0 | 0.05921 | 4.0877 | 0 | 0 | 0 | 54.6437 | off_peak | 881.5663 | 0 | 100 | 5.84 | 0 | 94.16 | 223.368 | 0
977 | 922.76 | 277.854 | 23.1 | 45.3202 | 45.3202 | 0 | 0 | 0.57721 | 0.57721 | 0 | 0 | 0 | 74.137 | 878.017 | 0 | 0.05921 | 4.3219 | 0 | 0 | 0 | 45.3202 | off_peak | 877.4398 | 0 | 100 | 4.91 | 0 | 95.09 | 195.87 | 0
978 | 929.14 | 96.1262 | 22.8 | 15.6958 | 15.6958 | 0 | 0 | 0.037279 | 0.037279 | 0 | 0 | 0 | 74.1718 | 913.4815 | 0 | 0.05921 | 4.5704 | 0 | 0 | 0 | 15.6958 | off_peak | 913.4442 | 0 | 100 | 1.69 | 0 | 98.31 | 71.7353 | 0
979 | 900.59 | 0 | 22.6 | 0 | 0 | 0 | 0 | 0 | 0 | 22.7143 | 22.7143 | 0 | 49.8892 | 877.8757 | 0 | 0.088511 | 4.8065 | 0 | 0 | 0 | 0 | on_peak | 877.8757 |  |  | 0 | 2.52 | 97.48 | 0 | 0
980 | 902.37 | 0 | 22.5 | 0 | 0 | 0 | 0 | 0 | 0 | 24.4943 | 24.4943 | 0 | 23.7036 | 877.8757 | 0 | 0.088511 | 5.2167 | 0 | 0 | 0 | 0 | on_peak | 877.8757 |  |  | 0 | 2.71 | 97.29 | 0 | 0
981 | 893.11 | 0 | 22.4 | 0 | 0 | 0 | 0 | 0 | 0 | 15.2343 | 15.2343 | 0 | 7.4174 | 877.8757 | 0 | 0.088511 | 5.6789 | 0 | 0 | 0 | 0 | on_peak | 877.8757 |  |  | 0 | 1.71 | 98.29 | 0 | 0
982 | 858.5 | 0 | 22.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 858.5 | 0 | 0.088511 | 5.9645 | 0 | 0 | 0 | 0 | on_peak | 858.5 |  |  | 0 | 0 | 100 | 0 | 0
983 | 842.12 | 0 | 22.1 | 0 | 0 | 0 | 0 | 8.7006 | 8.7006 | 0 | 0 | 0 | 15.5561 | 850.8206 | 0 | 0.05921 | 6.1351 | 0 | 0 | 0 | 0 | off_peak | 842.12 | 0 | 100 | 0 | 0 | 100 | 0 | 0
984 | 859.88 | 0 | 21.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15.5561 | 859.88 | 0 | 0.05921 | 6.2342 | 0 | 0 | 0 | 0 | off_peak | 859.88 |  |  | 0 | 0 | 100 | 0 | 0
985 | 800.45 | 0 | 21.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15.5561 | 800.45 | 0 | 0.05921 | 6.1814 | 0 | 0 | 0 | 0 | off_peak | 800.45 |  |  | 0 | 0 | 100 | 0 | 0
986 | 687.42 | 0 | 21.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15.5561 | 687.42 | 0 | 0.05921 | 5.8417 | 0 | 0 | 0 | 0 | off_peak | 687.42 |  |  | 0 | 0 | 100 | 0 | 0
987 | 664.44 | 0 | 21.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15.5561 | 664.44 | 0 | 0.05921 | 5.448 | 0 | 0 | 0 | 0 | off_peak | 664.44 |  |  | 0 | 0 | 100 | 0 | 0
988 | 661.38 | 0 | 21.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15.5561 | 661.38 | 0 | 0.05921 | 4.9546 | 0 | 0 | 0 | 0 | off_peak | 661.38 |  |  | 0 | 0 | 100 | 0 | 0
989 | 694.5 | 0 | 21.4 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 27.12 | 706.8624 | 0 | 0.05921 | 4.5388 | 0 | 0 | 0 | 0 | off_peak | 694.5 | 0 | 100 | 0 | 0 | 100 | 0 | 0
990 | 783.43 | 0 | 21.5 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 38.684 | 795.7924 | 0 | 0.05921 | 4.0703 | 0 | 0 | 0 | 0 | off_peak | 783.43 | 0 | 100 | 0 | 0 | 100 | 0 | 0
991 | 848.33 | 0 | 21.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 38.684 | 848.33 | 0 | 0.05921 | 3.6269 | 0 | 0 | 0 | 0 | off_peak | 848.33 |  |  | 0 | 0 | 100 | 0 | 0
992 | 804.41 | 61.9107 | 22.7 | 10.1126 | 10.1126 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 38.684 | 794.2974 | 0 | 0.05921 | 3.2595 | 0 | 0 | 0 | 10.1126 | off_peak | 794.2974 |  |  | 1.26 | 0 | 98.74 | 32.9623 | 0
993 | 792.68 | 173.32 | 23.4 | 28.2396 | 28.2396 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 38.684 | 764.4404 | 0 | 0.05921 | 2.9814 | 0 | 0 | 0 | 28.2396 | off_peak | 764.4404 |  |  | 3.56 | 0 | 96.44 | 84.193 | 0
994 | 748.07 | 348.6 | 23.9 | 56.6968 | 56.6968 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 38.684 | 691.3732 | 0 | 0.05921 | 2.8385 | 0 | 0 | 0 | 56.6968 | off_peak | 691.3732 |  |  | 7.58 | 0 | 92.42 | 160.9342 | 0
995 | 765.96 | 436.589 | 24.3 | 70.9057 | 70.9057 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 38.684 | 695.0543 | 0 | 0.05921 | 2.776 | 0 | 0 | 0 | 70.9057 | off_peak | 695.0543 |  |  | 9.26 | 0 | 90.74 | 196.8357 | 0
996 | 794.42 | 360.349 | 24.5 | 58.4816 | 58.4816 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 38.684 | 735.9384 | 0 | 0.05921 | 2.8564 | 0 | 0 | 0 | 58.4816 | off_peak | 735.9384 |  |  | 7.36 | 0 | 92.64 | 167.047 | 0
997 | 777.69 | 647.387 | 24.7 | 104.99 | 104.99 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 38.684 | 672.7 | 0 | 0.05921 | 3.0662 | 0 | 0 | 0 | 104.99 | off_peak | 672.7 |  |  | 13.5 | 0 | 86.5 | 321.9187 | 0
998 | 787.9 | 560.852 | 24.8 | 90.9234 | 90.9234 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 38.684 | 696.9766 | 0 | 0.05921 | 3.3615 | 0 | 0 | 0 | 90.9234 | off_peak | 696.9766 |  |  | 11.54 | 0 | 88.46 | 305.6413 | 0
999 | 733.47 | 342.61 | 24.7 | 55.5628 | 55.5628 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 38.684 | 677.9072 | 0 | 0.05921 | 3.7989 | 0 | 0 | 0 | 55.5628 | off_peak | 677.9072 |  |  | 7.58 | 0 | 92.42 | 211.0797 | 0
1000 | 737.62 | 311.139 | 24.5 | 50.4952 | 50.4952 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 38.684 | 687.1248 | 0 | 0.05921 | 4.1966 | 0 | 0 | 0 | 50.4952 | off_peak | 687.1248 |  |  | 6.85 | 0 | 93.15 | 211.9094 | 0
1001 | 729.8 | 263.935 | 24.1 | 42.896 | 42.896 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 38.684 | 686.904 | 0 | 0.05921 | 4.589 | 0 | 0 | 0 | 42.896 | off_peak | 686.904 |  |  | 5.88 | 0 | 94.12 | 196.8487 | 0
1002 | 659.51 | 92.6034 | 23.5 | 15.0828 | 15.0828 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 38.684 | 644.4272 | 0 | 0.05921 | 4.9279 | 0 | 0 | 0 | 15.0828 | off_peak | 644.4272 |  |  | 2.29 | 0 | 97.71 | 74.3268 | 0
1003 | 633.22 | 0 | 23.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 38.684 | 633.22 | 0 | 0.05921 | 5.2089 | 0 | 0 | 0 | 0 | off_peak | 633.22 |  |  | 0 | 0 | 100 | 0 | 0
1004 | 612.91 | 0 | 23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 38.684 | 612.91 | 0 | 0.05921 | 5.5203 | 0 | 0 | 0 | 0 | off_peak | 612.91 |  |  | 0 | 0 | 100 | 0 | 0
1005 | 631.27 | 0 | 22.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 38.684 | 631.27 | 0 | 0.05921 | 5.7024 | 0 | 0 | 0 | 0 | off_peak | 631.27 |  |  | 0 | 0 | 100 | 0 | 0
1006 | 626.65 | 0 | 22.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 38.684 | 626.65 | 0 | 0.05921 | 5.8325 | 0 | 0 | 0 | 0 | off_peak | 626.65 |  |  | 0 | 0 | 100 | 0 | 0
1007 | 583.94 | 0 | 22.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 38.684 | 583.94 | 0 | 0.05921 | 6.11 | 0 | 0 | 0 | 0 | off_peak | 583.94 |  |  | 0 | 0 | 100 | 0 | 0
1008 | 629.35 | 0 | 22.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 38.684 | 629.35 | 0 | 0.05921 | 6.0581 | 0 | 0 | 0 | 0 | off_peak | 629.35 |  |  | 0 | 0 | 100 | 0 | 0
1009 | 573.35 | 0 | 22.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 38.684 | 573.35 | 0 | 0.05921 | 5.9712 | 0 | 0 | 0 | 0 | off_peak | 573.35 |  |  | 0 | 0 | 100 | 0 | 0
1010 | 599.15 | 0 | 22.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 38.684 | 599.15 | 0 | 0.05921 | 5.9081 | 0 | 0 | 0 | 0 | off_peak | 599.15 |  |  | 0 | 0 | 100 | 0 | 0
1011 | 606.22 | 0 | 22.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 38.684 | 606.22 | 0 | 0.05921 | 5.5384 | 0 | 0 | 0 | 0 | off_peak | 606.22 |  |  | 0 | 0 | 100 | 0 | 0
1012 | 576.55 | 0 | 22.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 38.684 | 576.55 | 0 | 0.05921 | 5.1019 | 0 | 0 | 0 | 0 | off_peak | 576.55 |  |  | 0 | 0 | 100 | 0 | 0
1013 | 634.16 | 0 | 22.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 38.684 | 634.16 | 0 | 0.05921 | 4.7399 | 0 | 0 | 0 | 0 | off_peak | 634.16 |  |  | 0 | 0 | 100 | 0 | 0
1014 | 663.36 | 0 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 38.684 | 663.36 | 0 | 0.05921 | 4.2993 | 0 | 0 | 0 | 0 | off_peak | 663.36 |  |  | 0 | 0 | 100 | 0 | 0
1015 | 707.07 | 0 | 22.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 38.684 | 707.07 | 0 | 0.05921 | 3.8948 | 0 | 0 | 0 | 0 | off_peak | 707.07 |  |  | 0 | 0 | 100 | 0 | 0
1016 | 731.91 | 67.4486 | 23.4 | 10.9896 | 10.9896 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 38.684 | 720.9204 | 0 | 0.05921 | 3.5363 | 0 | 0 | 0 | 10.9896 | off_peak | 720.9204 |  |  | 1.5 | 0 | 98.5 | 38.8631 | 0
1017 | 749.85 | 265.992 | 24.2 | 43.2148 | 43.2148 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 38.684 | 706.6352 | 0 | 0.05921 | 3.2406 | 0 | 0 | 0 | 43.2148 | off_peak | 706.6352 |  |  | 5.76 | 0 | 94.24 | 140.0419 | 0
1018 | 732.83 | 464.045 | 24.8 | 75.2294 | 75.2294 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 38.684 | 657.6006 | 0 | 0.05921 | 3.0169 | 0 | 0 | 0 | 75.2294 | off_peak | 657.6006 |  |  | 10.27 | 0 | 89.73 | 226.9574 | 0
1019 | 719.27 | 612.793 | 25.3 | 99.1653 | 99.1653 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 38.684 | 620.1047 | 0 | 0.05921 | 2.9149 | 0 | 0 | 0 | 99.1653 | off_peak | 620.1047 |  |  | 13.79 | 0 | 86.21 | 289.0554 | 0
1020 | 703.21 | 664.851 | 25.6 | 107.4732 | 107.4732 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 38.684 | 595.7368 | 0 | 0.05921 | 2.9055 | 0 | 0 | 0 | 107.4732 | off_peak | 595.7368 |  |  | 15.28 | 0 | 84.72 | 312.2584 | 0
1021 | 736.46 | 598.834 | 25.8 | 96.7317 | 96.7317 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 38.684 | 639.7283 | 0 | 0.05921 | 2.9918 | 0 | 0 | 0 | 96.7317 | off_peak | 639.7283 |  |  | 13.13 | 0 | 86.87 | 289.4046 | 0
1022 | 627.79 | 711.849 | 26 | 114.9044 | 114.9044 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 38.684 | 512.8856 | 0 | 0.05921 | 3.24 | 0 | 0 | 0 | 114.9044 | off_peak | 512.8856 |  |  | 18.3 | 0 | 81.7 | 372.2942 | 0
1023 | 692.05 | 643.827 | 26 | 103.9245 | 103.9245 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 38.684 | 588.1255 | 0 | 0.05921 | 3.4752 | 0 | 0 | 0 | 103.9245 | off_peak | 588.1255 |  |  | 15.02 | 0 | 84.98 | 361.1571 | 0
1024 | 625.02 | 491.334 | 25.9 | 79.3382 | 79.3382 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 38.684 | 545.6818 | 0 | 0.05921 | 3.6233 | 0 | 0 | 0 | 79.3382 | off_peak | 545.6818 |  |  | 12.69 | 0 | 87.31 | 287.4689 | 0
1025 | 620.1 | 298.519 | 25.4 | 48.2904 | 48.2904 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 38.684 | 571.8096 | 0 | 0.05921 | 3.8571 | 0 | 0 | 0 | 48.2904 | off_peak | 571.8096 |  |  | 7.79 | 0 | 92.21 | 186.2633 | 0
1026 | 601.83 | 97.1824 | 24.8 | 15.7549 | 15.7549 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 38.684 | 586.0751 | 0 | 0.05921 | 3.9069 | 0 | 0 | 0 | 15.7549 | off_peak | 586.0751 |  |  | 2.62 | 0 | 97.38 | 61.5525 | 0
1027 | 562.92 | 0 | 24.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 38.684 | 562.92 | 0 | 0.05921 | 3.7848 | 0 | 0 | 0 | 0 | off_peak | 562.92 |  |  | 0 | 0 | 100 | 0 | 0
1028 | 557.13 | 0 | 23.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 38.684 | 557.13 | 0 | 0.05921 | 3.7468 | 0 | 0 | 0 | 0 | off_peak | 557.13 |  |  | 0 | 0 | 100 | 0 | 0
1029 | 557.89 | 0 | 23.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 38.684 | 557.89 | 0 | 0.05921 | 3.7434 | 0 | 0 | 0 | 0 | off_peak | 557.89 |  |  | 0 | 0 | 100 | 0 | 0
1030 | 520.15 | 0 | 23.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 38.684 | 520.15 | 0 | 0.05921 | 3.7348 | 0 | 0 | 0 | 0 | off_peak | 520.15 |  |  | 0 | 0 | 100 | 0 | 0
1031 | 556.63 | 0 | 23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 38.684 | 556.63 | 0 | 0.05921 | 4.0092 | 0 | 0 | 0 | 0 | off_peak | 556.63 |  |  | 0 | 0 | 100 | 0 | 0
1032 | 535.61 | 0 | 23 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 50.2479 | 547.9724 | 0 | 0.05921 | 4.5225 | 0 | 0 | 0 | 0 | off_peak | 535.61 | 0 | 100 | 0 | 0 | 100 | 0 | 0
1033 | 538.08 | 0 | 23 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 61.8119 | 550.4424 | 0 | 0.05921 | 4.7741 | 0 | 0 | 0 | 0 | off_peak | 538.08 | 0 | 100 | 0 | 0 | 100 | 0 | 0
1034 | 541.98 | 0 | 23.1 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 73.3758 | 554.3424 | 0 | 0.05921 | 4.5159 | 0 | 0 | 0 | 0 | off_peak | 541.98 | 0 | 100 | 0 | 0 | 100 | 0 | 0
1035 | 520.83 | 0 | 23.1 | 0 | 0 | 0 | 0 | 0.79843 | 0.79843 | 0 | 0 | 0 | 74.1227 | 521.6284 | 0 | 0.05921 | 4.1653 | 0 | 0 | 0 | 0 | off_peak | 520.83 | 0 | 100 | 0 | 0 | 100 | 0 | 0
1036 | 541.37 | 0 | 23.1 | 0 | 0 | 0 | 0 | 0.051567 | 0.051567 | 0 | 0 | 0 | 74.1709 | 541.4216 | 0 | 0.05921 | 3.9645 | 0 | 0 | 0 | 0 | off_peak | 541.37 | 0 | 100 | 0 | 0 | 100 | 0 | 0
1037 | 553.73 | 0 | 23.2 | 0 | 0 | 0 | 0 | 0.0033305 | 0.0033305 | 0 | 0 | 0 | 74.174 | 553.7333 | 0 | 0.05921 | 3.7457 | 0 | 0 | 0 | 0 | off_peak | 553.73 | 0 | 100 | 0 | 0 | 100 | 0 | 0
1038 | 650.29 | 0 | 23.2 | 0 | 0 | 0 | 0 | 0.0002151 | 0.0002151 | 0 | 0 | 0 | 74.1742 | 650.2902 | 0 | 0.05921 | 3.4019 | 0 | 0 | 0 | 0 | off_peak | 650.29 | 0 | 100 | 0 | 0 | 100 | 0 | 0
1039 | 737.21 | 0 | 23.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1742 | 737.21 | 0 | 0.088511 | 2.9156 | 0 | 0 | 0 | 0 | on_peak | 737.21 |  |  | 0 | 0 | 100 | 0 | 0
1040 | 751.08 | 69.6742 | 24.3 | 11.3157 | 11.3157 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1742 | 739.7643 | 0 | 0.088511 | 2.6406 | 0 | 0 | 0 | 11.3157 | on_peak | 739.7643 |  |  | 1.51 | 0 | 98.49 | 29.88 | 0
1041 | 826.73 | 267.795 | 25 | 43.3828 | 43.3828 | 0 | 0 | 0 | 0 | 62.4453 | 62.4453 | 0 | 7.4174 | 720.9019 | 0 | 0.088511 | 2.5151 | 0 | 0 | 0 | 43.3828 | on_peak | 720.9019 |  |  | 5.25 | 7.55 | 87.2 | 109.1116 | 0
1042 | 798.2 | 465.581 | 25.5 | 75.2884 | 75.2884 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 722.9116 | 0 | 0.088511 | 2.4984 | 0 | 0 | 0 | 75.2884 | on_peak | 722.9116 |  |  | 9.43 | 0 | 90.57 | 188.1009 | 0
1043 | 806.95 | 567.959 | 26 | 91.6781 | 91.6781 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 18.9814 | 727.6343 | 0 | 0.05921 | 2.6828 | 0 | 0 | 0 | 91.6781 | off_peak | 715.2719 | 0 | 100 | 11.36 | 0 | 88.64 | 245.9546 | 0
1044 | 855.47 | 702.509 | 26.3 | 113.2738 | 113.2738 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 30.5453 | 754.5585 | 0 | 0.05921 | 2.9947 | 0 | 0 | 0 | 113.2738 | off_peak | 742.1962 | 0 | 100 | 13.24 | 0 | 86.76 | 339.2177 | 0
1045 | 775.69 | 756.558 | 26.5 | 121.9006 | 121.9006 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 42.1093 | 666.1518 | 0 | 0.05921 | 3.6245 | 0 | 0 | 0 | 121.9006 | off_peak | 653.7894 | 0 | 100 | 15.72 | 0 | 84.28 | 441.8233 | 0
1046 | 833.69 | 690.177 | 26.5 | 111.2049 | 111.2049 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 53.6732 | 734.8475 | 0 | 0.05921 | 4.0021 | 0 | 0 | 0 | 111.2049 | off_peak | 722.4851 | 0 | 100 | 13.34 | 0 | 86.66 | 445.055 | 0
1047 | 873.67 | 621.074 | 26.4 | 100.1069 | 100.1069 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 65.2371 | 785.9255 | 0 | 0.05921 | 3.6843 | 0 | 0 | 0 | 100.1069 | off_peak | 773.5631 | 0 | 100 | 11.46 | 0 | 88.54 | 368.8192 | 0
1048 | 809.3 | 459.834 | 26.2 | 74.1713 | 74.1713 | 0 | 0 | 8.9371 | 8.9371 | 0 | 0 | 0 | 73.597 | 744.0658 | 0 | 0.05921 | 3.1924 | 0 | 0 | 0 | 74.1713 | off_peak | 735.1287 | 0 | 100 | 9.16 | 0 | 90.84 | 236.7829 | 0
1049 | 841.83 | 256.802 | 25.8 | 41.4821 | 41.4821 | 0 | 0 | 0.57721 | 0.57721 | 0 | 0 | 0 | 74.137 | 800.9251 | 0 | 0.05921 | 2.8563 | 0 | 0 | 0 | 41.4821 | off_peak | 800.3479 | 0 | 100 | 4.93 | 0 | 95.07 | 118.4858 | 0
1050 | 847.54 | 81.2215 | 25.2 | 13.1484 | 13.1484 | 0 | 0 | 0.037279 | 0.037279 | 0 | 0 | 0 | 74.1718 | 834.4289 | 0 | 0.05921 | 2.7386 | 0 | 0 | 0 | 13.1484 | off_peak | 834.3916 | 0 | 100 | 1.55 | 0 | 98.45 | 36.008 | 0
1051 | 804.81 | 0 | 24.8 | 0 | 0 | 0 | 0 | 0 | 0 | 62.443 | 62.443 | 0 | 7.4174 | 742.367 | 0 | 0.088511 | 2.6804 | 0 | 0 | 0 | 0 | on_peak | 742.367 |  |  | 0 | 7.76 | 92.24 | 0 | 0
1052 | 801.36 | 0 | 24.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 801.36 | 0 | 0.088511 | 2.5969 | 0 | 0 | 0 | 0 | on_peak | 801.36 |  |  | 0 | 0 | 100 | 0 | 0
1053 | 776.37 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 776.37 | 0 | 0.088511 | 2.6465 | 0 | 0 | 0 | 0 | on_peak | 776.37 |  |  | 0 | 0 | 100 | 0 | 0
1054 | 744.5 | 0 | 23.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 744.5 | 0 | 0.088511 | 2.8954 | 0 | 0 | 0 | 0 | on_peak | 744.5 |  |  | 0 | 0 | 100 | 0 | 0
1055 | 739.7 | 0 | 23.7 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 18.9814 | 752.0624 | 0 | 0.05921 | 3.3822 | 0 | 0 | 0 | 0 | off_peak | 739.7 | 0 | 100 | 0 | 0 | 100 | 0 | 0
1056 | 722.19 | 0 | 23.5 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 30.5453 | 734.5524 | 0 | 0.05921 | 4.1278 | 0 | 0 | 0 | 0 | off_peak | 722.19 | 0 | 100 | 0 | 0 | 100 | 0 | 0
1057 | 723.49 | 0 | 23.5 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 42.1093 | 735.8524 | 0 | 0.05921 | 4.589 | 0 | 0 | 0 | 0 | off_peak | 723.49 | 0 | 100 | 0 | 0 | 100 | 0 | 0
1058 | 630.14 | 0 | 23.5 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 53.6732 | 642.5024 | 0 | 0.05921 | 4.627 | 0 | 0 | 0 | 0 | off_peak | 630.14 | 0 | 100 | 0 | 0 | 100 | 0 | 0
1059 | 559.48 | 0 | 23.4 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 65.2371 | 571.8424 | 0 | 0.05921 | 4.3748 | 0 | 0 | 0 | 0 | off_peak | 559.48 | 0 | 100 | 0 | 0 | 100 | 0 | 0
1060 | 589.59 | 0 | 23.4 | 0 | 0 | 0 | 0 | 8.9371 | 8.9371 | 0 | 0 | 0 | 73.597 | 598.5271 | 0 | 0.05921 | 4.1014 | 0 | 0 | 0 | 0 | off_peak | 589.59 | 0 | 100 | 0 | 0 | 100 | 0 | 0
1061 | 596.07 | 0 | 23.4 | 0 | 0 | 0 | 0 | 0.57721 | 0.57721 | 0 | 0 | 0 | 74.137 | 596.6472 | 0 | 0.05921 | 3.6588 | 0 | 0 | 0 | 0 | off_peak | 596.07 | 0 | 100 | 0 | 0 | 100 | 0 | 0
1062 | 659.39 | 0 | 23.6 | 0 | 0 | 0 | 0 | 0.037279 | 0.037279 | 0 | 0 | 0 | 74.1718 | 659.4273 | 0 | 0.05921 | 3.1684 | 0 | 0 | 0 | 0 | off_peak | 659.39 | 0 | 100 | 0 | 0 | 100 | 0 | 0
1063 | 729.4 | 0 | 23.8 | 0 | 0 | 0 | 0 | 0 | 0 | 62.443 | 62.443 | 0 | 7.4174 | 666.957 | 0 | 0.088511 | 2.7606 | 0 | 0 | 0 | 0 | on_peak | 666.957 |  |  | 0 | 8.56 | 91.44 | 0 | 0
1064 | 773.91 | 66.2581 | 24.3 | 10.7609 | 10.7609 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 763.1491 | 0 | 0.088511 | 2.5325 | 0 | 0 | 0 | 10.7609 | on_peak | 763.1491 |  |  | 1.39 | 0 | 98.61 | 27.252 | 0
1065 | 866.43 | 244.907 | 25 | 39.6749 | 39.6749 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 826.7551 | 0 | 0.088511 | 2.4404 | 0 | 0 | 0 | 39.6749 | on_peak | 826.7551 |  |  | 4.58 | 0 | 95.42 | 96.8237 | 0
1066 | 852.26 | 466.577 | 25.8 | 75.3678 | 75.3678 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 776.8922 | 0 | 0.088511 | 2.4485 | 0 | 0 | 0 | 75.3678 | on_peak | 776.8922 |  |  | 8.84 | 0 | 91.16 | 184.5346 | 0
1067 | 819.35 | 636.13 | 26.3 | 102.5708 | 102.5708 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 18.9814 | 729.1416 | 0 | 0.05921 | 2.7159 | 0 | 0 | 0 | 102.5708 | off_peak | 716.7792 | 0 | 100 | 12.52 | 0 | 87.48 | 278.5709 | 0
1068 | 878.67 | 736.303 | 26.7 | 118.5511 | 118.5511 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 30.5453 | 772.4813 | 0 | 0.05921 | 3.0489 | 0 | 0 | 0 | 118.5511 | off_peak | 760.1189 | 0 | 100 | 13.49 | 0 | 86.51 | 361.4547 | 0
1069 | 810.29 | 757.069 | 26.8 | 121.8504 | 121.8504 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 42.1093 | 700.8019 | 0 | 0.05921 | 3.8455 | 0 | 0 | 0 | 121.8504 | off_peak | 688.4396 | 0 | 100 | 15.04 | 0 | 84.96 | 468.5769 | 0
1070 | 856.17 | 750.831 | 26.7 | 120.8902 | 120.8902 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 53.6732 | 747.6422 | 0 | 0.05921 | 4.1688 | 0 | 0 | 0 | 120.8902 | off_peak | 735.2798 | 0 | 100 | 14.12 | 0 | 85.88 | 503.9728 | 0
1071 | 897.5 | 653.529 | 26.4 | 105.3381 | 105.3381 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 65.2371 | 804.5243 | 0 | 0.05921 | 3.7452 | 0 | 0 | 0 | 105.3381 | off_peak | 792.1619 | 0 | 100 | 11.74 | 0 | 88.26 | 394.5118 | 0
1072 | 867.7 | 499.634 | 25.9 | 80.6785 | 80.6785 | 0 | 0 | 8.9371 | 8.9371 | 0 | 0 | 0 | 73.597 | 795.9587 | 0 | 0.05921 | 3.2554 | 0 | 0 | 0 | 80.6785 | off_peak | 787.0215 | 0 | 100 | 9.3 | 0 | 90.7 | 262.6437 | 0
1073 | 838.91 | 306.145 | 25.3 | 49.5419 | 49.5419 | 0 | 0 | 0.57721 | 0.57721 | 0 | 0 | 0 | 74.137 | 789.9453 | 0 | 0.05921 | 2.8145 | 0 | 0 | 0 | 49.5419 | off_peak | 789.3681 | 0 | 100 | 5.91 | 0 | 94.09 | 139.435 | 0
1074 | 849.94 | 102.44 | 24.6 | 16.6192 | 16.6192 | 0 | 0 | 0.037279 | 0.037279 | 0 | 0 | 0 | 74.1718 | 833.3581 | 0 | 0.05921 | 2.6262 | 0 | 0 | 0 | 16.6192 | off_peak | 833.3208 | 0 | 100 | 1.96 | 0 | 98.04 | 43.6449 | 0
1075 | 815.23 | 0 | 24.3 | 0 | 0 | 0 | 0 | 0 | 0 | 62.443 | 62.443 | 0 | 7.4174 | 752.787 | 0 | 0.088511 | 2.5694 | 0 | 0 | 0 | 0 | on_peak | 752.787 |  |  | 0 | 7.66 | 92.34 | 0 | 0
1076 | 817.57 | 0 | 23.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 817.57 | 0 | 0.088511 | 2.6313 | 0 | 0 | 0 | 0 | on_peak | 817.57 |  |  | 0 | 0 | 100 | 0 | 0
1077 | 779.57 | 0 | 23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 779.57 | 0 | 0.088511 | 2.7403 | 0 | 0 | 0 | 0 | on_peak | 779.57 |  |  | 0 | 0 | 100 | 0 | 0
1078 | 777.5 | 0 | 22.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 777.5 | 0 | 0.088511 | 3.0864 | 0 | 0 | 0 | 0 | on_peak | 777.5 |  |  | 0 | 0 | 100 | 0 | 0
1079 | 780.95 | 0 | 21.6 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 18.9814 | 793.3124 | 0 | 0.05921 | 3.6528 | 0 | 0 | 0 | 0 | off_peak | 780.95 | 0 | 100 | 0 | 0 | 100 | 0 | 0
1080 | 800.62 | 0 | 21.1 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 30.5453 | 812.9824 | 0 | 0.05921 | 4.3917 | 0 | 0 | 0 | 0 | off_peak | 800.62 | 0 | 100 | 0 | 0 | 100 | 0 | 0
1081 | 731.36 | 0 | 20.6 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 42.1093 | 743.7224 | 0 | 0.05921 | 4.8413 | 0 | 0 | 0 | 0 | off_peak | 731.36 | 0 | 100 | 0 | 0 | 100 | 0 | 0
1082 | 652.19 | 0 | 20.3 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 53.6732 | 664.5524 | 0 | 0.05921 | 4.7887 | 0 | 0 | 0 | 0 | off_peak | 652.19 | 0 | 100 | 0 | 0 | 100 | 0 | 0
1083 | 590.45 | 0 | 20 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 65.2371 | 602.8124 | 0 | 0.05921 | 4.503 | 0 | 0 | 0 | 0 | off_peak | 590.45 | 0 | 100 | 0 | 0 | 100 | 0 | 0
1084 | 573.39 | 0 | 20.1 | 0 | 0 | 0 | 0 | 8.9371 | 8.9371 | 0 | 0 | 0 | 73.597 | 582.3271 | 0 | 0.05921 | 4.1264 | 0 | 0 | 0 | 0 | off_peak | 573.39 | 0 | 100 | 0 | 0 | 100 | 0 | 0
1085 | 622.11 | 0 | 20.4 | 0 | 0 | 0 | 0 | 0.57721 | 0.57721 | 0 | 0 | 0 | 74.137 | 622.6872 | 0 | 0.05921 | 3.6776 | 0 | 0 | 0 | 0 | off_peak | 622.11 | 0 | 100 | 0 | 0 | 100 | 0 | 0
1086 | 682.44 | 0 | 20.6 | 0 | 0 | 0 | 0 | 0.037279 | 0.037279 | 0 | 0 | 0 | 74.1718 | 682.4773 | 0 | 0.05921 | 3.2032 | 0 | 0 | 0 | 0 | off_peak | 682.44 | 0 | 100 | 0 | 0 | 100 | 0 | 0
1087 | 811.84 | 0 | 20.9 | 0 | 0 | 0 | 0 | 0 | 0 | 62.443 | 62.443 | 0 | 7.4174 | 749.397 | 0 | 0.088511 | 2.8304 | 0 | 0 | 0 | 0 | on_peak | 749.397 |  |  | 0 | 7.69 | 92.31 | 0 | 0
1088 | 841.7 | 77.9964 | 21.4 | 12.7992 | 12.7992 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 828.9008 | 0 | 0.088511 | 2.5587 | 0 | 0 | 0 | 12.7992 | on_peak | 828.9008 |  |  | 1.52 | 0 | 98.48 | 32.7486 | 0
1089 | 899.87 | 284.648 | 22 | 46.611 | 46.611 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 853.259 | 0 | 0.088511 | 2.4249 | 0 | 0 | 0 | 46.611 | on_peak | 853.259 |  |  | 5.18 | 0 | 94.82 | 113.0271 | 0
1090 | 839.64 | 431.159 | 22.5 | 70.4764 | 70.4764 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 769.1636 | 0 | 0.088511 | 2.4052 | 0 | 0 | 0 | 70.4764 | on_peak | 769.1636 |  |  | 8.39 | 0 | 91.61 | 169.5086 | 0
1091 | 814.04 | 602.808 | 22.8 | 98.4283 | 98.4283 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 18.9814 | 727.9741 | 0 | 0.05921 | 2.501 | 0 | 0 | 0 | 98.4283 | off_peak | 715.6117 | 0 | 100 | 12.09 | 0 | 87.91 | 246.1725 | 0
1092 | 859.04 | 758.319 | 23 | 123.7322 | 123.7322 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 30.5453 | 747.6702 | 0 | 0.05921 | 2.7942 | 0 | 0 | 0 | 123.7322 | off_peak | 735.3078 | 0 | 100 | 14.4 | 0 | 85.6 | 345.7377 | 0
1093 | 844.16 | 799.556 | 22.9 | 130.5073 | 130.5073 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 42.1093 | 726.0151 | 0 | 0.05921 | 3.3831 | 0 | 0 | 0 | 130.5073 | off_peak | 713.6527 | 0 | 100 | 15.46 | 0 | 84.54 | 441.5197 | 0
1094 | 880.34 | 770.068 | 22.7 | 125.784 | 125.784 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 53.6732 | 766.9184 | 0 | 0.05921 | 3.7148 | 0 | 0 | 0 | 125.784 | off_peak | 754.556 | 0 | 100 | 14.29 | 0 | 85.71 | 467.2657 | 0
1095 | 919.93 | 671.534 | 22.5 | 109.7676 | 109.7676 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 65.2371 | 822.5248 | 0 | 0.05921 | 3.4672 | 0 | 0 | 0 | 109.7676 | off_peak | 810.1624 | 0 | 100 | 11.93 | 0 | 88.07 | 380.5809 | 0
1096 | 896.95 | 517.54 | 22.1 | 84.7168 | 84.7168 | 0 | 0 | 8.9371 | 8.9371 | 0 | 0 | 0 | 73.597 | 821.1703 | 0 | 0.05921 | 3.1948 | 0 | 0 | 0 | 84.7168 | off_peak | 812.2332 | 0 | 100 | 9.44 | 0 | 90.56 | 270.6538 | 0
1097 | 875.24 | 320.468 | 21.6 | 52.5513 | 52.5513 | 0 | 0 | 0.57721 | 0.57721 | 0 | 0 | 0 | 74.137 | 823.2659 | 0 | 0.05921 | 3.3503 | 0 | 0 | 0 | 52.5513 | off_peak | 822.6887 | 0 | 100 | 6 | 0 | 94 | 176.0616 | 0
1098 | 857.11 | 111.473 | 21 | 18.3187 | 18.3187 | 0 | 0 | 0.037279 | 0.037279 | 0 | 0 | 0 | 74.1718 | 838.8286 | 0 | 0.05921 | 3.5522 | 0 | 0 | 0 | 18.3187 | off_peak | 838.7913 | 0 | 100 | 2.14 | 0 | 97.86 | 65.0707 | 0
1099 | 826.14 | 0 | 20.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1718 | 826.14 | 0 | 0.088511 | 3.7395 | 0 | 0 | 0 | 0 | on_peak | 826.14 |  |  | 0 | 0 | 100 | 0 | 0
1100 | 860.97 | 0 | 20.4 | 0 | 0 | 0 | 0 | 0 | 0 | 62.443 | 62.443 | 0 | 7.4174 | 798.527 | 0 | 0.088511 | 3.9014 | 0 | 0 | 0 | 0 | on_peak | 798.527 |  |  | 0 | 7.25 | 92.75 | 0 | 0
1101 | 809.95 | 0 | 20.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 809.95 | 0 | 0.088511 | 4.0427 | 0 | 0 | 0 | 0 | on_peak | 809.95 |  |  | 0 | 0 | 100 | 0 | 0
1102 | 778.73 | 0 | 20.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 778.73 | 0 | 0.088511 | 4.3561 | 0 | 0 | 0 | 0 | on_peak | 778.73 |  |  | 0 | 0 | 100 | 0 | 0
1103 | 761.33 | 0 | 20 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 18.9814 | 773.6924 | 0 | 0.05921 | 4.7057 | 0 | 0 | 0 | 0 | off_peak | 761.33 | 0 | 100 | 0 | 0 | 100 | 0 | 0
1104 | 798.99 | 0 | 19.9 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 30.5453 | 811.3524 | 0 | 0.05921 | 5.1907 | 0 | 0 | 0 | 0 | off_peak | 798.99 | 0 | 100 | 0 | 0 | 100 | 0 | 0
1105 | 751.91 | 0 | 19.8 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 42.1093 | 764.2724 | 0 | 0.05921 | 5.4946 | 0 | 0 | 0 | 0 | off_peak | 751.91 | 0 | 100 | 0 | 0 | 100 | 0 | 0
1106 | 652.49 | 0 | 19.7 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 53.6732 | 664.8524 | 0 | 0.05921 | 5.4392 | 0 | 0 | 0 | 0 | off_peak | 652.49 | 0 | 100 | 0 | 0 | 100 | 0 | 0
1107 | 611.66 | 0 | 19.7 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 65.2371 | 624.0224 | 0 | 0.05921 | 5.1191 | 0 | 0 | 0 | 0 | off_peak | 611.66 | 0 | 100 | 0 | 0 | 100 | 0 | 0
1108 | 574.88 | 0 | 19.7 | 0 | 0 | 0 | 0 | 8.9371 | 8.9371 | 0 | 0 | 0 | 73.597 | 583.8171 | 0 | 0.05921 | 4.6913 | 0 | 0 | 0 | 0 | off_peak | 574.88 | 0 | 100 | 0 | 0 | 100 | 0 | 0
1109 | 622.8 | 0 | 19.6 | 0 | 0 | 0 | 0 | 0.57721 | 0.57721 | 0 | 0 | 0 | 74.137 | 623.3772 | 0 | 0.05921 | 4.2043 | 0 | 0 | 0 | 0 | off_peak | 622.8 | 0 | 100 | 0 | 0 | 100 | 0 | 0
1110 | 680.97 | 0 | 19.5 | 0 | 0 | 0 | 0 | 0.037279 | 0.037279 | 0 | 0 | 0 | 74.1718 | 681.0073 | 0 | 0.05921 | 3.6399 | 0 | 0 | 0 | 0 | off_peak | 680.97 | 0 | 100 | 0 | 0 | 100 | 0 | 0
1111 | 796.03 | 0 | 19.6 | 0 | 0 | 0 | 0 | 0 | 0 | 62.443 | 62.443 | 0 | 7.4174 | 733.587 | 0 | 0.088511 | 3.1644 | 0 | 0 | 0 | 0 | on_peak | 733.587 |  |  | 0 | 7.84 | 92.16 | 0 | 0
1112 | 838.18 | 82.9223 | 19.7 | 13.6897 | 13.6897 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 824.4903 | 0 | 0.088511 | 2.8091 | 0 | 0 | 0 | 13.6897 | on_peak | 824.4903 |  |  | 1.63 | 0 | 98.37 | 38.4564 | 0
1113 | 842.8 | 293.814 | 19.7 | 48.506 | 48.506 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 794.294 | 0 | 0.088511 | 2.6256 | 0 | 0 | 0 | 48.506 | on_peak | 794.294 |  |  | 5.76 | 0 | 94.24 | 127.357 | 0
1114 | 857.32 | 499.394 | 19.7 | 82.4454 | 82.4454 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 774.8746 | 0 | 0.088511 | 2.5373 | 0 | 0 | 0 | 82.4454 | on_peak | 774.8746 |  |  | 9.62 | 0 | 90.38 | 209.1918 | 0
1115 | 853.29 | 666.32 | 20.1 | 109.848 | 109.848 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 18.9814 | 755.8044 | 0 | 0.05921 | 2.5903 | 0 | 0 | 0 | 109.848 | off_peak | 743.442 | 0 | 100 | 12.87 | 0 | 87.13 | 284.5388 | 0
1116 | 899.97 | 773.363 | 20.5 | 127.3144 | 127.3144 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 30.5453 | 785.018 | 0 | 0.05921 | 2.9089 | 0 | 0 | 0 | 127.3144 | off_peak | 772.6556 | 0 | 100 | 14.15 | 0 | 85.85 | 370.3495 | 0
1117 | 848.23 | 814.373 | 20.8 | 133.9232 | 133.9232 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 42.1093 | 726.6692 | 0 | 0.05921 | 3.5216 | 0 | 0 | 0 | 133.9232 | off_peak | 714.3068 | 0 | 100 | 15.79 | 0 | 84.21 | 471.6237 | 0
1118 | 883.39 | 783.155 | 21.4 | 128.5154 | 128.5154 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 53.6732 | 767.237 | 0 | 0.05921 | 3.8392 | 0 | 0 | 0 | 128.5154 | off_peak | 754.8746 | 0 | 100 | 14.55 | 0 | 85.45 | 493.3899 | 0
1119 | 890.97 | 685.369 | 21.9 | 112.2689 | 112.2689 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 65.2371 | 791.0635 | 0 | 0.05921 | 3.8174 | 0 | 0 | 0 | 112.2689 | off_peak | 778.7011 | 0 | 100 | 12.6 | 0 | 87.4 | 428.5755 | 0
1120 | 902.45 | 528.606 | 22 | 86.559 | 86.559 | 0 | 0 | 8.9371 | 8.9371 | 0 | 0 | 0 | 73.597 | 824.8281 | 0 | 0.05921 | 3.8921 | 0 | 0 | 0 | 86.559 | off_peak | 815.891 | 0 | 100 | 9.59 | 0 | 90.41 | 336.8946 | 0
1121 | 895.35 | 326.552 | 21.3 | 53.6061 | 53.6061 | 0 | 0 | 0.57721 | 0.57721 | 0 | 0 | 0 | 74.137 | 842.3211 | 0 | 0.05921 | 4.0611 | 0 | 0 | 0 | 53.6061 | off_peak | 841.7439 | 0 | 100 | 5.99 | 0 | 94.01 | 217.7017 | 0
1122 | 905.6 | 116.812 | 20.2 | 19.2505 | 19.2505 | 0 | 0 | 0.037279 | 0.037279 | 0 | 0 | 0 | 74.1718 | 886.3867 | 0 | 0.05921 | 4.2751 | 0 | 0 | 0 | 19.2505 | off_peak | 886.3495 | 0 | 100 | 2.13 | 0 | 97.87 | 82.2972 | 0
1123 | 839.12 | 0 | 19.6 | 0 | 0 | 0 | 0 | 0 | 0 | 62.443 | 62.443 | 0 | 7.4174 | 776.677 | 0 | 0.088511 | 4.5608 | 0 | 0 | 0 | 0 | on_peak | 776.677 |  |  | 0 | 7.44 | 92.56 | 0 | 0
1124 | 871.39 | 0 | 18.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 871.39 | 0 | 0.088511 | 4.8627 | 0 | 0 | 0 | 0 | on_peak | 871.39 |  |  | 0 | 0 | 100 | 0 | 0
1125 | 877.86 | 0 | 17.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 877.86 | 0 | 0.088511 | 5.0883 | 0 | 0 | 0 | 0 | on_peak | 877.86 |  |  | 0 | 0 | 100 | 0 | 0
1126 | 799.13 | 0 | 16.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 799.13 | 0 | 0.088511 | 5.2612 | 0 | 0 | 0 | 0 | on_peak | 799.13 |  |  | 0 | 0 | 100 | 0 | 0
1127 | 810.5 | 0 | 15.8 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 18.9814 | 822.8624 | 0 | 0.05921 | 5.6345 | 0 | 0 | 0 | 0 | off_peak | 810.5 | 0 | 100 | 0 | 0 | 100 | 0 | 0
1128 | 837.08 | 0 | 15.1 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 30.5453 | 849.4424 | 0 | 0.05921 | 5.9444 | 0 | 0 | 0 | 0 | off_peak | 837.08 | 0 | 100 | 0 | 0 | 100 | 0 | 0
1129 | 777.01 | 0 | 14.7 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 42.1093 | 789.3724 | 0 | 0.05921 | 6.0334 | 0 | 0 | 0 | 0 | off_peak | 777.01 | 0 | 100 | 0 | 0 | 100 | 0 | 0
1130 | 680.42 | 0 | 14.4 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 53.6732 | 692.7824 | 0 | 0.05921 | 5.8865 | 0 | 0 | 0 | 0 | off_peak | 680.42 | 0 | 100 | 0 | 0 | 100 | 0 | 0
1131 | 672.14 | 0 | 14.1 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 65.2371 | 684.5024 | 0 | 0.05921 | 5.5007 | 0 | 0 | 0 | 0 | off_peak | 672.14 | 0 | 100 | 0 | 0 | 100 | 0 | 0
1132 | 608.39 | 0 | 13.6 | 0 | 0 | 0 | 0 | 8.9371 | 8.9371 | 0 | 0 | 0 | 73.597 | 617.3271 | 0 | 0.05921 | 5.1746 | 0 | 0 | 0 | 0 | off_peak | 608.39 | 0 | 100 | 0 | 0 | 100 | 0 | 0
1133 | 680.26 | 0 | 12.8 | 0 | 0 | 0 | 0 | 0.57721 | 0.57721 | 0 | 0 | 0 | 74.137 | 680.8372 | 0 | 0.05921 | 4.6757 | 0 | 0 | 0 | 0 | off_peak | 680.26 | 0 | 100 | 0 | 0 | 100 | 0 | 0
1134 | 728.95 | 0 | 11.9 | 0 | 0 | 0 | 0 | 0.037279 | 0.037279 | 0 | 0 | 0 | 74.1718 | 728.9873 | 0 | 0.05921 | 4.072 | 0 | 0 | 0 | 0 | off_peak | 728.95 | 0 | 100 | 0 | 0 | 100 | 0 | 0
1135 | 825.66 | 0 | 11.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1718 | 825.66 | 0 | 0.088511 | 3.724 | 0 | 0 | 0 | 0 | on_peak | 825.66 |  |  | 0 | 0 | 100 | 0 | 0
1136 | 877.66 | 87.9749 | 11 | 14.9702 | 14.9702 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1718 | 862.6898 | 0 | 0.088511 | 3.4424 | 0 | 0 | 0 | 14.9702 | on_peak | 862.6898 |  |  | 1.71 | 0 | 98.29 | 51.5328 | 0
1137 | 867.3 | 300.651 | 11.3 | 51.1076 | 51.1076 | 0 | 0 | 0 | 0 | 62.443 | 62.443 | 0 | 7.4174 | 753.7493 | 0 | 0.088511 | 3.2649 | 0 | 0 | 0 | 51.1076 | on_peak | 753.7493 |  |  | 5.89 | 7.2 | 86.91 | 166.8599 | 0
1138 | 896.2 | 502.084 | 12 | 85.1442 | 85.1442 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 811.0558 | 0 | 0.088511 | 3.1712 | 0 | 0 | 0 | 85.1442 | on_peak | 811.0558 |  |  | 9.5 | 0 | 90.5 | 270.0098 | 0
1139 | 880.11 | 664.901 | 12.8 | 112.4448 | 112.4448 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 18.9814 | 780.0276 | 0 | 0.05921 | 3.1921 | 0 | 0 | 0 | 112.4448 | off_peak | 767.6652 | 0 | 100 | 12.78 | 0 | 87.22 | 358.9387 | 0
1140 | 925.11 | 727.243 | 13.6 | 122.6484 | 122.6484 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 30.5453 | 814.8239 | 0 | 0.05921 | 3.4238 | 0 | 0 | 0 | 122.6484 | off_peak | 802.4616 | 0 | 100 | 13.26 | 0 | 86.74 | 419.9227 | 0
1141 | 919.06 | 757.013 | 14.3 | 127.36 | 127.36 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 42.1093 | 804.0623 | 0 | 0.05921 | 3.9515 | 0 | 0 | 0 | 127.36 | off_peak | 791.7 | 0 | 100 | 13.86 | 0 | 86.14 | 503.265 | 0
1142 | 952 | 703.108 | 14.8 | 118.086 | 118.086 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 53.6732 | 846.2763 | 0 | 0.05921 | 4.2778 | 0 | 0 | 0 | 118.086 | off_peak | 833.914 | 0 | 100 | 12.4 | 0 | 87.6 | 505.1455 | 0
1143 | 960.21 | 643.956 | 15.1 | 108.0389 | 108.0389 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 65.2371 | 864.5335 | 0 | 0.05921 | 4.4766 | 0 | 0 | 0 | 108.0389 | off_peak | 852.1711 | 0 | 100 | 11.25 | 0 | 88.75 | 483.6421 | 0
1144 | 838.14 | 508.298 | 15.2 | 85.2494 | 85.2494 | 0 | 0 | 8.9371 | 8.9371 | 0 | 0 | 0 | 73.597 | 761.8277 | 0 | 0.05921 | 4.5869 | 0 | 0 | 0 | 85.2494 | off_peak | 752.8906 | 0 | 100 | 10.17 | 0 | 89.83 | 391.0285 | 0
1145 | 914.41 | 326.299 | 14.9 | 54.7824 | 54.7824 | 0 | 0 | 0.57721 | 0.57721 | 0 | 0 | 0 | 74.137 | 860.2048 | 0 | 0.05921 | 4.7635 | 0 | 0 | 0 | 54.7824 | off_peak | 859.6276 | 0 | 100 | 5.99 | 0 | 94.01 | 260.9536 | 0
1146 | 901.95 | 115.994 | 14.2 | 19.5216 | 19.5216 | 0 | 0 | 0.037279 | 0.037279 | 0 | 0 | 0 | 74.1718 | 882.4657 | 0 | 0.05921 | 4.9988 | 0 | 0 | 0 | 19.5216 | off_peak | 882.4284 | 0 | 100 | 2.16 | 0 | 97.84 | 97.5847 | 0
1147 | 838.77 | 0 | 13.7 | 0 | 0 | 0 | 0 | 0 | 0 | 62.443 | 62.443 | 0 | 7.4174 | 776.327 | 0 | 0.088511 | 5.1696 | 0 | 0 | 0 | 0 | on_peak | 776.327 |  |  | 0 | 7.44 | 92.56 | 0 | 0
1148 | 870.49 | 0 | 13.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 870.49 | 0 | 0.088511 | 5.3128 | 0 | 0 | 0 | 0 | on_peak | 870.49 |  |  | 0 | 0 | 100 | 0 | 0
1149 | 872.93 | 0 | 13.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 872.93 | 0 | 0.088511 | 5.4298 | 0 | 0 | 0 | 0 | on_peak | 872.93 |  |  | 0 | 0 | 100 | 0 | 0
1150 | 824.6 | 0 | 13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 824.6 | 0 | 0.088511 | 5.5681 | 0 | 0 | 0 | 0 | on_peak | 824.6 |  |  | 0 | 0 | 100 | 0 | 0
1151 | 853.23 | 0 | 12.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 853.23 | 0 | 0.05921 | 5.8165 | 0 | 0 | 0 | 0 | off_peak | 853.23 |  |  | 0 | 0 | 100 | 0 | 0
1152 | 832.12 | 0 | 12.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 832.12 | 0 | 0.05921 | 6.0861 | 0 | 0 | 0 | 0 | off_peak | 832.12 |  |  | 0 | 0 | 100 | 0 | 0
1153 | 777.37 | 0 | 12.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 777.37 | 0 | 0.05921 | 6.2374 | 0 | 0 | 0 | 0 | off_peak | 777.37 |  |  | 0 | 0 | 100 | 0 | 0
1154 | 713.3 | 0 | 13.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 713.3 | 0 | 0.05921 | 6.0483 | 0 | 0 | 0 | 0 | off_peak | 713.3 |  |  | 0 | 0 | 100 | 0 | 0
1155 | 624.09 | 0 | 13.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 624.09 | 0 | 0.05921 | 5.6912 | 0 | 0 | 0 | 0 | off_peak | 624.09 |  |  | 0 | 0 | 100 | 0 | 0
1156 | 651.37 | 0 | 13.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 651.37 | 0 | 0.05921 | 5.3516 | 0 | 0 | 0 | 0 | off_peak | 651.37 |  |  | 0 | 0 | 100 | 0 | 0
1157 | 645.21 | 0 | 13.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 645.21 | 0 | 0.05921 | 4.974 | 0 | 0 | 0 | 0 | off_peak | 645.21 |  |  | 0 | 0 | 100 | 0 | 0
1158 | 727.23 | 0 | 14.1 | 0 | 0 | 0 | 0 | 8.7006 | 8.7006 | 0 | 0 | 0 | 15.5561 | 735.9306 | 0 | 0.05921 | 4.3642 | 0 | 0 | 0 | 0 | off_peak | 727.23 | 0 | 100 | 0 | 0 | 100 | 0 | 0
1159 | 789.71 | 0 | 14.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15.5561 | 789.71 | 0 | 0.05921 | 4.0932 | 0 | 0 | 0 | 0 | off_peak | 789.71 |  |  | 0 | 0 | 100 | 0 | 0
1160 | 800.65 | 82.8796 | 16.2 | 13.8518 | 13.8518 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 27.12 | 799.1605 | 0 | 0.05921 | 3.7198 | 0 | 0 | 0 | 13.8518 | off_peak | 786.7982 | 0 | 100 | 1.73 | 0 | 98.27 | 51.5267 | 0
1161 | 803.81 | 285.71 | 17.4 | 47.5514 | 47.5514 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27.12 | 756.2586 | 0 | 0.05921 | 3.4741 | 0 | 0 | 0 | 47.5514 | off_peak | 756.2586 |  |  | 5.92 | 0 | 94.08 | 165.1989 | 0
1162 | 811.18 | 486.369 | 18.4 | 80.6639 | 80.6639 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27.12 | 730.5161 | 0 | 0.05921 | 3.3678 | 0 | 0 | 0 | 80.6639 | off_peak | 730.5161 |  |  | 9.94 | 0 | 90.06 | 271.6558 | 0
1163 | 769.19 | 570.868 | 19.1 | 94.4449 | 94.4449 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27.12 | 674.7451 | 0 | 0.05921 | 3.3436 | 0 | 0 | 0 | 94.4449 | off_peak | 674.7451 |  |  | 12.28 | 0 | 87.72 | 315.7906 | 0
1164 | 800.69 | 711.486 | 19.5 | 117.5429 | 117.5429 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27.12 | 683.1471 | 0 | 0.05921 | 3.4543 | 0 | 0 | 0 | 117.5429 | off_peak | 683.1471 |  |  | 14.68 | 0 | 85.32 | 406.0261 | 0
1165 | 732.92 | 797.257 | 19.8 | 131.5734 | 131.5734 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27.12 | 601.3466 | 0 | 0.05921 | 3.693 | 0 | 0 | 0 | 131.5734 | off_peak | 601.3466 |  |  | 17.95 | 0 | 82.05 | 485.8974 | 0
1166 | 718.54 | 769.957 | 20 | 126.9782 | 126.9782 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27.12 | 591.5618 | 0 | 0.05921 | 4.0085 | 0 | 0 | 0 | 126.9782 | off_peak | 591.5618 |  |  | 17.67 | 0 | 82.33 | 508.9925 | 0
1167 | 706.04 | 675.201 | 20.1 | 111.3121 | 111.3121 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27.12 | 594.7279 | 0 | 0.05921 | 4.2051 | 0 | 0 | 0 | 111.3121 | off_peak | 594.7279 |  |  | 15.77 | 0 | 84.23 | 468.0778 | 0
1168 | 675.48 | 522.099 | 20.1 | 86.072 | 86.072 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27.12 | 589.408 | 0 | 0.05921 | 4.3083 | 0 | 0 | 0 | 86.072 | off_peak | 589.408 |  |  | 12.74 | 0 | 87.26 | 370.8256 | 0
1169 | 689.31 | 324.854 | 19.8 | 53.6115 | 53.6115 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27.12 | 635.6985 | 0 | 0.05921 | 4.2178 | 0 | 0 | 0 | 53.6115 | off_peak | 635.6985 |  |  | 7.78 | 0 | 92.22 | 226.1217 | 0
1170 | 675.82 | 116.636 | 19.3 | 19.2828 | 19.2828 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27.12 | 656.5372 | 0 | 0.05921 | 4.1443 | 0 | 0 | 0 | 19.2828 | off_peak | 656.5372 |  |  | 2.85 | 0 | 97.15 | 79.9138 | 0
1171 | 609.87 | 0 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27.12 | 609.87 | 0 | 0.05921 | 4.159 | 0 | 0 | 0 | 0 | off_peak | 609.87 |  |  | 0 | 0 | 100 | 0 | 0
1172 | 593.96 | 0 | 19.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27.12 | 593.96 | 0 | 0.05921 | 4.2426 | 0 | 0 | 0 | 0 | off_peak | 593.96 |  |  | 0 | 0 | 100 | 0 | 0
1173 | 559.84 | 0 | 19.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27.12 | 559.84 | 0 | 0.05921 | 4.2636 | 0 | 0 | 0 | 0 | off_peak | 559.84 |  |  | 0 | 0 | 100 | 0 | 0
1174 | 549.36 | 0 | 19.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27.12 | 549.36 | 0 | 0.05921 | 4.4082 | 0 | 0 | 0 | 0 | off_peak | 549.36 |  |  | 0 | 0 | 100 | 0 | 0
1175 | 562.63 | 0 | 19.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27.12 | 562.63 | 0 | 0.05921 | 4.7421 | 0 | 0 | 0 | 0 | off_peak | 562.63 |  |  | 0 | 0 | 100 | 0 | 0
1176 | 565.25 | 0 | 19.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27.12 | 565.25 | 0 | 0.05921 | 5.1498 | 0 | 0 | 0 | 0 | off_peak | 565.25 |  |  | 0 | 0 | 100 | 0 | 0
1177 | 565.88 | 0 | 19.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27.12 | 565.88 | 0 | 0.05921 | 5.5359 | 0 | 0 | 0 | 0 | off_peak | 565.88 |  |  | 0 | 0 | 100 | 0 | 0
1178 | 539.98 | 0 | 19.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27.12 | 539.98 | 0 | 0.05921 | 5.4502 | 0 | 0 | 0 | 0 | off_peak | 539.98 |  |  | 0 | 0 | 100 | 0 | 0
1179 | 539.91 | 0 | 19.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27.12 | 539.91 | 0 | 0.05921 | 5.2377 | 0 | 0 | 0 | 0 | off_peak | 539.91 |  |  | 0 | 0 | 100 | 0 | 0
1180 | 579.23 | 0 | 19.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27.12 | 579.23 | 0 | 0.05921 | 4.9413 | 0 | 0 | 0 | 0 | off_peak | 579.23 |  |  | 0 | 0 | 100 | 0 | 0
1181 | 543.97 | 0 | 19.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27.12 | 543.97 | 0 | 0.05921 | 4.6337 | 0 | 0 | 0 | 0 | off_peak | 543.97 |  |  | 0 | 0 | 100 | 0 | 0
1182 | 659.89 | 0 | 19.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27.12 | 659.89 | 0 | 0.05921 | 4.2052 | 0 | 0 | 0 | 0 | off_peak | 659.89 |  |  | 0 | 0 | 100 | 0 | 0
1183 | 700.05 | 0 | 20.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27.12 | 700.05 | 0 | 0.05921 | 3.8653 | 0 | 0 | 0 | 0 | off_peak | 700.05 |  |  | 0 | 0 | 100 | 0 | 0
1184 | 699.77 | 84.1199 | 21.2 | 13.8138 | 13.8138 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27.12 | 685.9562 | 0 | 0.05921 | 3.5362 | 0 | 0 | 0 | 13.8138 | off_peak | 685.9562 |  |  | 1.97 | 0 | 98.03 | 48.8489 | 0
1185 | 720.49 | 105.961 | 22 | 17.3511 | 17.3511 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27.12 | 703.1389 | 0 | 0.05921 | 3.3099 | 0 | 0 | 0 | 17.3511 | off_peak | 703.1389 |  |  | 2.41 | 0 | 97.59 | 57.4305 | 0
1186 | 747.38 | 114.5 | 22.4 | 18.7226 | 18.7226 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27.12 | 728.6574 | 0 | 0.05921 | 3.1356 | 0 | 0 | 0 | 18.7226 | off_peak | 728.6574 |  |  | 2.51 | 0 | 97.49 | 58.7064 | 0
1187 | 736.04 | 124.45 | 22.8 | 20.3206 | 20.3206 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27.12 | 715.7194 | 0 | 0.05921 | 3.08 | 0 | 0 | 0 | 20.3206 | off_peak | 715.7194 |  |  | 2.76 | 0 | 97.24 | 62.5875 | 0
1188 | 733.62 | 374.268 | 23 | 61.068 | 61.068 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27.12 | 672.552 | 0 | 0.05921 | 3.161 | 0 | 0 | 0 | 61.068 | off_peak | 672.552 |  |  | 8.32 | 0 | 91.68 | 193.0332 | 0
1189 | 713.01 | 458.078 | 23 | 74.7429 | 74.7429 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27.12 | 638.2671 | 0 | 0.05921 | 3.3516 | 0 | 0 | 0 | 74.7429 | off_peak | 638.2671 |  |  | 10.48 | 0 | 89.52 | 250.5088 | 0
1190 | 736.02 | 457.837 | 23 | 74.7036 | 74.7036 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27.12 | 661.3164 | 0 | 0.05921 | 3.6885 | 0 | 0 | 0 | 74.7036 | off_peak | 661.3164 |  |  | 10.15 | 0 | 89.85 | 275.5456 | 0
1191 | 705.43 | 651.638 | 22.9 | 106.3634 | 106.3634 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27.12 | 599.0666 | 0 | 0.05921 | 3.9442 | 0 | 0 | 0 | 106.3634 | off_peak | 599.0666 |  |  | 15.08 | 0 | 84.92 | 419.5211 | 0
1192 | 719.21 | 401.364 | 22.9 | 65.5125 | 65.5125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27.12 | 653.6975 | 0 | 0.05921 | 4.0932 | 0 | 0 | 0 | 65.5125 | off_peak | 653.6975 |  |  | 9.11 | 0 | 90.89 | 268.1567 | 0
1193 | 704.44 | 98.5688 | 22.6 | 16.1061 | 16.1061 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27.12 | 688.3339 | 0 | 0.05921 | 4.2827 | 0 | 0 | 0 | 16.1061 | off_peak | 688.3339 |  |  | 2.29 | 0 | 97.71 | 68.9779 | 0
1194 | 620.38 | 112.83 | 22.2 | 18.4627 | 18.4627 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27.12 | 601.9173 | 0 | 0.05921 | 4.636 | 0 | 0 | 0 | 18.4627 | off_peak | 601.9173 |  |  | 2.98 | 0 | 97.02 | 85.5938 | 0
1195 | 570.14 | 0 | 21.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27.12 | 570.14 | 0 | 0.05921 | 5.0404 | 0 | 0 | 0 | 0 | off_peak | 570.14 |  |  | 0 | 0 | 100 | 0 | 0
1196 | 562.55 | 0 | 21.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27.12 | 562.55 | 0 | 0.05921 | 5.2746 | 0 | 0 | 0 | 0 | off_peak | 562.55 |  |  | 0 | 0 | 100 | 0 | 0
1197 | 564.1 | 0 | 21.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27.12 | 564.1 | 0 | 0.05921 | 5.4022 | 0 | 0 | 0 | 0 | off_peak | 564.1 |  |  | 0 | 0 | 100 | 0 | 0
1198 | 556.93 | 0 | 21.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27.12 | 556.93 | 0 | 0.05921 | 5.7099 | 0 | 0 | 0 | 0 | off_peak | 556.93 |  |  | 0 | 0 | 100 | 0 | 0
1199 | 567.59 | 0 | 21.4 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 38.684 | 579.9524 | 0 | 0.05921 | 6.0021 | 0 | 0 | 0 | 0 | off_peak | 567.59 | 0 | 100 | 0 | 0 | 100 | 0 | 0
1200 | 548.54 | 0 | 21.4 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 50.2479 | 560.9024 | 0 | 0.05921 | 6.1875 | 0 | 0 | 0 | 0 | off_peak | 548.54 | 0 | 100 | 0 | 0 | 100 | 0 | 0
1201 | 537.9 | 0 | 21.3 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 61.8119 | 550.2624 | 0 | 0.05921 | 6.2892 | 0 | 0 | 0 | 0 | off_peak | 537.9 | 0 | 100 | 0 | 0 | 100 | 0 | 0
1202 | 558.16 | 0 | 21.1 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 73.3758 | 570.5224 | 0 | 0.05921 | 6.1471 | 0 | 0 | 0 | 0 | off_peak | 558.16 | 0 | 100 | 0 | 0 | 100 | 0 | 0
1203 | 546.92 | 0 | 21 | 0 | 0 | 0 | 0 | 0.79843 | 0.79843 | 0 | 0 | 0 | 74.1227 | 547.7184 | 0 | 0.05921 | 5.8651 | 0 | 0 | 0 | 0 | off_peak | 546.92 | 0 | 100 | 0 | 0 | 100 | 0 | 0
1204 | 529.83 | 0 | 20.8 | 0 | 0 | 0 | 0 | 0.051567 | 0.051567 | 0 | 0 | 0 | 74.1709 | 529.8816 | 0 | 0.05921 | 5.4619 | 0 | 0 | 0 | 0 | off_peak | 529.83 | 0 | 100 | 0 | 0 | 100 | 0 | 0
1205 | 588.99 | 0 | 20.5 | 0 | 0 | 0 | 0 | 0.0033305 | 0.0033305 | 0 | 0 | 0 | 74.174 | 588.9933 | 0 | 0.05921 | 4.9539 | 0 | 0 | 0 | 0 | off_peak | 588.99 | 0 | 100 | 0 | 0 | 100 | 0 | 0
1206 | 707.97 | 0 | 20.2 | 0 | 0 | 0 | 0 | 0.0002151 | 0.0002151 | 0 | 0 | 0 | 74.1742 | 707.9702 | 0 | 0.05921 | 4.3864 | 0 | 0 | 0 | 0 | off_peak | 707.97 | 0 | 100 | 0 | 0 | 100 | 0 | 0
1207 | 737.23 | 0 | 20.3 | 0 | 0 | 0 | 0 | 0 | 0 | 62.4453 | 62.4453 | 0 | 7.4174 | 674.7847 | 0 | 0.088511 | 3.8394 | 0 | 0 | 0 | 0 | on_peak | 674.7847 |  |  | 0 | 8.47 | 91.53 | 0 | 0
1208 | 782.42 | 84.3471 | 20.9 | 13.8659 | 13.8659 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 768.5541 | 0 | 0.088511 | 3.5187 | 0 | 0 | 0 | 13.8659 | on_peak | 768.5541 |  |  | 1.77 | 0 | 98.23 | 48.7897 | 0
1209 | 821.96 | 287.703 | 21.7 | 47.1616 | 47.1616 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 774.7984 | 0 | 0.088511 | 3.2956 | 0 | 0 | 0 | 47.1616 | on_peak | 774.7984 |  |  | 5.74 | 0 | 94.26 | 155.425 | 0
1210 | 810.66 | 414.707 | 22.5 | 67.7872 | 67.7872 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 742.8728 | 0 | 0.088511 | 3.1594 | 0 | 0 | 0 | 67.7872 | on_peak | 742.8728 |  |  | 8.36 | 0 | 91.64 | 214.1694 | 0
1211 | 808.52 | 458.175 | 23.2 | 74.7053 | 74.7053 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 18.9814 | 746.1771 | 0 | 0.05921 | 3.1657 | 0 | 0 | 0 | 74.7053 | off_peak | 733.8147 | 0 | 100 | 9.24 | 0 | 90.76 | 236.4978 | 0
1212 | 889.36 | 649.976 | 23.7 | 105.7889 | 105.7889 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 30.5453 | 795.9335 | 0 | 0.05921 | 3.3805 | 0 | 0 | 0 | 105.7889 | off_peak | 783.5711 | 0 | 100 | 11.89 | 0 | 88.11 | 357.623 | 0
1213 | 843.24 | 681.145 | 24 | 110.7427 | 110.7427 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 42.1093 | 744.8596 | 0 | 0.05921 | 3.7623 | 0 | 0 | 0 | 110.7427 | off_peak | 732.4973 | 0 | 100 | 13.13 | 0 | 86.87 | 416.6424 | 0
1214 | 891.36 | 636.873 | 24.3 | 103.4334 | 103.4334 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 53.6732 | 800.289 | 0 | 0.05921 | 4.0651 | 0 | 0 | 0 | 103.4334 | off_peak | 787.9266 | 0 | 100 | 11.6 | 0 | 88.4 | 420.4716 | 0
1215 | 879.67 | 580.407 | 24.3 | 94.2629 | 94.2629 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 65.2371 | 797.7695 | 0 | 0.05921 | 4.1897 | 0 | 0 | 0 | 94.2629 | off_peak | 785.4071 | 0 | 100 | 10.72 | 0 | 89.28 | 394.9363 | 0
1216 | 879.53 | 515.532 | 24.1 | 83.7868 | 83.7868 | 0 | 0 | 8.9371 | 8.9371 | 0 | 0 | 0 | 73.597 | 804.6803 | 0 | 0.05921 | 4.338 | 0 | 0 | 0 | 83.7868 | off_peak | 795.7432 | 0 | 100 | 9.53 | 0 | 90.47 | 363.4641 | 0
1217 | 891.73 | 317.667 | 23.6 | 51.7214 | 51.7214 | 0 | 0 | 0.57721 | 0.57721 | 0 | 0 | 0 | 74.137 | 840.5858 | 0 | 0.05921 | 4.4323 | 0 | 0 | 0 | 51.7214 | off_peak | 840.0086 | 0 | 100 | 5.8 | 0 | 94.2 | 229.243 | 0
1218 | 858.81 | 111.849 | 22.9 | 18.2565 | 18.2565 | 0 | 0 | 0.037279 | 0.037279 | 0 | 0 | 0 | 74.1718 | 840.5908 | 0 | 0.05921 | 4.6881 | 0 | 0 | 0 | 18.2565 | off_peak | 840.5535 | 0 | 100 | 2.13 | 0 | 97.87 | 85.5886 | 0
1219 | 846.23 | 0 | 22.6 | 0 | 0 | 0 | 0 | 0 | 0 | 62.443 | 62.443 | 0 | 7.4174 | 783.787 | 0 | 0.088511 | 5.0777 | 0 | 0 | 0 | 0 | on_peak | 783.787 |  |  | 0 | 7.38 | 92.62 | 0 | 0
1220 | 854.3 | 0 | 22.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 854.3 | 0 | 0.088511 | 5.4337 | 0 | 0 | 0 | 0 | on_peak | 854.3 |  |  | 0 | 0 | 100 | 0 | 0
1221 | 820.06 | 0 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 820.06 | 0 | 0.088511 | 5.6612 | 0 | 0 | 0 | 0 | on_peak | 820.06 |  |  | 0 | 0 | 100 | 0 | 0
1222 | 794.03 | 0 | 21.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 794.03 | 0 | 0.088511 | 5.9001 | 0 | 0 | 0 | 0 | on_peak | 794.03 |  |  | 0 | 0 | 100 | 0 | 0
1223 | 810.02 | 0 | 21.7 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 18.9814 | 822.3824 | 0 | 0.05921 | 6.2244 | 0 | 0 | 0 | 0 | off_peak | 810.02 | 0 | 100 | 0 | 0 | 100 | 0 | 0
1224 | 818.68 | 0 | 21.6 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 30.5453 | 831.0424 | 0 | 0.05921 | 6.6813 | 0 | 0 | 0 | 0 | off_peak | 818.68 | 0 | 100 | 0 | 0 | 100 | 0 | 0
1225 | 756 | 0 | 21.5 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 42.1093 | 768.3624 | 0 | 0.05921 | 6.7907 | 0 | 0 | 0 | 0 | off_peak | 756 | 0 | 100 | 0 | 0 | 100 | 0 | 0
1226 | 666.36 | 0 | 21.4 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 53.6732 | 678.7224 | 0 | 0.05921 | 6.684 | 0 | 0 | 0 | 0 | off_peak | 666.36 | 0 | 100 | 0 | 0 | 100 | 0 | 0
1227 | 623.76 | 0 | 21.4 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 65.2371 | 636.1224 | 0 | 0.05921 | 6.1995 | 0 | 0 | 0 | 0 | off_peak | 623.76 | 0 | 100 | 0 | 0 | 100 | 0 | 0
1228 | 594.88 | 0 | 21.4 | 0 | 0 | 0 | 0 | 8.9371 | 8.9371 | 0 | 0 | 0 | 73.597 | 603.8171 | 0 | 0.05921 | 5.8234 | 0 | 0 | 0 | 0 | off_peak | 594.88 | 0 | 100 | 0 | 0 | 100 | 0 | 0
1229 | 599.54 | 0 | 21.4 | 0 | 0 | 0 | 0 | 0.57721 | 0.57721 | 0 | 0 | 0 | 74.137 | 600.1172 | 0 | 0.05921 | 5.2347 | 0 | 0 | 0 | 0 | off_peak | 599.54 | 0 | 100 | 0 | 0 | 100 | 0 | 0
1230 | 715.14 | 0 | 21.4 | 0 | 0 | 0 | 0 | 0.037279 | 0.037279 | 0 | 0 | 0 | 74.1718 | 715.1773 | 0 | 0.05921 | 4.5398 | 0 | 0 | 0 | 0 | off_peak | 715.14 | 0 | 100 | 0 | 0 | 100 | 0 | 0
1231 | 812.24 | 0 | 21.9 | 0 | 0 | 0 | 0 | 0 | 0 | 62.443 | 62.443 | 0 | 7.4174 | 749.797 | 0 | 0.088511 | 4.016 | 0 | 0 | 0 | 0 | on_peak | 749.797 |  |  | 0 | 7.69 | 92.31 | 0 | 0
1232 | 791.04 | 84.0958 | 22.9 | 13.7265 | 13.7265 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 777.3135 | 0 | 0.088511 | 3.5727 | 0 | 0 | 0 | 13.7265 | on_peak | 777.3135 |  |  | 1.74 | 0 | 98.26 | 49.0408 | 0
1233 | 846.66 | 289.001 | 23.7 | 47.0373 | 47.0373 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 799.6227 | 0 | 0.088511 | 3.3035 | 0 | 0 | 0 | 47.0373 | on_peak | 799.6227 |  |  | 5.56 | 0 | 94.44 | 155.3887 | 0
1234 | 858.28 | 489.782 | 24.2 | 79.5732 | 79.5732 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 778.7068 | 0 | 0.088511 | 3.164 | 0 | 0 | 0 | 79.5732 | on_peak | 778.7068 |  |  | 9.27 | 0 | 90.73 | 251.7668 | 0
1235 | 843.26 | 617.932 | 24.6 | 100.2491 | 100.2491 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 18.9814 | 755.3732 | 0 | 0.05921 | 3.1735 | 0 | 0 | 0 | 100.2491 | off_peak | 743.0109 | 0 | 100 | 11.89 | 0 | 88.11 | 318.1394 | 0
1236 | 895.57 | 570.158 | 24.9 | 92.3988 | 92.3988 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 30.5453 | 815.5335 | 0 | 0.05921 | 3.473 | 0 | 0 | 0 | 92.3988 | off_peak | 803.1712 | 0 | 100 | 10.32 | 0 | 89.68 | 320.8987 | 0
1237 | 884.48 | 613.746 | 25 | 99.4269 | 99.4269 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 42.1093 | 797.4155 | 0 | 0.05921 | 4.0317 | 0 | 0 | 0 | 99.4269 | off_peak | 785.0531 | 0 | 100 | 11.24 | 0 | 88.76 | 400.8605 | 0
1238 | 896.42 | 698.899 | 25.1 | 113.1809 | 113.1809 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 53.6732 | 795.6015 | 0 | 0.05921 | 4.2887 | 0 | 0 | 0 | 113.1809 | off_peak | 783.2391 | 0 | 100 | 12.63 | 0 | 87.37 | 485.4 | 0
1239 | 926.63 | 590.818 | 25 | 95.7125 | 95.7125 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 65.2371 | 843.2799 | 0 | 0.05921 | 4.444 | 0 | 0 | 0 | 95.7125 | off_peak | 830.9175 | 0 | 100 | 10.33 | 0 | 89.67 | 425.3492 | 0
1240 | 950.18 | 515.34 | 24.8 | 83.5452 | 83.5452 | 0 | 0 | 8.9371 | 8.9371 | 0 | 0 | 0 | 73.597 | 875.5719 | 0 | 0.05921 | 4.531 | 0 | 0 | 0 | 83.5452 | off_peak | 866.6348 | 0 | 100 | 8.79 | 0 | 91.21 | 378.5462 | 0
1241 | 890.5 | 314.068 | 24.4 | 50.9889 | 50.9889 | 0 | 0 | 0.57721 | 0.57721 | 0 | 0 | 0 | 74.137 | 840.0883 | 0 | 0.05921 | 4.6146 | 0 | 0 | 0 | 50.9889 | off_peak | 839.5111 | 0 | 100 | 5.73 | 0 | 94.27 | 235.2933 | 0
1242 | 899.97 | 117.592 | 23.7 | 19.1391 | 19.1391 | 0 | 0 | 0.037279 | 0.037279 | 0 | 0 | 0 | 74.1718 | 880.8682 | 0 | 0.05921 | 4.7401 | 0 | 0 | 0 | 19.1391 | off_peak | 880.8309 | 0 | 100 | 2.13 | 0 | 97.87 | 90.7211 | 0
1243 | 843.47 | 0 | 23.3 | 0 | 0 | 0 | 0 | 0 | 0 | 33.7287 | 33.7287 | 0 | 38.1144 | 809.7413 | 0 | 0.088511 | 5.0829 | 0 | 0 | 0 | 0 | on_peak | 809.7413 |  |  | 0 | 4 | 96 | 0 | 0
1244 | 847.14 | 0 | 22.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 38.1144 | 847.14 | 0 | 0.088511 | 5.4119 | 0 | 0 | 0 | 0 | on_peak | 847.14 |  |  | 0 | 0 | 100 | 0 | 0
1245 | 906.59 | 0 | 22.8 | 0 | 0 | 0 | 0 | 0 | 0 | 28.7143 | 28.7143 | 0 | 7.4174 | 877.8757 | 0 | 0.088511 | 5.7462 | 0 | 0 | 0 | 0 | on_peak | 877.8757 |  |  | 0 | 3.17 | 96.83 | 0 | 0
1246 | 813.74 | 0 | 22.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 813.74 | 0 | 0.088511 | 6.0652 | 0 | 0 | 0 | 0 | on_peak | 813.74 |  |  | 0 | 0 | 100 | 0 | 0
1247 | 828.36 | 0 | 22.6 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 18.9814 | 840.7224 | 0 | 0.05921 | 6.5167 | 0 | 0 | 0 | 0 | off_peak | 828.36 | 0 | 100 | 0 | 0 | 100 | 0 | 0
1248 | 874.32 | 0 | 22.5 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 30.5453 | 886.6824 | 0 | 0.05921 | 6.9448 | 0 | 0 | 0 | 0 | off_peak | 874.32 | 0 | 100 | 0 | 0 | 100 | 0 | 0
1249 | 733.02 | 0 | 22.4 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 42.1093 | 745.3824 | 0 | 0.05921 | 7.1038 | 0 | 0 | 0 | 0 | off_peak | 733.02 | 0 | 100 | 0 | 0 | 100 | 0 | 0
1250 | 696 | 0 | 22.3 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 53.6732 | 708.3624 | 0 | 0.05921 | 6.9614 | 0 | 0 | 0 | 0 | off_peak | 696 | 0 | 100 | 0 | 0 | 100 | 0 | 0
1251 | 618.96 | 0 | 22.3 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 65.2371 | 631.3224 | 0 | 0.05921 | 6.4484 | 0 | 0 | 0 | 0 | off_peak | 618.96 | 0 | 100 | 0 | 0 | 100 | 0 | 0
1252 | 609.62 | 0 | 22.4 | 0 | 0 | 0 | 0 | 8.9371 | 8.9371 | 0 | 0 | 0 | 73.597 | 618.5571 | 0 | 0.05921 | 5.8439 | 0 | 0 | 0 | 0 | off_peak | 609.62 | 0 | 100 | 0 | 0 | 100 | 0 | 0
1253 | 646.75 | 0 | 22.4 | 0 | 0 | 0 | 0 | 0.57721 | 0.57721 | 0 | 0 | 0 | 74.137 | 647.3272 | 0 | 0.05921 | 5.2164 | 0 | 0 | 0 | 0 | off_peak | 646.75 | 0 | 100 | 0 | 0 | 100 | 0 | 0
1254 | 698.18 | 0 | 22.5 | 0 | 0 | 0 | 0 | 0.037279 | 0.037279 | 0 | 0 | 0 | 74.1718 | 698.2173 | 0 | 0.05921 | 4.564 | 0 | 0 | 0 | 0 | off_peak | 698.18 | 0 | 100 | 0 | 0 | 100 | 0 | 0
1255 | 796.1 | 0 | 23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1718 | 796.1 | 0 | 0.088511 | 3.9193 | 0 | 0 | 0 | 0 | on_peak | 796.1 |  |  | 0 | 0 | 100 | 0 | 0
1256 | 839.7 | 86.0723 | 23.8 | 14.0039 | 14.0039 | 0 | 0 | 0 | 0 | 62.443 | 62.443 | 0 | 7.4174 | 763.253 | 0 | 0.088511 | 3.5114 | 0 | 0 | 0 | 14.0039 | on_peak | 763.253 |  |  | 1.67 | 7.44 | 90.9 | 49.1735 | 0
1257 | 847.73 | 290.018 | 24.4 | 47.0844 | 47.0844 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 800.6456 | 0 | 0.088511 | 3.2875 | 0 | 0 | 0 | 47.0844 | on_peak | 800.6456 |  |  | 5.55 | 0 | 94.45 | 154.792 | 0
1258 | 859.82 | 488.463 | 24.9 | 79.1595 | 79.1595 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 780.6605 | 0 | 0.088511 | 3.1319 | 0 | 0 | 0 | 79.1595 | on_peak | 780.6605 |  |  | 9.21 | 0 | 90.79 | 247.9186 | 0
1259 | 858.96 | 629.715 | 25.2 | 101.9404 | 101.9404 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 18.9814 | 769.382 | 0 | 0.05921 | 3.1382 | 0 | 0 | 0 | 101.9404 | off_peak | 757.0196 | 0 | 100 | 11.87 | 0 | 88.13 | 319.9054 | 0
1260 | 941.17 | 656.828 | 25.5 | 106.2146 | 106.2146 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 30.5453 | 847.3178 | 0 | 0.05921 | 3.0918 | 0 | 0 | 0 | 106.2146 | off_peak | 834.9554 | 0 | 100 | 11.29 | 0 | 88.71 | 328.3961 | 0
1261 | 845.41 | 610.664 | 25.6 | 98.7139 | 98.7139 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 42.1093 | 759.0585 | 0 | 0.05921 | 3.937 | 0 | 0 | 0 | 98.7139 | off_peak | 746.6961 | 0 | 100 | 11.68 | 0 | 88.32 | 388.634 | 0
1262 | 901.05 | 523.975 | 25.7 | 84.67 | 84.67 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 53.6732 | 828.7423 | 0 | 0.05921 | 4.2366 | 0 | 0 | 0 | 84.67 | off_peak | 816.38 | 0 | 100 | 9.4 | 0 | 90.6 | 358.7103 | 0
1263 | 949.87 | 459.157 | 25.7 | 74.196 | 74.196 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 65.2371 | 888.0364 | 0 | 0.05921 | 4.279 | 0 | 0 | 0 | 74.196 | off_peak | 875.674 | 0 | 100 | 7.81 | 0 | 92.19 | 317.481 | 0
1264 | 925.36 | 523.977 | 25.5 | 84.7315 | 84.7315 | 0 | 0 | 8.9371 | 8.9371 | 0 | 0 | 0 | 73.597 | 849.5656 | 0 | 0.05921 | 4.3335 | 0 | 0 | 0 | 84.7315 | off_peak | 840.6285 | 0 | 100 | 9.16 | 0 | 90.84 | 367.1814 | 0
1265 | 965.85 | 329.216 | 25.2 | 53.2946 | 53.2946 | 0 | 0 | 0.57721 | 0.57721 | 0 | 0 | 0 | 74.137 | 913.1326 | 0 | 0.05921 | 4.5301 | 0 | 0 | 0 | 53.2946 | off_peak | 912.5554 | 0 | 100 | 5.52 | 0 | 94.48 | 241.4284 | 0
1266 | 908.69 | 121.063 | 24.6 | 19.6404 | 19.6404 | 0 | 0 | 0.037279 | 0.037279 | 0 | 0 | 0 | 74.1718 | 889.0868 | 0 | 0.05921 | 4.8975 | 0 | 0 | 0 | 19.6404 | off_peak | 889.0496 | 0 | 100 | 2.16 | 0 | 97.84 | 96.1896 | 0
1267 | 865.94 | 0 | 24.2 | 0 | 0 | 0 | 0 | 0 | 0 | 35.8043 | 35.8043 | 0 | 35.8954 | 830.1357 | 0 | 0.088511 | 5.3406 | 0 | 0 | 0 | 0 | on_peak | 830.1357 |  |  | 0 | 4.13 | 95.87 | 0 | 0
1268 | 902.62 | 0 | 23.8 | 0 | 0 | 0 | 0 | 0 | 0 | 24.7443 | 24.7443 | 0 | 9.4426 | 877.8757 | 0 | 0.088511 | 5.7237 | 0 | 0 | 0 | 0 | on_peak | 877.8757 |  |  | 0 | 2.74 | 97.26 | 0 | 0
1269 | 879.77 | 0 | 23.7 | 0 | 0 | 0 | 0 | 0 | 0 | 1.8943 | 1.8943 | 0 | 7.4174 | 877.8757 | 0 | 0.088511 | 6.0668 | 0 | 0 | 0 | 0 | on_peak | 877.8757 |  |  | 0 | 0.22 | 99.78 | 0 | 0
1270 | 814.88 | 0 | 23.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 814.88 | 0 | 0.088511 | 6.3216 | 0 | 0 | 0 | 0 | on_peak | 814.88 |  |  | 0 | 0 | 100 | 0 | 0
1271 | 877.3 | 0 | 23.5 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 18.9814 | 889.6624 | 0 | 0.05921 | 6.7311 | 0 | 0 | 0 | 0 | off_peak | 877.3 | 0 | 100 | 0 | 0 | 100 | 0 | 0
1272 | 814.65 | 0 | 23.4 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 30.5453 | 827.0124 | 0 | 0.05921 | 7.1733 | 0 | 0 | 0 | 0 | off_peak | 814.65 | 0 | 100 | 0 | 0 | 100 | 0 | 0
1273 | 779.18 | 0 | 23.2 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 42.1093 | 791.5424 | 0 | 0.05921 | 7.2198 | 0 | 0 | 0 | 0 | off_peak | 779.18 | 0 | 100 | 0 | 0 | 100 | 0 | 0
1274 | 691.77 | 0 | 23.1 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 53.6732 | 704.1324 | 0 | 0.05921 | 7.0403 | 0 | 0 | 0 | 0 | off_peak | 691.77 | 0 | 100 | 0 | 0 | 100 | 0 | 0
1275 | 650.03 | 0 | 22.9 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 65.2371 | 662.3924 | 0 | 0.05921 | 6.6079 | 0 | 0 | 0 | 0 | off_peak | 650.03 | 0 | 100 | 0 | 0 | 100 | 0 | 0
1276 | 628.17 | 0 | 22.9 | 0 | 0 | 0 | 0 | 8.9371 | 8.9371 | 0 | 0 | 0 | 73.597 | 637.1071 | 0 | 0.05921 | 6.0261 | 0 | 0 | 0 | 0 | off_peak | 628.17 | 0 | 100 | 0 | 0 | 100 | 0 | 0
1277 | 665.28 | 0 | 22.9 | 0 | 0 | 0 | 0 | 0.57721 | 0.57721 | 0 | 0 | 0 | 74.137 | 665.8572 | 0 | 0.05921 | 5.4472 | 0 | 0 | 0 | 0 | off_peak | 665.28 | 0 | 100 | 0 | 0 | 100 | 0 | 0
1278 | 737.66 | 0 | 22.9 | 0 | 0 | 0 | 0 | 0.037279 | 0.037279 | 0 | 0 | 0 | 74.1718 | 737.6973 | 0 | 0.05921 | 4.7747 | 0 | 0 | 0 | 0 | off_peak | 737.66 | 0 | 100 | 0 | 0 | 100 | 0 | 0
1279 | 812.31 | 0 | 23.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1718 | 812.31 | 0 | 0.088511 | 4.2256 | 0 | 0 | 0 | 0 | on_peak | 812.31 |  |  | 0 | 0 | 100 | 0 | 0
1280 | 817.99 | 94.3593 | 24.2 | 15.3302 | 15.3302 | 0 | 0 | 0 | 0 | 62.443 | 62.443 | 0 | 7.4174 | 740.2167 | 0 | 0.088511 | 3.8035 | 0 | 0 | 0 | 15.3302 | on_peak | 740.2167 |  |  | 1.87 | 7.63 | 90.49 | 58.3082 | 0
1281 | 855.69 | 253.8 | 24.9 | 41.1304 | 41.1304 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 814.5596 | 0 | 0.088511 | 3.5865 | 0 | 0 | 0 | 41.1304 | on_peak | 814.5596 |  |  | 4.81 | 0 | 95.19 | 147.5131 | 0
1282 | 874.53 | 498.245 | 25.4 | 80.5995 | 80.5995 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 793.9305 | 0 | 0.088511 | 3.441 | 0 | 0 | 0 | 80.5995 | on_peak | 793.9305 |  |  | 9.22 | 0 | 90.78 | 277.3462 | 0
1283 | 835.08 | 668.357 | 25.8 | 107.962 | 107.962 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 18.9814 | 739.4804 | 0 | 0.05921 | 3.4186 | 0 | 0 | 0 | 107.962 | off_peak | 727.118 | 0 | 100 | 12.93 | 0 | 87.07 | 369.0764 | 0
1284 | 961.88 | 669.598 | 26.2 | 108.0063 | 108.0063 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 30.5453 | 866.2361 | 0 | 0.05921 | 3.6487 | 0 | 0 | 0 | 108.0063 | off_peak | 853.8737 | 0 | 100 | 11.23 | 0 | 88.77 | 394.083 | 0
1285 | 908.96 | 809.228 | 26.3 | 130.4814 | 130.4814 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 42.1093 | 790.841 | 0 | 0.05921 | 4.1507 | 0 | 0 | 0 | 130.4814 | off_peak | 778.4786 | 0 | 100 | 14.36 | 0 | 85.64 | 541.5829 | 0
1286 | 908.75 | 740.343 | 26.4 | 119.3311 | 119.3311 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 53.6732 | 801.7813 | 0 | 0.05921 | 4.5366 | 0 | 0 | 0 | 119.3311 | off_peak | 789.4189 | 0 | 100 | 13.13 | 0 | 86.87 | 541.3565 | 0
1287 | 979.68 | 426.386 | 26.3 | 68.7513 | 68.7513 | 0 | 0 | 2.5528 | 2.5528 | 0 | 0 | 0 | 56.0611 | 913.4815 | 0 | 0.05921 | 4.6069 | 0 | 0 | 0 | 68.7513 | off_peak | 910.9287 | 0 | 100 | 7.02 | 0 | 92.98 | 316.7319 | 0
1288 | 895.22 | 356.58 | 26.1 | 57.5372 | 57.5372 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 67.625 | 850.0452 | 0 | 0.05921 | 4.7762 | 0 | 0 | 0 | 57.5372 | off_peak | 837.6828 | 0 | 100 | 6.43 | 0 | 93.57 | 274.8116 | 0
1289 | 902.81 | 272.261 | 25.8 | 43.9793 | 43.9793 | 0 | 0 | 6.5492 | 6.5492 | 0 | 0 | 0 | 73.7513 | 865.38 | 0 | 0.05921 | 5.16 | 0 | 0 | 0 | 43.9793 | off_peak | 858.8307 | 0 | 100 | 4.87 | 0 | 95.13 | 226.9326 | 0
1290 | 910.42 | 122.554 | 25.2 | 19.8395 | 19.8395 | 0 | 0 | 0.42299 | 0.42299 | 0 | 0 | 0 | 74.1469 | 891.0035 | 0 | 0.05921 | 5.5262 | 0 | 0 | 0 | 19.8395 | off_peak | 890.5805 | 0 | 100 | 2.18 | 0 | 97.82 | 109.6359 | 0
1291 | 824.63 | 0 | 24.8 | 0 | 0 | 0 | 0 | 0 | 0 | 62.4197 | 62.4197 | 0 | 7.4174 | 762.2103 | 0 | 0.088511 | 5.9399 | 0 | 0 | 0 | 0 | on_peak | 762.2103 |  |  | 0 | 7.57 | 92.43 | 0 | 0
1292 | 865.53 | 0 | 24.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 865.53 | 0 | 0.088511 | 6.2467 | 0 | 0 | 0 | 0 | on_peak | 865.53 |  |  | 0 | 0 | 100 | 0 | 0
1293 | 836.31 | 0 | 24.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 836.31 | 0 | 0.088511 | 6.641 | 0 | 0 | 0 | 0 | on_peak | 836.31 |  |  | 0 | 0 | 100 | 0 | 0
1294 | 792.52 | 0 | 23.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 792.52 | 0 | 0.088511 | 7.05 | 0 | 0 | 0 | 0 | on_peak | 792.52 |  |  | 0 | 0 | 100 | 0 | 0
1295 | 811.96 | 0 | 23.7 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 18.9814 | 824.3224 | 0 | 0.05921 | 7.3613 | 0 | 0 | 0 | 0 | off_peak | 811.96 | 0 | 100 | 0 | 0 | 100 | 0 | 0
1296 | 831.95 | 0 | 23.6 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 30.5453 | 844.3124 | 0 | 0.05921 | 7.4896 | 0 | 0 | 0 | 0 | off_peak | 831.95 | 0 | 100 | 0 | 0 | 100 | 0 | 0
1297 | 745.59 | 0 | 23.4 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 42.1093 | 757.9524 | 0 | 0.05921 | 7.4209 | 0 | 0 | 0 | 0 | off_peak | 745.59 | 0 | 100 | 0 | 0 | 100 | 0 | 0
1298 | 679.3 | 0 | 23.3 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 53.6732 | 691.6624 | 0 | 0.05921 | 7.3328 | 0 | 0 | 0 | 0 | off_peak | 679.3 | 0 | 100 | 0 | 0 | 100 | 0 | 0
1299 | 604.27 | 0 | 23.2 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 65.2371 | 616.6324 | 0 | 0.05921 | 6.7743 | 0 | 0 | 0 | 0 | off_peak | 604.27 | 0 | 100 | 0 | 0 | 100 | 0 | 0
1300 | 618.26 | 0 | 23 | 0 | 0 | 0 | 0 | 8.9371 | 8.9371 | 0 | 0 | 0 | 73.597 | 627.1971 | 0 | 0.05921 | 6.1063 | 0 | 0 | 0 | 0 | off_peak | 618.26 | 0 | 100 | 0 | 0 | 100 | 0 | 0
1301 | 582.23 | 0 | 23 | 0 | 0 | 0 | 0 | 0.57721 | 0.57721 | 0 | 0 | 0 | 74.137 | 582.8072 | 0 | 0.05921 | 5.5827 | 0 | 0 | 0 | 0 | off_peak | 582.23 | 0 | 100 | 0 | 0 | 100 | 0 | 0
1302 | 686.15 | 0 | 22.9 | 0 | 0 | 0 | 0 | 0.037279 | 0.037279 | 0 | 0 | 0 | 74.1718 | 686.1873 | 0 | 0.05921 | 4.8015 | 0 | 0 | 0 | 0 | off_peak | 686.15 | 0 | 100 | 0 | 0 | 100 | 0 | 0
1303 | 787.85 | 0 | 23.4 | 0 | 0 | 0 | 0 | 0 | 0 | 62.443 | 62.443 | 0 | 7.4174 | 725.407 | 0 | 0.088511 | 4.2305 | 0 | 0 | 0 | 0 | on_peak | 725.407 |  |  | 0 | 7.93 | 92.07 | 0 | 0
1304 | 851.25 | 99.4476 | 24.2 | 16.1569 | 16.1569 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 835.0931 | 0 | 0.088511 | 3.8057 | 0 | 0 | 0 | 16.1569 | on_peak | 835.0931 |  |  | 1.9 | 0 | 98.1 | 61.4879 | 0
1305 | 893.43 | 310.409 | 25 | 50.2863 | 50.2863 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 843.1437 | 0 | 0.088511 | 3.5205 | 0 | 0 | 0 | 50.2863 | on_peak | 843.1437 |  |  | 5.63 | 0 | 94.37 | 177.0344 | 0
1306 | 917.77 | 478.162 | 25.8 | 77.2392 | 77.2392 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 840.5308 | 0 | 0.088511 | 3.3651 | 0 | 0 | 0 | 77.2392 | on_peak | 840.5308 |  |  | 8.42 | 0 | 91.58 | 259.9147 | 0
1307 | 874.61 | 552.021 | 26.4 | 88.9767 | 88.9767 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 18.9814 | 797.9957 | 0 | 0.05921 | 3.3545 | 0 | 0 | 0 | 88.9767 | off_peak | 785.6333 | 0 | 100 | 10.17 | 0 | 89.83 | 298.4702 | 0
1308 | 1002.35 | 660.915 | 26.9 | 106.3359 | 106.3359 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 30.5453 | 908.3765 | 0 | 0.05921 | 3.5627 | 0 | 0 | 0 | 106.3359 | off_peak | 896.0141 | 0 | 100 | 10.61 | 0 | 89.39 | 378.8425 | 0
1309 | 871.01 | 704.699 | 27.2 | 113.2571 | 113.2571 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 42.1093 | 770.1153 | 0 | 0.05921 | 4.0388 | 0 | 0 | 0 | 113.2571 | off_peak | 757.7529 | 0 | 100 | 13 | 0 | 87 | 457.4218 | 0
1310 | 979.68 | 605.774 | 27.4 | 97.2875 | 97.2875 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 53.6732 | 894.7549 | 0 | 0.05921 | 4.4716 | 0 | 0 | 0 | 97.2875 | off_peak | 882.3925 | 0 | 100 | 9.93 | 0 | 90.07 | 435.0263 | 0
1311 | 1021.2 | 683.486 | 27.5 | 109.7282 | 109.7282 | 0 | 0 | 2.0097 | 2.0097 | 0 | 0 | 0 | 55.5531 | 913.4815 | 0 | 0.05921 | 4.5786 | 0 | 0 | 0 | 109.7282 | off_peak | 911.4718 | 0 | 100 | 10.75 | 0 | 89.25 | 502.4047 | 0
1312 | 938.33 | 485.764 | 27.4 | 78.0139 | 78.0139 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 67.1171 | 872.6785 | 0 | 0.05921 | 4.6403 | 0 | 0 | 0 | 78.0139 | off_peak | 860.3161 | 0 | 100 | 8.31 | 0 | 91.69 | 362.0079 | 0
1313 | 952.68 | 338.268 | 27 | 54.4049 | 54.4049 | 0 | 0 | 7.0572 | 7.0572 | 0 | 0 | 0 | 73.7185 | 905.3323 | 0 | 0.05921 | 4.8437 | 0 | 0 | 0 | 54.4049 | off_peak | 898.2751 | 0 | 100 | 5.71 | 0 | 94.29 | 263.5207 | 0
1314 | 893.53 | 126.877 | 26.3 | 20.4579 | 20.4579 | 0 | 0 | 0.45579 | 0.45579 | 0 | 0 | 0 | 74.1448 | 873.5279 | 0 | 0.05921 | 5.3749 | 0 | 0 | 0 | 20.4579 | off_peak | 873.0721 | 0 | 100 | 2.29 | 0 | 97.71 | 109.9596 | 0
1315 | 868.4 | 0 | 25.8 | 0 | 0 | 0 | 0 | 0 | 0 | 44.1034 | 44.1034 | 0 | 26.9963 | 824.2966 | 0 | 0.088511 | 5.8319 | 0 | 0 | 0 | 0 | on_peak | 824.2966 |  |  | 0 | 5.08 | 94.92 | 0 | 0
1316 | 896.19 | 0 | 25.2 | 0 | 0 | 0 | 0 | 0 | 0 | 18.3143 | 18.3143 | 0 | 7.4174 | 877.8757 | 0 | 0.088511 | 6.206 | 0 | 0 | 0 | 0 | on_peak | 877.8757 |  |  | 0 | 2.04 | 97.96 | 0 | 0
1317 | 813.03 | 0 | 24.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 813.03 | 0 | 0.088511 | 6.7031 | 0 | 0 | 0 | 0 | on_peak | 813.03 |  |  | 0 | 0 | 100 | 0 | 0
1318 | 809.76 | 0 | 24.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 809.76 | 0 | 0.088511 | 6.9753 | 0 | 0 | 0 | 0 | on_peak | 809.76 |  |  | 0 | 0 | 100 | 0 | 0
1319 | 851.24 | 0 | 24 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 18.9814 | 863.6024 | 0 | 0.05921 | 7.2501 | 0 | 0 | 0 | 0 | off_peak | 851.24 | 0 | 100 | 0 | 0 | 100 | 0 | 0
1320 | 786.42 | 0 | 23.8 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 30.5453 | 798.7824 | 0 | 0.05921 | 7.4019 | 0 | 0 | 0 | 0 | off_peak | 786.42 | 0 | 100 | 0 | 0 | 100 | 0 | 0
1321 | 785.94 | 0 | 23.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30.5453 | 785.94 | 0 | 0.05921 | 7.3454 | 0 | 0 | 0 | 0 | off_peak | 785.94 |  |  | 0 | 0 | 100 | 0 | 0
1322 | 683.68 | 0 | 23.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30.5453 | 683.68 | 0 | 0.05921 | 7.0736 | 0 | 0 | 0 | 0 | off_peak | 683.68 |  |  | 0 | 0 | 100 | 0 | 0
1323 | 671.34 | 0 | 23.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30.5453 | 671.34 | 0 | 0.05921 | 6.4155 | 0 | 0 | 0 | 0 | off_peak | 671.34 |  |  | 0 | 0 | 100 | 0 | 0
1324 | 683.15 | 0 | 23.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30.5453 | 683.15 | 0 | 0.05921 | 5.8487 | 0 | 0 | 0 | 0 | off_peak | 683.15 |  |  | 0 | 0 | 100 | 0 | 0
1325 | 688.84 | 0 | 23.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30.5453 | 688.84 | 0 | 0.05921 | 5.3848 | 0 | 0 | 0 | 0 | off_peak | 688.84 |  |  | 0 | 0 | 100 | 0 | 0
1326 | 782.05 | 0 | 23.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30.5453 | 782.05 | 0 | 0.05921 | 4.7556 | 0 | 0 | 0 | 0 | off_peak | 782.05 |  |  | 0 | 0 | 100 | 0 | 0
1327 | 773.98 | 0 | 23.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30.5453 | 773.98 | 0 | 0.05921 | 4.1928 | 0 | 0 | 0 | 0 | off_peak | 773.98 |  |  | 0 | 0 | 100 | 0 | 0
1328 | 820.85 | 102.683 | 24.7 | 16.6526 | 16.6526 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30.5453 | 804.1974 | 0 | 0.05921 | 3.7835 | 0 | 0 | 0 | 16.6526 | off_peak | 804.1974 |  |  | 2.03 | 0 | 97.97 | 63.0054 | 0
1329 | 878.55 | 260.099 | 25.5 | 42.0602 | 42.0602 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30.5453 | 836.4898 | 0 | 0.05921 | 3.4869 | 0 | 0 | 0 | 42.0602 | off_peak | 836.4898 |  |  | 4.79 | 0 | 95.21 | 146.6617 | 0
1330 | 852.11 | 476.95 | 26 | 76.9877 | 76.9877 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30.5453 | 775.1223 | 0 | 0.05921 | 3.2928 | 0 | 0 | 0 | 76.9877 | off_peak | 775.1223 |  |  | 9.03 | 0 | 90.97 | 253.5049 | 0
1331 | 845.48 | 367.929 | 26.4 | 59.3041 | 59.3041 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30.5453 | 786.1759 | 0 | 0.05921 | 3.1929 | 0 | 0 | 0 | 59.3041 | off_peak | 786.1759 |  |  | 7.01 | 0 | 92.99 | 189.3514 | 0
1332 | 926.17 | 788.221 | 26.8 | 126.8644 | 126.8644 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30.5453 | 799.3056 | 0 | 0.05921 | 3.2076 | 0 | 0 | 0 | 126.8644 | off_peak | 799.3056 |  |  | 13.7 | 0 | 86.3 | 406.93 | 0
1333 | 821.78 | 798.657 | 26.9 | 128.4975 | 128.4975 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30.5453 | 693.2825 | 0 | 0.05921 | 3.3693 | 0 | 0 | 0 | 128.4975 | off_peak | 693.2825 |  |  | 15.64 | 0 | 84.36 | 432.9406 | 0
1334 | 834.13 | 796.58 | 27 | 128.1168 | 128.1168 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30.5453 | 706.0132 | 0 | 0.05921 | 3.7438 | 0 | 0 | 0 | 128.1168 | off_peak | 706.0132 |  |  | 15.36 | 0 | 84.64 | 479.6431 | 0
1335 | 764.41 | 677.839 | 27 | 109.0193 | 109.0193 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30.5453 | 655.3907 | 0 | 0.05921 | 4.1606 | 0 | 0 | 0 | 109.0193 | off_peak | 655.3907 |  |  | 14.26 | 0 | 85.74 | 453.5895 | 0
1336 | 777.33 | 544.052 | 26.8 | 87.5653 | 87.5653 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30.5453 | 689.7647 | 0 | 0.05921 | 4.4845 | 0 | 0 | 0 | 87.5653 | off_peak | 689.7647 |  |  | 11.26 | 0 | 88.74 | 392.6872 | 0
1337 | 793.52 | 345.212 | 26.4 | 55.6425 | 55.6425 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30.5453 | 737.8775 | 0 | 0.05921 | 4.8106 | 0 | 0 | 0 | 55.6425 | off_peak | 737.8775 |  |  | 7.01 | 0 | 92.99 | 267.672 | 0
1338 | 728.87 | 131.66 | 25.7 | 21.2752 | 21.2752 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30.5453 | 707.5948 | 0 | 0.05921 | 5.2791 | 0 | 0 | 0 | 21.2752 | off_peak | 707.5948 |  |  | 2.92 | 0 | 97.08 | 112.3129 | 0
1339 | 686.95 | 0 | 25.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30.5453 | 686.95 | 0 | 0.05921 | 5.5543 | 0 | 0 | 0 | 0 | off_peak | 686.95 |  |  | 0 | 0 | 100 | 0 | 0
1340 | 677.14 | 0 | 24.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30.5453 | 677.14 | 0 | 0.05921 | 5.9 | 0 | 0 | 0 | 0 | off_peak | 677.14 |  |  | 0 | 0 | 100 | 0 | 0
1341 | 632.6 | 0 | 24.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30.5453 | 632.6 | 0 | 0.05921 | 6.1607 | 0 | 0 | 0 | 0 | off_peak | 632.6 |  |  | 0 | 0 | 100 | 0 | 0
1342 | 632.63 | 0 | 24.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30.5453 | 632.63 | 0 | 0.05921 | 6.4375 | 0 | 0 | 0 | 0 | off_peak | 632.63 |  |  | 0 | 0 | 100 | 0 | 0
1343 | 613.82 | 0 | 24.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30.5453 | 613.82 | 0 | 0.05921 | 6.7212 | 0 | 0 | 0 | 0 | off_peak | 613.82 |  |  | 0 | 0 | 100 | 0 | 0
1344 | 622.37 | 0 | 24.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30.5453 | 622.37 | 0 | 0.05921 | 6.9964 | 0 | 0 | 0 | 0 | off_peak | 622.37 |  |  | 0 | 0 | 100 | 0 | 0
1345 | 624.01 | 0 | 24.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30.5453 | 624.01 | 0 | 0.05921 | 6.8431 | 0 | 0 | 0 | 0 | off_peak | 624.01 |  |  | 0 | 0 | 100 | 0 | 0
1346 | 603.95 | 0 | 24.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30.5453 | 603.95 | 0 | 0.05921 | 6.4869 | 0 | 0 | 0 | 0 | off_peak | 603.95 |  |  | 0 | 0 | 100 | 0 | 0
1347 | 608.53 | 0 | 24.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30.5453 | 608.53 | 0 | 0.05921 | 5.9803 | 0 | 0 | 0 | 0 | off_peak | 608.53 |  |  | 0 | 0 | 100 | 0 | 0
1348 | 606.28 | 0 | 24.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30.5453 | 606.28 | 0 | 0.05921 | 5.5065 | 0 | 0 | 0 | 0 | off_peak | 606.28 |  |  | 0 | 0 | 100 | 0 | 0
1349 | 632.87 | 0 | 24.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30.5453 | 632.87 | 0 | 0.05921 | 5.0524 | 0 | 0 | 0 | 0 | off_peak | 632.87 |  |  | 0 | 0 | 100 | 0 | 0
1350 | 687.47 | 0 | 24.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30.5453 | 687.47 | 0 | 0.05921 | 4.4626 | 0 | 0 | 0 | 0 | off_peak | 687.47 |  |  | 0 | 0 | 100 | 0 | 0
1351 | 775.47 | 0 | 24.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30.5453 | 775.47 | 0 | 0.05921 | 3.9825 | 0 | 0 | 0 | 0 | off_peak | 775.47 |  |  | 0 | 0 | 100 | 0 | 0
1352 | 802.57 | 102.221 | 25.4 | 16.536 | 16.536 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30.5453 | 786.034 | 0 | 0.05921 | 3.6424 | 0 | 0 | 0 | 16.536 | off_peak | 786.034 |  |  | 2.06 | 0 | 97.94 | 60.2305 | 0
1353 | 773.56 | 297.899 | 26 | 48.0859 | 48.0859 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30.5453 | 725.4741 | 0 | 0.05921 | 3.3508 | 0 | 0 | 0 | 48.0859 | off_peak | 725.4741 |  |  | 6.22 | 0 | 93.78 | 161.1259 | 0
1354 | 755.49 | 497.454 | 26.5 | 80.1524 | 80.1524 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30.5453 | 675.3376 | 0 | 0.05921 | 3.157 | 0 | 0 | 0 | 80.1524 | off_peak | 675.3376 |  |  | 10.61 | 0 | 89.39 | 253.0411 | 0
1355 | 756.31 | 675.192 | 26.8 | 108.6723 | 108.6723 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30.5453 | 647.6377 | 0 | 0.05921 | 3.0704 | 0 | 0 | 0 | 108.6723 | off_peak | 647.6377 |  |  | 14.37 | 0 | 85.63 | 333.6703 | 0
1356 | 736.01 | 781.789 | 27 | 125.7379 | 125.7379 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30.5453 | 610.2721 | 0 | 0.05921 | 3.027 | 0 | 0 | 0 | 125.7379 | off_peak | 610.2721 |  |  | 17.08 | 0 | 82.92 | 380.6143 | 0
1357 | 725.18 | 707.536 | 27.2 | 113.713 | 113.713 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30.5453 | 611.467 | 0 | 0.05921 | 3.1041 | 0 | 0 | 0 | 113.713 | off_peak | 611.467 |  |  | 15.68 | 0 | 84.32 | 352.9741 | 0
1358 | 746.1 | 300.174 | 27.3 | 48.2255 | 48.2255 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30.5453 | 697.8745 | 0 | 0.05921 | 3.4637 | 0 | 0 | 0 | 48.2255 | off_peak | 697.8745 |  |  | 6.46 | 0 | 93.54 | 167.0408 | 0
1359 | 732.31 | 263.149 | 27.2 | 42.2925 | 42.2925 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30.5453 | 690.0175 | 0 | 0.05921 | 3.7666 | 0 | 0 | 0 | 42.2925 | off_peak | 690.0175 |  |  | 5.78 | 0 | 94.22 | 159.298 | 0
1360 | 733.57 | 295.771 | 27.1 | 47.5527 | 47.5527 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30.5453 | 686.0173 | 0 | 0.05921 | 3.8312 | 0 | 0 | 0 | 47.5527 | off_peak | 686.0173 |  |  | 6.48 | 0 | 93.52 | 182.1855 | 0
1361 | 705.62 | 261.578 | 26.8 | 42.101 | 42.101 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30.5453 | 663.519 | 0 | 0.05921 | 4.1179 | 0 | 0 | 0 | 42.101 | off_peak | 663.519 |  |  | 5.97 | 0 | 94.03 | 173.3676 | 0
1362 | 701.94 | 130.806 | 26.3 | 21.0914 | 21.0914 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30.5453 | 680.8486 | 0 | 0.05921 | 4.5536 | 0 | 0 | 0 | 21.0914 | off_peak | 680.8486 |  |  | 3 | 0 | 97 | 96.0422 | 0
1363 | 677.93 | 0 | 26.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30.5453 | 677.93 | 0 | 0.05921 | 5.0703 | 0 | 0 | 0 | 0 | off_peak | 677.93 |  |  | 0 | 0 | 100 | 0 | 0
1364 | 616.98 | 0 | 25.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30.5453 | 616.98 | 0 | 0.05921 | 5.5436 | 0 | 0 | 0 | 0 | off_peak | 616.98 |  |  | 0 | 0 | 100 | 0 | 0
1365 | 608.36 | 0 | 25.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30.5453 | 608.36 | 0 | 0.05921 | 5.827 | 0 | 0 | 0 | 0 | off_peak | 608.36 |  |  | 0 | 0 | 100 | 0 | 0
1366 | 616.42 | 0 | 25.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30.5453 | 616.42 | 0 | 0.05921 | 6.2219 | 0 | 0 | 0 | 0 | off_peak | 616.42 |  |  | 0 | 0 | 100 | 0 | 0
1367 | 589.33 | 0 | 25 | 0 | 0 | 0 | 0 | 8.7006 | 8.7006 | 0 | 0 | 0 | 38.684 | 598.0306 | 0 | 0.05921 | 6.5499 | 0 | 0 | 0 | 0 | off_peak | 589.33 | 0 | 100 | 0 | 0 | 100 | 0 | 0
1368 | 585.97 | 0 | 24.8 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 50.2479 | 598.3324 | 0 | 0.05921 | 6.8449 | 0 | 0 | 0 | 0 | off_peak | 585.97 | 0 | 100 | 0 | 0 | 100 | 0 | 0
1369 | 599.52 | 0 | 24.7 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 61.8119 | 611.8824 | 0 | 0.05921 | 6.8674 | 0 | 0 | 0 | 0 | off_peak | 599.52 | 0 | 100 | 0 | 0 | 100 | 0 | 0
1370 | 560.84 | 0 | 24.6 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 73.3758 | 573.2024 | 0 | 0.05921 | 6.6445 | 0 | 0 | 0 | 0 | off_peak | 560.84 | 0 | 100 | 0 | 0 | 100 | 0 | 0
1371 | 588.03 | 0 | 24.4 | 0 | 0 | 0 | 0 | 0.79843 | 0.79843 | 0 | 0 | 0 | 74.1227 | 588.8284 | 0 | 0.05921 | 6.1792 | 0 | 0 | 0 | 0 | off_peak | 588.03 | 0 | 100 | 0 | 0 | 100 | 0 | 0
1372 | 583.1 | 0 | 24.2 | 0 | 0 | 0 | 0 | 0.051567 | 0.051567 | 0 | 0 | 0 | 74.1709 | 583.1516 | 0 | 0.05921 | 5.6738 | 0 | 0 | 0 | 0 | off_peak | 583.1 | 0 | 100 | 0 | 0 | 100 | 0 | 0
1373 | 595.64 | 0 | 24 | 0 | 0 | 0 | 0 | 0.0033305 | 0.0033305 | 0 | 0 | 0 | 74.174 | 595.6433 | 0 | 0.05921 | 5.1035 | 0 | 0 | 0 | 0 | off_peak | 595.64 | 0 | 100 | 0 | 0 | 100 | 0 | 0
1374 | 713.09 | 0 | 23.7 | 0 | 0 | 0 | 0 | 0.0002151 | 0.0002151 | 0 | 0 | 0 | 74.1742 | 713.0902 | 0 | 0.05921 | 4.4306 | 0 | 0 | 0 | 0 | off_peak | 713.09 | 0 | 100 | 0 | 0 | 100 | 0 | 0
1375 | 755.34 | 0 | 23.5 | 0 | 0 | 0 | 0 | 0 | 0 | 62.4453 | 62.4453 | 0 | 7.4174 | 692.8947 | 0 | 0.088511 | 3.8078 | 0 | 0 | 0 | 0 | on_peak | 692.8947 |  |  | 0 | 8.27 | 91.73 | 0 | 0
1376 | 831.29 | 102.762 | 23.6 | 16.7313 | 16.7313 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 814.5587 | 0 | 0.088511 | 3.4227 | 0 | 0 | 0 | 16.7313 | on_peak | 814.5587 |  |  | 2.01 | 0 | 97.99 | 57.2669 | 0
1377 | 819.82 | 308.991 | 23.9 | 50.2548 | 50.2548 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 769.5652 | 0 | 0.088511 | 3.195 | 0 | 0 | 0 | 50.2548 | on_peak | 769.5652 |  |  | 6.13 | 0 | 93.87 | 160.5622 | 0
1378 | 888.87 | 507.343 | 24.4 | 82.3671 | 82.3671 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 806.5029 | 0 | 0.088511 | 3.0452 | 0 | 0 | 0 | 82.3671 | on_peak | 806.5029 |  |  | 9.27 | 0 | 90.73 | 250.8204 | 0
1379 | 832.08 | 665.987 | 24.8 | 107.9676 | 107.9676 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 18.9814 | 736.4748 | 0 | 0.05921 | 3.0611 | 0 | 0 | 0 | 107.9676 | off_peak | 724.1124 | 0 | 100 | 12.98 | 0 | 87.02 | 330.4965 | 0
1380 | 923.63 | 693.208 | 25.4 | 112.138 | 112.138 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 30.5453 | 823.8544 | 0 | 0.05921 | 3.255 | 0 | 0 | 0 | 112.138 | off_peak | 811.492 | 0 | 100 | 12.14 | 0 | 87.86 | 365.0127 | 0
1381 | 886.8 | 645.376 | 26 | 104.1745 | 104.1745 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 42.1093 | 794.9878 | 0 | 0.05921 | 3.7803 | 0 | 0 | 0 | 104.1745 | off_peak | 782.6255 | 0 | 100 | 11.75 | 0 | 88.25 | 393.8103 | 0
1382 | 920.39 | 250.143 | 26.1 | 40.3627 | 40.3627 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 53.6732 | 892.3897 | 0 | 0.05921 | 4.1305 | 0 | 0 | 0 | 40.3627 | off_peak | 880.0273 | 0 | 100 | 4.39 | 0 | 95.61 | 166.7167 | 0
1383 | 948.3 | 133.186 | 26 | 21.4985 | 21.4985 | 0 | 0 | 0 | 0 | 13.32 | 13.32 | 0 | 39.4335 | 913.4815 | 0 | 0.05921 | 4.1484 | 0 | 0 | 0 | 21.4985 | off_peak | 913.4815 |  |  | 2.27 | 1.4 | 96.33 | 89.1838 | 0
1384 | 938.88 | 324.071 | 25.7 | 52.3672 | 52.3672 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 50.9974 | 898.8752 | 0 | 0.05921 | 4.0743 | 0 | 0 | 0 | 52.3672 | off_peak | 886.5128 | 0 | 100 | 5.58 | 0 | 94.42 | 213.3583 | 0
1385 | 922 | 221.503 | 25.2 | 35.8576 | 35.8576 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 62.5614 | 898.5047 | 0 | 0.05921 | 4.3082 | 0 | 0 | 0 | 35.8576 | off_peak | 886.1424 | 0 | 100 | 3.89 | 0 | 96.11 | 154.4832 | 0
1386 | 927.07 | 123.381 | 24.5 | 20.0237 | 20.0237 | 0 | 0 | 6.4352 | 6.4352 | 0 | 0 | 0 | 68.5809 | 913.4815 | 0 | 0.05921 | 4.5724 | 0 | 0 | 0 | 20.0237 | off_peak | 907.0463 | 0 | 100 | 2.16 | 0 | 97.84 | 91.5566 | 0
1387 | 868.11 | 0 | 24.1 | 0 | 0 | 0 | 0 | 0 | 0 | 46.6189 | 46.6189 | 0 | 18.7433 | 821.4911 | 0 | 0.088511 | 4.906 | 0 | 0 | 0 | 0 | on_peak | 821.4911 |  |  | 0 | 5.37 | 94.63 | 0 | 0
1388 | 888.47 | 0 | 23 | 0 | 0 | 0 | 0 | 0 | 0 | 10.5943 | 10.5943 | 0 | 7.4174 | 877.8757 | 0 | 0.088511 | 5.3476 | 0 | 0 | 0 | 0 | on_peak | 877.8757 |  |  | 0 | 1.19 | 98.81 | 0 | 0
1389 | 860 | 0 | 22.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 860 | 0 | 0.088511 | 5.639 | 0 | 0 | 0 | 0 | on_peak | 860 |  |  | 0 | 0 | 100 | 0 | 0
1390 | 799.79 | 0 | 22.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 799.79 | 0 | 0.088511 | 6.0175 | 0 | 0 | 0 | 0 | on_peak | 799.79 |  |  | 0 | 0 | 100 | 0 | 0
1391 | 822.63 | 0 | 21.8 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 18.9814 | 834.9924 | 0 | 0.05921 | 6.6068 | 0 | 0 | 0 | 0 | off_peak | 822.63 | 0 | 100 | 0 | 0 | 100 | 0 | 0
1392 | 829.46 | 0 | 21.4 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 30.5453 | 841.8224 | 0 | 0.05921 | 7.0196 | 0 | 0 | 0 | 0 | off_peak | 829.46 | 0 | 100 | 0 | 0 | 100 | 0 | 0
1393 | 774.9 | 0 | 21 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 42.1093 | 787.2624 | 0 | 0.05921 | 7.1517 | 0 | 0 | 0 | 0 | off_peak | 774.9 | 0 | 100 | 0 | 0 | 100 | 0 | 0
1394 | 711.22 | 0 | 20.6 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 53.6732 | 723.5824 | 0 | 0.05921 | 6.9959 | 0 | 0 | 0 | 0 | off_peak | 711.22 | 0 | 100 | 0 | 0 | 100 | 0 | 0
1395 | 670.63 | 0 | 20.3 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 65.2371 | 682.9924 | 0 | 0.05921 | 6.4852 | 0 | 0 | 0 | 0 | off_peak | 670.63 | 0 | 100 | 0 | 0 | 100 | 0 | 0
1396 | 632.88 | 0 | 19.9 | 0 | 0 | 0 | 0 | 8.9371 | 8.9371 | 0 | 0 | 0 | 73.597 | 641.8171 | 0 | 0.05921 | 5.856 | 0 | 0 | 0 | 0 | off_peak | 632.88 | 0 | 100 | 0 | 0 | 100 | 0 | 0
1397 | 654.57 | 0 | 19.4 | 0 | 0 | 0 | 0 | 0.57721 | 0.57721 | 0 | 0 | 0 | 74.137 | 655.1472 | 0 | 0.05921 | 5.2165 | 0 | 0 | 0 | 0 | off_peak | 654.57 | 0 | 100 | 0 | 0 | 100 | 0 | 0
1398 | 717.71 | 0 | 18.8 | 0 | 0 | 0 | 0 | 0.037279 | 0.037279 | 0 | 0 | 0 | 74.1718 | 717.7473 | 0 | 0.05921 | 4.4304 | 0 | 0 | 0 | 0 | off_peak | 717.71 | 0 | 100 | 0 | 0 | 100 | 0 | 0
1399 | 818.87 | 0 | 18.3 | 0 | 0 | 0 | 0 | 0 | 0 | 62.443 | 62.443 | 0 | 7.4174 | 756.427 | 0 | 0.088511 | 3.8234 | 0 | 0 | 0 | 0 | on_peak | 756.427 |  |  | 0 | 7.63 | 92.37 | 0 | 0
1400 | 847.26 | 111.317 | 18.3 | 18.4683 | 18.4683 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 828.7917 | 0 | 0.088511 | 3.4166 | 0 | 0 | 0 | 18.4683 | on_peak | 828.7917 |  |  | 2.18 | 0 | 97.82 | 63.0996 | 0
1401 | 836.9 | 324.246 | 18.8 | 53.7003 | 53.7003 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 783.1997 | 0 | 0.088511 | 3.1612 | 0 | 0 | 0 | 53.7003 | on_peak | 783.1997 |  |  | 6.42 | 0 | 93.58 | 169.756 | 0
1402 | 852.74 | 474.924 | 19.6 | 78.4334 | 78.4334 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 774.3066 | 0 | 0.088511 | 3.0134 | 0 | 0 | 0 | 78.4334 | on_peak | 774.3066 |  |  | 9.2 | 0 | 90.8 | 236.3519 | 0
1403 | 856.44 | 503.199 | 20.5 | 82.8388 | 82.8388 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 18.9814 | 785.9635 | 0 | 0.05921 | 3.0027 | 0 | 0 | 0 | 82.8388 | off_peak | 773.6012 | 0 | 100 | 9.67 | 0 | 90.33 | 248.7391 | 0
1404 | 927.29 | 728.04 | 21.4 | 119.471 | 119.471 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 30.5453 | 820.1814 | 0 | 0.05921 | 3.2754 | 0 | 0 | 0 | 119.471 | off_peak | 807.819 | 0 | 100 | 12.88 | 0 | 87.12 | 391.3123 | 0
1405 | 842.69 | 778.276 | 22.1 | 127.397 | 127.397 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 42.1093 | 727.6554 | 0 | 0.05921 | 3.7871 | 0 | 0 | 0 | 127.397 | off_peak | 715.293 | 0 | 100 | 15.12 | 0 | 84.88 | 482.4708 | 0
1406 | 892.97 | 453.462 | 22.6 | 74.0955 | 74.0955 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 53.6732 | 831.2368 | 0 | 0.05921 | 4.0594 | 0 | 0 | 0 | 74.0955 | off_peak | 818.8745 | 0 | 100 | 8.3 | 0 | 91.7 | 300.7804 | 0
1407 | 935.72 | 614.154 | 22.9 | 100.2451 | 100.2451 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 65.2371 | 847.8373 | 0 | 0.05921 | 4.0405 | 0 | 0 | 0 | 100.2451 | off_peak | 835.4749 | 0 | 100 | 10.71 | 0 | 89.29 | 405.0397 | 0
1408 | 905.34 | 531.081 | 22.9 | 86.6855 | 86.6855 | 0 | 0 | 8.9371 | 8.9371 | 0 | 0 | 0 | 73.597 | 827.5916 | 0 | 0.05921 | 4.1207 | 0 | 0 | 0 | 86.6855 | off_peak | 818.6545 | 0 | 100 | 9.57 | 0 | 90.43 | 357.2037 | 0
1409 | 872.27 | 335.242 | 22.6 | 54.7784 | 54.7784 | 0 | 0 | 0.57721 | 0.57721 | 0 | 0 | 0 | 74.137 | 818.0688 | 0 | 0.05921 | 4.3433 | 0 | 0 | 0 | 54.7784 | off_peak | 817.4916 | 0 | 100 | 6.28 | 0 | 93.72 | 237.9195 | 0
1410 | 875.28 | 127.149 | 22.1 | 20.8132 | 20.8132 | 0 | 0 | 0.037279 | 0.037279 | 0 | 0 | 0 | 74.1718 | 854.5041 | 0 | 0.05921 | 4.5761 | 0 | 0 | 0 | 20.8132 | off_peak | 854.4668 | 0 | 100 | 2.38 | 0 | 97.62 | 95.2442 | 0
1411 | 854.19 | 0 | 21.8 | 0 | 0 | 0 | 0 | 0 | 0 | 62.443 | 62.443 | 0 | 7.4174 | 791.747 | 0 | 0.088511 | 4.9169 | 0 | 0 | 0 | 0 | on_peak | 791.747 |  |  | 0 | 7.31 | 92.69 | 0 | 0
1412 | 811.54 | 0 | 19.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 811.54 | 0 | 0.088511 | 5.3114 | 0 | 0 | 0 | 0 | on_peak | 811.54 |  |  | 0 | 0 | 100 | 0 | 0
1413 | 832.98 | 0 | 19.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 832.98 | 0 | 0.088511 | 5.6638 | 0 | 0 | 0 | 0 | on_peak | 832.98 |  |  | 0 | 0 | 100 | 0 | 0
1414 | 788.17 | 0 | 19.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 788.17 | 0 | 0.088511 | 6.1068 | 0 | 0 | 0 | 0 | on_peak | 788.17 |  |  | 0 | 0 | 100 | 0 | 0
1415 | 772.49 | 0 | 19.7 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 18.9814 | 784.8524 | 0 | 0.05921 | 6.6083 | 0 | 0 | 0 | 0 | off_peak | 772.49 | 0 | 100 | 0 | 0 | 100 | 0 | 0
1416 | 746.25 | 0 | 19.7 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 30.5453 | 758.6124 | 0 | 0.05921 | 7.0374 | 0 | 0 | 0 | 0 | off_peak | 746.25 | 0 | 100 | 0 | 0 | 100 | 0 | 0
1417 | 748.27 | 0 | 19.7 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 42.1093 | 760.6324 | 0 | 0.05921 | 7.0852 | 0 | 0 | 0 | 0 | off_peak | 748.27 | 0 | 100 | 0 | 0 | 100 | 0 | 0
1418 | 688.11 | 0 | 19.7 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 53.6732 | 700.4724 | 0 | 0.05921 | 6.8778 | 0 | 0 | 0 | 0 | off_peak | 688.11 | 0 | 100 | 0 | 0 | 100 | 0 | 0
1419 | 634.99 | 0 | 19.9 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 65.2371 | 647.3524 | 0 | 0.05921 | 6.3242 | 0 | 0 | 0 | 0 | off_peak | 634.99 | 0 | 100 | 0 | 0 | 100 | 0 | 0
1420 | 650.15 | 0 | 20.2 | 0 | 0 | 0 | 0 | 8.9371 | 8.9371 | 0 | 0 | 0 | 73.597 | 659.0871 | 0 | 0.05921 | 5.7774 | 0 | 0 | 0 | 0 | off_peak | 650.15 | 0 | 100 | 0 | 0 | 100 | 0 | 0
1421 | 629.36 | 0 | 20.4 | 0 | 0 | 0 | 0 | 0.57721 | 0.57721 | 0 | 0 | 0 | 74.137 | 629.9372 | 0 | 0.05921 | 5.1032 | 0 | 0 | 0 | 0 | off_peak | 629.36 | 0 | 100 | 0 | 0 | 100 | 0 | 0
1422 | 640.49 | 0 | 20.5 | 0 | 0 | 0 | 0 | 0.037279 | 0.037279 | 0 | 0 | 0 | 74.1718 | 640.5273 | 0 | 0.05921 | 4.4549 | 0 | 0 | 0 | 0 | off_peak | 640.49 | 0 | 100 | 0 | 0 | 100 | 0 | 0
1423 | 702.84 | 0 | 20.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1718 | 702.84 | 0 | 0.088511 | 3.8026 | 0 | 0 | 0 | 0 | on_peak | 702.84 |  |  | 0 | 0 | 100 | 0 | 0
1424 | 666.85 | 121.903 | 21.3 | 20.0113 | 20.0113 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1718 | 646.8387 | 0 | 0.088511 | 3.37 | 0 | 0 | 0 | 20.0113 | on_peak | 646.8387 |  |  | 3 | 0 | 97 | 67.4378 | 0
1425 | 703.1 | 344.872 | 22 | 56.4727 | 56.4727 | 0 | 0 | 0 | 0 | 62.443 | 62.443 | 0 | 7.4174 | 584.1843 | 0 | 0.088511 | 3.1166 | 0 | 0 | 0 | 56.4727 | on_peak | 584.1843 |  |  | 8.03 | 8.88 | 83.09 | 176.0002 | 0
1426 | 756.28 | 557.356 | 22.6 | 91.0718 | 91.0718 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 665.2082 | 0 | 0.088511 | 2.9987 | 0 | 0 | 0 | 91.0718 | on_peak | 665.2082 |  |  | 12.04 | 0 | 87.96 | 273.0939 | 0
1427 | 713.31 | 727.11 | 23.3 | 118.5127 | 118.5127 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 18.9814 | 607.1597 | 0 | 0.05921 | 2.9754 | 0 | 0 | 0 | 118.5127 | off_peak | 594.7973 | 0 | 100 | 16.61 | 0 | 83.39 | 352.6203 | 0
1428 | 705.26 | 833.79 | 23.7 | 135.7061 | 135.7061 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 30.5453 | 581.9162 | 0 | 0.05921 | 3.1882 | 0 | 0 | 0 | 135.7061 | off_peak | 569.5539 | 0 | 100 | 19.24 | 0 | 80.76 | 432.6533 | 0
1429 | 774.07 | 872.585 | 24 | 141.8677 | 141.8677 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 42.1093 | 644.5647 | 0 | 0.05921 | 3.7054 | 0 | 0 | 0 | 141.8677 | off_peak | 632.2023 | 0 | 100 | 18.33 | 0 | 81.67 | 525.6775 | 0
1430 | 755.58 | 837.045 | 24.2 | 135.9918 | 135.9918 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 53.6732 | 631.9506 | 0 | 0.05921 | 3.9528 | 0 | 0 | 0 | 135.9918 | off_peak | 619.5882 | 0 | 100 | 18 | 0 | 82 | 537.5482 | 0
1431 | 765.93 | 735.965 | 24.3 | 119.5268 | 119.5268 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 65.2371 | 658.7656 | 0 | 0.05921 | 4.0232 | 0 | 0 | 0 | 119.5268 | off_peak | 646.4032 | 0 | 100 | 15.61 | 0 | 84.39 | 480.8838 | 0
1432 | 769.76 | 571.107 | 24.2 | 92.7858 | 92.7858 | 0 | 0 | 8.9371 | 8.9371 | 0 | 0 | 0 | 73.597 | 685.9113 | 0 | 0.05921 | 4.1304 | 0 | 0 | 0 | 92.7858 | off_peak | 676.9742 | 0 | 100 | 12.05 | 0 | 87.95 | 383.239 | 0
1433 | 730.21 | 365.194 | 23.7 | 59.4383 | 59.4383 | 0 | 0 | 0.57721 | 0.57721 | 0 | 0 | 0 | 74.137 | 671.3489 | 0 | 0.05921 | 4.221 | 0 | 0 | 0 | 59.4383 | off_peak | 670.7717 | 0 | 100 | 8.14 | 0 | 91.86 | 250.8909 | 0
1434 | 755.78 | 143.915 | 22.9 | 23.4905 | 23.4905 | 0 | 0 | 0.037279 | 0.037279 | 0 | 0 | 0 | 74.1718 | 732.3268 | 0 | 0.05921 | 4.3959 | 0 | 0 | 0 | 23.4905 | off_peak | 732.2895 | 0 | 100 | 3.11 | 0 | 96.89 | 103.2607 | 0
1435 | 746.64 | 0 | 22.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1718 | 746.64 | 0 | 0.088511 | 4.8205 | 0 | 0 | 0 | 0 | on_peak | 746.64 |  |  | 0 | 0 | 100 | 0 | 0
1436 | 733.02 | 0 | 21.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1718 | 733.02 | 0 | 0.088511 | 5.2553 | 0 | 0 | 0 | 0 | on_peak | 733.02 |  |  | 0 | 0 | 100 | 0 | 0
1437 | 762.21 | 0 | 21.3 | 0 | 0 | 0 | 0 | 0 | 0 | 62.443 | 62.443 | 0 | 7.4174 | 699.767 | 0 | 0.088511 | 5.7523 | 0 | 0 | 0 | 0 | on_peak | 699.767 |  |  | 0 | 8.19 | 91.81 | 0 | 0
1438 | 729.21 | 0 | 21.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 729.21 | 0 | 0.088511 | 6.0576 | 0 | 0 | 0 | 0 | on_peak | 729.21 |  |  | 0 | 0 | 100 | 0 | 0
1439 | 781.38 | 0 | 20.9 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 18.9814 | 793.7424 | 0 | 0.05921 | 6.4253 | 0 | 0 | 0 | 0 | off_peak | 781.38 | 0 | 100 | 0 | 0 | 100 | 0 | 0
1440 | 703.65 | 0 | 20.8 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 30.5453 | 716.0124 | 0 | 0.05921 | 6.7028 | 0 | 0 | 0 | 0 | off_peak | 703.65 | 0 | 100 | 0 | 0 | 100 | 0 | 0
1441 | 672.74 | 0 | 20.7 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 42.1093 | 685.1024 | 0 | 0.05921 | 6.7376 | 0 | 0 | 0 | 0 | off_peak | 672.74 | 0 | 100 | 0 | 0 | 100 | 0 | 0
1442 | 651.88 | 0 | 20.7 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 53.6732 | 664.2424 | 0 | 0.05921 | 6.5502 | 0 | 0 | 0 | 0 | off_peak | 651.88 | 0 | 100 | 0 | 0 | 100 | 0 | 0
1443 | 592.88 | 0 | 20.7 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 65.2371 | 605.2424 | 0 | 0.05921 | 6.0355 | 0 | 0 | 0 | 0 | off_peak | 592.88 | 0 | 100 | 0 | 0 | 100 | 0 | 0
1444 | 579.02 | 0 | 20.7 | 0 | 0 | 0 | 0 | 8.9371 | 8.9371 | 0 | 0 | 0 | 73.597 | 587.9571 | 0 | 0.05921 | 5.4871 | 0 | 0 | 0 | 0 | off_peak | 579.02 | 0 | 100 | 0 | 0 | 100 | 0 | 0
1445 | 584.93 | 0 | 20.8 | 0 | 0 | 0 | 0 | 0.57721 | 0.57721 | 0 | 0 | 0 | 74.137 | 585.5072 | 0 | 0.05921 | 4.8915 | 0 | 0 | 0 | 0 | off_peak | 584.93 | 0 | 100 | 0 | 0 | 100 | 0 | 0
1446 | 655.33 | 0 | 20.9 | 0 | 0 | 0 | 0 | 0.037279 | 0.037279 | 0 | 0 | 0 | 74.1718 | 655.3673 | 0 | 0.05921 | 4.2701 | 0 | 0 | 0 | 0 | off_peak | 655.33 | 0 | 100 | 0 | 0 | 100 | 0 | 0
1447 | 741.6 | 0 | 21.2 | 0 | 0 | 0 | 0 | 0 | 0 | 62.443 | 62.443 | 0 | 7.4174 | 679.157 | 0 | 0.088511 | 3.7579 | 0 | 0 | 0 | 0 | on_peak | 679.157 |  |  | 0 | 8.42 | 91.58 | 0 | 0
1448 | 785.16 | 123.351 | 22 | 20.1987 | 20.1987 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 764.9613 | 0 | 0.088511 | 3.3794 | 0 | 0 | 0 | 20.1987 | on_peak | 764.9613 |  |  | 2.57 | 0 | 97.43 | 68.26 | 0
1449 | 813.45 | 344.232 | 22.7 | 56.2273 | 56.2273 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 757.2227 | 0 | 0.088511 | 3.1516 | 0 | 0 | 0 | 56.2273 | on_peak | 757.2227 |  |  | 6.91 | 0 | 93.09 | 177.2065 | 0
1450 | 897.96 | 550.988 | 23.2 | 89.8385 | 89.8385 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 808.1215 | 0 | 0.088511 | 3.0186 | 0 | 0 | 0 | 89.8385 | on_peak | 808.1215 |  |  | 10 | 0 | 90 | 271.1908 | 0
1451 | 901.86 | 714.126 | 23.7 | 116.2298 | 116.2298 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 18.9814 | 797.9925 | 0 | 0.05921 | 3.0041 | 0 | 0 | 0 | 116.2298 | off_peak | 785.6302 | 0 | 100 | 12.89 | 0 | 87.11 | 349.1687 | 0
1452 | 901.3 | 814.186 | 24.2 | 132.278 | 132.278 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 30.5453 | 781.3844 | 0 | 0.05921 | 3.1868 | 0 | 0 | 0 | 132.278 | off_peak | 769.022 | 0 | 100 | 14.68 | 0 | 85.32 | 421.548 | 0
1453 | 895.21 | 810.726 | 24.5 | 131.574 | 131.574 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 42.1093 | 775.9984 | 0 | 0.05921 | 3.6476 | 0 | 0 | 0 | 131.574 | off_peak | 763.636 | 0 | 100 | 14.7 | 0 | 85.3 | 479.9343 | 0
1454 | 917.29 | 826.905 | 24.8 | 134.0551 | 134.0551 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 53.6732 | 795.5973 | 0 | 0.05921 | 3.9678 | 0 | 0 | 0 | 134.0551 | off_peak | 783.2349 | 0 | 100 | 14.61 | 0 | 85.39 | 531.8989 | 0
1455 | 936.11 | 725.633 | 25.1 | 117.5102 | 117.5102 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 65.2371 | 830.9621 | 0 | 0.05921 | 3.9464 | 0 | 0 | 0 | 117.5102 | off_peak | 818.5998 | 0 | 100 | 12.55 | 0 | 87.45 | 463.739 | 0
1456 | 925.84 | 565.271 | 25.1 | 91.5409 | 91.5409 | 0 | 0 | 8.9371 | 8.9371 | 0 | 0 | 0 | 73.597 | 843.2362 | 0 | 0.05921 | 4.0322 | 0 | 0 | 0 | 91.5409 | off_peak | 834.2991 | 0 | 100 | 9.89 | 0 | 90.11 | 369.1119 | 0
1457 | 894.16 | 360.78 | 24.7 | 58.5095 | 58.5095 | 0 | 0 | 0.57721 | 0.57721 | 0 | 0 | 0 | 74.137 | 836.2277 | 0 | 0.05921 | 4.2273 | 0 | 0 | 0 | 58.5095 | off_peak | 835.6505 | 0 | 100 | 6.54 | 0 | 93.46 | 247.3365 | 0
1458 | 923.09 | 140.951 | 24.1 | 22.908 | 22.908 | 0 | 0 | 0.037279 | 0.037279 | 0 | 0 | 0 | 74.1718 | 900.2192 | 0 | 0.05921 | 4.5793 | 0 | 0 | 0 | 22.908 | off_peak | 900.182 | 0 | 100 | 2.48 | 0 | 97.52 | 104.9029 | 0
1459 | 876.35 | 0 | 23.7 | 0 | 0 | 0 | 0 | 0 | 0 | 9.581 | 9.581 | 0 | 63.9293 | 866.769 | 0 | 0.088511 | 4.9478 | 0 | 0 | 0 | 0 | on_peak | 866.769 |  |  | 0 | 1.09 | 98.91 | 0 | 0
1460 | 881.78 | 0 | 22.8 | 0 | 0 | 0 | 0 | 0 | 0 | 45.0711 | 45.0711 | 0 | 15.7463 | 836.7089 | 0 | 0.088511 | 5.3899 | 0 | 0 | 0 | 0 | on_peak | 836.7089 |  |  | 0 | 5.11 | 94.89 | 0 | 0
1461 | 874.56 | 0 | 22.4 | 0 | 0 | 0 | 0 | 0 | 0 | 7.791 | 7.791 | 0 | 7.4174 | 866.769 | 0 | 0.088511 | 5.5981 | 0 | 0 | 0 | 0 | on_peak | 866.769 |  |  | 0 | 0.89 | 99.11 | 0 | 0
1462 | 782.41 | 0 | 22.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 782.41 | 0 | 0.088511 | 6.0385 | 0 | 0 | 0 | 0 | on_peak | 782.41 |  |  | 0 | 0 | 100 | 0 | 0
1463 | 813.76 | 0 | 21.9 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 18.9814 | 826.1224 | 0 | 0.05921 | 6.3769 | 0 | 0 | 0 | 0 | off_peak | 813.76 | 0 | 100 | 0 | 0 | 100 | 0 | 0
1464 | 812.72 | 0 | 21.7 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 30.5453 | 825.0824 | 0 | 0.05921 | 6.652 | 0 | 0 | 0 | 0 | off_peak | 812.72 | 0 | 100 | 0 | 0 | 100 | 0 | 0
1465 | 766.73 | 0 | 21.5 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 42.1093 | 779.0924 | 0 | 0.05921 | 6.7059 | 0 | 0 | 0 | 0 | off_peak | 766.73 | 0 | 100 | 0 | 0 | 100 | 0 | 0
1466 | 680.62 | 0 | 21.2 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 53.6732 | 692.9824 | 0 | 0.05921 | 6.5523 | 0 | 0 | 0 | 0 | off_peak | 680.62 | 0 | 100 | 0 | 0 | 100 | 0 | 0
1467 | 628.31 | 0 | 21 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 65.2371 | 640.6724 | 0 | 0.05921 | 6.1067 | 0 | 0 | 0 | 0 | off_peak | 628.31 | 0 | 100 | 0 | 0 | 100 | 0 | 0
1468 | 629.73 | 0 | 20.8 | 0 | 0 | 0 | 0 | 8.9371 | 8.9371 | 0 | 0 | 0 | 73.597 | 638.6671 | 0 | 0.05921 | 5.5947 | 0 | 0 | 0 | 0 | off_peak | 629.73 | 0 | 100 | 0 | 0 | 100 | 0 | 0
1469 | 662.4 | 0 | 20.6 | 0 | 0 | 0 | 0 | 0.57721 | 0.57721 | 0 | 0 | 0 | 74.137 | 662.9772 | 0 | 0.05921 | 5.0661 | 0 | 0 | 0 | 0 | off_peak | 662.4 | 0 | 100 | 0 | 0 | 100 | 0 | 0
1470 | 740.47 | 0 | 20.5 | 0 | 0 | 0 | 0 | 0.037279 | 0.037279 | 0 | 0 | 0 | 74.1718 | 740.5073 | 0 | 0.05921 | 4.3599 | 0 | 0 | 0 | 0 | off_peak | 740.47 | 0 | 100 | 0 | 0 | 100 | 0 | 0
1471 | 817.39 | 0 | 20.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1718 | 817.39 | 0 | 0.088511 | 3.8556 | 0 | 0 | 0 | 0 | on_peak | 817.39 |  |  | 0 | 0 | 100 | 0 | 0
1472 | 823.86 | 118.669 | 21.5 | 19.4666 | 19.4666 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1718 | 804.3934 | 0 | 0.088511 | 3.4967 | 0 | 0 | 0 | 19.4666 | on_peak | 804.3934 |  |  | 2.36 | 0 | 97.64 | 68.068 | 0
1473 | 890.22 | 337.185 | 22.4 | 55.1353 | 55.1353 | 0 | 0 | 0 | 0 | 62.443 | 62.443 | 0 | 7.4174 | 772.6417 | 0 | 0.088511 | 3.3247 | 0 | 0 | 0 | 55.1353 | on_peak | 772.6417 |  |  | 6.19 | 7.01 | 86.79 | 183.3078 | 0
1474 | 896.62 | 537.365 | 23.5 | 87.5232 | 87.5232 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 809.0968 | 0 | 0.088511 | 3.2164 | 0 | 0 | 0 | 87.5232 | on_peak | 809.0968 |  |  | 9.76 | 0 | 90.24 | 281.5097 | 0
1475 | 875.24 | 639.929 | 24.4 | 103.8924 | 103.8924 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 18.9814 | 783.71 | 0 | 0.05921 | 3.2148 | 0 | 0 | 0 | 103.8924 | off_peak | 771.3476 | 0 | 100 | 11.87 | 0 | 88.13 | 333.9944 | 0
1476 | 956.11 | 796.46 | 25.1 | 128.9801 | 128.9801 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 30.5453 | 839.4923 | 0 | 0.05921 | 3.4719 | 0 | 0 | 0 | 128.9801 | off_peak | 827.1299 | 0 | 100 | 13.49 | 0 | 86.51 | 447.8074 | 0
1477 | 917.8 | 820.181 | 25.5 | 132.6302 | 132.6302 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 42.1093 | 797.5322 | 0 | 0.05921 | 3.9582 | 0 | 0 | 0 | 132.6302 | off_peak | 785.1698 | 0 | 100 | 14.45 | 0 | 85.55 | 524.9787 | 0
1478 | 937.32 | 809.001 | 25.8 | 130.6807 | 130.6807 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 53.6732 | 819.0017 | 0 | 0.05921 | 4.3001 | 0 | 0 | 0 | 130.6807 | off_peak | 806.6393 | 0 | 100 | 13.94 | 0 | 86.06 | 561.9345 | 0
1479 | 967.02 | 709.126 | 25.9 | 114.5062 | 114.5062 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 65.2371 | 864.8762 | 0 | 0.05921 | 4.4189 | 0 | 0 | 0 | 114.5062 | off_peak | 852.5138 | 0 | 100 | 11.84 | 0 | 88.16 | 505.9956 | 0
1480 | 891.99 | 550.774 | 25.8 | 88.9684 | 88.9684 | 0 | 0 | 8.9371 | 8.9371 | 0 | 0 | 0 | 73.597 | 811.9587 | 0 | 0.05921 | 4.6948 | 0 | 0 | 0 | 88.9684 | off_peak | 803.0216 | 0 | 100 | 9.97 | 0 | 90.03 | 417.6929 | 0
1481 | 888.07 | 347.632 | 25.4 | 56.2353 | 56.2353 | 0 | 0 | 0.57721 | 0.57721 | 0 | 0 | 0 | 74.137 | 832.4119 | 0 | 0.05921 | 4.934 | 0 | 0 | 0 | 56.2353 | off_peak | 831.8347 | 0 | 100 | 6.33 | 0 | 93.67 | 277.4627 | 0
1482 | 858.23 | 133.233 | 24.7 | 21.6071 | 21.6071 | 0 | 0 | 0.037279 | 0.037279 | 0 | 0 | 0 | 74.1718 | 836.6602 | 0 | 0.05921 | 5.3129 | 0 | 0 | 0 | 21.6071 | off_peak | 836.6229 | 0 | 100 | 2.52 | 0 | 97.48 | 114.7963 | 0
1483 | 800.28 | 0 | 24.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1718 | 800.28 | 0 | 0.088511 | 5.6352 | 0 | 0 | 0 | 0 | on_peak | 800.28 |  |  | 0 | 0 | 100 | 0 | 0
1484 | 822.33 | 0 | 23.5 | 0 | 0 | 0 | 0 | 0 | 0 | 62.443 | 62.443 | 0 | 7.4174 | 759.887 | 0 | 0.088511 | 5.9797 | 0 | 0 | 0 | 0 | on_peak | 759.887 |  |  | 0 | 7.59 | 92.41 | 0 | 0
1485 | 815.89 | 0 | 22.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 815.89 | 0 | 0.088511 | 6.2317 | 0 | 0 | 0 | 0 | on_peak | 815.89 |  |  | 0 | 0 | 100 | 0 | 0
1486 | 819.59 | 0 | 22.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 819.59 | 0 | 0.088511 | 6.6077 | 0 | 0 | 0 | 0 | on_peak | 819.59 |  |  | 0 | 0 | 100 | 0 | 0
1487 | 841.36 | 0 | 21.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 841.36 | 0 | 0.05921 | 7.046 | 0 | 0 | 0 | 0 | off_peak | 841.36 |  |  | 0 | 0 | 100 | 0 | 0
1488 | 804.13 | 0 | 21.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 804.13 | 0 | 0.05921 | 7.1208 | 0 | 0 | 0 | 0 | off_peak | 804.13 |  |  | 0 | 0 | 100 | 0 | 0
1489 | 770.26 | 0 | 20.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 770.26 | 0 | 0.05921 | 6.9421 | 0 | 0 | 0 | 0 | off_peak | 770.26 |  |  | 0 | 0 | 100 | 0 | 0
1490 | 622.6 | 0 | 20.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 622.6 | 0 | 0.05921 | 6.7109 | 0 | 0 | 0 | 0 | off_peak | 622.6 |  |  | 0 | 0 | 100 | 0 | 0
1491 | 626.57 | 0 | 19.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 626.57 | 0 | 0.05921 | 6.2206 | 0 | 0 | 0 | 0 | off_peak | 626.57 |  |  | 0 | 0 | 100 | 0 | 0
1492 | 651.89 | 0 | 19.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 651.89 | 0 | 0.05921 | 5.9 | 0 | 0 | 0 | 0 | off_peak | 651.89 |  |  | 0 | 0 | 100 | 0 | 0
1493 | 635.49 | 0 | 19.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 635.49 | 0 | 0.05921 | 5.4219 | 0 | 0 | 0 | 0 | off_peak | 635.49 |  |  | 0 | 0 | 100 | 0 | 0
1494 | 722.06 | 0 | 19.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 722.06 | 0 | 0.05921 | 4.8382 | 0 | 0 | 0 | 0 | off_peak | 722.06 |  |  | 0 | 0 | 100 | 0 | 0
1495 | 821.8 | 0 | 19.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 821.8 | 0 | 0.05921 | 4.3942 | 0 | 0 | 0 | 0 | off_peak | 821.8 |  |  | 0 | 0 | 100 | 0 | 0
1496 | 836.02 | 109.383 | 20.8 | 17.988 | 17.988 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 18.9814 | 830.3944 | 0 | 0.05921 | 3.9787 | 0 | 0 | 0 | 17.988 | off_peak | 818.032 | 0 | 100 | 2.15 | 0 | 97.85 | 71.5681 | 0
1497 | 862.61 | 316.576 | 22.1 | 51.8207 | 51.8207 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18.9814 | 810.7893 | 0 | 0.05921 | 3.7146 | 0 | 0 | 0 | 51.8207 | off_peak | 810.7893 |  |  | 6.01 | 0 | 93.99 | 192.4935 | 0
1498 | 838.49 | 497.322 | 23.2 | 81.0882 | 81.0882 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 30.5453 | 769.7641 | 0 | 0.05921 | 3.5601 | 0 | 0 | 0 | 81.0882 | off_peak | 757.4018 | 0 | 100 | 9.67 | 0 | 90.33 | 288.6835 | 0
1499 | 813.94 | 629.862 | 23.9 | 102.4417 | 102.4417 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 42.1093 | 723.8607 | 0 | 0.05921 | 3.4664 | 0 | 0 | 0 | 102.4417 | off_peak | 711.4983 | 0 | 100 | 12.59 | 0 | 87.41 | 355.1037 | 0
1500 | 859.78 | 552.104 | 24.3 | 89.6662 | 89.6662 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 42.1093 | 770.1138 | 0 | 0.05921 | 3.5431 | 0 | 0 | 0 | 89.6662 | off_peak | 770.1138 |  |  | 10.43 | 0 | 89.57 | 317.692 | 0
1501 | 769.61 | 511.919 | 24.5 | 83.0802 | 83.0802 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 42.1093 | 686.5298 | 0 | 0.05921 | 3.6523 | 0 | 0 | 0 | 83.0802 | off_peak | 686.5298 |  |  | 10.8 | 0 | 89.2 | 303.4336 | 0
1502 | 818.28 | 335.567 | 24.5 | 54.4597 | 54.4597 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 42.1093 | 763.8203 | 0 | 0.05921 | 3.937 | 0 | 0 | 0 | 54.4597 | off_peak | 763.8203 |  |  | 6.66 | 0 | 93.34 | 214.4058 | 0
1503 | 783.54 | 410.181 | 24.4 | 66.5929 | 66.5929 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 42.1093 | 716.9471 | 0 | 0.05921 | 4.2703 | 0 | 0 | 0 | 66.5929 | off_peak | 716.9471 |  |  | 8.5 | 0 | 91.5 | 284.3699 | 0
1504 | 798.08 | 385.808 | 24.1 | 62.7034 | 62.7034 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 42.1093 | 735.3766 | 0 | 0.05921 | 4.555 | 0 | 0 | 0 | 62.7034 | off_peak | 735.3766 |  |  | 7.86 | 0 | 92.14 | 285.6124 | 0
1505 | 778.68 | 340.495 | 23.5 | 55.4581 | 55.4581 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 42.1093 | 723.2219 | 0 | 0.05921 | 4.9319 | 0 | 0 | 0 | 55.4581 | off_peak | 723.2219 |  |  | 7.12 | 0 | 92.88 | 273.5145 | 0
1506 | 693.62 | 131.166 | 22.8 | 21.4172 | 21.4172 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 42.1093 | 672.2028 | 0 | 0.05921 | 5.319 | 0 | 0 | 0 | 21.4172 | off_peak | 672.2028 |  |  | 3.09 | 0 | 96.91 | 113.9179 | 0
1507 | 644.82 | 0 | 22.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 42.1093 | 644.82 | 0 | 0.05921 | 5.8117 | 0 | 0 | 0 | 0 | off_peak | 644.82 |  |  | 0 | 0 | 100 | 0 | 0
1508 | 635.93 | 0 | 21.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 42.1093 | 635.93 | 0 | 0.05921 | 6.0737 | 0 | 0 | 0 | 0 | off_peak | 635.93 |  |  | 0 | 0 | 100 | 0 | 0
1509 | 633.27 | 0 | 21.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 42.1093 | 633.27 | 0 | 0.05921 | 6.2439 | 0 | 0 | 0 | 0 | off_peak | 633.27 |  |  | 0 | 0 | 100 | 0 | 0
1510 | 625.73 | 0 | 21.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 42.1093 | 625.73 | 0 | 0.05921 | 6.5394 | 0 | 0 | 0 | 0 | off_peak | 625.73 |  |  | 0 | 0 | 100 | 0 | 0
1511 | 628.85 | 0 | 20.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 42.1093 | 628.85 | 0 | 0.05921 | 6.8449 | 0 | 0 | 0 | 0 | off_peak | 628.85 |  |  | 0 | 0 | 100 | 0 | 0
1512 | 602.12 | 0 | 20.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 42.1093 | 602.12 | 0 | 0.05921 | 7.1165 | 0 | 0 | 0 | 0 | off_peak | 602.12 |  |  | 0 | 0 | 100 | 0 | 0
1513 | 600.9 | 0 | 20.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 42.1093 | 600.9 | 0 | 0.05921 | 7.0401 | 0 | 0 | 0 | 0 | off_peak | 600.9 |  |  | 0 | 0 | 100 | 0 | 0
1514 | 607.49 | 0 | 20.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 42.1093 | 607.49 | 0 | 0.05921 | 6.7525 | 0 | 0 | 0 | 0 | off_peak | 607.49 |  |  | 0 | 0 | 100 | 0 | 0
1515 | 600.52 | 0 | 19.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 42.1093 | 600.52 | 0 | 0.05921 | 6.1938 | 0 | 0 | 0 | 0 | off_peak | 600.52 |  |  | 0 | 0 | 100 | 0 | 0
1516 | 594.82 | 0 | 19.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 42.1093 | 594.82 | 0 | 0.05921 | 5.6683 | 0 | 0 | 0 | 0 | off_peak | 594.82 |  |  | 0 | 0 | 100 | 0 | 0
1517 | 615.06 | 0 | 19.7 | 0 | 0 | 0 | 0 | 8.7006 | 8.7006 | 0 | 0 | 0 | 50.2479 | 623.7606 | 0 | 0.05921 | 5.119 | 0 | 0 | 0 | 0 | off_peak | 615.06 | 0 | 100 | 0 | 0 | 100 | 0 | 0
1518 | 678.88 | 0 | 19.6 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 61.8119 | 691.2424 | 0 | 0.05921 | 4.491 | 0 | 0 | 0 | 0 | off_peak | 678.88 | 0 | 100 | 0 | 0 | 100 | 0 | 0
1519 | 714.73 | 0 | 20.1 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 73.3758 | 727.0924 | 0 | 0.05921 | 4.0188 | 0 | 0 | 0 | 0 | off_peak | 714.73 | 0 | 100 | 0 | 0 | 100 | 0 | 0
1520 | 787.43 | 131.139 | 20.9 | 21.5581 | 21.5581 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 73.3758 | 765.8719 | 0 | 0.05921 | 3.5803 | 0 | 0 | 0 | 21.5581 | off_peak | 765.8719 |  |  | 2.74 | 0 | 97.26 | 77.1838 | 0
1521 | 784.57 | 352.395 | 21.4 | 57.8279 | 57.8279 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 73.3758 | 726.7421 | 0 | 0.05921 | 3.2894 | 0 | 0 | 0 | 57.8279 | off_peak | 726.7421 |  |  | 7.37 | 0 | 92.63 | 190.2211 | 0
1522 | 745.48 | 560.871 | 21.9 | 91.8751 | 91.8751 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 73.3758 | 653.6049 | 0 | 0.05921 | 3.1053 | 0 | 0 | 0 | 91.8751 | off_peak | 653.6049 |  |  | 12.32 | 0 | 87.68 | 285.2974 | 0
1523 | 769.49 | 724.385 | 22.3 | 118.491 | 118.491 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 73.3758 | 650.999 | 0 | 0.05921 | 3.0166 | 0 | 0 | 0 | 118.491 | off_peak | 650.999 |  |  | 15.4 | 0 | 84.6 | 357.4376 | 0
1524 | 768.02 | 831.787 | 22.6 | 135.9137 | 135.9137 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 73.3758 | 632.1063 | 0 | 0.05921 | 3.0507 | 0 | 0 | 0 | 135.9137 | off_peak | 632.1063 |  |  | 17.7 | 0 | 82.3 | 414.6345 | 0
1525 | 729.54 | 861.533 | 22.7 | 140.724 | 140.724 | 0 | 0 | 0.79843 | 0.79843 | 0 | 0 | 0 | 74.1227 | 589.6145 | 0 | 0.05921 | 3.1235 | 0 | 0 | 0 | 140.724 | off_peak | 588.816 | 0 | 100 | 19.29 | 0 | 80.71 | 439.5451 | 0
1526 | 752.52 | 697.244 | 22.8 | 113.8481 | 113.8481 | 0 | 0 | 0.051567 | 0.051567 | 0 | 0 | 0 | 74.1709 | 638.7234 | 0 | 0.05921 | 3.276 | 0 | 0 | 0 | 113.8481 | off_peak | 638.6719 | 0 | 100 | 15.13 | 0 | 84.87 | 372.9704 | 0
1527 | 757.16 | 638.403 | 22.9 | 104.2032 | 104.2032 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1709 | 652.9568 | 0 | 0.05921 | 3.5175 | 0 | 0 | 0 | 104.2032 | off_peak | 652.9568 |  |  | 13.76 | 0 | 86.24 | 366.5316 | 0
1528 | 768.13 | 566.699 | 22.8 | 92.5323 | 92.5323 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1709 | 675.5977 | 0 | 0.05921 | 3.9474 | 0 | 0 | 0 | 92.5323 | off_peak | 675.5977 |  |  | 12.05 | 0 | 87.95 | 365.2649 | 0
1529 | 738.37 | 361.969 | 22.5 | 59.1667 | 59.1667 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1709 | 679.2033 | 0 | 0.05921 | 4.475 | 0 | 0 | 0 | 59.1667 | off_peak | 679.2033 |  |  | 8.01 | 0 | 91.99 | 264.7712 | 0
1530 | 679.18 | 143.318 | 21.8 | 23.485 | 23.485 | 0 | 0 | 0.0033305 | 0.0033305 | 0 | 0 | 0 | 74.174 | 655.6983 | 0 | 0.05921 | 5.1013 | 0 | 0 | 0 | 23.485 | off_peak | 655.695 | 0 | 100 | 3.46 | 0 | 96.54 | 119.8041 | 0
1531 | 628.39 | 0 | 21.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.174 | 628.39 | 0 | 0.05921 | 5.5948 | 0 | 0 | 0 | 0 | off_peak | 628.39 |  |  | 0 | 0 | 100 | 0 | 0
1532 | 624.91 | 0 | 20.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.174 | 624.91 | 0 | 0.05921 | 6.1393 | 0 | 0 | 0 | 0 | off_peak | 624.91 |  |  | 0 | 0 | 100 | 0 | 0
1533 | 608.09 | 0 | 20.4 | 0 | 0 | 0 | 0 | 0.0002151 | 0.0002151 | 0 | 0 | 0 | 74.1742 | 608.0902 | 0 | 0.05921 | 6.5073 | 0 | 0 | 0 | 0 | off_peak | 608.09 | 0 | 100 | 0 | 0 | 100 | 0 | 0
1534 | 625.32 | 0 | 20.1 | 0 | 0 | 0 | 0 | 1.4852e-05 | 1.4852e-05 | 0 | 0 | 0 | 74.1743 | 625.32 | 0 | 0.05921 | 6.6784 | 0 | 0 | 0 | 0 | off_peak | 625.32 | 0 | 100 | 0 | 0 | 100 | 0 | 0
1535 | 575.64 | 0 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1743 | 575.64 | 0 | 0.05921 | 6.9471 | 0 | 0 | 0 | 0 | off_peak | 575.64 |  |  | 0 | 0 | 100 | 0 | 0
1536 | 604.73 | 0 | 19.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1743 | 604.73 | 0 | 0.05921 | 7.1828 | 0 | 0 | 0 | 0 | off_peak | 604.73 |  |  | 0 | 0 | 100 | 0 | 0
1537 | 593.29 | 0 | 19.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1743 | 593.29 | 0 | 0.05921 | 7.1842 | 0 | 0 | 0 | 0 | off_peak | 593.29 |  |  | 0 | 0 | 100 | 0 | 0
1538 | 628.41 | 0 | 19.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1743 | 628.41 | 0 | 0.05921 | 7.0341 | 0 | 0 | 0 | 0 | off_peak | 628.41 |  |  | 0 | 0 | 100 | 0 | 0
1539 | 564.06 | 0 | 19.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1743 | 564.06 | 0 | 0.05921 | 6.5189 | 0 | 0 | 0 | 0 | off_peak | 564.06 |  |  | 0 | 0 | 100 | 0 | 0
1540 | 589.92 | 0 | 19.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1743 | 589.92 | 0 | 0.05921 | 5.908 | 0 | 0 | 0 | 0 | off_peak | 589.92 |  |  | 0 | 0 | 100 | 0 | 0
1541 | 618.85 | 0 | 19.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1743 | 618.85 | 0 | 0.05921 | 5.2501 | 0 | 0 | 0 | 0 | off_peak | 618.85 |  |  | 0 | 0 | 100 | 0 | 0
1542 | 701.29 | 0 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1743 | 701.29 | 0 | 0.05921 | 4.6472 | 0 | 0 | 0 | 0 | off_peak | 701.29 |  |  | 0 | 0 | 100 | 0 | 0
1543 | 768.23 | 0 | 20.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1743 | 768.23 | 0 | 0.088511 | 4.0957 | 0 | 0 | 0 | 0 | on_peak | 768.23 |  |  | 0 | 0 | 100 | 0 | 0
1544 | 817.53 | 121.366 | 21 | 19.9444 | 19.9444 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1743 | 797.5856 | 0 | 0.088511 | 3.6569 | 0 | 0 | 0 | 19.9444 | on_peak | 797.5856 |  |  | 2.44 | 0 | 97.56 | 72.9339 | 0
1545 | 874.51 | 326.529 | 21.6 | 53.5452 | 53.5452 | 0 | 0 | 0 | 0 | 62.4453 | 62.4453 | 0 | 7.4174 | 758.5195 | 0 | 0.088511 | 3.4022 | 0 | 0 | 0 | 53.5452 | on_peak | 758.5195 |  |  | 6.12 | 7.14 | 86.74 | 182.1693 | 0
1546 | 865.3 | 525.579 | 22.2 | 86.002 | 86.002 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 779.298 | 0 | 0.088511 | 3.2685 | 0 | 0 | 0 | 86.002 | on_peak | 779.298 |  |  | 9.94 | 0 | 90.06 | 281.0963 | 0
1547 | 868.72 | 689.746 | 22.8 | 112.6238 | 112.6238 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 18.9814 | 768.4586 | 0 | 0.05921 | 3.2607 | 0 | 0 | 0 | 112.6238 | off_peak | 756.0962 | 0 | 100 | 12.96 | 0 | 87.04 | 367.2353 | 0
1548 | 889.16 | 793.827 | 23.4 | 129.3407 | 129.3407 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 30.5453 | 772.1817 | 0 | 0.05921 | 3.485 | 0 | 0 | 0 | 129.3407 | off_peak | 759.8193 | 0 | 100 | 14.55 | 0 | 85.45 | 450.747 | 0
1549 | 914 | 678.663 | 23.9 | 110.3788 | 110.3788 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 42.1093 | 815.9836 | 0 | 0.05921 | 3.9846 | 0 | 0 | 0 | 110.3788 | off_peak | 803.6212 | 0 | 100 | 12.08 | 0 | 87.92 | 439.8107 | 0
1550 | 961.73 | 782.336 | 24.2 | 127.1034 | 127.1034 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 53.6732 | 846.9889 | 0 | 0.05921 | 4.2268 | 0 | 0 | 0 | 127.1034 | off_peak | 834.6266 | 0 | 100 | 13.22 | 0 | 86.78 | 537.2431 | 0
1551 | 958.72 | 601.169 | 24.5 | 97.5647 | 97.5647 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 65.2371 | 873.5177 | 0 | 0.05921 | 4.3199 | 0 | 0 | 0 | 97.5647 | off_peak | 861.1553 | 0 | 100 | 10.18 | 0 | 89.82 | 421.4685 | 0
1552 | 916.76 | 239.886 | 24.4 | 38.9455 | 38.9455 | 0 | 0 | 8.9371 | 8.9371 | 0 | 0 | 0 | 73.597 | 886.7516 | 0 | 0.05921 | 4.4941 | 0 | 0 | 0 | 38.9455 | off_peak | 877.8145 | 0 | 100 | 4.25 | 0 | 95.75 | 175.0247 | 0
1553 | 873.44 | 196.455 | 24 | 31.9403 | 31.9403 | 0 | 0 | 0.57721 | 0.57721 | 0 | 0 | 0 | 74.137 | 842.0769 | 0 | 0.05921 | 4.8086 | 0 | 0 | 0 | 31.9403 | off_peak | 841.4997 | 0 | 100 | 3.66 | 0 | 96.34 | 153.5889 | 0
1554 | 880.47 | 126.087 | 23.1 | 20.5658 | 20.5285 | 0 | 0.037279 | 0.037279 | 0 | 0 | 0 | 0 | 74.1718 | 859.9415 | 0 | 0.05921 | 5.3054 | 0 | 0 | 0.034872 | 20.5285 | off_peak | 859.9415 | 100 | 0 | 2.33 | 0 | 97.67 | 108.9115 | 0
1555 | 841.11 | 0 | 22.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1718 | 841.11 | 0 | 0.088511 | 5.9979 | 0 | 0 | 0.034872 | 0 | on_peak | 841.11 |  |  | 0 | 0 | 100 | 0 | 0
1556 | 863.38 | 0 | 21.5 | 0 | 0 | 0 | 0 | 0 | 0 | 62.443 | 62.443 | 0 | 7.4174 | 800.937 | 0 | 0.088511 | 6.4712 | 0.032619 | 0 | 0 | 0.032619 | on_peak | 800.937 |  |  | 0 | 7.23 | 92.77 | 0.21109 | 0
1557 | 849.65 | 0 | 20.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 849.65 | 0 | 0.088511 | 6.7817 | 0 | 0 | 0 | 0 | on_peak | 849.65 |  |  | 0 | 0 | 100 | 0 | 0
1558 | 834.2 | 0 | 20.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 834.2 | 0 | 0.088511 | 7.01 | 0 | 0 | 0 | 0 | on_peak | 834.2 |  |  | 0 | 0 | 100 | 0 | 0
1559 | 870.11 | 0 | 19.7 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 18.9814 | 882.4724 | 0 | 0.05921 | 7.214 | 0 | 0 | 0 | 0 | off_peak | 870.11 | 0 | 100 | 0 | 0 | 100 | 0 | 0
1560 | 854.74 | 0 | 19.3 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 30.5453 | 867.1024 | 0 | 0.05921 | 7.5789 | 0 | 0 | 0 | 0 | off_peak | 854.74 | 0 | 100 | 0 | 0 | 100 | 0 | 0
1561 | 789.14 | 0 | 19.1 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 42.1093 | 801.5024 | 0 | 0.05921 | 7.5353 | 0 | 0 | 0 | 0 | off_peak | 789.14 | 0 | 100 | 0 | 0 | 100 | 0 | 0
1562 | 713.04 | 0 | 19 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 53.6732 | 725.4024 | 0 | 0.05921 | 7.3773 | 0 | 0 | 0 | 0 | off_peak | 713.04 | 0 | 100 | 0 | 0 | 100 | 0 | 0
1563 | 642.46 | 0 | 18.9 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 65.2371 | 654.8224 | 0 | 0.05921 | 6.9058 | 0 | 0 | 0 | 0 | off_peak | 642.46 | 0 | 100 | 0 | 0 | 100 | 0 | 0
1564 | 662.03 | 0 | 18.9 | 0 | 0 | 0 | 0 | 8.9371 | 8.9371 | 0 | 0 | 0 | 73.597 | 670.9671 | 0 | 0.05921 | 6.3894 | 0 | 0 | 0 | 0 | off_peak | 662.03 | 0 | 100 | 0 | 0 | 100 | 0 | 0
1565 | 689.73 | 0 | 19 | 0 | 0 | 0 | 0 | 0.57721 | 0.57721 | 0 | 0 | 0 | 74.137 | 690.3072 | 0 | 0.05921 | 5.6393 | 0 | 0 | 0 | 0 | off_peak | 689.73 | 0 | 100 | 0 | 0 | 100 | 0 | 0
1566 | 778.76 | 0 | 19.1 | 0 | 0 | 0 | 0 | 0.037279 | 0.037279 | 0 | 0 | 0 | 74.1718 | 778.7973 | 0 | 0.05921 | 4.9295 | 0 | 0 | 0 | 0 | off_peak | 778.76 | 0 | 100 | 0 | 0 | 100 | 0 | 0
1567 | 817.95 | 0 | 19.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1718 | 817.95 | 0 | 0.088511 | 4.3135 | 0 | 0 | 0 | 0 | on_peak | 817.95 |  |  | 0 | 0 | 100 | 0 | 0
1568 | 853.03 | 121.944 | 20.2 | 20.0963 | 20.0963 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1718 | 832.9337 | 0 | 0.088511 | 3.8104 | 0 | 0 | 0 | 20.0963 | on_peak | 832.9337 |  |  | 2.36 | 0 | 97.64 | 76.5753 | 0
1569 | 851.77 | 332.37 | 21 | 54.6193 | 54.6193 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1718 | 797.1507 | 0 | 0.088511 | 3.5209 | 0 | 0 | 0 | 54.6193 | on_peak | 797.1507 |  |  | 6.41 | 0 | 93.59 | 192.3086 | 0
1570 | 946.35 | 535.886 | 21.9 | 87.7824 | 87.7824 | 0 | 0 | 0 | 0 | 60.4396 | 60.4396 | 0 | 9.5592 | 798.1281 | 0 | 0.088511 | 3.3516 | 0 | 0 | 0 | 87.7824 | on_peak | 798.1281 |  |  | 9.28 | 6.39 | 84.34 | 294.2095 | 0
1571 | 884.8 | 701 | 22.7 | 114.5023 | 114.5023 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 21.1232 | 782.6601 | 0 | 0.05921 | 3.3102 | 0 | 0 | 0 | 114.5023 | off_peak | 770.2977 | 0 | 100 | 12.94 | 0 | 87.06 | 379.0283 | 0
1572 | 945.24 | 803.422 | 23.2 | 130.9978 | 130.9978 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 32.6871 | 826.6046 | 0 | 0.05921 | 3.4948 | 0 | 0 | 0 | 130.9978 | off_peak | 814.2422 | 0 | 100 | 13.86 | 0 | 86.14 | 457.8147 | 0
1573 | 917.54 | 824.986 | 23.6 | 134.3213 | 134.3213 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 44.251 | 795.5811 | 0 | 0.05921 | 4.0141 | 0 | 0 | 0 | 134.3213 | off_peak | 783.2187 | 0 | 100 | 14.64 | 0 | 85.36 | 539.1743 | 0
1574 | 960.4 | 222.47 | 23.7 | 36.2088 | 36.2088 | 0 | 0 | 0 | 0 | 4.5602 | 4.5602 | 0 | 39.376 | 919.631 | 0 | 0.05921 | 4.1926 | 0 | 0 | 0 | 36.2088 | off_peak | 919.631 |  |  | 3.77 | 0.47 | 95.76 | 151.8079 | 0
1575 | 1007.46 | 478.011 | 23.6 | 77.8281 | 77.8281 | 0 | 0 | 0 | 0 | 10.0009 | 10.0009 | 0 | 28.6846 | 919.631 | 0 | 0.05921 | 4.2086 | 0 | 0 | 0 | 77.8281 | off_peak | 919.631 |  |  | 7.73 | 0.99 | 91.28 | 327.5452 | 0
1576 | 961.08 | 217.448 | 23.3 | 35.4422 | 35.4422 | 0 | 0 | 0 | 0 | 6.0068 | 6.0068 | 0 | 22.2631 | 919.631 | 0 | 0.05921 | 4.3333 | 0 | 0 | 0 | 35.4422 | off_peak | 919.631 |  |  | 3.69 | 0.63 | 95.69 | 153.5821 | 0
1577 | 933.65 | 162.695 | 22.5 | 26.5938 | 26.5938 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 33.827 | 919.4186 | 0 | 0.05921 | 4.7043 | 0 | 0 | 0 | 26.5938 | off_peak | 907.0562 | 0 | 100 | 2.85 | 0 | 97.15 | 125.1041 | 0
1578 | 910.67 | 137.678 | 21.3 | 22.6009 | 22.6009 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 45.391 | 900.4315 | 0 | 0.05921 | 5.272 | 0 | 0 | 0 | 22.6009 | off_peak | 888.0691 | 0 | 100 | 2.48 | 0 | 97.52 | 119.1522 | 0
1579 | 850.74 | 0 | 20.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 45.391 | 850.74 | 0 | 0.088511 | 5.9706 | 0 | 0 | 0 | 0 | on_peak | 850.74 |  |  | 0 | 0 | 100 | 0 | 0
1580 | 860.87 | 0 | 19.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 45.391 | 860.87 | 0 | 0.088511 | 6.45 | 0 | 0 | 0 | 0 | on_peak | 860.87 |  |  | 0 | 0 | 100 | 0 | 0
1581 | 902.29 | 0 | 18.9 | 0 | 0 | 0 | 0 | 0 | 0 | 35.521 | 35.521 | 0 | 7.4174 | 866.769 | 0 | 0.088511 | 6.5479 | 0 | 0 | 0 | 0 | on_peak | 866.769 |  |  | 0 | 3.94 | 96.06 | 0 | 0
1582 | 824.93 | 0 | 18.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 824.93 | 0 | 0.088511 | 6.7727 | 0 | 0 | 0 | 0 | on_peak | 824.93 |  |  | 0 | 0 | 100 | 0 | 0
1583 | 839.5 | 0 | 18.2 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 18.9814 | 851.8624 | 0 | 0.05921 | 7.1364 | 0 | 0 | 0 | 0 | off_peak | 839.5 | 0 | 100 | 0 | 0 | 100 | 0 | 0
1584 | 866.04 | 0 | 18.1 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 30.5453 | 878.4024 | 0 | 0.05921 | 7.408 | 0 | 0 | 0 | 0 | off_peak | 866.04 | 0 | 100 | 0 | 0 | 100 | 0 | 0
1585 | 763.96 | 0 | 18 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 42.1093 | 776.3224 | 0 | 0.05921 | 7.4565 | 0 | 0 | 0 | 0 | off_peak | 763.96 | 0 | 100 | 0 | 0 | 100 | 0 | 0
1586 | 710.74 | 0 | 17.9 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 53.6732 | 723.1024 | 0 | 0.05921 | 7.4033 | 0 | 0 | 0 | 0 | off_peak | 710.74 | 0 | 100 | 0 | 0 | 100 | 0 | 0
1587 | 639.39 | 0 | 17.8 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 65.2371 | 651.7524 | 0 | 0.05921 | 6.9024 | 0 | 0 | 0 | 0 | off_peak | 639.39 | 0 | 100 | 0 | 0 | 100 | 0 | 0
1588 | 646.66 | 0 | 17.8 | 0 | 0 | 0 | 0 | 8.9371 | 8.9371 | 0 | 0 | 0 | 73.597 | 655.5971 | 0 | 0.05921 | 6.2487 | 0 | 0 | 0 | 0 | off_peak | 646.66 | 0 | 100 | 0 | 0 | 100 | 0 | 0
1589 | 661.21 | 0 | 17.7 | 0 | 0 | 0 | 0 | 0.57721 | 0.57721 | 0 | 0 | 0 | 74.137 | 661.7872 | 0 | 0.05921 | 5.5756 | 0 | 0 | 0 | 0 | off_peak | 661.21 | 0 | 100 | 0 | 0 | 100 | 0 | 0
1590 | 759.93 | 0 | 17.7 | 0 | 0 | 0 | 0 | 0.037279 | 0.037279 | 0 | 0 | 0 | 74.1718 | 759.9673 | 0 | 0.05921 | 4.8197 | 0 | 0 | 0 | 0 | off_peak | 759.93 | 0 | 100 | 0 | 0 | 100 | 0 | 0
1591 | 820.03 | 0 | 18.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1718 | 820.03 | 0 | 0.088511 | 4.3223 | 0 | 0 | 0 | 0 | on_peak | 820.03 |  |  | 0 | 0 | 100 | 0 | 0
1592 | 862.43 | 131.278 | 19.2 | 21.7111 | 21.7111 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1718 | 840.7189 | 0 | 0.088511 | 3.9271 | 0 | 0 | 0 | 21.7111 | on_peak | 840.7189 |  |  | 2.52 | 0 | 97.48 | 85.2615 | 0
1593 | 871.57 | 345.356 | 19.9 | 56.9749 | 56.9749 | 0 | 0 | 0 | 0 | 62.443 | 62.443 | 0 | 7.4174 | 752.1521 | 0 | 0.088511 | 3.6937 | 0 | 0 | 0 | 56.9749 | on_peak | 752.1521 |  |  | 6.54 | 7.16 | 86.3 | 210.4472 | 0
1594 | 902.71 | 545.154 | 20.4 | 89.7774 | 89.7774 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 812.9326 | 0 | 0.088511 | 3.5284 | 0 | 0 | 0 | 89.7774 | on_peak | 812.9326 |  |  | 9.95 | 0 | 90.05 | 316.7682 | 0
1595 | 831.62 | 703.762 | 20.9 | 115.6922 | 115.6922 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 18.9814 | 728.2902 | 0 | 0.05921 | 3.4746 | 0 | 0 | 0 | 115.6922 | off_peak | 715.9278 | 0 | 100 | 13.91 | 0 | 86.09 | 401.9888 | 0
1596 | 899.99 | 805.362 | 21.2 | 132.2535 | 132.2535 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 30.5453 | 780.0989 | 0 | 0.05921 | 3.6777 | 0 | 0 | 0 | 132.2535 | off_peak | 767.7365 | 0 | 100 | 14.69 | 0 | 85.31 | 486.385 | 0
1597 | 862.46 | 825.413 | 21.4 | 135.4499 | 135.4499 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 42.1093 | 739.3725 | 0 | 0.05921 | 4.1268 | 0 | 0 | 0 | 135.4499 | off_peak | 727.0101 | 0 | 100 | 15.71 | 0 | 84.29 | 558.9795 | 0
1598 | 898.67 | 301.524 | 21.4 | 49.4799 | 49.4799 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 53.6732 | 861.5524 | 0 | 0.05921 | 4.309 | 0 | 0 | 0 | 49.4799 | off_peak | 849.1901 | 0 | 100 | 5.51 | 0 | 94.49 | 213.2112 | 0
1599 | 945.6 | 662.037 | 21.3 | 108.6786 | 108.6786 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 65.2371 | 849.2838 | 0 | 0.05921 | 4.3437 | 0 | 0 | 0 | 108.6786 | off_peak | 836.9214 | 0 | 100 | 11.49 | 0 | 88.51 | 472.0629 | 0
1600 | 939.44 | 519.612 | 21.1 | 85.359 | 85.359 | 0 | 0 | 8.9371 | 8.9371 | 0 | 0 | 0 | 73.597 | 863.0181 | 0 | 0.05921 | 4.3181 | 0 | 0 | 0 | 85.359 | off_peak | 854.081 | 0 | 100 | 9.09 | 0 | 90.91 | 368.5893 | 0
1601 | 909.03 | 112.14 | 20.7 | 18.4479 | 18.4479 | 0 | 0 | 0.57721 | 0.57721 | 0 | 0 | 0 | 74.137 | 891.1593 | 0 | 0.05921 | 4.5296 | 0 | 0 | 0 | 18.4479 | off_peak | 890.5821 | 0 | 100 | 2.03 | 0 | 97.97 | 83.5621 | 0
1602 | 857.04 | 13.3 | 20 | 2.1934 | 2.1561 | 0 | 0.037279 | 0.037279 | 0 | 0 | 0 | 0 | 74.1718 | 854.8839 | 0 | 0.05921 | 5.0606 | 0 | 0 | 0.034872 | 2.1561 | off_peak | 854.8839 | 100 | 0 | 0.25 | 0 | 99.75 | 10.9113 | 0
1603 | 783.61 | 0 | 19.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1718 | 783.61 | 0 | 0.088511 | 5.6701 | 0 | 0 | 0.034872 | 0 | on_peak | 783.61 |  |  | 0 | 0 | 100 | 0 | 0
1604 | 868.84 | 0 | 19.4 | 0 | 0 | 0 | 0 | 0 | 0 | 2.071 | 2.071 | 0 | 71.9579 | 866.769 | 0 | 0.088511 | 6.1068 | 0 | 0 | 0.034872 | 0 | on_peak | 866.769 |  |  | 0 | 0.24 | 99.76 | 0 | 0
1605 | 796.95 | 0 | 19.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 71.9579 | 796.95 | 0 | 0.088511 | 6.3458 | 0 | 0 | 0.034872 | 0 | on_peak | 796.95 |  |  | 0 | 0 | 100 | 0 | 0
1606 | 787.06 | 0 | 19.2 | 0 | 0 | 0 | 0 | 0 | 0 | 60.3721 | 60.3721 | 0 | 7.4174 | 726.6879 | 0 | 0.088511 | 6.5311 | 0.032619 | 0 | 0 | 0.032619 | on_peak | 726.6879 |  |  | 0 | 7.67 | 92.33 | 0.21304 | 0
1607 | 809.66 | 0 | 19.1 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 18.9814 | 822.0224 | 0 | 0.05921 | 6.7853 | 0 | 0 | 0 | 0 | off_peak | 809.66 | 0 | 100 | 0 | 0 | 100 | 0 | 0
1608 | 804.49 | 0 | 19.1 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 30.5453 | 816.8524 | 0 | 0.05921 | 6.9129 | 0 | 0 | 0 | 0 | off_peak | 804.49 | 0 | 100 | 0 | 0 | 100 | 0 | 0
1609 | 761.61 | 0 | 19 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 42.1093 | 773.9724 | 0 | 0.05921 | 7.1005 | 0 | 0 | 0 | 0 | off_peak | 761.61 | 0 | 100 | 0 | 0 | 100 | 0 | 0
1610 | 694.39 | 0 | 18.9 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 53.6732 | 706.7524 | 0 | 0.05921 | 6.9686 | 0 | 0 | 0 | 0 | off_peak | 694.39 | 0 | 100 | 0 | 0 | 100 | 0 | 0
1611 | 618.26 | 0 | 18.9 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 65.2371 | 630.6224 | 0 | 0.05921 | 6.495 | 0 | 0 | 0 | 0 | off_peak | 618.26 | 0 | 100 | 0 | 0 | 100 | 0 | 0
1612 | 647.41 | 0 | 18.9 | 0 | 0 | 0 | 0 | 8.9371 | 8.9371 | 0 | 0 | 0 | 73.597 | 656.3471 | 0 | 0.05921 | 5.9723 | 0 | 0 | 0 | 0 | off_peak | 647.41 | 0 | 100 | 0 | 0 | 100 | 0 | 0
1613 | 663.04 | 0 | 19 | 0 | 0 | 0 | 0 | 0.57721 | 0.57721 | 0 | 0 | 0 | 74.137 | 663.6172 | 0 | 0.05921 | 5.3483 | 0 | 0 | 0 | 0 | off_peak | 663.04 | 0 | 100 | 0 | 0 | 100 | 0 | 0
1614 | 717.43 | 0 | 19.1 | 0 | 0 | 0 | 0 | 0.037279 | 0.037279 | 0 | 0 | 0 | 74.1718 | 717.4673 | 0 | 0.05921 | 4.7336 | 0 | 0 | 0 | 0 | off_peak | 717.43 | 0 | 100 | 0 | 0 | 100 | 0 | 0
1615 | 806.83 | 0 | 19.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1718 | 806.83 | 0 | 0.088511 | 4.1324 | 0 | 0 | 0 | 0 | on_peak | 806.83 |  |  | 0 | 0 | 100 | 0 | 0
1616 | 850.83 | 130.449 | 20.6 | 21.4675 | 21.4675 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1718 | 829.3625 | 0 | 0.088511 | 3.7184 | 0 | 0 | 0 | 21.4675 | on_peak | 829.3625 |  |  | 2.52 | 0 | 97.48 | 79.8254 | 0
1617 | 924.91 | 342.773 | 21.1 | 56.3089 | 56.3089 | 0 | 0 | 0 | 0 | 1.8321 | 1.8321 | 0 | 72.2132 | 866.769 | 0 | 0.088511 | 3.4467 | 0 | 0 | 0 | 56.3089 | on_peak | 866.769 |  |  | 6.09 | 0.2 | 93.71 | 194.0781 | 0
1618 | 866.09 | 545.426 | 21.5 | 89.4723 | 89.4723 | 0 | 0 | 0 | 0 | 60.6109 | 60.6109 | 0 | 7.4174 | 716.0067 | 0 | 0.088511 | 3.28 | 0 | 0 | 0 | 89.4723 | on_peak | 716.0067 |  |  | 10.33 | 7 | 82.67 | 293.4687 | 0
1619 | 875.4 | 704.444 | 21.8 | 115.4346 | 115.4346 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 18.9814 | 772.3278 | 0 | 0.05921 | 3.2215 | 0 | 0 | 0 | 115.4346 | off_peak | 759.9654 | 0 | 100 | 13.19 | 0 | 86.81 | 371.8696 | 0
1620 | 955.34 | 747.84 | 22.2 | 122.3713 | 122.3713 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 30.5453 | 845.3311 | 0 | 0.05921 | 3.404 | 0 | 0 | 0 | 122.3713 | off_peak | 832.9687 | 0 | 100 | 12.81 | 0 | 87.19 | 416.5499 | 0
1621 | 834.64 | 705.849 | 22.5 | 115.3767 | 115.3767 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 42.1093 | 731.6257 | 0 | 0.05921 | 3.8509 | 0 | 0 | 0 | 115.3767 | off_peak | 719.2633 | 0 | 100 | 13.82 | 0 | 86.18 | 444.3095 | 0
1622 | 885.71 | 590.027 | 22.7 | 96.3758 | 96.3758 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 53.6732 | 801.6966 | 0 | 0.05921 | 4.0942 | 0 | 0 | 0 | 96.3758 | off_peak | 789.3342 | 0 | 100 | 10.88 | 0 | 89.12 | 394.5813 | 0
1623 | 925.03 | 596.304 | 22.8 | 97.3663 | 97.3663 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 65.2371 | 840.026 | 0 | 0.05921 | 4.1803 | 0 | 0 | 0 | 97.3663 | off_peak | 827.6637 | 0 | 100 | 10.53 | 0 | 89.47 | 407.0178 | 0
1624 | 882.58 | 531.198 | 22.8 | 86.7356 | 86.7356 | 0 | 0 | 8.9371 | 8.9371 | 0 | 0 | 0 | 73.597 | 804.7815 | 0 | 0.05921 | 4.1584 | 0 | 0 | 0 | 86.7356 | off_peak | 795.8444 | 0 | 100 | 9.83 | 0 | 90.17 | 360.6803 | 0
1625 | 896.12 | 362.444 | 22.6 | 59.2232 | 59.2232 | 0 | 0 | 0.57721 | 0.57721 | 0 | 0 | 0 | 74.137 | 837.474 | 0 | 0.05921 | 4.3484 | 0 | 0 | 0 | 59.2232 | off_peak | 836.8968 | 0 | 100 | 6.61 | 0 | 93.39 | 257.5275 | 0
1626 | 852.81 | 147.025 | 22.3 | 24.0496 | 24.0496 | 0 | 0 | 0.037279 | 0.037279 | 0 | 0 | 0 | 74.1718 | 828.7977 | 0 | 0.05921 | 4.6081 | 0 | 0 | 0 | 24.0496 | off_peak | 828.7604 | 0 | 100 | 2.82 | 0 | 97.18 | 110.8218 | 0
1627 | 820.4 | 0 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1718 | 820.4 | 0 | 0.088511 | 4.8911 | 0 | 0 | 0 | 0 | on_peak | 820.4 |  |  | 0 | 0 | 100 | 0 | 0
1628 | 802.77 | 0 | 21.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1718 | 802.77 | 0 | 0.088511 | 5.1157 | 0 | 0 | 0 | 0 | on_peak | 802.77 |  |  | 0 | 0 | 100 | 0 | 0
1629 | 822.8 | 0 | 21.9 | 0 | 0 | 0 | 0 | 0 | 0 | 62.443 | 62.443 | 0 | 7.4174 | 760.357 | 0 | 0.088511 | 5.3783 | 0 | 0 | 0 | 0 | on_peak | 760.357 |  |  | 0 | 7.59 | 92.41 | 0 | 0
1630 | 775.04 | 0 | 21.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 775.04 | 0 | 0.088511 | 5.6217 | 0 | 0 | 0 | 0 | on_peak | 775.04 |  |  | 0 | 0 | 100 | 0 | 0
1631 | 791.19 | 0 | 22 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 18.9814 | 803.5524 | 0 | 0.05921 | 5.9141 | 0 | 0 | 0 | 0 | off_peak | 791.19 | 0 | 100 | 0 | 0 | 100 | 0 | 0
1632 | 791.45 | 0 | 22 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 30.5453 | 803.8124 | 0 | 0.05921 | 6.185 | 0 | 0 | 0 | 0 | off_peak | 791.45 | 0 | 100 | 0 | 0 | 100 | 0 | 0
1633 | 753.23 | 0 | 22 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 42.1093 | 765.5924 | 0 | 0.05921 | 6.2909 | 0 | 0 | 0 | 0 | off_peak | 753.23 | 0 | 100 | 0 | 0 | 100 | 0 | 0
1634 | 673.8 | 0 | 22 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 53.6732 | 686.1624 | 0 | 0.05921 | 6.2805 | 0 | 0 | 0 | 0 | off_peak | 673.8 | 0 | 100 | 0 | 0 | 100 | 0 | 0
1635 | 627.83 | 0 | 21.9 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 65.2371 | 640.1924 | 0 | 0.05921 | 5.8817 | 0 | 0 | 0 | 0 | off_peak | 627.83 | 0 | 100 | 0 | 0 | 100 | 0 | 0
1636 | 609.69 | 0 | 21.9 | 0 | 0 | 0 | 0 | 8.9371 | 8.9371 | 0 | 0 | 0 | 73.597 | 618.6271 | 0 | 0.05921 | 5.3257 | 0 | 0 | 0 | 0 | off_peak | 609.69 | 0 | 100 | 0 | 0 | 100 | 0 | 0
1637 | 616.44 | 0 | 21.9 | 0 | 0 | 0 | 0 | 0.57721 | 0.57721 | 0 | 0 | 0 | 74.137 | 617.0172 | 0 | 0.05921 | 4.6981 | 0 | 0 | 0 | 0 | off_peak | 616.44 | 0 | 100 | 0 | 0 | 100 | 0 | 0
1638 | 720.55 | 0 | 22 | 0 | 0 | 0 | 0 | 0.037279 | 0.037279 | 0 | 0 | 0 | 74.1718 | 720.5873 | 0 | 0.05921 | 4.0773 | 0 | 0 | 0 | 0 | off_peak | 720.55 | 0 | 100 | 0 | 0 | 100 | 0 | 0
1639 | 700.75 | 0 | 22.4 | 0 | 0 | 0 | 0 | 0 | 0 | 62.443 | 62.443 | 0 | 7.4174 | 638.307 | 0 | 0.088511 | 3.4941 | 0 | 0 | 0 | 0 | on_peak | 638.307 |  |  | 0 | 8.91 | 91.09 | 0 | 0
1640 | 821.19 | 141.506 | 23.1 | 23.0808 | 23.0808 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 798.1092 | 0 | 0.088511 | 3.1426 | 0 | 0 | 0 | 23.0808 | on_peak | 798.1092 |  |  | 2.81 | 0 | 97.19 | 72.5336 | 0
1641 | 904.74 | 358.603 | 23.6 | 58.3865 | 58.3865 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 846.3535 | 0 | 0.088511 | 2.9245 | 0 | 0 | 0 | 58.3865 | on_peak | 846.3535 |  |  | 6.45 | 0 | 93.55 | 170.7532 | 0
1642 | 856.59 | 563.383 | 24 | 91.5966 | 91.5966 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 764.9934 | 0 | 0.088511 | 2.8043 | 0 | 0 | 0 | 91.5966 | on_peak | 764.9934 |  |  | 10.69 | 0 | 89.31 | 256.8599 | 0
1643 | 831.89 | 726.019 | 24.3 | 117.9115 | 117.9115 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 18.9814 | 726.3409 | 0 | 0.05921 | 2.8017 | 0 | 0 | 0 | 117.9115 | off_peak | 713.9785 | 0 | 100 | 14.17 | 0 | 85.83 | 330.358 | 0
1644 | 971.3 | 811.624 | 24.6 | 131.6724 | 131.6724 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 30.5453 | 851.99 | 0 | 0.05921 | 3.0177 | 0 | 0 | 0 | 131.6724 | off_peak | 839.6276 | 0 | 100 | 13.56 | 0 | 86.44 | 397.3524 | 0
1645 | 866.97 | 840.38 | 24.8 | 136.2396 | 136.2396 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 42.1093 | 743.0928 | 0 | 0.05921 | 3.4465 | 0 | 0 | 0 | 136.2396 | off_peak | 730.7304 | 0 | 100 | 15.71 | 0 | 84.29 | 469.5517 | 0
1646 | 908.29 | 785.158 | 24.9 | 127.2414 | 127.2414 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 53.6732 | 793.411 | 0 | 0.05921 | 3.7963 | 0 | 0 | 0 | 127.2414 | off_peak | 781.0486 | 0 | 100 | 14.01 | 0 | 85.99 | 483.05 | 0
1647 | 979.62 | 707.691 | 24.9 | 114.6872 | 114.6872 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 65.2371 | 877.2952 | 0 | 0.05921 | 3.8906 | 0 | 0 | 0 | 114.6872 | off_peak | 864.9328 | 0 | 100 | 11.71 | 0 | 88.29 | 446.203 | 0
1648 | 902.92 | 564.301 | 24.8 | 91.4826 | 91.4826 | 0 | 0 | 8.9371 | 8.9371 | 0 | 0 | 0 | 73.597 | 820.3745 | 0 | 0.05921 | 3.9886 | 0 | 0 | 0 | 91.4826 | off_peak | 811.4374 | 0 | 100 | 10.13 | 0 | 89.87 | 364.8892 | 0
1649 | 910.16 | 363.586 | 24.5 | 59.007 | 59.007 | 0 | 0 | 0.57721 | 0.57721 | 0 | 0 | 0 | 74.137 | 851.7303 | 0 | 0.05921 | 4.0516 | 0 | 0 | 0 | 59.007 | off_peak | 851.153 | 0 | 100 | 6.48 | 0 | 93.52 | 239.0721 | 0
1650 | 889.51 | 148.271 | 23.9 | 24.115 | 24.115 | 0 | 0 | 0.037279 | 0.037279 | 0 | 0 | 0 | 74.1718 | 865.4323 | 0 | 0.05921 | 4.3486 | 0 | 0 | 0 | 24.115 | off_peak | 865.395 | 0 | 100 | 2.71 | 0 | 97.29 | 104.8657 | 0
1651 | 838.1 | 0 | 23.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1718 | 838.1 | 0 | 0.088511 | 4.8109 | 0 | 0 | 0 | 0 | on_peak | 838.1 |  |  | 0 | 0 | 100 | 0 | 0
1652 | 816.47 | 0 | 23 | 0 | 0 | 0 | 0 | 0 | 0 | 62.443 | 62.443 | 0 | 7.4174 | 754.027 | 0 | 0.088511 | 5.2899 | 0 | 0 | 0 | 0 | on_peak | 754.027 |  |  | 0 | 7.65 | 92.35 | 0 | 0
1653 | 815.59 | 0 | 22.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 815.59 | 0 | 0.088511 | 5.7059 | 0 | 0 | 0 | 0 | on_peak | 815.59 |  |  | 0 | 0 | 100 | 0 | 0
1654 | 811.11 | 0 | 22.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 811.11 | 0 | 0.088511 | 6.0024 | 0 | 0 | 0 | 0 | on_peak | 811.11 |  |  | 0 | 0 | 100 | 0 | 0
1655 | 817.83 | 0 | 22.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 817.83 | 0 | 0.05921 | 6.2294 | 0 | 0 | 0 | 0 | off_peak | 817.83 |  |  | 0 | 0 | 100 | 0 | 0
1656 | 775.92 | 0 | 22.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 775.92 | 0 | 0.05921 | 6.4163 | 0 | 0 | 0 | 0 | off_peak | 775.92 |  |  | 0 | 0 | 100 | 0 | 0
1657 | 726.6 | 0 | 22.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 726.6 | 0 | 0.05921 | 6.3439 | 0 | 0 | 0 | 0 | off_peak | 726.6 |  |  | 0 | 0 | 100 | 0 | 0
1658 | 652.88 | 0 | 22.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 652.88 | 0 | 0.05921 | 6.1672 | 0 | 0 | 0 | 0 | off_peak | 652.88 |  |  | 0 | 0 | 100 | 0 | 0
1659 | 637.87 | 0 | 21.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 637.87 | 0 | 0.05921 | 5.7224 | 0 | 0 | 0 | 0 | off_peak | 637.87 |  |  | 0 | 0 | 100 | 0 | 0
1660 | 617.87 | 0 | 21.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 617.87 | 0 | 0.05921 | 5.2905 | 0 | 0 | 0 | 0 | off_peak | 617.87 |  |  | 0 | 0 | 100 | 0 | 0
1661 | 595.1 | 0 | 21.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 595.1 | 0 | 0.05921 | 4.8198 | 0 | 0 | 0 | 0 | off_peak | 595.1 |  |  | 0 | 0 | 100 | 0 | 0
1662 | 710.12 | 0 | 21.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 710.12 | 0 | 0.05921 | 4.2305 | 0 | 0 | 0 | 0 | off_peak | 710.12 |  |  | 0 | 0 | 100 | 0 | 0
1663 | 795.12 | 0 | 22.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 795.12 | 0 | 0.05921 | 3.7718 | 0 | 0 | 0 | 0 | off_peak | 795.12 |  |  | 0 | 0 | 100 | 0 | 0
1664 | 798.51 | 120.494 | 23.3 | 19.6395 | 19.6395 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 778.8705 | 0 | 0.05921 | 3.4334 | 0 | 0 | 0 | 19.6395 | off_peak | 778.8705 |  |  | 2.46 | 0 | 97.54 | 67.4305 | 0
1665 | 815.53 | 352.399 | 23.8 | 57.3353 | 57.3353 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 758.1947 | 0 | 0.05921 | 3.1857 | 0 | 0 | 0 | 57.3353 | off_peak | 758.1947 |  |  | 7.03 | 0 | 92.97 | 182.6532 | 0
1666 | 767.42 | 556.442 | 24.2 | 90.4032 | 90.4032 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 677.0168 | 0 | 0.05921 | 3.0588 | 0 | 0 | 0 | 90.4032 | off_peak | 677.0168 |  |  | 11.78 | 0 | 88.22 | 276.5241 | 0
1667 | 807.79 | 719.766 | 24.6 | 116.77 | 116.77 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 691.02 | 0 | 0.05921 | 3.0181 | 0 | 0 | 0 | 116.77 | off_peak | 691.02 |  |  | 14.46 | 0 | 85.54 | 352.4254 | 0
1668 | 813.29 | 825.589 | 24.8 | 133.8417 | 133.8417 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 679.4483 | 0 | 0.05921 | 3.1159 | 0 | 0 | 0 | 133.8417 | off_peak | 679.4483 |  |  | 16.46 | 0 | 83.54 | 417.043 | 0
1669 | 771.98 | 774.649 | 24.9 | 125.5383 | 125.5383 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 646.4417 | 0 | 0.05921 | 3.3147 | 0 | 0 | 0 | 125.5383 | off_peak | 646.4417 |  |  | 16.26 | 0 | 83.74 | 416.1276 | 0
1670 | 764.29 | 728.786 | 24.9 | 118.1058 | 118.1058 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 646.1842 | 0 | 0.05921 | 3.4789 | 0 | 0 | 0 | 118.1058 | off_peak | 646.1842 |  |  | 15.45 | 0 | 84.55 | 410.8798 | 0
1671 | 739.16 | 576.36 | 24.9 | 93.4039 | 93.4039 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 645.7561 | 0 | 0.05921 | 3.5742 | 0 | 0 | 0 | 93.4039 | off_peak | 645.7561 |  |  | 12.64 | 0 | 87.36 | 333.8409 | 0
1672 | 730.79 | 91.6785 | 24.7 | 14.868 | 14.868 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 715.922 | 0 | 0.05921 | 3.8966 | 0 | 0 | 0 | 14.868 | off_peak | 715.922 |  |  | 2.03 | 0 | 97.97 | 57.9341 | 0
1673 | 737.46 | 106.918 | 24.4 | 17.3581 | 17.3581 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 720.1019 | 0 | 0.05921 | 4.1359 | 0 | 0 | 0 | 17.3581 | off_peak | 720.1019 |  |  | 2.35 | 0 | 97.65 | 71.7919 | 0
1674 | 693.37 | 55.1531 | 23.8 | 8.9734 | 8.9734 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 684.3966 | 0 | 0.05921 | 4.5182 | 0 | 0 | 0 | 8.9734 | off_peak | 684.3966 |  |  | 1.29 | 0 | 98.71 | 40.5434 | 0
1675 | 609.23 | 0 | 23.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 609.23 | 0 | 0.05921 | 4.712 | 0 | 0 | 0 | 0 | off_peak | 609.23 |  |  | 0 | 0 | 100 | 0 | 0
1676 | 585.48 | 0 | 23.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 585.48 | 0 | 0.05921 | 4.9902 | 0 | 0 | 0 | 0 | off_peak | 585.48 |  |  | 0 | 0 | 100 | 0 | 0
1677 | 600.76 | 0 | 23.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 600.76 | 0 | 0.05921 | 5.2632 | 0 | 0 | 0 | 0 | off_peak | 600.76 |  |  | 0 | 0 | 100 | 0 | 0
1678 | 596.59 | 0 | 23.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 596.59 | 0 | 0.05921 | 5.416 | 0 | 0 | 0 | 0 | off_peak | 596.59 |  |  | 0 | 0 | 100 | 0 | 0
1679 | 591.45 | 0 | 22.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 591.45 | 0 | 0.05921 | 5.6911 | 0 | 0 | 0 | 0 | off_peak | 591.45 |  |  | 0 | 0 | 100 | 0 | 0
1680 | 609.21 | 0 | 22.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 609.21 | 0 | 0.05921 | 6.0691 | 0 | 0 | 0 | 0 | off_peak | 609.21 |  |  | 0 | 0 | 100 | 0 | 0
1681 | 578.31 | 0 | 22.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 578.31 | 0 | 0.05921 | 6.1458 | 0 | 0 | 0 | 0 | off_peak | 578.31 |  |  | 0 | 0 | 100 | 0 | 0
1682 | 574.63 | 0 | 22.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 574.63 | 0 | 0.05921 | 5.9744 | 0 | 0 | 0 | 0 | off_peak | 574.63 |  |  | 0 | 0 | 100 | 0 | 0
1683 | 574.63 | 0 | 22.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 574.63 | 0 | 0.05921 | 5.5937 | 0 | 0 | 0 | 0 | off_peak | 574.63 |  |  | 0 | 0 | 100 | 0 | 0
1684 | 574.63 | 0 | 22.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 574.63 | 0 | 0.05921 | 5.1707 | 0 | 0 | 0 | 0 | off_peak | 574.63 |  |  | 0 | 0 | 100 | 0 | 0
1685 | 599.92 | 0 | 22.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 599.92 | 0 | 0.05921 | 4.7271 | 0 | 0 | 0 | 0 | off_peak | 599.92 |  |  | 0 | 0 | 100 | 0 | 0
1686 | 669.45 | 0 | 22.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 669.45 | 0 | 0.05921 | 4.1959 | 0 | 0 | 0 | 0 | off_peak | 669.45 |  |  | 0 | 0 | 100 | 0 | 0
1687 | 747.7 | 0 | 22.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 747.7 | 0 | 0.05921 | 3.6791 | 0 | 0 | 0 | 0 | off_peak | 747.7 |  |  | 0 | 0 | 100 | 0 | 0
1688 | 784.87 | 149.217 | 23.5 | 24.3037 | 24.3037 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 18.9814 | 772.9287 | 0 | 0.05921 | 0 | 0 | 0 | 0 | 24.3037 | off_peak | 760.5663 | 0 | 100 | 3.1 | 0 | 96.9 | 0 | 0
1689 | 793.94 | 366.841 | 24 | 59.6422 | 59.6422 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18.9814 | 734.2978 | 0 | 0.05921 | 3.3164 | 0 | 0 | 0 | 59.6422 | off_peak | 734.2978 |  |  | 7.51 | 0 | 92.49 | 197.7983 | 0
1690 | 746.76 | 571.38 | 24.4 | 92.7635 | 92.7635 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 30.5453 | 666.3589 | 0 | 0.05921 | 3.0601 | 0 | 0 | 0 | 92.7635 | off_peak | 653.9965 | 0 | 100 | 12.42 | 0 | 87.58 | 283.8671 | 0
1691 | 748.17 | 621.398 | 24.7 | 100.7752 | 100.7752 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30.5453 | 647.3948 | 0 | 0.05921 | 2.9246 | 0 | 0 | 0 | 100.7752 | off_peak | 647.3948 |  |  | 13.47 | 0 | 86.53 | 294.7225 | 0
1692 | 802.98 | 727.307 | 24.9 | 117.8662 | 117.8662 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30.5453 | 685.1138 | 0 | 0.05921 | 2.8896 | 0 | 0 | 0 | 117.8662 | off_peak | 685.1138 |  |  | 14.68 | 0 | 85.32 | 340.5851 | 0
1693 | 733.66 | 824.387 | 24.9 | 133.5988 | 133.5988 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30.5453 | 600.0612 | 0 | 0.05921 | 2.9704 | 0 | 0 | 0 | 133.5988 | off_peak | 600.0612 |  |  | 18.21 | 0 | 81.79 | 396.8401 | 0
1694 | 743.93 | 670.536 | 24.9 | 108.6659 | 108.6659 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30.5453 | 635.2641 | 0 | 0.05921 | 3.2052 | 0 | 0 | 0 | 108.6659 | off_peak | 635.2641 |  |  | 14.61 | 0 | 85.39 | 348.3012 | 0
1695 | 722.12 | 649.334 | 24.7 | 105.3057 | 105.3057 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30.5453 | 616.8143 | 0 | 0.05921 | 3.3831 | 0 | 0 | 0 | 105.3057 | off_peak | 616.8143 |  |  | 14.58 | 0 | 85.42 | 356.2566 | 0
1696 | 711.31 | 569.212 | 24.5 | 92.3783 | 92.3783 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30.5453 | 618.9317 | 0 | 0.05921 | 3.4986 | 0 | 0 | 0 | 92.3783 | off_peak | 618.9317 |  |  | 12.99 | 0 | 87.01 | 323.1967 | 0
1697 | 717.56 | 367.005 | 24.2 | 59.626 | 59.626 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 42.1093 | 670.2963 | 0 | 0.05921 | 3.7123 | 0 | 0 | 0 | 59.626 | off_peak | 657.934 | 0 | 100 | 8.31 | 0 | 91.69 | 221.3511 | 0
1698 | 650.06 | 152.425 | 23.6 | 24.8173 | 24.8173 | 0 | 0 | 8.7006 | 8.7006 | 0 | 0 | 0 | 50.2479 | 633.9433 | 0 | 0.05921 | 3.9391 | 0 | 0 | 0 | 24.8173 | off_peak | 625.2427 | 0 | 100 | 3.82 | 0 | 96.18 | 97.7583 | 0
1699 | 603.97 | 0 | 23.3 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 61.8119 | 616.3324 | 0 | 0.05921 | 4.394 | 0 | 0 | 0 | 0 | off_peak | 603.97 | 0 | 100 | 0 | 0 | 100 | 0 | 0
1700 | 586.93 | 0 | 23.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 61.8119 | 586.93 | 0 | 0.05921 | 4.9323 | 0 | 0 | 0 | 0 | off_peak | 586.93 |  |  | 0 | 0 | 100 | 0 | 0
1701 | 587.62 | 0 | 23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 61.8119 | 587.62 | 0 | 0.05921 | 5.3567 | 0 | 0 | 0 | 0 | off_peak | 587.62 |  |  | 0 | 0 | 100 | 0 | 0
1702 | 609.26 | 0 | 23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 61.8119 | 609.26 | 0 | 0.05921 | 5.7688 | 0 | 0 | 0 | 0 | off_peak | 609.26 |  |  | 0 | 0 | 100 | 0 | 0
1703 | 568.28 | 0 | 22.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 61.8119 | 568.28 | 0 | 0.05921 | 6.2299 | 0 | 0 | 0 | 0 | off_peak | 568.28 |  |  | 0 | 0 | 100 | 0 | 0
1704 | 583.66 | 0 | 22.8 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 73.3758 | 596.0224 | 0 | 0.05921 | 6.4964 | 0 | 0 | 0 | 0 | off_peak | 583.66 | 0 | 100 | 0 | 0 | 100 | 0 | 0
1705 | 567.29 | 0 | 22.7 | 0 | 0 | 0 | 0 | 0.79843 | 0.79843 | 0 | 0 | 0 | 74.1227 | 568.0884 | 0 | 0.05921 | 6.7196 | 0 | 0 | 0 | 0 | off_peak | 567.29 | 0 | 100 | 0 | 0 | 100 | 0 | 0
1706 | 550.26 | 0 | 22.6 | 0 | 0 | 0 | 0 | 0.051567 | 0.051567 | 0 | 0 | 0 | 74.1709 | 550.3116 | 0 | 0.05921 | 6.7051 | 0 | 0 | 0 | 0 | off_peak | 550.26 | 0 | 100 | 0 | 0 | 100 | 0 | 0
1707 | 558.68 | 0 | 22.4 | 0 | 0 | 0 | 0 | 0.0033305 | 0.0033305 | 0 | 0 | 0 | 74.174 | 558.6833 | 0 | 0.05921 | 6.5639 | 0 | 0 | 0 | 0 | off_peak | 558.68 | 0 | 100 | 0 | 0 | 100 | 0 | 0
1708 | 553.99 | 0 | 22.3 | 0 | 0 | 0 | 0 | 0.0002151 | 0.0002151 | 0 | 0 | 0 | 74.1742 | 553.9902 | 0 | 0.05921 | 6.0659 | 0 | 0 | 0 | 0 | off_peak | 553.99 | 0 | 100 | 0 | 0 | 100 | 0 | 0
1709 | 570.26 | 0 | 22.2 | 0 | 0 | 0 | 0 | 1.3893e-05 | 1.3893e-05 | 0 | 0 | 0 | 74.1743 | 570.26 | 0 | 0.05921 | 5.4747 | 0 | 0 | 0 | 0 | off_peak | 570.26 | 0 | 100 | 0 | 0 | 100 | 0 | 0
1710 | 721.86 | 0 | 22.2 | 0 | 0 | 0 | 0 | 8.9726e-07 | 8.9726e-07 | 0 | 0 | 0 | 74.1743 | 721.86 | 0 | 0.05921 | 4.1099 | 0 | 0 | 0 | 0 | off_peak | 721.86 | 0 | 100 | 0 | 0 | 100 | 0 | 0
1711 | 780.51 | 0 | 22.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1743 | 780.51 | 0 | 0.088511 | 3.672 | 0 | 0 | 0 | 0 | on_peak | 780.51 |  |  | 0 | 0 | 100 | 0 | 0
1712 | 834.81 | 141.453 | 23.7 | 23.0226 | 23.0226 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1743 | 811.7874 | 0 | 0.088511 | 3.4553 | 0 | 0 | 0 | 23.0226 | on_peak | 811.7874 |  |  | 2.76 | 0 | 97.24 | 79.5494 | 0
1713 | 909.69 | 354.179 | 24.3 | 57.5216 | 57.5216 | 0 | 0 | 0 | 0 | 62.4453 | 62.4453 | 0 | 7.4174 | 789.7231 | 0 | 0.088511 | 3.3389 | 0 | 0 | 0 | 57.5216 | on_peak | 789.7231 |  |  | 6.32 | 6.86 | 86.81 | 192.0578 | 0
1714 | 876.24 | 555.783 | 24.8 | 90.1017 | 90.1017 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 786.1383 | 0 | 0.088511 | 3.2867 | 0 | 0 | 0 | 90.1017 | on_peak | 786.1383 |  |  | 10.28 | 0 | 89.72 | 296.1361 | 0
1715 | 828.55 | 707.971 | 25.1 | 114.65 | 114.65 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 18.9814 | 726.2624 | 0 | 0.05921 | 3.5284 | 0 | 0 | 0 | 114.65 | off_peak | 713.9 | 0 | 100 | 13.84 | 0 | 86.16 | 404.5304 | 0
1716 | 961.11 | 806.913 | 25.3 | 130.5787 | 130.5787 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 30.5453 | 842.8936 | 0 | 0.05921 | 3.9299 | 0 | 0 | 0 | 130.5787 | off_peak | 830.5313 | 0 | 100 | 13.59 | 0 | 86.41 | 513.1561 | 0
1717 | 906.47 | 825.898 | 25.3 | 133.651 | 133.651 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 42.1093 | 785.1814 | 0 | 0.05921 | 4.2651 | 0 | 0 | 0 | 133.651 | off_peak | 772.819 | 0 | 100 | 14.74 | 0 | 85.26 | 570.0329 | 0
1718 | 944.52 | 793.266 | 25.2 | 128.4166 | 128.4166 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 53.6732 | 828.4658 | 0 | 0.05921 | 4.4591 | 0 | 0 | 0 | 128.4166 | off_peak | 816.1034 | 0 | 100 | 13.6 | 0 | 86.4 | 572.616 | 0
1719 | 993.81 | 686.373 | 25 | 111.1924 | 111.1924 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 65.2371 | 894.9799 | 0 | 0.05921 | 4.7369 | 0 | 0 | 0 | 111.1924 | off_peak | 882.6176 | 0 | 100 | 11.19 | 0 | 88.81 | 526.7129 | 0
1720 | 859.74 | 555.193 | 24.8 | 90.006 | 90.006 | 0 | 0 | 8.9371 | 8.9371 | 0 | 0 | 0 | 73.597 | 778.6711 | 0 | 0.05921 | 5.0304 | 0 | 0 | 0 | 90.006 | off_peak | 769.734 | 0 | 100 | 10.47 | 0 | 89.53 | 452.7635 | 0
1721 | 911.12 | 356.039 | 24.6 | 57.7614 | 57.7614 | 0 | 0 | 0.57721 | 0.57721 | 0 | 0 | 0 | 74.137 | 853.9358 | 0 | 0.05921 | 5.284 | 0 | 0 | 0 | 57.7614 | off_peak | 853.3586 | 0 | 100 | 6.34 | 0 | 93.66 | 305.2091 | 0
1722 | 888.88 | 145.078 | 24.3 | 23.5619 | 23.5246 | 0 | 0.037279 | 0.037279 | 0 | 0 | 0 | 0 | 74.1718 | 865.3554 | 0 | 0.05921 | 5.5898 | 0 | 0 | 0.034872 | 23.5246 | off_peak | 865.3554 | 100 | 0 | 2.65 | 0 | 97.35 | 131.497 | 0
1723 | 845.93 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1718 | 845.93 | 0 | 0.088511 | 5.828 | 0 | 0 | 0.034872 | 0 | on_peak | 845.93 |  |  | 0 | 0 | 100 | 0 | 0
1724 | 847.66 | 0 | 23.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1718 | 847.66 | 0 | 0.088511 | 5.9392 | 0 | 0 | 0.034872 | 0 | on_peak | 847.66 |  |  | 0 | 0 | 100 | 0 | 0
1725 | 850.04 | 0 | 23.7 | 0 | 0 | 0 | 0 | 0 | 0 | 62.443 | 62.443 | 0 | 7.4174 | 787.597 | 0 | 0.088511 | 6.3208 | 0 | 0 | 0.034872 | 0 | on_peak | 787.597 |  |  | 0 | 7.35 | 92.65 | 0 | 0
1726 | 792.93 | 0 | 23.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 792.93 | 0 | 0.088511 | 6.5974 | 0 | 0 | 0.034872 | 0 | on_peak | 792.93 |  |  | 0 | 0 | 100 | 0 | 0
1727 | 798.91 | 0 | 23.4 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 18.9814 | 811.2724 | 0 | 0.05921 | 6.6911 | 0 | 0 | 0.034872 | 0 | off_peak | 798.91 | 0 | 100 | 0 | 0 | 100 | 0 | 0
1728 | 804.16 | 0 | 23.3 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 30.5453 | 816.5224 | 0 | 0.05921 | 6.7765 | 0 | 0 | 0.034872 | 0 | off_peak | 804.16 | 0 | 100 | 0 | 0 | 100 | 0 | 0
1729 | 761.41 | 0 | 23.3 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 42.1093 | 773.7724 | 0 | 0.05921 | 6.7022 | 0 | 0 | 0.034872 | 0 | off_peak | 761.41 | 0 | 100 | 0 | 0 | 100 | 0 | 0
1730 | 688.56 | 0 | 23.1 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 53.6732 | 700.9224 | 0 | 0.05921 | 6.594 | 0 | 0 | 0.034872 | 0 | off_peak | 688.56 | 0 | 100 | 0 | 0 | 100 | 0 | 0
1731 | 617.91 | 0 | 22.9 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 65.2371 | 630.2724 | 0 | 0.05921 | 6.1859 | 0 | 0 | 0.034872 | 0 | off_peak | 617.91 | 0 | 100 | 0 | 0 | 100 | 0 | 0
1732 | 652.6 | 0 | 22.8 | 0 | 0 | 0 | 0 | 8.9371 | 8.9371 | 0 | 0 | 0 | 73.597 | 661.5371 | 0 | 0.05921 | 5.5334 | 0 | 0 | 0.034872 | 0 | off_peak | 652.6 | 0 | 100 | 0 | 0 | 100 | 0 | 0
1733 | 634.11 | 0 | 22.7 | 0 | 0 | 0 | 0 | 0.57721 | 0.57721 | 0 | 0 | 0 | 74.137 | 634.6872 | 0 | 0.05921 | 4.8023 | 0 | 0 | 0.034872 | 0 | off_peak | 634.11 | 0 | 100 | 0 | 0 | 100 | 0 | 0
1734 | 755.48 | 0 | 22.8 | 0 | 0 | 0 | 0 | 0.037279 | 0.037279 | 0 | 0 | 0 | 74.1718 | 755.5173 | 0 | 0.05921 | 4.2489 | 0 | 0 | 0.034872 | 0 | off_peak | 755.48 | 0 | 100 | 0 | 0 | 100 | 0 | 0
1735 | 789.63 | 0 | 23.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0.032619 | 0.032619 | 0 | 74.137 | 789.5974 | 0 | 0.088511 | 3.8315 | 0.032619 | 0 | 0 | 0.032619 | on_peak | 789.5974 |  |  | 0 | 0 | 100 | 0.12498 | 0
1736 | 799.26 | 98.2648 | 24.4 | 15.9533 | 15.9533 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.137 | 783.3067 | 0 | 0.088511 | 3.5918 | 0 | 0 | 0 | 15.9533 | on_peak | 783.3067 |  |  | 2 | 0 | 98 | 57.3012 | 0
1737 | 827.23 | 340.003 | 25 | 55.0805 | 55.0805 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.137 | 772.1495 | 0 | 0.088511 | 3.3641 | 0 | 0 | 0 | 55.0805 | on_peak | 772.1495 |  |  | 6.66 | 0 | 93.34 | 185.2989 | 0
1738 | 810.54 | 525.568 | 25.5 | 84.9888 | 84.9888 | 0 | 0 | 0 | 0 | 62.4104 | 62.4104 | 0 | 7.4174 | 663.1408 | 0 | 0.088511 | 3.3094 | 0 | 0 | 0 | 84.9888 | on_peak | 663.1408 |  |  | 10.49 | 7.7 | 81.81 | 281.263 | 0
1739 | 833.3 | 666.365 | 26 | 107.5625 | 107.5625 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 18.9814 | 738.0999 | 0 | 0.05921 | 3.4648 | 0 | 0 | 0 | 107.5625 | off_peak | 725.7375 | 0 | 100 | 12.91 | 0 | 87.09 | 372.6794 | 0
1740 | 960.52 | 507.027 | 26.4 | 81.7244 | 81.7244 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 30.5453 | 891.158 | 0 | 0.05921 | 3.9707 | 0 | 0 | 0 | 81.7244 | off_peak | 878.7956 | 0 | 100 | 8.51 | 0 | 91.49 | 324.5016 | 0
1741 | 839.3 | 525.004 | 26.7 | 84.5301 | 84.5301 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 42.1093 | 767.1322 | 0 | 0.05921 | 4.3025 | 0 | 0 | 0 | 84.5301 | off_peak | 754.7699 | 0 | 100 | 10.07 | 0 | 89.93 | 363.6914 | 0
1742 | 927.61 | 681.843 | 26.9 | 109.703 | 109.703 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 53.6732 | 830.2693 | 0 | 0.05921 | 4.3216 | 0 | 0 | 0 | 109.703 | off_peak | 817.907 | 0 | 100 | 11.83 | 0 | 88.17 | 474.0957 | 0
1743 | 938.71 | 447.201 | 26.9 | 71.951 | 71.951 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 65.2371 | 879.1213 | 0 | 0.05921 | 4.1881 | 0 | 0 | 0 | 71.951 | off_peak | 866.759 | 0 | 100 | 7.66 | 0 | 92.34 | 301.338 | 0
1744 | 930.31 | 390.336 | 26.7 | 62.8474 | 62.8474 | 0 | 0 | 8.9371 | 8.9371 | 0 | 0 | 0 | 73.597 | 876.3997 | 0 | 0.05921 | 4.1851 | 0 | 0 | 0 | 62.8474 | off_peak | 867.4626 | 0 | 100 | 6.76 | 0 | 93.24 | 263.0227 | 0
1745 | 904.44 | 222.158 | 26.4 | 35.8082 | 35.8082 | 0 | 0 | 0.57721 | 0.57721 | 0 | 0 | 0 | 74.137 | 869.209 | 0 | 0.05921 | 4.2976 | 0 | 0 | 0 | 35.8082 | off_peak | 868.6318 | 0 | 100 | 3.96 | 0 | 96.04 | 153.8906 | 0
1746 | 845.63 | 146.106 | 25.8 | 23.601 | 23.601 | 0 | 0 | 0.037279 | 0.037279 | 0 | 0 | 0 | 74.1718 | 822.0663 | 0 | 0.05921 | 4.198 | 0 | 0 | 0 | 23.601 | off_peak | 822.029 | 0 | 100 | 2.79 | 0 | 97.21 | 99.0763 | 0
1747 | 858.09 | 0 | 25.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1718 | 858.09 | 0 | 0.088511 | 4.2215 | 0 | 0 | 0 | 0 | on_peak | 858.09 |  |  | 0 | 0 | 100 | 0 | 0
1748 | 881.4 | 0 | 24.7 | 0 | 0 | 0 | 0 | 0 | 0 | 62.443 | 62.443 | 0 | 7.4174 | 818.957 | 0 | 0.088511 | 4.3246 | 0 | 0 | 0 | 0 | on_peak | 818.957 |  |  | 0 | 7.08 | 92.92 | 0 | 0
1749 | 840.57 | 0 | 24.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 840.57 | 0 | 0.088511 | 4.5134 | 0 | 0 | 0 | 0 | on_peak | 840.57 |  |  | 0 | 0 | 100 | 0 | 0
1750 | 818.32 | 0 | 23.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 818.32 | 0 | 0.088511 | 4.8088 | 0 | 0 | 0 | 0 | on_peak | 818.32 |  |  | 0 | 0 | 100 | 0 | 0
1751 | 809.86 | 0 | 22.8 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 18.9814 | 822.2224 | 0 | 0.05921 | 5.0746 | 0 | 0 | 0 | 0 | off_peak | 809.86 | 0 | 100 | 0 | 0 | 100 | 0 | 0
1752 | 781.55 | 0 | 22.3 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 30.5453 | 793.9124 | 0 | 0.05921 | 5.5818 | 0 | 0 | 0 | 0 | off_peak | 781.55 | 0 | 100 | 0 | 0 | 100 | 0 | 0
1753 | 785.4 | 0 | 21.9 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 42.1093 | 797.7624 | 0 | 0.05921 | 5.8579 | 0 | 0 | 0 | 0 | off_peak | 785.4 | 0 | 100 | 0 | 0 | 100 | 0 | 0
1754 | 690.82 | 0 | 21.7 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 53.6732 | 703.1824 | 0 | 0.05921 | 5.8293 | 0 | 0 | 0 | 0 | off_peak | 690.82 | 0 | 100 | 0 | 0 | 100 | 0 | 0
1755 | 642.01 | 0 | 21.6 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 65.2371 | 654.3724 | 0 | 0.05921 | 5.4623 | 0 | 0 | 0 | 0 | off_peak | 642.01 | 0 | 100 | 0 | 0 | 100 | 0 | 0
1756 | 640.23 | 0 | 21.7 | 0 | 0 | 0 | 0 | 8.9371 | 8.9371 | 0 | 0 | 0 | 73.597 | 649.1671 | 0 | 0.05921 | 4.926 | 0 | 0 | 0 | 0 | off_peak | 640.23 | 0 | 100 | 0 | 0 | 100 | 0 | 0
1757 | 642.84 | 0 | 21.7 | 0 | 0 | 0 | 0 | 0.57721 | 0.57721 | 0 | 0 | 0 | 74.137 | 643.4172 | 0 | 0.05921 | 4.1978 | 0 | 0 | 0 | 0 | off_peak | 642.84 | 0 | 100 | 0 | 0 | 100 | 0 | 0
1758 | 743.67 | 0 | 21.8 | 0 | 0 | 0 | 0 | 0.037279 | 0.037279 | 0 | 0 | 0 | 74.1718 | 743.7073 | 0 | 0.05921 | 3.5386 | 0 | 0 | 0 | 0 | off_peak | 743.67 | 0 | 100 | 0 | 0 | 100 | 0 | 0
1759 | 765.1 | 0 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1718 | 765.1 | 0 | 0.088511 | 3.1591 | 0 | 0 | 0 | 0 | on_peak | 765.1 |  |  | 0 | 0 | 100 | 0 | 0
1760 | 862.6 | 67.7378 | 22.7 | 11.0644 | 11.0644 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1718 | 851.5356 | 0 | 0.088511 | 2.9548 | 0 | 0 | 0 | 11.0644 | on_peak | 851.5356 |  |  | 1.28 | 0 | 98.72 | 32.6931 | 0
1761 | 874.18 | 220.072 | 23.5 | 35.8442 | 35.8442 | 0 | 0 | 0 | 0 | 62.443 | 62.443 | 0 | 7.4174 | 775.8928 | 0 | 0.088511 | 2.8958 | 0 | 0 | 0 | 35.8442 | on_peak | 775.8928 |  |  | 4.1 | 7.14 | 88.76 | 103.797 | 0
1762 | 823.52 | 392.275 | 24.2 | 63.7316 | 63.7316 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 759.7884 | 0 | 0.088511 | 2.9127 | 0 | 0 | 0 | 63.7316 | on_peak | 759.7884 |  |  | 7.74 | 0 | 92.26 | 185.6282 | 0
1763 | 850.19 | 324.113 | 24.7 | 52.563 | 52.563 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 18.9814 | 809.9894 | 0 | 0.05921 | 3.1544 | 0 | 0 | 0 | 52.563 | off_peak | 797.627 | 0 | 100 | 6.18 | 0 | 93.82 | 165.8066 | 0
1764 | 947.96 | 481.018 | 25 | 77.9249 | 77.9249 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 30.5453 | 882.3975 | 0 | 0.05921 | 3.6357 | 0 | 0 | 0 | 77.9249 | off_peak | 870.0351 | 0 | 100 | 8.22 | 0 | 91.78 | 283.3093 | 0
1765 | 853.05 | 192.74 | 25.1 | 31.2126 | 31.2126 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 42.1093 | 834.1997 | 0 | 0.05921 | 4.0979 | 0 | 0 | 0 | 31.2126 | off_peak | 821.8374 | 0 | 100 | 3.66 | 0 | 96.34 | 127.906 | 0
1766 | 961.59 | 294.011 | 24.9 | 47.6469 | 47.6469 | 0 | 0 | 5.688 | 5.688 | 0 | 0 | 0 | 47.4299 | 919.631 | 0 | 0.05921 | 4.269 | 0 | 0 | 0 | 47.6469 | off_peak | 913.9431 | 0 | 100 | 4.96 | 0 | 95.04 | 203.4062 | 0
1767 | 946.9 | 105.952 | 24.6 | 17.1889 | 17.1889 | 0 | 0 | 0 | 0 | 10.08 | 10.08 | 0 | 36.6538 | 919.631 | 0 | 0.05921 | 4.3004 | 0 | 0 | 0 | 17.1889 | off_peak | 919.631 |  |  | 1.82 | 1.06 | 97.12 | 73.9187 | 0
1768 | 930.75 | 110.071 | 24.1 | 17.8893 | 17.8893 | 0 | 0 | 6.7703 | 6.7703 | 0 | 0 | 0 | 42.9869 | 919.631 | 0 | 0.05921 | 4.1346 | 0 | 0 | 0 | 17.8893 | off_peak | 912.8607 | 0 | 100 | 1.92 | 0 | 98.08 | 73.9654 | 0
1769 | 868.42 | 75.4637 | 23.6 | 12.2867 | 12.2867 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 54.5508 | 868.4956 | 0 | 0.05921 | 4.1266 | 0 | 0 | 0 | 12.2867 | off_peak | 856.1333 | 0 | 100 | 1.41 | 0 | 98.59 | 50.7022 | 0
1770 | 831.17 | 64.2502 | 23 | 10.4835 | 10.4835 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 66.1148 | 833.0489 | 0 | 0.05921 | 4.0695 | 0 | 0 | 0 | 10.4835 | off_peak | 820.6865 | 0 | 100 | 1.26 | 0 | 98.74 | 42.6621 | 0
1771 | 826.81 | 0 | 22.7 | 0 | 0 | 0 | 0 | 0 | 0 | 54.9063 | 54.9063 | 0 | 7.4174 | 771.9037 | 0 | 0.088511 | 3.9366 | 0 | 0 | 0 | 0 | on_peak | 771.9037 |  |  | 0 | 6.64 | 93.36 | 0 | 0
1772 | 811.34 | 0 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 811.34 | 0 | 0.088511 | 3.5924 | 0 | 0 | 0 | 0 | on_peak | 811.34 |  |  | 0 | 0 | 100 | 0 | 0
1773 | 815.38 | 0 | 21.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 815.38 | 0 | 0.088511 | 3.2528 | 0 | 0 | 0 | 0 | on_peak | 815.38 |  |  | 0 | 0 | 100 | 0 | 0
1774 | 785.81 | 0 | 21.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 785.81 | 0 | 0.088511 | 3.1633 | 0 | 0 | 0 | 0 | on_peak | 785.81 |  |  | 0 | 0 | 100 | 0 | 0
1775 | 793.61 | 0 | 21.2 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 18.9814 | 805.9724 | 0 | 0.05921 | 3.5635 | 0 | 0 | 0 | 0 | off_peak | 793.61 | 0 | 100 | 0 | 0 | 100 | 0 | 0
1776 | 789.97 | 0 | 21 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 30.5453 | 802.3324 | 0 | 0.05921 | 4.2586 | 0 | 0 | 0 | 0 | off_peak | 789.97 | 0 | 100 | 0 | 0 | 100 | 0 | 0
1777 | 750.13 | 0 | 20.8 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 42.1093 | 762.4924 | 0 | 0.05921 | 4.7609 | 0 | 0 | 0 | 0 | off_peak | 750.13 | 0 | 100 | 0 | 0 | 100 | 0 | 0
1778 | 630.49 | 0 | 20.7 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 53.6732 | 642.8524 | 0 | 0.05921 | 4.9116 | 0 | 0 | 0 | 0 | off_peak | 630.49 | 0 | 100 | 0 | 0 | 100 | 0 | 0
1779 | 633.1 | 0 | 20.6 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 65.2371 | 645.4624 | 0 | 0.05921 | 4.6382 | 0 | 0 | 0 | 0 | off_peak | 633.1 | 0 | 100 | 0 | 0 | 100 | 0 | 0
1780 | 598.97 | 0 | 20.5 | 0 | 0 | 0 | 0 | 8.9371 | 8.9371 | 0 | 0 | 0 | 73.597 | 607.9071 | 0 | 0.05921 | 4.2241 | 0 | 0 | 0 | 0 | off_peak | 598.97 | 0 | 100 | 0 | 0 | 100 | 0 | 0
1781 | 598.72 | 0 | 20.5 | 0 | 0 | 0 | 0 | 0.57721 | 0.57721 | 0 | 0 | 0 | 74.137 | 599.2972 | 0 | 0.05921 | 3.5725 | 0 | 0 | 0 | 0 | off_peak | 598.72 | 0 | 100 | 0 | 0 | 100 | 0 | 0
1782 | 752.84 | 0 | 20.4 | 0 | 0 | 0 | 0 | 0.037279 | 0.037279 | 0 | 0 | 0 | 74.1718 | 752.8773 | 0 | 0.05921 | 3.1176 | 0 | 0 | 0 | 0 | off_peak | 752.84 | 0 | 100 | 0 | 0 | 100 | 0 | 0
1783 | 773.48 | 6.65 | 21 | 1.0928 | 1.0928 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1718 | 772.3872 | 0 | 0.088511 | 2.847 | 0 | 0 | 0 | 1.0928 | on_peak | 772.3872 |  |  | 0.14 | 0 | 99.86 | 3.1112 | 0
1784 | 840.4 | 169.576 | 21.8 | 27.7878 | 27.7878 | 0 | 0 | 0 | 0 | 62.443 | 62.443 | 0 | 7.4174 | 750.1692 | 0 | 0.088511 | 2.7104 | 0 | 0 | 0 | 27.7878 | on_peak | 750.1692 |  |  | 3.31 | 7.43 | 89.26 | 75.3154 | 0
1785 | 893.76 | 289.681 | 22.4 | 47.3676 | 47.3676 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 846.3924 | 0 | 0.088511 | 2.68 | 0 | 0 | 0 | 47.3676 | on_peak | 846.3924 |  |  | 5.3 | 0 | 94.7 | 126.9428 | 0
1786 | 885.23 | 455.155 | 22.8 | 74.3191 | 74.3191 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 810.9109 | 0 | 0.088511 | 2.7994 | 0 | 0 | 0 | 74.3191 | on_peak | 810.9109 |  |  | 8.4 | 0 | 91.6 | 208.0478 | 0
1787 | 859.27 | 667.871 | 23.1 | 108.9352 | 108.9352 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 18.9814 | 762.6972 | 0 | 0.05921 | 3.1099 | 0 | 0 | 0 | 108.9352 | off_peak | 750.3348 | 0 | 100 | 12.68 | 0 | 87.32 | 338.7721 | 0
1788 | 877.17 | 871.968 | 23.4 | 142.0725 | 142.0725 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 30.5453 | 747.4599 | 0 | 0.05921 | 3.6985 | 0 | 0 | 0 | 142.0725 | off_peak | 735.0975 | 0 | 100 | 16.2 | 0 | 83.8 | 525.4482 | 0
1789 | 847.27 | 916.546 | 23.6 | 149.2288 | 149.2288 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 42.1093 | 710.4036 | 0 | 0.05921 | 4.2934 | 0 | 0 | 0 | 149.2288 | off_peak | 698.0412 | 0 | 100 | 17.61 | 0 | 82.39 | 640.7051 | 0
1790 | 922.46 | 881.526 | 23.6 | 143.527 | 143.527 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 53.6732 | 791.2954 | 0 | 0.05921 | 4.1999 | 0 | 0 | 0 | 143.527 | off_peak | 778.933 | 0 | 100 | 15.56 | 0 | 84.44 | 602.7981 | 0
1791 | 939.4 | 757.529 | 23.6 | 123.3382 | 123.3382 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 65.2371 | 828.4242 | 0 | 0.05921 | 3.6412 | 0 | 0 | 0 | 123.3382 | off_peak | 816.0618 | 0 | 100 | 13.13 | 0 | 86.87 | 449.0979 | 0
1792 | 854.49 | 610.146 | 23.4 | 99.413 | 99.413 | 0 | 0 | 8.9371 | 8.9371 | 0 | 0 | 0 | 73.597 | 764.0141 | 0 | 0.05921 | 3.2083 | 0 | 0 | 0 | 99.413 | off_peak | 755.077 | 0 | 100 | 11.63 | 0 | 88.37 | 318.9462 | 0
1793 | 891.22 | 400.195 | 23 | 65.2984 | 65.2984 | 0 | 0 | 0.57721 | 0.57721 | 0 | 0 | 0 | 74.137 | 826.4988 | 0 | 0.05921 | 3.0388 | 0 | 0 | 0 | 65.2984 | off_peak | 825.9216 | 0 | 100 | 7.33 | 0 | 92.67 | 198.431 | 0
1794 | 788.93 | 172.531 | 22.3 | 28.2217 | 28.1844 | 0 | 0.037279 | 0.037279 | 0 | 0 | 0 | 0 | 74.1718 | 760.7456 | 0 | 0.05921 | 3.0304 | 0 | 0 | 0.034872 | 28.1844 | off_peak | 760.7456 | 100 | 0 | 3.57 | 0 | 96.43 | 85.411 | 0
1795 | 774.98 | 6.65 | 21.8 | 1.0897 | 1.0897 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1718 | 773.8903 | 0 | 0.088511 | 3.1204 | 0 | 0 | 0.034872 | 1.0897 | on_peak | 773.8903 |  |  | 0.14 | 0 | 99.86 | 3.4003 | 0
1796 | 793.81 | 0 | 21.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1718 | 793.81 | 0 | 0.088511 | 3.2532 | 0 | 0 | 0.034872 | 0 | on_peak | 793.81 |  |  | 0 | 0 | 100 | 0 | 0
1797 | 799.67 | 0 | 21.3 | 0 | 0 | 0 | 0 | 0 | 0 | 62.443 | 62.443 | 0 | 7.4174 | 737.227 | 0 | 0.088511 | 3.451 | 0.032619 | 0 | 0 | 0.032619 | on_peak | 737.227 |  |  | 0 | 7.81 | 92.19 | 0.11257 | 0
1798 | 768.62 | 0 | 21.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 768.62 | 0 | 0.088511 | 3.7343 | 0 | 0 | 0 | 0 | on_peak | 768.62 |  |  | 0 | 0 | 100 | 0 | 0
1799 | 806.14 | 0 | 21.1 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 18.9814 | 818.5024 | 0 | 0.05921 | 4.1901 | 0 | 0 | 0 | 0 | off_peak | 806.14 | 0 | 100 | 0 | 0 | 100 | 0 | 0
1800 | 734.12 | 0 | 21 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 30.5453 | 746.4824 | 0 | 0.05921 | 4.7701 | 0 | 0 | 0 | 0 | off_peak | 734.12 | 0 | 100 | 0 | 0 | 100 | 0 | 0
1801 | 743.63 | 0 | 21 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 42.1093 | 755.9924 | 0 | 0.05921 | 5.1611 | 0 | 0 | 0 | 0 | off_peak | 743.63 | 0 | 100 | 0 | 0 | 100 | 0 | 0
1802 | 627.65 | 0 | 21.1 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 53.6732 | 640.0124 | 0 | 0.05921 | 5.1478 | 0 | 0 | 0 | 0 | off_peak | 627.65 | 0 | 100 | 0 | 0 | 100 | 0 | 0
1803 | 607.82 | 0 | 21.1 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 65.2371 | 620.1824 | 0 | 0.05921 | 4.8557 | 0 | 0 | 0 | 0 | off_peak | 607.82 | 0 | 100 | 0 | 0 | 100 | 0 | 0
1804 | 604.45 | 0 | 21.1 | 0 | 0 | 0 | 0 | 8.9371 | 8.9371 | 0 | 0 | 0 | 73.597 | 613.3871 | 0 | 0.05921 | 4.401 | 0 | 0 | 0 | 0 | off_peak | 604.45 | 0 | 100 | 0 | 0 | 100 | 0 | 0
1805 | 577.18 | 0 | 21.1 | 0 | 0 | 0 | 0 | 0.57721 | 0.57721 | 0 | 0 | 0 | 74.137 | 577.7572 | 0 | 0.05921 | 3.7937 | 0 | 0 | 0 | 0 | off_peak | 577.18 | 0 | 100 | 0 | 0 | 100 | 0 | 0
1806 | 754.18 | 0 | 21.2 | 0 | 0 | 0 | 0 | 0.037279 | 0.037279 | 0 | 0 | 0 | 74.1718 | 754.2173 | 0 | 0.05921 | 3.2304 | 0 | 0 | 0 | 0 | off_peak | 754.18 | 0 | 100 | 0 | 0 | 100 | 0 | 0
1807 | 822.57 | 7.6155 | 21.6 | 1.2488 | 1.2488 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1718 | 821.3212 | 0 | 0.088511 | 2.9055 | 0 | 0 | 0 | 1.2488 | on_peak | 821.3212 |  |  | 0.15 | 0 | 99.85 | 3.6284 | 0
1808 | 821.44 | 168.263 | 22.3 | 27.5236 | 27.5236 | 0 | 0 | 0 | 0 | 62.443 | 62.443 | 0 | 7.4174 | 731.4734 | 0 | 0.088511 | 2.7528 | 0 | 0 | 0 | 27.5236 | on_peak | 731.4734 |  |  | 3.35 | 7.6 | 89.05 | 75.7671 | 0
1809 | 892.42 | 390.782 | 22.9 | 63.7853 | 63.7853 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 828.6347 | 0 | 0.088511 | 2.6687 | 0 | 0 | 0 | 63.7853 | on_peak | 828.6347 |  |  | 7.15 | 0 | 92.85 | 170.2265 | 0
1810 | 868.75 | 596.18 | 23.5 | 97.1027 | 97.1027 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 771.6473 | 0 | 0.088511 | 2.6506 | 0 | 0 | 0 | 97.1027 | on_peak | 771.6473 |  |  | 11.18 | 0 | 88.82 | 257.3794 | 0
1811 | 868.01 | 760.303 | 24.2 | 123.5238 | 123.5238 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 18.9814 | 756.8486 | 0 | 0.05921 | 2.8776 | 0 | 0 | 0 | 123.5238 | off_peak | 744.4862 | 0 | 100 | 14.23 | 0 | 85.77 | 355.4521 | 0
1812 | 893 | 841.082 | 24.7 | 136.4024 | 136.4024 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 30.5453 | 768.9599 | 0 | 0.05921 | 3.2839 | 0 | 0 | 0 | 136.4024 | off_peak | 756.5976 | 0 | 100 | 15.27 | 0 | 84.73 | 447.9319 | 0
1813 | 860.13 | 885.377 | 25.1 | 143.3794 | 143.3794 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 42.1093 | 729.1129 | 0 | 0.05921 | 3.6866 | 0 | 0 | 0 | 143.3794 | off_peak | 716.7506 | 0 | 100 | 16.67 | 0 | 83.33 | 528.584 | 0
1814 | 885.51 | 861.997 | 25.4 | 139.4424 | 139.4424 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 53.6732 | 758.4299 | 0 | 0.05921 | 3.7842 | 0 | 0 | 0 | 139.4424 | off_peak | 746.0676 | 0 | 100 | 15.75 | 0 | 84.25 | 527.6822 | 0
1815 | 895.58 | 757.678 | 25.7 | 122.4345 | 122.4345 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 65.2371 | 785.5079 | 0 | 0.05921 | 3.6004 | 0 | 0 | 0 | 122.4345 | off_peak | 773.1455 | 0 | 100 | 13.67 | 0 | 86.33 | 440.8123 | 0
1816 | 880.68 | 593.098 | 25.8 | 95.8052 | 95.8052 | 0 | 0 | 8.9371 | 8.9371 | 0 | 0 | 0 | 73.597 | 793.812 | 0 | 0.05921 | 3.4628 | 0 | 0 | 0 | 95.8052 | off_peak | 784.8748 | 0 | 100 | 10.88 | 0 | 89.12 | 331.7574 | 0
1817 | 910.57 | 386.791 | 25.5 | 62.5474 | 62.5474 | 0 | 0 | 0.57721 | 0.57721 | 0 | 0 | 0 | 74.137 | 848.5999 | 0 | 0.05921 | 3.5866 | 0 | 0 | 0 | 62.5474 | off_peak | 848.0226 | 0 | 100 | 6.87 | 0 | 93.13 | 224.3347 | 0
1818 | 868.3 | 164.263 | 24.9 | 26.6202 | 26.6202 | 0 | 0 | 0.037279 | 0.037279 | 0 | 0 | 0 | 74.1718 | 841.7171 | 0 | 0.05921 | 3.8583 | 0 | 0 | 0 | 26.6202 | off_peak | 841.6798 | 0 | 100 | 3.07 | 0 | 96.93 | 102.7099 | 0
1819 | 805.96 | 6.65 | 24.5 | 1.0792 | 1.0792 | 0 | 0 | 0 | 0 | 62.443 | 62.443 | 0 | 7.4174 | 742.4377 | 0 | 0.088511 | 4.1339 | 0 | 0 | 0 | 1.0792 | on_peak | 742.4377 |  |  | 0.13 | 7.75 | 92.12 | 4.4615 | 0
1820 | 829.5 | 0 | 23.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 829.5 | 0 | 0.088511 | 4.4745 | 0 | 0 | 0 | 0 | on_peak | 829.5 |  |  | 0 | 0 | 100 | 0 | 0
1821 | 767.13 | 0 | 23.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 767.13 | 0 | 0.088511 | 4.7995 | 0 | 0 | 0 | 0 | on_peak | 767.13 |  |  | 0 | 0 | 100 | 0 | 0
1822 | 744.87 | 0 | 22.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 744.87 | 0 | 0.088511 | 5.129 | 0 | 0 | 0 | 0 | on_peak | 744.87 |  |  | 0 | 0 | 100 | 0 | 0
1823 | 797.77 | 0 | 22.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 797.77 | 0 | 0.05921 | 5.5191 | 0 | 0 | 0 | 0 | off_peak | 797.77 |  |  | 0 | 0 | 100 | 0 | 0
1824 | 788.77 | 0 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 788.77 | 0 | 0.05921 | 5.8157 | 0 | 0 | 0 | 0 | off_peak | 788.77 |  |  | 0 | 0 | 100 | 0 | 0
1825 | 711.76 | 0 | 21.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 711.76 | 0 | 0.05921 | 5.7927 | 0 | 0 | 0 | 0 | off_peak | 711.76 |  |  | 0 | 0 | 100 | 0 | 0
1826 | 644.74 | 0 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 644.74 | 0 | 0.05921 | 5.5798 | 0 | 0 | 0 | 0 | off_peak | 644.74 |  |  | 0 | 0 | 100 | 0 | 0
1827 | 601.01 | 0 | 20.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 601.01 | 0 | 0.05921 | 5.1473 | 0 | 0 | 0 | 0 | off_peak | 601.01 |  |  | 0 | 0 | 100 | 0 | 0
1828 | 599.58 | 0 | 20.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 599.58 | 0 | 0.05921 | 4.6593 | 0 | 0 | 0 | 0 | off_peak | 599.58 |  |  | 0 | 0 | 100 | 0 | 0
1829 | 620.42 | 0 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 620.42 | 0 | 0.05921 | 4.1609 | 0 | 0 | 0 | 0 | off_peak | 620.42 |  |  | 0 | 0 | 100 | 0 | 0
1830 | 713.82 | 0 | 19.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 713.82 | 0 | 0.05921 | 3.639 | 0 | 0 | 0 | 0 | off_peak | 713.82 |  |  | 0 | 0 | 100 | 0 | 0
1831 | 749.98 | 8.7068 | 20.3 | 1.4344 | 1.4344 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 748.5456 | 0 | 0.05921 | 3.2447 | 0 | 0 | 0 | 1.4344 | off_peak | 748.5456 |  |  | 0.19 | 0 | 99.81 | 4.6541 | 0
1832 | 771.02 | 173.144 | 21.2 | 28.433 | 28.433 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 742.587 | 0 | 0.05921 | 2.9934 | 0 | 0 | 0 | 28.433 | off_peak | 742.587 |  |  | 3.69 | 0 | 96.31 | 85.1113 | 0
1833 | 836.56 | 394.098 | 22.2 | 64.4874 | 64.4874 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 772.0726 | 0 | 0.05921 | 2.8407 | 0 | 0 | 0 | 64.4874 | off_peak | 772.0726 |  |  | 7.71 | 0 | 92.29 | 183.1864 | 0
1834 | 792.5 | 596.579 | 23.1 | 97.3069 | 97.3069 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 695.1931 | 0 | 0.05921 | 2.8122 | 0 | 0 | 0 | 97.3069 | off_peak | 695.1931 |  |  | 12.28 | 0 | 87.72 | 273.6433 | 0
1835 | 786.68 | 703.962 | 23.9 | 114.4934 | 114.4934 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 672.1866 | 0 | 0.05921 | 2.8521 | 0 | 0 | 0 | 114.4934 | off_peak | 672.1866 |  |  | 14.55 | 0 | 85.45 | 326.5437 | 0
1836 | 815.27 | 855.517 | 24.6 | 138.7933 | 138.7933 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 676.4767 | 0 | 0.05921 | 3.0038 | 0 | 0 | 0 | 138.7933 | off_peak | 676.4767 |  |  | 17.02 | 0 | 82.98 | 416.9006 | 0
1837 | 781.63 | 708.427 | 25.1 | 114.7239 | 114.7239 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 666.9061 | 0 | 0.05921 | 3.3206 | 0 | 0 | 0 | 114.7239 | off_peak | 666.9061 |  |  | 14.68 | 0 | 85.32 | 380.9496 | 0
1838 | 753.71 | 703.557 | 25.5 | 113.7711 | 113.7711 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 639.9389 | 0 | 0.05921 | 3.6764 | 0 | 0 | 0 | 113.7711 | off_peak | 639.9389 |  |  | 15.09 | 0 | 84.91 | 418.2688 | 0
1839 | 743.71 | 748.432 | 25.8 | 120.8968 | 120.8968 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 622.8132 | 0 | 0.05921 | 4.0847 | 0 | 0 | 0 | 120.8968 | off_peak | 622.8132 |  |  | 16.26 | 0 | 83.74 | 493.8254 | 0
1840 | 762.81 | 537.507 | 25.9 | 86.794 | 86.794 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 18.9814 | 688.3784 | 0 | 0.05921 | 4.4164 | 0 | 0 | 0 | 86.794 | off_peak | 676.016 | 0 | 100 | 11.38 | 0 | 88.62 | 383.3142 | 0
1841 | 799.61 | 325.896 | 25.6 | 52.6811 | 52.6811 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18.9814 | 746.9289 | 0 | 0.05921 | 4.6503 | 0 | 0 | 0 | 52.6811 | off_peak | 746.9289 |  |  | 6.59 | 0 | 93.41 | 244.9841 | 0
1842 | 679.42 | 82.5613 | 25 | 13.3749 | 13.3749 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18.9814 | 666.0451 | 0 | 0.05921 | 4.941 | 0 | 0 | 0 | 13.3749 | off_peak | 666.0451 |  |  | 1.97 | 0 | 98.03 | 66.0849 | 0
1843 | 652.68 | 5.7042 | 24.5 | 0.92574 | 0.92574 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18.9814 | 651.7543 | 0 | 0.05921 | 5.2343 | 0 | 0 | 0 | 0.92574 | off_peak | 651.7543 |  |  | 0.14 | 0 | 99.86 | 4.8456 | 0
1844 | 635.12 | 0 | 23.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18.9814 | 635.12 | 0 | 0.05921 | 5.5657 | 0 | 0 | 0 | 0 | off_peak | 635.12 |  |  | 0 | 0 | 100 | 0 | 0
1845 | 605.48 | 0 | 23.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18.9814 | 605.48 | 0 | 0.05921 | 5.8448 | 0 | 0 | 0 | 0 | off_peak | 605.48 |  |  | 0 | 0 | 100 | 0 | 0
1846 | 606.84 | 0 | 22.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18.9814 | 606.84 | 0 | 0.05921 | 6.178 | 0 | 0 | 0 | 0 | off_peak | 606.84 |  |  | 0 | 0 | 100 | 0 | 0
1847 | 603.78 | 0 | 22.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18.9814 | 603.78 | 0 | 0.05921 | 6.4105 | 0 | 0 | 0 | 0 | off_peak | 603.78 |  |  | 0 | 0 | 100 | 0 | 0
1848 | 611.16 | 0 | 22.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18.9814 | 611.16 | 0 | 0.05921 | 6.3919 | 0 | 0 | 0 | 0 | off_peak | 611.16 |  |  | 0 | 0 | 100 | 0 | 0
1849 | 592.22 | 0 | 22.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18.9814 | 592.22 | 0 | 0.05921 | 6.161 | 0 | 0 | 0 | 0 | off_peak | 592.22 |  |  | 0 | 0 | 100 | 0 | 0
1850 | 586.83 | 0 | 22.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18.9814 | 586.83 | 0 | 0.05921 | 6.011 | 0 | 0 | 0 | 0 | off_peak | 586.83 |  |  | 0 | 0 | 100 | 0 | 0
1851 | 618.36 | 0 | 22.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18.9814 | 618.36 | 0 | 0.05921 | 5.4921 | 0 | 0 | 0 | 0 | off_peak | 618.36 |  |  | 0 | 0 | 100 | 0 | 0
1852 | 597.78 | 0 | 22.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18.9814 | 597.78 | 0 | 0.05921 | 4.9742 | 0 | 0 | 0 | 0 | off_peak | 597.78 |  |  | 0 | 0 | 100 | 0 | 0
1853 | 608.71 | 0 | 22.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18.9814 | 608.71 | 0 | 0.05921 | 4.4062 | 0 | 0 | 0 | 0 | off_peak | 608.71 |  |  | 0 | 0 | 100 | 0 | 0
1854 | 720.55 | 0 | 22.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18.9814 | 720.55 | 0 | 0.05921 | 3.9429 | 0 | 0 | 0 | 0 | off_peak | 720.55 |  |  | 0 | 0 | 100 | 0 | 0
1855 | 720.16 | 6.6719 | 22.7 | 1.0898 | 1.0898 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18.9814 | 719.0702 | 0 | 0.05921 | 3.534 | 0 | 0 | 0 | 1.0898 | off_peak | 719.0702 |  |  | 0.15 | 0 | 99.85 | 3.8513 | 0
1856 | 779.02 | 147.105 | 23.3 | 23.9769 | 23.9769 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18.9814 | 755.0431 | 0 | 0.05921 | 3.2397 | 0 | 0 | 0 | 23.9769 | off_peak | 755.0431 |  |  | 3.08 | 0 | 96.92 | 77.6788 | 0
1857 | 802.27 | 254.763 | 23.9 | 41.435 | 41.435 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18.9814 | 760.835 | 0 | 0.05921 | 3.0564 | 0 | 0 | 0 | 41.435 | off_peak | 760.835 |  |  | 5.16 | 0 | 94.84 | 126.6434 | 0
1858 | 767.51 | 399.616 | 24.5 | 64.8543 | 64.8543 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18.9814 | 702.6557 | 0 | 0.05921 | 2.9666 | 0 | 0 | 0 | 64.8543 | off_peak | 702.6557 |  |  | 8.45 | 0 | 91.55 | 192.3992 | 0
1859 | 753.03 | 424.011 | 24.9 | 68.7145 | 68.7145 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 30.5453 | 696.6779 | 0 | 0.05921 | 2.9918 | 0 | 0 | 0 | 68.7145 | off_peak | 684.3155 | 0 | 100 | 9.13 | 0 | 90.87 | 205.5786 | 0
1860 | 769.59 | 295.199 | 25.2 | 47.7878 | 47.7878 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30.5453 | 721.8022 | 0 | 0.05921 | 3.0731 | 0 | 0 | 0 | 47.7878 | off_peak | 721.8022 |  |  | 6.21 | 0 | 93.79 | 146.8546 | 0
1861 | 716.23 | 392.151 | 25.5 | 63.4141 | 63.4141 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30.5453 | 652.8159 | 0 | 0.05921 | 3.325 | 0 | 0 | 0 | 63.4141 | off_peak | 652.8159 |  |  | 8.85 | 0 | 91.15 | 210.8514 | 0
1862 | 753.43 | 415.717 | 25.6 | 67.2007 | 67.2007 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30.5453 | 686.2293 | 0 | 0.05921 | 3.5934 | 0 | 0 | 0 | 67.2007 | off_peak | 686.2293 |  |  | 8.92 | 0 | 91.08 | 241.476 | 0
1863 | 771.68 | 185.342 | 25.6 | 29.9605 | 29.9605 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 42.1093 | 754.0818 | 0 | 0.05921 | 3.8257 | 0 | 0 | 0 | 29.9605 | off_peak | 741.7195 | 0 | 100 | 3.88 | 0 | 96.12 | 114.6207 | 0
1864 | 743.16 | 231.884 | 25.3 | 37.5246 | 37.5246 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 42.1093 | 705.6354 | 0 | 0.05921 | 3.869 | 0 | 0 | 0 | 37.5246 | off_peak | 705.6354 |  |  | 5.05 | 0 | 94.95 | 145.1815 | 0
1865 | 733.61 | 164.334 | 25 | 26.6221 | 26.6221 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 53.6732 | 719.3503 | 0 | 0.05921 | 4.0049 | 0 | 0 | 0 | 26.6221 | off_peak | 706.9879 | 0 | 100 | 3.63 | 0 | 96.37 | 106.62 | 0
1866 | 654.03 | 50.35 | 24.4 | 8.1743 | 8.1743 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 65.2371 | 658.2181 | 0 | 0.05921 | 4.0308 | 0 | 0 | 0 | 8.1743 | off_peak | 645.8557 | 0 | 100 | 1.25 | 0 | 98.75 | 32.9489 | 0
1867 | 592.08 | 2.85 | 24.1 | 0.4632 | 0.4632 | 0 | 0 | 8.9371 | 8.9371 | 0 | 0 | 0 | 73.597 | 600.5539 | 0 | 0.05921 | 4.0841 | 0 | 0 | 0 | 0.4632 | off_peak | 591.6168 | 0 | 100 | 0.08 | 0 | 99.92 | 1.8917 | 0
1868 | 572.23 | 0 | 23.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 73.597 | 572.23 | 0 | 0.05921 | 4.2387 | 0 | 0 | 0 | 0 | off_peak | 572.23 |  |  | 0 | 0 | 100 | 0 | 0
1869 | 562.73 | 0 | 23.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 73.597 | 562.73 | 0 | 0.05921 | 4.3369 | 0 | 0 | 0 | 0 | off_peak | 562.73 |  |  | 0 | 0 | 100 | 0 | 0
1870 | 556.99 | 0 | 23.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 73.597 | 556.99 | 0 | 0.05921 | 4.4316 | 0 | 0 | 0 | 0 | off_peak | 556.99 |  |  | 0 | 0 | 100 | 0 | 0
1871 | 573.41 | 0 | 23.3 | 0 | 0 | 0 | 0 | 0.57721 | 0.57721 | 0 | 0 | 0 | 74.137 | 573.9872 | 0 | 0.05921 | 4.4576 | 0 | 0 | 0 | 0 | off_peak | 573.41 | 0 | 100 | 0 | 0 | 100 | 0 | 0
1872 | 565.19 | 0 | 23.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.137 | 565.19 | 0 | 0.05921 | 4.5582 | 0 | 0 | 0 | 0 | off_peak | 565.19 |  |  | 0 | 0 | 100 | 0 | 0
1873 | 559.96 | 0 | 23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.137 | 559.96 | 0 | 0.05921 | 4.759 | 0 | 0 | 0 | 0 | off_peak | 559.96 |  |  | 0 | 0 | 100 | 0 | 0
1874 | 561.16 | 0 | 22.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.137 | 561.16 | 0 | 0.05921 | 4.6822 | 0 | 0 | 0 | 0 | off_peak | 561.16 |  |  | 0 | 0 | 100 | 0 | 0
1875 | 567.83 | 0 | 22.7 | 0 | 0 | 0 | 0 | 0.037279 | 0.037279 | 0 | 0 | 0 | 74.1718 | 567.8673 | 0 | 0.05921 | 4.367 | 0 | 0 | 0 | 0 | off_peak | 567.83 | 0 | 100 | 0 | 0 | 100 | 0 | 0
1876 | 569.05 | 0 | 22.6 | 0 | 0 | 0 | 0 | 0.0024077 | 0.0024077 | 0 | 0 | 0 | 74.1741 | 569.0524 | 0 | 0.05921 | 3.9786 | 0 | 0 | 0 | 0 | off_peak | 569.05 | 0 | 100 | 0 | 0 | 100 | 0 | 0
1877 | 576.51 | 0 | 22.6 | 0 | 0 | 0 | 0 | 0.0001555 | 0.0001555 | 0 | 0 | 0 | 74.1742 | 576.5102 | 0 | 0.05921 | 3.434 | 0 | 0 | 0 | 0 | off_peak | 576.51 | 0 | 100 | 0 | 0 | 100 | 0 | 0
1878 | 675.66 | 0 | 22.6 | 0 | 0 | 0 | 0 | 1.0737e-05 | 1.0737e-05 | 0 | 0 | 0 | 74.1743 | 675.66 | 0 | 0.05921 | 2.9654 | 0 | 0 | 0 | 0 | off_peak | 675.66 | 0 | 100 | 0 | 0 | 100 | 0 | 0
1879 | 738.67 | 2.85 | 23.2 | 0.46469 | 0.46469 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1743 | 738.2053 | 0 | 0.088511 | 2.6267 | 0 | 0 | 0 | 0.46469 | on_peak | 738.2053 |  |  | 0.06 | 0 | 99.94 | 1.2206 | 0
1880 | 753.94 | 48.0374 | 24.1 | 7.8073 | 7.8073 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1743 | 746.1327 | 0 | 0.088511 | 2.5277 | 0 | 0 | 0 | 7.8073 | on_peak | 746.1327 |  |  | 1.04 | 0 | 98.96 | 19.7343 | 0
1881 | 836.18 | 98.6245 | 24.7 | 15.9944 | 15.9944 | 0 | 0 | 0 | 0 | 62.4453 | 62.4453 | 0 | 7.4174 | 757.7403 | 0 | 0.088511 | 2.4854 | 0 | 0 | 0 | 15.9944 | on_peak | 757.7403 |  |  | 1.91 | 7.47 | 90.62 | 39.7533 | 0
1882 | 784.13 | 317.671 | 25.1 | 51.4442 | 51.4442 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 732.6858 | 0 | 0.088511 | 2.5668 | 0 | 0 | 0 | 51.4442 | on_peak | 732.6858 |  |  | 6.56 | 0 | 93.44 | 132.047 | 0
1883 | 776.5 | 578.014 | 25.5 | 93.4697 | 93.4697 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 18.9814 | 695.3927 | 0 | 0.05921 | 2.8425 | 0 | 0 | 0 | 93.4697 | off_peak | 683.0303 | 0 | 100 | 12.04 | 0 | 87.96 | 265.6893 | 0
1884 | 867.59 | 716.705 | 25.8 | 115.7718 | 115.7718 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 30.5453 | 764.1806 | 0 | 0.05921 | 3.421 | 0 | 0 | 0 | 115.7718 | off_peak | 751.8182 | 0 | 100 | 13.34 | 0 | 86.66 | 396.0588 | 0
1885 | 835.09 | 588.74 | 25.9 | 95.0669 | 95.0669 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 42.1093 | 752.3855 | 0 | 0.05921 | 3.9138 | 0 | 0 | 0 | 95.0669 | off_peak | 740.0231 | 0 | 100 | 11.38 | 0 | 88.62 | 372.0722 | 0
1886 | 852.08 | 776.858 | 25.9 | 125.4432 | 125.4432 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 53.6732 | 738.9991 | 0 | 0.05921 | 3.9753 | 0 | 0 | 0 | 125.4432 | off_peak | 726.6368 | 0 | 100 | 14.72 | 0 | 85.28 | 498.6695 | 0
1887 | 851.56 | 681.318 | 25.8 | 110.0556 | 110.0556 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 65.2371 | 753.8667 | 0 | 0.05921 | 3.5004 | 0 | 0 | 0 | 110.0556 | off_peak | 741.5044 | 0 | 100 | 12.92 | 0 | 87.08 | 385.2436 | 0
1888 | 835.07 | 528.214 | 25.5 | 85.4166 | 85.4166 | 0 | 0 | 8.9371 | 8.9371 | 0 | 0 | 0 | 73.597 | 758.5905 | 0 | 0.05921 | 3.0847 | 0 | 0 | 0 | 85.4166 | off_peak | 749.6534 | 0 | 100 | 10.23 | 0 | 89.77 | 263.4825 | 0
1889 | 841.69 | 137.889 | 25.2 | 22.3219 | 22.3219 | 0 | 0 | 0.57721 | 0.57721 | 0 | 0 | 0 | 74.137 | 819.9453 | 0 | 0.05921 | 2.8395 | 0 | 0 | 0 | 22.3219 | off_peak | 819.3681 | 0 | 100 | 2.65 | 0 | 97.35 | 63.3841 | 0
1890 | 841.61 | 158.202 | 24.6 | 25.6656 | 25.6283 | 0 | 0.037279 | 0.037279 | 0 | 0 | 0 | 0 | 74.1718 | 815.9817 | 0 | 0.05921 | 2.7419 | 0 | 0 | 0.034872 | 25.6283 | off_peak | 815.9817 | 100 | 0 | 3.05 | 0 | 96.95 | 70.271 | 0
1891 | 821.39 | 7.6891 | 24.3 | 1.2488 | 1.2488 | 0 | 0 | 0 | 0 | 62.443 | 62.443 | 0 | 7.4174 | 757.6982 | 0 | 0.088511 | 2.6109 | 0.032619 | 0 | 0 | 1.2814 | on_peak | 757.6982 |  |  | 0.15 | 7.6 | 92.25 | 3.3455 | 0
1892 | 819.31 | 0 | 23.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 819.31 | 0 | 0.088511 | 2.5631 | 0 | 0 | 0 | 0 | on_peak | 819.31 |  |  | 0 | 0 | 100 | 0 | 0
1893 | 795.14 | 0 | 23.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 795.14 | 0 | 0.088511 | 2.6187 | 0 | 0 | 0 | 0 | on_peak | 795.14 |  |  | 0 | 0 | 100 | 0 | 0
1894 | 759.44 | 0 | 23.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 759.44 | 0 | 0.088511 | 2.7665 | 0 | 0 | 0 | 0 | on_peak | 759.44 |  |  | 0 | 0 | 100 | 0 | 0
1895 | 785.36 | 0 | 23.6 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 18.9814 | 797.7224 | 0 | 0.05921 | 3.1412 | 0 | 0 | 0 | 0 | off_peak | 785.36 | 0 | 100 | 0 | 0 | 100 | 0 | 0
1896 | 803.72 | 0 | 23.6 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 30.5453 | 816.0824 | 0 | 0.05921 | 3.7911 | 0 | 0 | 0 | 0 | off_peak | 803.72 | 0 | 100 | 0 | 0 | 100 | 0 | 0
1897 | 726.3 | 0 | 23.6 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 42.1093 | 738.6624 | 0 | 0.05921 | 4.4013 | 0 | 0 | 0 | 0 | off_peak | 726.3 | 0 | 100 | 0 | 0 | 100 | 0 | 0
1898 | 667.95 | 0 | 23.5 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 53.6732 | 680.3124 | 0 | 0.05921 | 4.5175 | 0 | 0 | 0 | 0 | off_peak | 667.95 | 0 | 100 | 0 | 0 | 100 | 0 | 0
1899 | 634.75 | 0 | 23.5 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 65.2371 | 647.1124 | 0 | 0.05921 | 4.2265 | 0 | 0 | 0 | 0 | off_peak | 634.75 | 0 | 100 | 0 | 0 | 100 | 0 | 0
1900 | 579.05 | 0 | 23.5 | 0 | 0 | 0 | 0 | 8.9371 | 8.9371 | 0 | 0 | 0 | 73.597 | 587.9871 | 0 | 0.05921 | 3.7856 | 0 | 0 | 0 | 0 | off_peak | 579.05 | 0 | 100 | 0 | 0 | 100 | 0 | 0
1901 | 602.87 | 0 | 23.5 | 0 | 0 | 0 | 0 | 0.57721 | 0.57721 | 0 | 0 | 0 | 74.137 | 603.4472 | 0 | 0.05921 | 3.2618 | 0 | 0 | 0 | 0 | off_peak | 602.87 | 0 | 100 | 0 | 0 | 100 | 0 | 0
1902 | 709.7 | 0 | 23.6 | 0 | 0 | 0 | 0 | 0.037279 | 0.037279 | 0 | 0 | 0 | 74.1718 | 709.7373 | 0 | 0.05921 | 2.7818 | 0 | 0 | 0 | 0 | off_peak | 709.7 | 0 | 100 | 0 | 0 | 100 | 0 | 0
1903 | 702.36 | 10.9076 | 24.2 | 1.7721 | 1.7721 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1718 | 700.5879 | 0 | 0.088511 | 2.5205 | 0 | 0 | 0 | 1.7721 | on_peak | 700.5879 |  |  | 0.25 | 0 | 99.75 | 4.4666 | 0
1904 | 766.27 | 177.597 | 25 | 28.7707 | 28.7707 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1718 | 737.4993 | 0 | 0.088511 | 2.3927 | 0 | 0 | 0 | 28.7707 | on_peak | 737.4993 |  |  | 3.75 | 0 | 96.25 | 68.8395 | 0
1905 | 765.58 | 398.551 | 25.6 | 64.4258 | 64.4258 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1718 | 701.1542 | 0 | 0.088511 | 2.3687 | 0 | 0 | 0 | 64.4258 | on_peak | 701.1542 |  |  | 8.42 | 0 | 91.58 | 152.6024 | 0
1906 | 802.13 | 606.512 | 26.2 | 97.8305 | 97.8305 | 0 | 0 | 0 | 0 | 62.443 | 62.443 | 0 | 7.4174 | 641.8565 | 0 | 0.088511 | 2.4438 | 0 | 0 | 0 | 97.8305 | on_peak | 641.8565 |  |  | 12.2 | 7.78 | 80.02 | 239.0773 | 0
1907 | 788.94 | 614.625 | 26.8 | 98.924 | 98.924 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 18.9814 | 702.3783 | 0 | 0.05921 | 2.7718 | 0 | 0 | 0 | 98.924 | off_peak | 690.016 | 0 | 100 | 12.54 | 0 | 87.46 | 274.2007 | 0
1908 | 876.54 | 821.984 | 27.3 | 132.0588 | 132.0588 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 30.5453 | 756.8435 | 0 | 0.05921 | 3.3811 | 0 | 0 | 0 | 132.0588 | off_peak | 744.4812 | 0 | 100 | 15.07 | 0 | 84.93 | 446.5064 | 0
1909 | 848.37 | 896.988 | 27.6 | 143.9519 | 143.9519 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 42.1093 | 716.7804 | 0 | 0.05921 | 3.8877 | 0 | 0 | 0 | 143.9519 | off_peak | 704.4181 | 0 | 100 | 16.97 | 0 | 83.03 | 559.6366 | 0
1910 | 917.86 | 703.417 | 27.9 | 112.7639 | 112.7639 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 53.6732 | 817.4585 | 0 | 0.05921 | 3.8079 | 0 | 0 | 0 | 112.7639 | off_peak | 805.0961 | 0 | 100 | 12.29 | 0 | 87.71 | 429.3889 | 0
1911 | 932.17 | 720.69 | 27.9 | 115.5329 | 115.5329 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 65.2371 | 828.9995 | 0 | 0.05921 | 3.3059 | 0 | 0 | 0 | 115.5329 | off_peak | 816.6371 | 0 | 100 | 12.39 | 0 | 87.61 | 381.9437 | 0
1912 | 912.06 | 600.228 | 27.8 | 96.2568 | 96.2568 | 0 | 0 | 8.9371 | 8.9371 | 0 | 0 | 0 | 73.597 | 824.7403 | 0 | 0.05921 | 2.9433 | 0 | 0 | 0 | 96.2568 | off_peak | 815.8032 | 0 | 100 | 10.55 | 0 | 89.45 | 283.3123 | 0
1913 | 883.74 | 393.231 | 27.4 | 63.153 | 63.153 | 0 | 0 | 0.57721 | 0.57721 | 0 | 0 | 0 | 74.137 | 821.1642 | 0 | 0.05921 | 2.7635 | 0 | 0 | 0 | 63.153 | off_peak | 820.587 | 0 | 100 | 7.15 | 0 | 92.85 | 174.522 | 0
1914 | 869.47 | 170.157 | 26.7 | 27.3967 | 27.3967 | 0 | 0 | 0.037279 | 0.037279 | 0 | 0 | 0 | 74.1718 | 842.1105 | 0 | 0.05921 | 2.8546 | 0 | 0 | 0 | 27.3967 | off_peak | 842.0733 | 0 | 100 | 3.15 | 0 | 96.85 | 78.2055 | 0
1915 | 839.59 | 8.7466 | 26.2 | 1.4108 | 1.4108 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1718 | 838.1792 | 0 | 0.088511 | 2.9292 | 0 | 0 | 0 | 1.4108 | on_peak | 838.1792 |  |  | 0.17 | 0 | 99.83 | 4.1326 | 0
1916 | 823.95 | 0 | 25.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1718 | 823.95 | 0 | 0.088511 | 3.0344 | 0 | 0 | 0 | 0 | on_peak | 823.95 |  |  | 0 | 0 | 100 | 0 | 0
1917 | 799.43 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1718 | 799.43 | 0 | 0.088511 | 3.2084 | 0 | 0 | 0 | 0 | on_peak | 799.43 |  |  | 0 | 0 | 100 | 0 | 0
1918 | 753.67 | 0 | 24.6 | 0 | 0 | 0 | 0 | 0 | 0 | 62.443 | 62.443 | 0 | 7.4174 | 691.227 | 0 | 0.088511 | 3.554 | 0 | 0 | 0 | 0 | on_peak | 691.227 |  |  | 0 | 8.29 | 91.71 | 0 | 0
1919 | 822.87 | 0 | 24.4 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 18.9814 | 835.2324 | 0 | 0.05921 | 3.9968 | 0 | 0 | 0 | 0 | off_peak | 822.87 | 0 | 100 | 0 | 0 | 100 | 0 | 0
1920 | 773.78 | 0 | 24.2 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 30.5453 | 786.1424 | 0 | 0.05921 | 4.4813 | 0 | 0 | 0 | 0 | off_peak | 773.78 | 0 | 100 | 0 | 0 | 100 | 0 | 0
1921 | 738.56 | 0 | 24.1 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 42.1093 | 750.9224 | 0 | 0.05921 | 4.7934 | 0 | 0 | 0 | 0 | off_peak | 738.56 | 0 | 100 | 0 | 0 | 100 | 0 | 0
1922 | 688.39 | 0 | 24 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 53.6732 | 700.7524 | 0 | 0.05921 | 4.774 | 0 | 0 | 0 | 0 | off_peak | 688.39 | 0 | 100 | 0 | 0 | 100 | 0 | 0
1923 | 619.89 | 0 | 24 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 65.2371 | 632.2524 | 0 | 0.05921 | 4.3646 | 0 | 0 | 0 | 0 | off_peak | 619.89 | 0 | 100 | 0 | 0 | 100 | 0 | 0
1924 | 624.96 | 0 | 23.9 | 0 | 0 | 0 | 0 | 8.9371 | 8.9371 | 0 | 0 | 0 | 73.597 | 633.8971 | 0 | 0.05921 | 3.8768 | 0 | 0 | 0 | 0 | off_peak | 624.96 | 0 | 100 | 0 | 0 | 100 | 0 | 0
1925 | 622.18 | 0 | 23.8 | 0 | 0 | 0 | 0 | 0.57721 | 0.57721 | 0 | 0 | 0 | 74.137 | 622.7572 | 0 | 0.05921 | 3.323 | 0 | 0 | 0 | 0 | off_peak | 622.18 | 0 | 100 | 0 | 0 | 100 | 0 | 0
1926 | 700.72 | 0 | 23.7 | 0 | 0 | 0 | 0 | 0.037279 | 0.037279 | 0 | 0 | 0 | 74.1718 | 700.7573 | 0 | 0.05921 | 2.7348 | 0 | 0 | 0 | 0 | off_peak | 700.72 | 0 | 100 | 0 | 0 | 100 | 0 | 0
1927 | 781.82 | 14.4363 | 24.1 | 2.3463 | 2.3463 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1718 | 779.4737 | 0 | 0.088511 | 2.4101 | 0 | 0 | 0 | 2.3463 | on_peak | 779.4737 |  |  | 0.3 | 0 | 99.7 | 5.6546 | 0
1928 | 778.61 | 166.434 | 25 | 26.9623 | 26.9623 | 0 | 0 | 0 | 0 | 62.443 | 62.443 | 0 | 7.4174 | 689.2047 | 0 | 0.088511 | 2.2603 | 0 | 0 | 0 | 26.9623 | on_peak | 689.2047 |  |  | 3.46 | 8.02 | 88.52 | 60.944 | 0
1929 | 827.37 | 410.642 | 25.8 | 66.3324 | 66.3324 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 761.0376 | 0 | 0.088511 | 2.1911 | 0 | 0 | 0 | 66.3324 | on_peak | 761.0376 |  |  | 8.02 | 0 | 91.98 | 145.343 | 0
1930 | 834.53 | 614.371 | 26.5 | 98.9907 | 98.9907 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 735.5393 | 0 | 0.088511 | 2.2393 | 0 | 0 | 0 | 98.9907 | on_peak | 735.5393 |  |  | 11.86 | 0 | 88.14 | 221.667 | 0
1931 | 799.06 | 764.699 | 27.1 | 122.9447 | 122.9447 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 18.9814 | 688.4777 | 0 | 0.05921 | 2.4764 | 0 | 0 | 0 | 122.9447 | off_peak | 676.1153 | 0 | 100 | 15.39 | 0 | 84.61 | 304.4579 | 0
1932 | 866.03 | 861.91 | 27.6 | 138.3225 | 138.3225 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 30.5453 | 740.0699 | 0 | 0.05921 | 2.9292 | 0 | 0 | 0 | 138.3225 | off_peak | 727.7075 | 0 | 100 | 15.97 | 0 | 84.03 | 405.1747 | 0
1933 | 876.84 | 794.731 | 28.1 | 127.3096 | 127.3096 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 42.1093 | 761.8928 | 0 | 0.05921 | 3.3268 | 0 | 0 | 0 | 127.3096 | off_peak | 749.5304 | 0 | 100 | 14.52 | 0 | 85.48 | 423.5395 | 0
1934 | 889.41 | 766.15 | 28.4 | 122.5971 | 122.5971 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 53.6732 | 779.1753 | 0 | 0.05921 | 3.4131 | 0 | 0 | 0 | 122.5971 | off_peak | 766.8129 | 0 | 100 | 13.78 | 0 | 86.22 | 418.432 | 0
1935 | 938.1 | 754.838 | 28.5 | 120.743 | 120.743 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 65.2371 | 829.7194 | 0 | 0.05921 | 3.2323 | 0 | 0 | 0 | 120.743 | off_peak | 817.357 | 0 | 100 | 12.87 | 0 | 87.13 | 390.2799 | 0
1936 | 891.59 | 568.279 | 28.3 | 90.9675 | 90.9675 | 0 | 0 | 8.9371 | 8.9371 | 0 | 0 | 0 | 73.597 | 809.5596 | 0 | 0.05921 | 3.125 | 0 | 0 | 0 | 90.9675 | off_peak | 800.6225 | 0 | 100 | 10.2 | 0 | 89.8 | 284.2756 | 0
1937 | 867.63 | 267.681 | 27.8 | 42.9272 | 42.35 | 0 | 0.57721 | 0.57721 | 0 | 0 | 0 | 0 | 74.137 | 825.28 | 0 | 0.05921 | 3.2323 | 0 | 0 | 0.53993 | 42.35 | off_peak | 825.28 | 100 | 0 | 4.88 | 0 | 95.12 | 136.8858 | 0
1938 | 849.44 | 129.525 | 26.9 | 20.8395 | 20.8022 | 0 | 0.037279 | 0.037279 | 0 | 0 | 0 | 0 | 74.1718 | 828.6378 | 0 | 0.05921 | 3.3354 | 0 | 0 | 0.5748 | 20.8022 | off_peak | 828.6378 | 100 | 0 | 2.45 | 0 | 97.55 | 69.3832 | 0
1939 | 821.99 | 6.7021 | 26.3 | 1.0807 | 1.0807 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1718 | 820.9093 | 0 | 0.088511 | 3.4904 | 0 | 0 | 0.5748 | 1.0807 | on_peak | 820.9093 |  |  | 0.13 | 0 | 99.87 | 3.7719 | 0
1940 | 835.56 | 0 | 25.1 | 0 | 0 | 0 | 0 | 0 | 0 | 62.443 | 62.443 | 0 | 7.4174 | 773.117 | 0 | 0.088511 | 3.733 | 0.53768 | 0 | 0 | 0.53768 | on_peak | 773.117 |  |  | 0 | 7.47 | 92.53 | 2.0071 | 0
1941 | 827 | 0 | 24.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 827 | 0 | 0.088511 | 4.042 | 0 | 0 | 0 | 0 | on_peak | 827 |  |  | 0 | 0 | 100 | 0 | 0
1942 | 761.75 | 0 | 23.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 761.75 | 0 | 0.088511 | 4.3159 | 0 | 0 | 0 | 0 | on_peak | 761.75 |  |  | 0 | 0 | 100 | 0 | 0
1943 | 816.98 | 0 | 23.6 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 18.9814 | 829.3424 | 0 | 0.05921 | 4.6962 | 0 | 0 | 0 | 0 | off_peak | 816.98 | 0 | 100 | 0 | 0 | 100 | 0 | 0
1944 | 818.81 | 0 | 23.5 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 30.5453 | 831.1724 | 0 | 0.05921 | 5.1867 | 0 | 0 | 0 | 0 | off_peak | 818.81 | 0 | 100 | 0 | 0 | 100 | 0 | 0
1945 | 794.46 | 0 | 23.3 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 42.1093 | 806.8224 | 0 | 0.05921 | 5.327 | 0 | 0 | 0 | 0 | off_peak | 794.46 | 0 | 100 | 0 | 0 | 100 | 0 | 0
1946 | 735.11 | 0 | 23.1 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 53.6732 | 747.4724 | 0 | 0.05921 | 5.3095 | 0 | 0 | 0 | 0 | off_peak | 735.11 | 0 | 100 | 0 | 0 | 100 | 0 | 0
1947 | 672.81 | 0 | 23.1 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 65.2371 | 685.1724 | 0 | 0.05921 | 4.8386 | 0 | 0 | 0 | 0 | off_peak | 672.81 | 0 | 100 | 0 | 0 | 100 | 0 | 0
1948 | 656.32 | 0 | 23.1 | 0 | 0 | 0 | 0 | 8.9371 | 8.9371 | 0 | 0 | 0 | 73.597 | 665.2571 | 0 | 0.05921 | 4.3525 | 0 | 0 | 0 | 0 | off_peak | 656.32 | 0 | 100 | 0 | 0 | 100 | 0 | 0
1949 | 650.75 | 0 | 23.1 | 0 | 0 | 0 | 0 | 0.57721 | 0.57721 | 0 | 0 | 0 | 74.137 | 651.3272 | 0 | 0.05921 | 3.6507 | 0 | 0 | 0 | 0 | off_peak | 650.75 | 0 | 100 | 0 | 0 | 100 | 0 | 0
1950 | 687.76 | 0 | 23.2 | 0 | 0 | 0 | 0 | 0.037279 | 0.037279 | 0 | 0 | 0 | 74.1718 | 687.7973 | 0 | 0.05921 | 3.0834 | 0 | 0 | 0 | 0 | off_peak | 687.76 | 0 | 100 | 0 | 0 | 100 | 0 | 0
1951 | 771.32 | 14.7269 | 23.8 | 2.3961 | 2.3961 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1718 | 768.9239 | 0 | 0.088511 | 2.6912 | 0 | 0 | 0 | 2.3961 | on_peak | 768.9239 |  |  | 0.31 | 0 | 99.69 | 6.4483 | 0
1952 | 779.45 | 191.652 | 24.5 | 31.1035 | 31.1035 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1718 | 748.3465 | 0 | 0.088511 | 2.4642 | 0 | 0 | 0 | 31.1035 | on_peak | 748.3465 |  |  | 3.99 | 0 | 96.01 | 76.6466 | 0
1953 | 811.49 | 416.65 | 25.1 | 67.473 | 67.473 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1718 | 744.017 | 0 | 0.088511 | 2.3659 | 0 | 0 | 0 | 67.473 | on_peak | 744.017 |  |  | 8.31 | 0 | 91.69 | 159.6339 | 0
1954 | 838.96 | 623.401 | 25.5 | 100.8092 | 100.8092 | 0 | 0 | 0 | 0 | 62.443 | 62.443 | 0 | 7.4174 | 675.7078 | 0 | 0.088511 | 2.3742 | 0 | 0 | 0 | 100.8092 | on_peak | 675.7078 |  |  | 12.02 | 7.44 | 80.54 | 239.339 | 0
1955 | 829.32 | 775.007 | 25.8 | 125.1895 | 125.1895 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 18.9814 | 716.4928 | 0 | 0.05921 | 2.5867 | 0 | 0 | 0 | 125.1895 | off_peak | 704.1305 | 0 | 100 | 15.1 | 0 | 84.9 | 323.8234 | 0
1956 | 907.1 | 843.708 | 26 | 136.1886 | 136.1886 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 30.5453 | 783.2737 | 0 | 0.05921 | 3.066 | 0 | 0 | 0 | 136.1886 | off_peak | 770.9114 | 0 | 100 | 15.01 | 0 | 84.99 | 417.5604 | 0
1957 | 843.08 | 919.53 | 26 | 148.4276 | 148.4276 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 42.1093 | 707.0148 | 0 | 0.05921 | 3.4019 | 0 | 0 | 0 | 148.4276 | off_peak | 694.6524 | 0 | 100 | 17.61 | 0 | 82.39 | 504.9407 | 0
1958 | 866.78 | 870.782 | 26.1 | 140.5081 | 140.5081 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 53.6732 | 738.6343 | 0 | 0.05921 | 3.5222 | 0 | 0 | 0 | 140.5081 | off_peak | 726.2719 | 0 | 100 | 16.21 | 0 | 83.79 | 494.8917 | 0
1959 | 919.49 | 756.588 | 26.1 | 122.0819 | 122.0819 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 65.2371 | 809.7705 | 0 | 0.05921 | 3.4925 | 0 | 0 | 0 | 122.0819 | off_peak | 797.4081 | 0 | 100 | 13.28 | 0 | 86.72 | 426.3681 | 0
1960 | 842.79 | 570.695 | 25.9 | 92.153 | 92.153 | 0 | 0 | 8.9371 | 8.9371 | 0 | 0 | 0 | 73.597 | 759.5741 | 0 | 0.05921 | 3.3179 | 0 | 0 | 0 | 92.153 | off_peak | 750.637 | 0 | 100 | 10.93 | 0 | 89.07 | 305.7532 | 0
1961 | 904.28 | 404.093 | 25.5 | 65.3452 | 65.3452 | 0 | 0 | 0.57721 | 0.57721 | 0 | 0 | 0 | 74.137 | 839.512 | 0 | 0.05921 | 3.3902 | 0 | 0 | 0 | 65.3452 | off_peak | 838.9348 | 0 | 100 | 7.23 | 0 | 92.77 | 221.5315 | 0
1962 | 884.02 | 180.113 | 25 | 29.1783 | 29.1783 | 0 | 0 | 0.037279 | 0.037279 | 0 | 0 | 0 | 74.1718 | 854.879 | 0 | 0.05921 | 3.6477 | 0 | 0 | 0 | 29.1783 | off_peak | 854.8417 | 0 | 100 | 3.3 | 0 | 96.7 | 106.4336 | 0
1963 | 837.03 | 10.8416 | 24.7 | 1.7582 | 1.7582 | 0 | 0 | 0 | 0 | 44.8921 | 44.8921 | 0 | 26.1802 | 790.3797 | 0 | 0.088511 | 3.928 | 0 | 0 | 0 | 1.7582 | on_peak | 790.3797 |  |  | 0.21 | 5.36 | 94.43 | 6.9064 | 0
1964 | 884.32 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 17.551 | 17.551 | 0 | 7.4174 | 866.769 | 0 | 0.088511 | 4.2412 | 0 | 0 | 0 | 0 | on_peak | 866.769 |  |  | 0 | 1.98 | 98.02 | 0 | 0
1965 | 832.15 | 0 | 23.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 832.15 | 0 | 0.088511 | 4.5012 | 0 | 0 | 0 | 0 | on_peak | 832.15 |  |  | 0 | 0 | 100 | 0 | 0
1966 | 768.44 | 0 | 23.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 768.44 | 0 | 0.088511 | 4.8766 | 0 | 0 | 0 | 0 | on_peak | 768.44 |  |  | 0 | 0 | 100 | 0 | 0
1967 | 842.42 | 0 | 23.1 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 18.9814 | 854.7824 | 0 | 0.05921 | 5.2626 | 0 | 0 | 0 | 0 | off_peak | 842.42 | 0 | 100 | 0 | 0 | 100 | 0 | 0
1968 | 842.09 | 0 | 22.9 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 30.5453 | 854.4524 | 0 | 0.05921 | 5.6589 | 0 | 0 | 0 | 0 | off_peak | 842.09 | 0 | 100 | 0 | 0 | 100 | 0 | 0
1969 | 778.56 | 0 | 22.8 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 42.1093 | 790.9224 | 0 | 0.05921 | 5.7896 | 0 | 0 | 0 | 0 | off_peak | 778.56 | 0 | 100 | 0 | 0 | 100 | 0 | 0
1970 | 754.46 | 0 | 22.8 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 53.6732 | 766.8224 | 0 | 0.05921 | 5.703 | 0 | 0 | 0 | 0 | off_peak | 754.46 | 0 | 100 | 0 | 0 | 100 | 0 | 0
1971 | 660.8 | 0 | 22.7 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 65.2371 | 673.1624 | 0 | 0.05921 | 5.2334 | 0 | 0 | 0 | 0 | off_peak | 660.8 | 0 | 100 | 0 | 0 | 100 | 0 | 0
1972 | 605.6 | 0 | 22.6 | 0 | 0 | 0 | 0 | 8.9371 | 8.9371 | 0 | 0 | 0 | 73.597 | 614.5371 | 0 | 0.05921 | 4.6169 | 0 | 0 | 0 | 0 | off_peak | 605.6 | 0 | 100 | 0 | 0 | 100 | 0 | 0
1973 | 641.18 | 0 | 22.4 | 0 | 0 | 0 | 0 | 0.57721 | 0.57721 | 0 | 0 | 0 | 74.137 | 641.7572 | 0 | 0.05921 | 3.9276 | 0 | 0 | 0 | 0 | off_peak | 641.18 | 0 | 100 | 0 | 0 | 100 | 0 | 0
1974 | 728.6 | 0 | 22 | 0 | 0 | 0 | 0 | 0.037279 | 0.037279 | 0 | 0 | 0 | 74.1718 | 728.6373 | 0 | 0.05921 | 3.2733 | 0 | 0 | 0 | 0 | off_peak | 728.6 | 0 | 100 | 0 | 0 | 100 | 0 | 0
1975 | 771.58 | 18.1102 | 21.5 | 2.9708 | 2.9708 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1718 | 768.6092 | 0 | 0.088511 | 2.9007 | 0 | 0 | 0 | 2.9708 | on_peak | 768.6092 |  |  | 0.39 | 0 | 99.61 | 8.6176 | 0
1976 | 859.22 | 202.097 | 21.3 | 33.1758 | 33.1758 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1718 | 826.0442 | 0 | 0.088511 | 2.6584 | 0 | 0 | 0 | 33.1758 | on_peak | 826.0442 |  |  | 3.86 | 0 | 96.14 | 88.1949 | 0
1977 | 843.32 | 426.417 | 21.4 | 69.9748 | 69.9748 | 0 | 0 | 0 | 0 | 62.443 | 62.443 | 0 | 7.4174 | 710.9021 | 0 | 0.088511 | 2.5453 | 0 | 0 | 0 | 69.9748 | on_peak | 710.9021 |  |  | 8.3 | 7.4 | 84.3 | 178.1058 | 0
1978 | 915.07 | 611.334 | 21.9 | 100.1414 | 100.1414 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 814.9286 | 0 | 0.088511 | 2.5396 | 0 | 0 | 0 | 100.1414 | on_peak | 814.9286 |  |  | 10.94 | 0 | 89.06 | 254.3145 | 0
1979 | 851.88 | 700.589 | 22.4 | 114.5577 | 114.5577 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 18.9814 | 749.6846 | 0 | 0.05921 | 2.6726 | 0 | 0 | 0 | 114.5577 | off_peak | 737.3223 | 0 | 100 | 13.45 | 0 | 86.55 | 306.1658 | 0
1980 | 920.79 | 782.237 | 22.9 | 127.6804 | 127.6804 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 30.5453 | 805.472 | 0 | 0.05921 | 3.0663 | 0 | 0 | 0 | 127.6804 | off_peak | 793.1096 | 0 | 100 | 13.87 | 0 | 86.13 | 391.5127 | 0
1981 | 894.87 | 651.085 | 23.3 | 106.1213 | 106.1213 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 42.1093 | 801.1111 | 0 | 0.05921 | 3.4449 | 0 | 0 | 0 | 106.1213 | off_peak | 788.7487 | 0 | 100 | 11.86 | 0 | 88.14 | 365.5785 | 0
1982 | 889.92 | 755.459 | 23.6 | 123.0012 | 123.0012 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 53.6732 | 779.2812 | 0 | 0.05921 | 3.6325 | 0 | 0 | 0 | 123.0012 | off_peak | 766.9188 | 0 | 100 | 13.82 | 0 | 86.18 | 446.8005 | 0
1983 | 903.82 | 542.121 | 23.7 | 88.2346 | 88.2346 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 65.2371 | 827.9478 | 0 | 0.05921 | 3.5885 | 0 | 0 | 0 | 88.2346 | off_peak | 815.5854 | 0 | 100 | 9.76 | 0 | 90.24 | 316.6298 | 0
1984 | 883.85 | 508.505 | 23.6 | 82.793 | 82.793 | 0 | 0 | 8.9371 | 8.9371 | 0 | 0 | 0 | 73.597 | 809.9941 | 0 | 0.05921 | 3.5993 | 0 | 0 | 0 | 82.793 | off_peak | 801.057 | 0 | 100 | 9.37 | 0 | 90.63 | 297.999 | 0
1985 | 920.72 | 362.524 | 23.2 | 59.1095 | 59.1095 | 0 | 0 | 0.57721 | 0.57721 | 0 | 0 | 0 | 74.137 | 862.1878 | 0 | 0.05921 | 3.8723 | 0 | 0 | 0 | 59.1095 | off_peak | 861.6105 | 0 | 100 | 6.42 | 0 | 93.58 | 228.8881 | 0
1986 | 927.1 | 167.027 | 22.4 | 27.3116 | 27.2744 | 0 | 0.037279 | 0.037279 | 0 | 0 | 0 | 0 | 74.1718 | 899.8256 | 0 | 0.05921 | 4.2077 | 0 | 0 | 0.034872 | 27.2744 | off_peak | 899.8256 | 100 | 0 | 2.94 | 0 | 97.06 | 114.761 | 0
1987 | 857.78 | 9.9994 | 21.8 | 1.6386 | 1.6386 | 0 | 0 | 0 | 0 | 56.1394 | 56.1394 | 0 | 14.1563 | 800.002 | 0 | 0.088511 | 4.6016 | 0 | 0 | 0.034872 | 1.6386 | on_peak | 800.002 |  |  | 0.19 | 6.54 | 93.26 | 7.54 | 0
1988 | 873.04 | 0 | 20.4 | 0 | 0 | 0 | 0 | 0 | 0 | 6.271 | 6.271 | 0 | 7.4523 | 866.769 | 0 | 0.088511 | 5.0055 | 0 | 0 | 0.034872 | 0 | on_peak | 866.769 |  |  | 0 | 0.72 | 99.28 | 0 | 0
1989 | 817.61 | 0 | 19.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4523 | 817.61 | 0 | 0.088511 | 5.1505 | 0 | 0 | 0.034872 | 0 | on_peak | 817.61 |  |  | 0 | 0 | 100 | 0 | 0
1990 | 766.1 | 0 | 18.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0.032619 | 0.032619 | 0 | 7.4174 | 766.0674 | 0 | 0.088511 | 5.4918 | 0.032619 | 0 | 0 | 0.032619 | on_peak | 766.0674 |  |  | 0 | 0 | 100 | 0.17914 | 0
1991 | 860.31 | 0 | 17.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 860.31 | 0 | 0.05921 | 5.8736 | 0 | 0 | 0 | 0 | off_peak | 860.31 |  |  | 0 | 0 | 100 | 0 | 0
1992 | 777.98 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 777.98 | 0 | 0.05921 | 6.1382 | 0 | 0 | 0 | 0 | off_peak | 777.98 |  |  | 0 | 0 | 100 | 0 | 0
1993 | 729.53 | 0 | 16.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 729.53 | 0 | 0.05921 | 6.1441 | 0 | 0 | 0 | 0 | off_peak | 729.53 |  |  | 0 | 0 | 100 | 0 | 0
1994 | 617.28 | 0 | 15.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 617.28 | 0 | 0.05921 | 6.019 | 0 | 0 | 0 | 0 | off_peak | 617.28 |  |  | 0 | 0 | 100 | 0 | 0
1995 | 522.6 | 0 | 15.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 522.6 | 0 | 0.05921 | 5.5528 | 0 | 0 | 0 | 0 | off_peak | 522.6 |  |  | 0 | 0 | 100 | 0 | 0
1996 | 559.51 | 0 | 15.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 559.51 | 0 | 0.05921 | 5.0711 | 0 | 0 | 0 | 0 | off_peak | 559.51 |  |  | 0 | 0 | 100 | 0 | 0
1997 | 581.01 | 0 | 15.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 581.01 | 0 | 0.05921 | 4.4785 | 0 | 0 | 0 | 0 | off_peak | 581.01 |  |  | 0 | 0 | 100 | 0 | 0
1998 | 732.55 | 0 | 15.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 732.55 | 0 | 0.05921 | 3.986 | 0 | 0 | 0 | 0 | off_peak | 732.55 |  |  | 0 | 0 | 100 | 0 | 0
1999 | 797.18 | 17.9608 | 15.6 | 3.0081 | 3.0081 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 794.1719 | 0 | 0.05921 | 3.5568 | 0 | 0 | 0 | 3.0081 | off_peak | 794.1719 |  |  | 0.38 | 0 | 99.62 | 10.6993 | 0
2000 | 827.98 | 199.371 | 16.3 | 33.3097 | 33.3097 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 18.9814 | 807.0327 | 0 | 0.05921 | 3.2876 | 0 | 0 | 0 | 33.3097 | off_peak | 794.6703 | 0 | 100 | 4.02 | 0 | 95.98 | 109.5105 | 0
2001 | 795.9 | 420.826 | 17.1 | 70.1127 | 70.1127 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 30.5453 | 738.1497 | 0 | 0.05921 | 3.1145 | 0 | 0 | 0 | 70.1127 | off_peak | 725.7873 | 0 | 100 | 8.81 | 0 | 91.19 | 218.3625 | 0
2002 | 824.65 | 618.963 | 18 | 102.7989 | 102.7989 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 42.1093 | 734.2135 | 0 | 0.05921 | 3.0265 | 0 | 0 | 0 | 102.7989 | off_peak | 721.8511 | 0 | 100 | 12.47 | 0 | 87.53 | 311.1223 | 0
2003 | 808.91 | 771.737 | 18.8 | 127.8119 | 127.8119 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 42.1093 | 681.0981 | 0 | 0.05921 | 3.0337 | 0 | 0 | 0 | 127.8119 | off_peak | 681.0981 |  |  | 15.8 | 0 | 84.2 | 387.7439 | 0
2004 | 820.65 | 846.773 | 19.5 | 139.8933 | 139.8933 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 42.1093 | 680.7567 | 0 | 0.05921 | 3.1935 | 0 | 0 | 0 | 139.8933 | off_peak | 680.7567 |  |  | 17.05 | 0 | 82.95 | 446.7531 | 0
2005 | 798.08 | 899.675 | 20 | 148.3708 | 148.3708 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 42.1093 | 649.7092 | 0 | 0.05921 | 3.3507 | 0 | 0 | 0 | 148.3708 | off_peak | 649.7092 |  |  | 18.59 | 0 | 81.41 | 497.1421 | 0
2006 | 733.81 | 863.468 | 20.3 | 142.2486 | 142.2486 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 42.1093 | 591.5614 | 0 | 0.05921 | 3.8324 | 0 | 0 | 0 | 142.2486 | off_peak | 591.5614 |  |  | 19.38 | 0 | 80.62 | 545.1475 | 0
2007 | 708.21 | 757.887 | 20.5 | 124.7667 | 124.7667 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 42.1093 | 583.4433 | 0 | 0.05921 | 4.2641 | 0 | 0 | 0 | 124.7667 | off_peak | 583.4433 |  |  | 17.62 | 0 | 82.38 | 532.0123 | 0
2008 | 735.52 | 595.702 | 20.5 | 98.0671 | 98.0671 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 42.1093 | 637.4529 | 0 | 0.05921 | 4.5413 | 0 | 0 | 0 | 98.0671 | off_peak | 637.4529 |  |  | 13.33 | 0 | 86.67 | 445.3533 | 0
2009 | 697.4 | 391.311 | 20.2 | 64.4878 | 64.4878 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 42.1093 | 632.9122 | 0 | 0.05921 | 4.9286 | 0 | 0 | 0 | 64.4878 | off_peak | 632.9122 |  |  | 9.25 | 0 | 90.75 | 317.8353 | 0
2010 | 649.93 | 173.632 | 19.5 | 28.6853 | 28.6853 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 42.1093 | 621.2447 | 0 | 0.05921 | 5.1418 | 0 | 0 | 0 | 28.6853 | off_peak | 621.2447 |  |  | 4.41 | 0 | 95.59 | 147.4931 | 0
2011 | 587.47 | 10.9294 | 19 | 1.8088 | 1.8088 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 42.1093 | 585.6612 | 0 | 0.05921 | 5.5102 | 0 | 0 | 0 | 1.8088 | off_peak | 585.6612 |  |  | 0.31 | 0 | 99.69 | 9.9669 | 0
2012 | 561.04 | 0 | 18.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 42.1093 | 561.04 | 0 | 0.05921 | 5.9165 | 0 | 0 | 0 | 0 | off_peak | 561.04 |  |  | 0 | 0 | 100 | 0 | 0
2013 | 577.66 | 0 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 42.1093 | 577.66 | 0 | 0.05921 | 6.1329 | 0 | 0 | 0 | 0 | off_peak | 577.66 |  |  | 0 | 0 | 100 | 0 | 0
2014 | 556.45 | 0 | 17.5 | 0 | 0 | 0 | 0 | 8.7006 | 8.7006 | 0 | 0 | 0 | 50.2479 | 565.1506 | 0 | 0.05921 | 6.316 | 0 | 0 | 0 | 0 | off_peak | 556.45 | 0 | 100 | 0 | 0 | 100 | 0 | 0
2015 | 589.71 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50.2479 | 589.71 | 0 | 0.05921 | 6.6298 | 0 | 0 | 0 | 0 | off_peak | 589.71 |  |  | 0 | 0 | 100 | 0 | 0
2016 | 572.82 | 0 | 16.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50.2479 | 572.82 | 0 | 0.05921 | 6.8222 | 0 | 0 | 0 | 0 | off_peak | 572.82 |  |  | 0 | 0 | 100 | 0 | 0
2017 | 591.26 | 0 | 15.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50.2479 | 591.26 | 0 | 0.05921 | 6.6905 | 0 | 0 | 0 | 0 | off_peak | 591.26 |  |  | 0 | 0 | 100 | 0 | 0
2018 | 563.2 | 0 | 15.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50.2479 | 563.2 | 0 | 0.05921 | 6.5014 | 0 | 0 | 0 | 0 | off_peak | 563.2 |  |  | 0 | 0 | 100 | 0 | 0
2019 | 587.06 | 0 | 14.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50.2479 | 587.06 | 0 | 0.05921 | 6.0415 | 0 | 0 | 0 | 0 | off_peak | 587.06 |  |  | 0 | 0 | 100 | 0 | 0
2020 | 585.53 | 0 | 14.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50.2479 | 585.53 | 0 | 0.05921 | 5.5276 | 0 | 0 | 0 | 0 | off_peak | 585.53 |  |  | 0 | 0 | 100 | 0 | 0
2021 | 611.12 | 0 | 14.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50.2479 | 611.12 | 0 | 0.05921 | 4.9023 | 0 | 0 | 0 | 0 | off_peak | 611.12 |  |  | 0 | 0 | 100 | 0 | 0
2022 | 691.02 | 0 | 14.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50.2479 | 691.02 | 0 | 0.05921 | 4.3332 | 0 | 0 | 0 | 0 | off_peak | 691.02 |  |  | 0 | 0 | 100 | 0 | 0
2023 | 698.77 | 18.7018 | 14.9 | 3.1399 | 3.1399 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50.2479 | 695.6301 | 0 | 0.05921 | 4.0177 | 0 | 0 | 0 | 3.1399 | off_peak | 695.6301 |  |  | 0.45 | 0 | 99.55 | 12.6149 | 0
2024 | 736.1 | 204.89 | 16 | 34.2676 | 34.2676 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50.2479 | 701.8324 | 0 | 0.05921 | 3.6562 | 0 | 0 | 0 | 34.2676 | off_peak | 701.8324 |  |  | 4.66 | 0 | 95.34 | 125.2889 | 0
2025 | 777.12 | 427.621 | 17.2 | 71.2198 | 71.2198 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50.2479 | 705.9002 | 0 | 0.05921 | 3.4228 | 0 | 0 | 0 | 71.2198 | off_peak | 705.9002 |  |  | 9.16 | 0 | 90.84 | 243.7725 | 0
2026 | 759.01 | 629.632 | 18.3 | 104.4606 | 104.4606 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50.2479 | 654.5494 | 0 | 0.05921 | 3.2766 | 0 | 0 | 0 | 104.4606 | off_peak | 654.5494 |  |  | 13.76 | 0 | 86.24 | 342.2723 | 0
2027 | 731.1 | 787.858 | 19.2 | 130.298 | 130.298 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50.2479 | 600.802 | 0 | 0.05921 | 3.256 | 0 | 0 | 0 | 130.298 | off_peak | 600.802 |  |  | 17.82 | 0 | 82.18 | 424.2514 | 0
2028 | 764.03 | 888.45 | 19.9 | 146.5714 | 146.5714 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 61.8119 | 629.8209 | 0 | 0.05921 | 3.3552 | 0 | 0 | 0 | 146.5714 | off_peak | 617.4586 | 0 | 100 | 19.18 | 0 | 80.82 | 491.7709 | 0
2029 | 733.44 | 876.402 | 20.5 | 144.2772 | 144.2772 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 61.8119 | 589.1628 | 0 | 0.05921 | 3.5424 | 0 | 0 | 0 | 144.2772 | off_peak | 589.1628 |  |  | 19.67 | 0 | 80.33 | 511.0907 | 0
2030 | 699.84 | 880.795 | 20.8 | 144.8462 | 144.8462 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 61.8119 | 554.9938 | 0 | 0.05921 | 3.9273 | 0 | 0 | 0 | 144.8462 | off_peak | 554.9938 |  |  | 20.7 | 0 | 79.3 | 568.8548 | 0
2031 | 715.04 | 766.456 | 21 | 125.9539 | 125.9539 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 61.8119 | 589.0861 | 0 | 0.05921 | 4.2558 | 0 | 0 | 0 | 125.9539 | off_peak | 589.0861 |  |  | 17.61 | 0 | 82.39 | 536.0366 | 0
2032 | 715.64 | 612.238 | 21 | 100.6108 | 100.6108 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 73.3758 | 627.3916 | 0 | 0.05921 | 4.5717 | 0 | 0 | 0 | 100.6108 | off_peak | 615.0292 | 0 | 100 | 14.06 | 0 | 85.94 | 459.9618 | 0
2033 | 694.23 | 405.984 | 20.7 | 66.7875 | 66.7875 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 73.3758 | 627.4425 | 0 | 0.05921 | 4.9175 | 0 | 0 | 0 | 66.7875 | off_peak | 627.4425 |  |  | 9.62 | 0 | 90.38 | 328.4272 | 0
2034 | 620.39 | 183.709 | 19.9 | 30.3073 | 30.3073 | 0 | 0 | 0.79843 | 0.79843 | 0 | 0 | 0 | 74.1227 | 590.8812 | 0 | 0.05921 | 5.544 | 0 | 0 | 0 | 30.3073 | off_peak | 590.0827 | 0 | 100 | 4.89 | 0 | 95.11 | 168.0246 | 0
2035 | 576.26 | 11.3053 | 19.3 | 1.869 | 1.869 | 0 | 0 | 0.051567 | 0.051567 | 0 | 0 | 0 | 74.1709 | 574.4425 | 0 | 0.05921 | 6.0224 | 0 | 0 | 0 | 1.869 | off_peak | 574.391 | 0 | 100 | 0.32 | 0 | 99.68 | 11.2561 | 0
2036 | 581.76 | 0 | 18.7 | 0 | 0 | 0 | 0 | 0.0033305 | 0.0033305 | 0 | 0 | 0 | 74.174 | 581.7633 | 0 | 0.05921 | 6.3873 | 0 | 0 | 0 | 0 | off_peak | 581.76 | 0 | 100 | 0 | 0 | 100 | 0 | 0
2037 | 556.56 | 0 | 18.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.174 | 556.56 | 0 | 0.05921 | 6.5534 | 0 | 0 | 0 | 0 | off_peak | 556.56 |  |  | 0 | 0 | 100 | 0 | 0
2038 | 559.92 | 0 | 17.9 | 0 | 0 | 0 | 0 | 0.0002151 | 0.0002151 | 0 | 0 | 0 | 74.1742 | 559.9202 | 0 | 0.05921 | 6.7736 | 0 | 0 | 0 | 0 | off_peak | 559.92 | 0 | 100 | 0 | 0 | 100 | 0 | 0
2039 | 574.16 | 0 | 17.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1742 | 574.16 | 0 | 0.05921 | 7.091 | 0 | 0 | 0 | 0 | off_peak | 574.16 |  |  | 0 | 0 | 100 | 0 | 0
2040 | 578.2 | 0 | 17 | 0 | 0 | 0 | 0 | 1.4852e-05 | 1.4852e-05 | 0 | 0 | 0 | 74.1743 | 578.2 | 0 | 0.05921 | 7.2943 | 0 | 0 | 0 | 0 | off_peak | 578.2 | 0 | 100 | 0 | 0 | 100 | 0 | 0
2041 | 582.03 | 0 | 16.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1743 | 582.03 | 0 | 0.05921 | 7.224 | 0 | 0 | 0 | 0 | off_peak | 582.03 |  |  | 0 | 0 | 100 | 0 | 0
2042 | 583.26 | 0 | 16.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1743 | 583.26 | 0 | 0.05921 | 6.9581 | 0 | 0 | 0 | 0 | off_peak | 583.26 |  |  | 0 | 0 | 100 | 0 | 0
2043 | 586.09 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1743 | 586.09 | 0 | 0.05921 | 6.3454 | 0 | 0 | 0 | 0 | off_peak | 586.09 |  |  | 0 | 0 | 100 | 0 | 0
2044 | 568.94 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1743 | 568.94 | 0 | 0.05921 | 5.6247 | 0 | 0 | 0 | 0 | off_peak | 568.94 |  |  | 0 | 0 | 100 | 0 | 0
2045 | 576.7 | 0 | 16.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1743 | 576.7 | 0 | 0.05921 | 4.9215 | 0 | 0 | 0 | 0 | off_peak | 576.7 |  |  | 0 | 0 | 100 | 0 | 0
2046 | 685.97 | 0 | 16.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1743 | 685.97 | 0 | 0.05921 | 4.1922 | 0 | 0 | 0 | 0 | off_peak | 685.97 |  |  | 0 | 0 | 100 | 0 | 0
2047 | 770.85 | 22.1506 | 17.3 | 3.6879 | 3.6879 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1743 | 767.1621 | 0 | 0.088511 | 3.807 | 0 | 0 | 0 | 3.6879 | on_peak | 767.1621 |  |  | 0.48 | 0 | 99.52 | 14.0398 | 0
2048 | 848.51 | 203.376 | 18.7 | 33.6941 | 33.6941 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1743 | 814.8159 | 0 | 0.088511 | 3.5463 | 0 | 0 | 0 | 33.6941 | on_peak | 814.8159 |  |  | 3.97 | 0 | 96.03 | 119.4879 | 0
2049 | 880.15 | 425.947 | 19.8 | 70.2952 | 70.2952 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1743 | 809.8548 | 0 | 0.088511 | 3.3892 | 0 | 0 | 0 | 70.2952 | on_peak | 809.8548 |  |  | 7.99 | 0 | 92.01 | 238.2453 | 0
2050 | 854.76 | 626.28 | 20.7 | 103.0279 | 103.0279 | 0 | 0 | 0 | 0 | 62.4453 | 62.4453 | 0 | 7.4174 | 689.2868 | 0 | 0.088511 | 3.3431 | 0 | 0 | 0 | 103.0279 | on_peak | 689.2868 |  |  | 12.05 | 7.31 | 80.64 | 344.4368 | 0
2051 | 868.24 | 780.985 | 21.4 | 128.1593 | 128.1593 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 18.9814 | 752.4431 | 0 | 0.05921 | 3.5064 | 0 | 0 | 0 | 128.1593 | off_peak | 740.0807 | 0 | 100 | 14.76 | 0 | 85.24 | 449.3754 | 0
2052 | 928.66 | 880.847 | 21.8 | 144.3411 | 144.3411 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 30.5453 | 796.6813 | 0 | 0.05921 | 3.8903 | 0 | 0 | 0 | 144.3411 | off_peak | 784.3189 | 0 | 100 | 15.54 | 0 | 84.46 | 561.5258 | 0
2053 | 888.65 | 904.204 | 22.1 | 148.0103 | 148.0103 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 42.1093 | 753.0021 | 0 | 0.05921 | 4.135 | 0 | 0 | 0 | 148.0103 | off_peak | 740.6397 | 0 | 100 | 16.66 | 0 | 83.34 | 612.0199 | 0
2054 | 869.54 | 849.346 | 22.2 | 138.981 | 138.981 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 53.6732 | 742.9214 | 0 | 0.05921 | 4.2846 | 0 | 0 | 0 | 138.981 | off_peak | 730.559 | 0 | 100 | 15.98 | 0 | 84.02 | 595.4721 | 0
2055 | 925.4 | 752.721 | 22.2 | 123.17 | 123.17 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 65.2371 | 814.5924 | 0 | 0.05921 | 4.4294 | 0 | 0 | 0 | 123.17 | off_peak | 802.23 | 0 | 100 | 13.31 | 0 | 86.69 | 545.5681 | 0
2056 | 940.74 | 595.242 | 22 | 97.4706 | 97.4706 | 0 | 0 | 8.9371 | 8.9371 | 0 | 0 | 0 | 73.597 | 852.2065 | 0 | 0.05921 | 4.7026 | 0 | 0 | 0 | 97.4706 | off_peak | 843.2694 | 0 | 100 | 10.36 | 0 | 89.64 | 458.3641 | 0
2057 | 922.51 | 386.211 | 21.6 | 63.332 | 63.332 | 0 | 0 | 0.57721 | 0.57721 | 0 | 0 | 0 | 74.137 | 859.7552 | 0 | 0.05921 | 5.0739 | 0 | 0 | 0 | 63.332 | off_peak | 859.178 | 0 | 100 | 6.87 | 0 | 93.13 | 321.3383 | 0
2058 | 947.69 | 170.911 | 20.9 | 28.0963 | 28.0963 | 0 | 0 | 0.037279 | 0.037279 | 0 | 0 | 0 | 74.1718 | 919.631 | 0 | 0.05921 | 5.4229 | 0 | 0 | 0 | 28.0963 | off_peak | 919.5937 | 0 | 100 | 2.96 | 0 | 97.04 | 152.3622 | 0
2059 | 873.63 | 7.7112 | 20.4 | 1.2699 | 1.2699 | 0 | 0 | 0 | 0 | 5.5911 | 5.5911 | 0 | 68.1947 | 866.769 | 0 | 0.088511 | 5.8215 | 0 | 0 | 0 | 1.2699 | on_peak | 866.769 |  |  | 0.15 | 0.64 | 99.21 | 7.3927 | 0
2060 | 903.3 | 0 | 19.9 | 0 | 0 | 0 | 0 | 0 | 0 | 36.531 | 36.531 | 0 | 29.1415 | 866.769 | 0 | 0.088511 | 6.1267 | 0 | 0 | 0 | 0 | on_peak | 866.769 |  |  | 0 | 4.04 | 95.96 | 0 | 0
2061 | 887.09 | 0 | 19.8 | 0 | 0 | 0 | 0 | 0 | 0 | 20.321 | 20.321 | 0 | 7.4174 | 866.769 | 0 | 0.088511 | 6.3616 | 0 | 0 | 0 | 0 | on_peak | 866.769 |  |  | 0 | 2.29 | 97.71 | 0 | 0
2062 | 832.68 | 0 | 19.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 832.68 | 0 | 0.088511 | 6.8458 | 0 | 0 | 0 | 0 | on_peak | 832.68 |  |  | 0 | 0 | 100 | 0 | 0
2063 | 861.87 | 0 | 19.4 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 18.9814 | 874.2324 | 0 | 0.05921 | 7.1267 | 0 | 0 | 0 | 0 | off_peak | 861.87 | 0 | 100 | 0 | 0 | 100 | 0 | 0
2064 | 860.37 | 0 | 19.2 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 30.5453 | 872.7324 | 0 | 0.05921 | 7.265 | 0 | 0 | 0 | 0 | off_peak | 860.37 | 0 | 100 | 0 | 0 | 100 | 0 | 0
2065 | 822.52 | 0 | 19 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 42.1093 | 834.8824 | 0 | 0.05921 | 7.283 | 0 | 0 | 0 | 0 | off_peak | 822.52 | 0 | 100 | 0 | 0 | 100 | 0 | 0
2066 | 749.1 | 0 | 18.9 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 53.6732 | 761.4624 | 0 | 0.05921 | 7.1893 | 0 | 0 | 0 | 0 | off_peak | 749.1 | 0 | 100 | 0 | 0 | 100 | 0 | 0
2067 | 714.39 | 0 | 18.8 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 65.2371 | 726.7524 | 0 | 0.05921 | 6.497 | 0 | 0 | 0 | 0 | off_peak | 714.39 | 0 | 100 | 0 | 0 | 100 | 0 | 0
2068 | 684.08 | 0 | 18.7 | 0 | 0 | 0 | 0 | 8.9371 | 8.9371 | 0 | 0 | 0 | 73.597 | 693.0171 | 0 | 0.05921 | 5.8301 | 0 | 0 | 0 | 0 | off_peak | 684.08 | 0 | 100 | 0 | 0 | 100 | 0 | 0
2069 | 694.28 | 0 | 18.7 | 0 | 0 | 0 | 0 | 0.57721 | 0.57721 | 0 | 0 | 0 | 74.137 | 694.8572 | 0 | 0.05921 | 4.9676 | 0 | 0 | 0 | 0 | off_peak | 694.28 | 0 | 100 | 0 | 0 | 100 | 0 | 0
2070 | 781.65 | 0 | 18.9 | 0 | 0 | 0 | 0 | 0.037279 | 0.037279 | 0 | 0 | 0 | 74.1718 | 781.6873 | 0 | 0.05921 | 4.3472 | 0 | 0 | 0 | 0 | off_peak | 781.65 | 0 | 100 | 0 | 0 | 100 | 0 | 0
2071 | 809.79 | 23.2259 | 19.8 | 3.833 | 3.833 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1718 | 805.957 | 0 | 0.088511 | 3.9567 | 0 | 0 | 0 | 3.833 | on_peak | 805.957 |  |  | 0.47 | 0 | 99.53 | 15.1662 | 0
2072 | 859.75 | 203.649 | 21 | 33.4662 | 33.4662 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1718 | 826.2838 | 0 | 0.088511 | 3.6673 | 0 | 0 | 0 | 33.4662 | on_peak | 826.2838 |  |  | 3.89 | 0 | 96.11 | 122.729 | 0
2073 | 882.09 | 385.164 | 21.7 | 63.1378 | 63.1378 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1718 | 818.9522 | 0 | 0.088511 | 3.4951 | 0 | 0 | 0 | 63.1378 | on_peak | 818.9522 |  |  | 7.16 | 0 | 92.84 | 220.6745 | 0
2074 | 932.97 | 605.179 | 22.3 | 98.9919 | 98.9919 | 0 | 0 | 0 | 0 | 62.443 | 62.443 | 0 | 7.4174 | 771.535 | 0 | 0.088511 | 3.479 | 0 | 0 | 0 | 98.9919 | on_peak | 771.535 |  |  | 10.61 | 6.69 | 82.7 | 344.3961 | 0
2075 | 887.7 | 538.188 | 22.6 | 87.9397 | 87.9397 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 18.9814 | 812.1226 | 0 | 0.05921 | 3.7029 | 0 | 0 | 0 | 87.9397 | off_peak | 799.7603 | 0 | 100 | 9.91 | 0 | 90.09 | 325.6308 | 0
2076 | 899.63 | 783.783 | 22.8 | 127.9785 | 127.9785 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 30.5453 | 784.0139 | 0 | 0.05921 | 4.228 | 0 | 0 | 0 | 127.9785 | off_peak | 771.6515 | 0 | 100 | 14.23 | 0 | 85.77 | 541.0953 | 0
2077 | 894.69 | 686.713 | 22.9 | 112.0885 | 112.0885 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 42.1093 | 794.9638 | 0 | 0.05921 | 4.4159 | 0 | 0 | 0 | 112.0885 | off_peak | 782.6015 | 0 | 100 | 12.53 | 0 | 87.47 | 494.9736 | 0
2078 | 896.02 | 524.452 | 22.8 | 85.6341 | 85.6341 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 53.6732 | 822.7483 | 0 | 0.05921 | 4.5732 | 0 | 0 | 0 | 85.6341 | off_peak | 810.3859 | 0 | 100 | 9.56 | 0 | 90.44 | 391.6234 | 0
2079 | 922.53 | 753.532 | 22.6 | 123.1269 | 123.1269 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 65.2371 | 811.7655 | 0 | 0.05921 | 4.7123 | 0 | 0 | 0 | 123.1269 | off_peak | 799.4031 | 0 | 100 | 13.35 | 0 | 86.65 | 580.2126 | 0
2080 | 921.14 | 590.521 | 22.3 | 96.5943 | 96.5943 | 0 | 0 | 8.9371 | 8.9371 | 0 | 0 | 0 | 73.597 | 833.4829 | 0 | 0.05921 | 4.8428 | 0 | 0 | 0 | 96.5943 | off_peak | 824.5457 | 0 | 100 | 10.49 | 0 | 89.51 | 467.785 | 0
2081 | 893.38 | 118.222 | 21.9 | 19.3657 | 19.3657 | 0 | 0 | 0.57721 | 0.57721 | 0 | 0 | 0 | 74.137 | 874.5915 | 0 | 0.05921 | 5.1952 | 0 | 0 | 0 | 19.3657 | off_peak | 874.0143 | 0 | 100 | 2.17 | 0 | 97.83 | 100.6086 | 0
2082 | 912.61 | 26.6 | 21.4 | 4.365 | 4.365 | 0 | 0 | 0.037279 | 0.037279 | 0 | 0 | 0 | 74.1718 | 908.2822 | 0 | 0.05921 | 5.6494 | 0 | 0 | 0 | 4.365 | off_peak | 908.245 | 0 | 100 | 0.48 | 0 | 99.52 | 24.6601 | 0
2083 | 868.33 | 3.8 | 21 | 0.62446 | 0.62446 | 0 | 0 | 0 | 0 | 0.93652 | 0.93652 | 0 | 73.1707 | 866.769 | 0 | 0.088511 | 6.1688 | 0 | 0 | 0 | 0.62446 | on_peak | 866.769 |  |  | 0.07 | 0.11 | 99.82 | 3.8522 | 0
2084 | 871.68 | 0 | 20.6 | 0 | 0 | 0 | 0 | 0 | 0 | 61.5065 | 61.5065 | 0 | 7.4174 | 810.1735 | 0 | 0.088511 | 6.6449 | 0 | 0 | 0 | 0 | on_peak | 810.1735 |  |  | 0 | 7.06 | 92.94 | 0 | 0
2085 | 837.47 | 0 | 20.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 837.47 | 0 | 0.088511 | 6.9302 | 0 | 0 | 0 | 0 | on_peak | 837.47 |  |  | 0 | 0 | 100 | 0 | 0
2086 | 800.93 | 0 | 20.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 800.93 | 0 | 0.088511 | 7.3163 | 0 | 0 | 0 | 0 | on_peak | 800.93 |  |  | 0 | 0 | 100 | 0 | 0
2087 | 848.64 | 0 | 20.3 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 18.9814 | 861.0024 | 0 | 0.05921 | 7.3219 | 0 | 0 | 0 | 0 | off_peak | 848.64 | 0 | 100 | 0 | 0 | 100 | 0 | 0
2088 | 819.96 | 0 | 20.2 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 30.5453 | 832.3224 | 0 | 0.05921 | 7.348 | 0 | 0 | 0 | 0 | off_peak | 819.96 | 0 | 100 | 0 | 0 | 100 | 0 | 0
2089 | 768.22 | 0 | 20.2 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 42.1093 | 780.5824 | 0 | 0.05921 | 7.1448 | 0 | 0 | 0 | 0 | off_peak | 768.22 | 0 | 100 | 0 | 0 | 100 | 0 | 0
2090 | 742.66 | 0 | 20.2 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 53.6732 | 755.0224 | 0 | 0.05921 | 6.9614 | 0 | 0 | 0 | 0 | off_peak | 742.66 | 0 | 100 | 0 | 0 | 100 | 0 | 0
2091 | 638.62 | 0 | 20.3 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 65.2371 | 650.9824 | 0 | 0.05921 | 6.2815 | 0 | 0 | 0 | 0 | off_peak | 638.62 | 0 | 100 | 0 | 0 | 100 | 0 | 0
2092 | 628.86 | 0 | 20.4 | 0 | 0 | 0 | 0 | 8.9371 | 8.9371 | 0 | 0 | 0 | 73.597 | 637.7971 | 0 | 0.05921 | 5.524 | 0 | 0 | 0 | 0 | off_peak | 628.86 | 0 | 100 | 0 | 0 | 100 | 0 | 0
2093 | 649.54 | 0 | 20.5 | 0 | 0 | 0 | 0 | 0.57721 | 0.57721 | 0 | 0 | 0 | 74.137 | 650.1172 | 0 | 0.05921 | 4.6945 | 0 | 0 | 0 | 0 | off_peak | 649.54 | 0 | 100 | 0 | 0 | 100 | 0 | 0
2094 | 715.78 | 0 | 20.7 | 0 | 0 | 0 | 0 | 0.037279 | 0.037279 | 0 | 0 | 0 | 74.1718 | 715.8173 | 0 | 0.05921 | 4.1428 | 0 | 0 | 0 | 0 | off_peak | 715.78 | 0 | 100 | 0 | 0 | 100 | 0 | 0
2095 | 791.82 | 21.3147 | 21.3 | 3.499 | 3.499 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1718 | 788.321 | 0 | 0.088511 | 3.7548 | 0 | 0 | 0 | 3.499 | on_peak | 788.321 |  |  | 0.44 | 0 | 99.56 | 13.138 | 0
2096 | 804.01 | 206.256 | 22.2 | 33.7503 | 33.7503 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1718 | 770.2597 | 0 | 0.088511 | 3.4641 | 0 | 0 | 0 | 33.7503 | on_peak | 770.2597 |  |  | 4.2 | 0 | 95.8 | 116.9133 | 0
2097 | 777.63 | 424.897 | 22.9 | 69.3537 | 69.3537 | 0 | 0 | 0 | 0 | 62.443 | 62.443 | 0 | 7.4174 | 645.8333 | 0 | 0.088511 | 3.2933 | 0 | 0 | 0 | 69.3537 | on_peak | 645.8333 |  |  | 8.92 | 8.03 | 83.05 | 228.4037 | 0
2098 | 856.14 | 620.466 | 23.5 | 101.0583 | 101.0583 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 755.0817 | 0 | 0.088511 | 3.2251 | 0 | 0 | 0 | 101.0583 | on_peak | 755.0817 |  |  | 11.8 | 0 | 88.2 | 325.9232 | 0
2099 | 813.05 | 770.764 | 23.9 | 125.3582 | 125.3582 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 18.9814 | 700.0541 | 0 | 0.05921 | 3.3823 | 0 | 0 | 0 | 125.3582 | off_peak | 687.6918 | 0 | 100 | 15.42 | 0 | 84.58 | 423.9945 | 0
2100 | 864.28 | 764.596 | 24.2 | 124.2213 | 124.2213 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 30.5453 | 752.4211 | 0 | 0.05921 | 3.8804 | 0 | 0 | 0 | 124.2213 | off_peak | 740.0587 | 0 | 100 | 14.37 | 0 | 85.63 | 482.026 | 0
2101 | 863.44 | 684.446 | 24.4 | 111.1198 | 111.1198 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 42.1093 | 764.6826 | 0 | 0.05921 | 4.1323 | 0 | 0 | 0 | 111.1198 | off_peak | 752.3202 | 0 | 100 | 12.87 | 0 | 87.13 | 459.177 | 0
2102 | 868.64 | 203.206 | 24.4 | 32.9905 | 32.9905 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 53.6732 | 848.0119 | 0 | 0.05921 | 4.2214 | 0 | 0 | 0 | 32.9905 | off_peak | 835.6495 | 0 | 100 | 3.8 | 0 | 96.2 | 139.2651 | 0
2103 | 952.05 | 254.589 | 24.3 | 41.3474 | 41.3474 | 0 | 0 | 8.9284 | 8.9284 | 0 | 0 | 0 | 62.0249 | 919.631 | 0 | 0.05921 | 4.0277 | 0 | 0 | 0 | 41.3474 | off_peak | 910.7026 | 0 | 100 | 4.34 | 0 | 95.66 | 166.5331 | 0
2104 | 874.26 | 242.39 | 24.1 | 39.3944 | 39.3944 | 0 | 0 | 12.1493 | 12.1493 | 0 | 0 | 0 | 73.3896 | 847.0149 | 0 | 0.05921 | 4.1841 | 0 | 0 | 0 | 39.3944 | off_peak | 834.8656 | 0 | 100 | 4.51 | 0 | 95.49 | 164.8291 | 0
2105 | 882.98 | 289.05 | 23.8 | 47.0284 | 47.0284 | 0 | 0 | 0.78467 | 0.78467 | 0 | 0 | 0 | 74.1236 | 836.7363 | 0 | 0.05921 | 4.6761 | 0 | 0 | 0 | 47.0284 | off_peak | 835.9516 | 0 | 100 | 5.33 | 0 | 94.67 | 219.9091 | 0
2106 | 899.69 | 56.0128 | 23.1 | 9.1361 | 9.1361 | 0 | 0 | 0.050679 | 0.050679 | 0 | 0 | 0 | 74.171 | 890.6045 | 0 | 0.05921 | 4.8887 | 0 | 0 | 0 | 9.1361 | off_peak | 890.5539 | 0 | 100 | 1.02 | 0 | 98.98 | 44.6639 | 0
2107 | 807.95 | 5.7 | 22.6 | 0.93138 | 0.93138 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.171 | 807.0186 | 0 | 0.088511 | 5.3531 | 0 | 0 | 0 | 0.93138 | on_peak | 807.0186 |  |  | 0.12 | 0 | 99.88 | 4.9857 | 0
2108 | 828.31 | 0 | 22.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.171 | 828.31 | 0 | 0.088511 | 5.5508 | 0 | 0 | 0 | 0 | on_peak | 828.31 |  |  | 0 | 0 | 100 | 0 | 0
2109 | 827.8 | 0 | 21.9 | 0 | 0 | 0 | 0 | 0 | 0 | 62.4422 | 62.4422 | 0 | 7.4174 | 765.3578 | 0 | 0.088511 | 5.7008 | 0 | 0 | 0 | 0 | on_peak | 765.3578 |  |  | 0 | 7.54 | 92.46 | 0 | 0
2110 | 800.79 | 0 | 21.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 800.79 | 0 | 0.088511 | 5.9403 | 0 | 0 | 0 | 0 | on_peak | 800.79 |  |  | 0 | 0 | 100 | 0 | 0
2111 | 846.35 | 0 | 21.8 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 18.9814 | 858.7124 | 0 | 0.05921 | 6.1444 | 0 | 0 | 0 | 0 | off_peak | 846.35 | 0 | 100 | 0 | 0 | 100 | 0 | 0
2112 | 833.91 | 0 | 21.6 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 30.5453 | 846.2724 | 0 | 0.05921 | 6.3203 | 0 | 0 | 0 | 0 | off_peak | 833.91 | 0 | 100 | 0 | 0 | 100 | 0 | 0
2113 | 809.01 | 0 | 21.4 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 42.1093 | 821.3724 | 0 | 0.05921 | 6.3095 | 0 | 0 | 0 | 0 | off_peak | 809.01 | 0 | 100 | 0 | 0 | 100 | 0 | 0
2114 | 741.51 | 0 | 21.3 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 53.6732 | 753.8724 | 0 | 0.05921 | 6.2094 | 0 | 0 | 0 | 0 | off_peak | 741.51 | 0 | 100 | 0 | 0 | 100 | 0 | 0
2115 | 699.89 | 0 | 21.3 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 65.2371 | 712.2524 | 0 | 0.05921 | 5.6896 | 0 | 0 | 0 | 0 | off_peak | 699.89 | 0 | 100 | 0 | 0 | 100 | 0 | 0
2116 | 681.46 | 0 | 21.3 | 0 | 0 | 0 | 0 | 8.9371 | 8.9371 | 0 | 0 | 0 | 73.597 | 690.3971 | 0 | 0.05921 | 5.0896 | 0 | 0 | 0 | 0 | off_peak | 681.46 | 0 | 100 | 0 | 0 | 100 | 0 | 0
2117 | 680.56 | 0 | 21.2 | 0 | 0 | 0 | 0 | 0.57721 | 0.57721 | 0 | 0 | 0 | 74.137 | 681.1372 | 0 | 0.05921 | 4.3468 | 0 | 0 | 0 | 0 | off_peak | 680.56 | 0 | 100 | 0 | 0 | 100 | 0 | 0
2118 | 778.9 | 0 | 21.3 | 0 | 0 | 0 | 0 | 0.037279 | 0.037279 | 0 | 0 | 0 | 74.1718 | 778.9373 | 0 | 0.05921 | 3.777 | 0 | 0 | 0 | 0 | off_peak | 778.9 | 0 | 100 | 0 | 0 | 100 | 0 | 0
2119 | 810.52 | 22.2344 | 22 | 3.6409 | 3.6409 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1718 | 806.8791 | 0 | 0.088511 | 3.4524 | 0 | 0 | 0 | 3.6409 | on_peak | 806.8791 |  |  | 0.45 | 0 | 99.55 | 12.5699 | 0
2120 | 811.49 | 203.314 | 22.9 | 33.1859 | 33.1859 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1718 | 778.3041 | 0 | 0.088511 | 3.1889 | 0 | 0 | 0 | 33.1859 | on_peak | 778.3041 |  |  | 4.09 | 0 | 95.91 | 105.8256 | 0
2121 | 830.56 | 349.362 | 23.4 | 56.9226 | 56.9226 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1718 | 773.6374 | 0 | 0.088511 | 3.035 | 0 | 0 | 0 | 56.9226 | on_peak | 773.6374 |  |  | 6.85 | 0 | 93.15 | 172.7602 | 0
2122 | 909.88 | 145.403 | 23.9 | 23.6486 | 23.6486 | 0 | 0 | 0 | 0 | 62.443 | 62.443 | 0 | 7.4174 | 823.7884 | 0 | 0.088511 | 3.0195 | 0 | 0 | 0 | 23.6486 | on_peak | 823.7884 |  |  | 2.6 | 6.86 | 90.54 | 71.4077 | 0
2123 | 841.21 | 211.323 | 24.2 | 34.3329 | 34.3329 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 18.9814 | 819.2395 | 0 | 0.05921 | 3.2316 | 0 | 0 | 0 | 34.3329 | off_peak | 806.8771 | 0 | 100 | 4.08 | 0 | 95.92 | 110.9509 | 0
2124 | 861.99 | 126.35 | 24.5 | 20.5055 | 20.5055 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 30.5453 | 853.8468 | 0 | 0.05921 | 3.7081 | 0 | 0 | 0 | 20.5055 | off_peak | 841.4845 | 0 | 100 | 2.38 | 0 | 97.62 | 76.036 | 0
2125 | 820.13 | 288.297 | 24.6 | 46.7714 | 46.7714 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 42.1093 | 785.721 | 0 | 0.05921 | 4.0204 | 0 | 0 | 0 | 46.7714 | off_peak | 773.3586 | 0 | 100 | 5.7 | 0 | 94.3 | 188.0407 | 0
2126 | 874.94 | 257.786 | 24.5 | 41.8365 | 41.8365 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 53.6732 | 845.4659 | 0 | 0.05921 | 3.9046 | 0 | 0 | 0 | 41.8365 | off_peak | 833.1035 | 0 | 100 | 4.78 | 0 | 95.22 | 163.3536 | 0
2127 | 885.88 | 476.739 | 24.3 | 77.4263 | 77.4263 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 65.2371 | 820.816 | 0 | 0.05921 | 3.7363 | 0 | 0 | 0 | 77.4263 | off_peak | 808.4537 | 0 | 100 | 8.74 | 0 | 91.26 | 289.2873 | 0
2128 | 852.51 | 390.965 | 24 | 63.5643 | 63.5643 | 0 | 0 | 8.9371 | 8.9371 | 0 | 0 | 0 | 73.597 | 797.8828 | 0 | 0.05921 | 3.6867 | 0 | 0 | 0 | 63.5643 | off_peak | 788.9457 | 0 | 100 | 7.46 | 0 | 92.54 | 234.3422 | 0
2129 | 799.75 | 194.384 | 23.6 | 31.6489 | 31.6489 | 0 | 0 | 0.57721 | 0.57721 | 0 | 0 | 0 | 74.137 | 768.6783 | 0 | 0.05921 | 3.7991 | 0 | 0 | 0 | 31.6489 | off_peak | 768.1011 | 0 | 100 | 3.96 | 0 | 96.04 | 120.2366 | 0
2130 | 854.49 | 99.8733 | 23.2 | 16.2843 | 16.2843 | 0 | 0 | 0.037279 | 0.037279 | 0 | 0 | 0 | 74.1718 | 838.243 | 0 | 0.05921 | 3.9385 | 0 | 0 | 0 | 16.2843 | off_peak | 838.2057 | 0 | 100 | 1.91 | 0 | 98.09 | 64.1354 | 0
2131 | 798.65 | 12.1392 | 22.9 | 1.9814 | 1.9814 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1718 | 796.6686 | 0 | 0.088511 | 4.1306 | 0 | 0 | 0 | 1.9814 | on_peak | 796.6686 |  |  | 0.25 | 0 | 99.75 | 8.1845 | 0
2132 | 794.57 | 0 | 22.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1718 | 794.57 | 0 | 0.088511 | 4.3177 | 0 | 0 | 0 | 0 | on_peak | 794.57 |  |  | 0 | 0 | 100 | 0 | 0
2133 | 759.61 | 0 | 22.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1718 | 759.61 | 0 | 0.088511 | 4.562 | 0 | 0 | 0 | 0 | on_peak | 759.61 |  |  | 0 | 0 | 100 | 0 | 0
2134 | 804.71 | 0 | 22.5 | 0 | 0 | 0 | 0 | 0 | 0 | 62.443 | 62.443 | 0 | 7.4174 | 742.267 | 0 | 0.088511 | 4.915 | 0 | 0 | 0 | 0 | on_peak | 742.267 |  |  | 0 | 7.76 | 92.24 | 0 | 0
2135 | 825.43 | 0 | 22.5 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 18.9814 | 837.7924 | 0 | 0.05921 | 5.2899 | 0 | 0 | 0 | 0 | off_peak | 825.43 | 0 | 100 | 0 | 0 | 100 | 0 | 0
2136 | 807.78 | 0 | 22.5 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 30.5453 | 820.1424 | 0 | 0.05921 | 5.7247 | 0 | 0 | 0 | 0 | off_peak | 807.78 | 0 | 100 | 0 | 0 | 100 | 0 | 0
2137 | 736.91 | 0 | 22.4 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 42.1093 | 749.2724 | 0 | 0.05921 | 5.9804 | 0 | 0 | 0 | 0 | off_peak | 736.91 | 0 | 100 | 0 | 0 | 100 | 0 | 0
2138 | 713.23 | 0 | 22.3 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 53.6732 | 725.5924 | 0 | 0.05921 | 5.8898 | 0 | 0 | 0 | 0 | off_peak | 713.23 | 0 | 100 | 0 | 0 | 100 | 0 | 0
2139 | 617.49 | 0 | 22.2 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 65.2371 | 629.8524 | 0 | 0.05921 | 5.5153 | 0 | 0 | 0 | 0 | off_peak | 617.49 | 0 | 100 | 0 | 0 | 100 | 0 | 0
2140 | 601.16 | 0 | 22.1 | 0 | 0 | 0 | 0 | 8.9371 | 8.9371 | 0 | 0 | 0 | 73.597 | 610.0971 | 0 | 0.05921 | 5.0053 | 0 | 0 | 0 | 0 | off_peak | 601.16 | 0 | 100 | 0 | 0 | 100 | 0 | 0
2141 | 649.92 | 0 | 22 | 0 | 0 | 0 | 0 | 0.57721 | 0.57721 | 0 | 0 | 0 | 74.137 | 650.4972 | 0 | 0.05921 | 4.1675 | 0 | 0 | 0 | 0 | off_peak | 649.92 | 0 | 100 | 0 | 0 | 100 | 0 | 0
2142 | 687.11 | 0 | 22 | 0 | 0 | 0 | 0 | 0.037279 | 0.037279 | 0 | 0 | 0 | 74.1718 | 687.1473 | 0 | 0.05921 | 3.5861 | 0 | 0 | 0 | 0 | off_peak | 687.11 | 0 | 100 | 0 | 0 | 100 | 0 | 0
2143 | 781.5 | 25.4633 | 22.5 | 4.1622 | 4.1622 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1718 | 777.3378 | 0 | 0.088511 | 3.2343 | 0 | 0 | 0 | 4.1622 | on_peak | 777.3378 |  |  | 0.53 | 0 | 99.47 | 13.4618 | 0
2144 | 820.71 | 217.211 | 23.2 | 35.4162 | 35.4162 | 0 | 0 | 0 | 0 | 62.443 | 62.443 | 0 | 7.4174 | 722.8508 | 0 | 0.088511 | 2.9932 | 0 | 0 | 0 | 35.4162 | on_peak | 722.8508 |  |  | 4.32 | 7.61 | 88.08 | 106.0068 | 0
2145 | 903.67 | 438.856 | 23.7 | 71.4274 | 71.4274 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 832.2426 | 0 | 0.088511 | 2.8494 | 0 | 0 | 0 | 71.4274 | on_peak | 832.2426 |  |  | 7.9 | 0 | 92.1 | 203.527 | 0
2146 | 911.26 | 638.304 | 24.1 | 103.7403 | 103.7403 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 807.5197 | 0 | 0.088511 | 2.8293 | 0 | 0 | 0 | 103.7403 | on_peak | 807.5197 |  |  | 11.38 | 0 | 88.62 | 293.5152 | 0
2147 | 858.19 | 797.397 | 24.5 | 129.4108 | 129.4108 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 18.9814 | 741.1415 | 0 | 0.05921 | 3.0137 | 0 | 0 | 0 | 129.4108 | off_peak | 728.7792 | 0 | 100 | 15.08 | 0 | 84.92 | 390.0074 | 0
2148 | 925.18 | 864.442 | 24.7 | 140.1908 | 140.1908 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 30.5453 | 797.3515 | 0 | 0.05921 | 3.4852 | 0 | 0 | 0 | 140.1908 | off_peak | 784.9892 | 0 | 100 | 15.15 | 0 | 84.85 | 488.5893 | 0
2149 | 901.24 | 896.834 | 24.8 | 145.3917 | 145.3917 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 42.1093 | 768.2107 | 0 | 0.05921 | 3.8306 | 0 | 0 | 0 | 145.3917 | off_peak | 755.8483 | 0 | 100 | 16.13 | 0 | 83.87 | 556.9418 | 0
2150 | 838.78 | 866.675 | 24.8 | 140.5024 | 140.5024 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 53.6732 | 710.6399 | 0 | 0.05921 | 3.8556 | 0 | 0 | 0 | 140.5024 | off_peak | 698.2776 | 0 | 100 | 16.75 | 0 | 83.25 | 541.7213 | 0
2151 | 933.37 | 745.29 | 24.6 | 120.9108 | 120.9108 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 65.2371 | 824.8215 | 0 | 0.05921 | 3.7799 | 0 | 0 | 0 | 120.9108 | off_peak | 812.4592 | 0 | 100 | 12.95 | 0 | 87.05 | 457.0316 | 0
2152 | 793.18 | 610.367 | 24.4 | 99.093 | 99.093 | 0 | 0 | 8.9371 | 8.9371 | 0 | 0 | 0 | 73.597 | 703.0241 | 0 | 0.05921 | 3.8197 | 0 | 0 | 0 | 99.093 | off_peak | 694.087 | 0 | 100 | 12.49 | 0 | 87.51 | 378.505 | 0
2153 | 867.73 | 308.864 | 24 | 50.2161 | 50.2161 | 0 | 0 | 0.57721 | 0.57721 | 0 | 0 | 0 | 74.137 | 818.0911 | 0 | 0.05921 | 4.1346 | 0 | 0 | 0 | 50.2161 | off_peak | 817.5139 | 0 | 100 | 5.79 | 0 | 94.21 | 207.6255 | 0
2154 | 820.35 | 159.585 | 23.5 | 25.9924 | 25.9924 | 0 | 0 | 0.037279 | 0.037279 | 0 | 0 | 0 | 74.1718 | 794.3949 | 0 | 0.05921 | 4.4287 | 0 | 0 | 0 | 25.9924 | off_peak | 794.3576 | 0 | 100 | 3.17 | 0 | 96.83 | 115.1137 | 0
2155 | 799.11 | 14.4593 | 23.1 | 2.3584 | 2.3584 | 0 | 0 | 0 | 0 | 62.443 | 62.443 | 0 | 7.4174 | 734.3085 | 0 | 0.088511 | 4.7472 | 0 | 0 | 0 | 2.3584 | on_peak | 734.3085 |  |  | 0.3 | 7.81 | 91.89 | 11.1959 | 0
2156 | 793 | 0 | 25.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 793 | 0 | 0.088511 | 5.1394 | 0 | 0 | 0 | 0 | on_peak | 793 |  |  | 0 | 0 | 100 | 0 | 0
2157 | 795.78 | 0 | 25.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 795.78 | 0 | 0.088511 | 5.3764 | 0 | 0 | 0 | 0 | on_peak | 795.78 |  |  | 0 | 0 | 100 | 0 | 0
2158 | 768.27 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 768.27 | 0 | 0.088511 | 5.7423 | 0 | 0 | 0 | 0 | on_peak | 768.27 |  |  | 0 | 0 | 100 | 0 | 0
2159 | 782.26 | 0 | 24.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 782.26 | 0 | 0.05921 | 6.0616 | 0 | 0 | 0 | 0 | off_peak | 782.26 |  |  | 0 | 0 | 100 | 0 | 0
2160 | 803.89 | 0 | 24.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 803.89 | 0 | 0.05921 | 6.2023 | 0 | 0 | 0 | 0 | off_peak | 803.89 |  |  | 0 | 0 | 100 | 0 | 0
2161 | 734.4 | 0 | 24.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 734.4 | 0 | 0.05921 | 6.1568 | 0 | 0 | 0 | 0 | off_peak | 734.4 |  |  | 0 | 0 | 100 | 0 | 0
2162 | 684.73 | 0 | 24.4 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 18.9814 | 697.0924 | 0 | 0.05921 | 6.073 | 0 | 0 | 0 | 0 | off_peak | 684.73 | 0 | 100 | 0 | 0 | 100 | 0 | 0
2163 | 633.98 | 0 | 24.3 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 30.5453 | 646.3424 | 0 | 0.05921 | 5.6384 | 0 | 0 | 0 | 0 | off_peak | 633.98 | 0 | 100 | 0 | 0 | 100 | 0 | 0
2164 | 609.13 | 0 | 24 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 42.1093 | 621.4924 | 0 | 0.05921 | 5.1564 | 0 | 0 | 0 | 0 | off_peak | 609.13 | 0 | 100 | 0 | 0 | 100 | 0 | 0
2165 | 630.02 | 0 | 23.6 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 53.6732 | 642.3824 | 0 | 0.05921 | 4.4016 | 0 | 0 | 0 | 0 | off_peak | 630.02 | 0 | 100 | 0 | 0 | 100 | 0 | 0
2166 | 740.3 | 0 | 22.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 53.6732 | 740.3 | 0 | 0.05921 | 3.8009 | 0 | 0 | 0 | 0 | off_peak | 740.3 |  |  | 0 | 0 | 100 | 0 | 0
2167 | 768.3 | 27.3178 | 22.2 | 4.4701 | 4.4701 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 65.2371 | 776.1923 | 0 | 0.05921 | 3.4042 | 0 | 0 | 0 | 4.4701 | off_peak | 763.8299 | 0 | 100 | 0.58 | 0 | 99.42 | 15.2171 | 0
2168 | 806.07 | 212.012 | 22 | 34.7169 | 34.7169 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 65.2371 | 771.3531 | 0 | 0.05921 | 3.0778 | 0 | 0 | 0 | 34.7169 | off_peak | 771.3531 |  |  | 4.31 | 0 | 95.69 | 106.8505 | 0
2169 | 820.23 | 428.134 | 22.4 | 70.0069 | 70.0069 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 65.2371 | 750.2231 | 0 | 0.05921 | 2.8787 | 0 | 0 | 0 | 70.0069 | off_peak | 750.2231 |  |  | 8.54 | 0 | 91.46 | 201.5316 | 0
2170 | 815.29 | 623.839 | 23.2 | 101.7168 | 101.7168 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 65.2371 | 713.5732 | 0 | 0.05921 | 2.7879 | 0 | 0 | 0 | 101.7168 | off_peak | 713.5732 |  |  | 12.48 | 0 | 87.52 | 283.5798 | 0
2171 | 780.44 | 496.521 | 24 | 80.726 | 80.726 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 65.2371 | 699.714 | 0 | 0.05921 | 2.8612 | 0 | 0 | 0 | 80.726 | off_peak | 699.714 |  |  | 10.34 | 0 | 89.66 | 230.9744 | 0
2172 | 817.86 | 612.757 | 24.8 | 99.3381 | 99.3381 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 65.2371 | 718.5219 | 0 | 0.05921 | 3.026 | 0 | 0 | 0 | 99.3381 | off_peak | 718.5219 |  |  | 12.15 | 0 | 87.85 | 300.5953 | 0
2173 | 808.05 | 616.351 | 25.5 | 99.6691 | 99.6691 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 65.2371 | 708.3809 | 0 | 0.05921 | 3.2717 | 0 | 0 | 0 | 99.6691 | off_peak | 708.3809 |  |  | 12.33 | 0 | 87.67 | 326.0842 | 0
2174 | 754.61 | 696.078 | 26.1 | 112.3181 | 112.3181 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 65.2371 | 642.2919 | 0 | 0.05921 | 3.5627 | 0 | 0 | 0 | 112.3181 | off_peak | 642.2919 |  |  | 14.88 | 0 | 85.12 | 400.155 | 0
2175 | 797.13 | 628.947 | 26.5 | 101.3392 | 101.3392 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 65.2371 | 695.7908 | 0 | 0.05921 | 3.8137 | 0 | 0 | 0 | 101.3392 | off_peak | 695.7908 |  |  | 12.71 | 0 | 87.29 | 386.4785 | 0
2176 | 769.08 | 491.165 | 26.8 | 79.0531 | 79.0531 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 65.2371 | 690.0269 | 0 | 0.05921 | 4.1979 | 0 | 0 | 0 | 79.0531 | off_peak | 690.0269 |  |  | 10.28 | 0 | 89.72 | 331.8601 | 0
2177 | 740.52 | 372.017 | 26.6 | 59.9196 | 59.9196 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 65.2371 | 680.6004 | 0 | 0.05921 | 4.6812 | 0 | 0 | 0 | 59.9196 | off_peak | 680.6004 |  |  | 8.09 | 0 | 91.91 | 280.4952 | 0
2178 | 651.62 | 169.533 | 25.9 | 27.3754 | 27.3754 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 65.2371 | 624.2446 | 0 | 0.05921 | 5.0247 | 0 | 0 | 0 | 27.3754 | off_peak | 624.2446 |  |  | 4.2 | 0 | 95.8 | 137.5527 | 0
2179 | 631.55 | 12.4256 | 25.3 | 2.0108 | 2.0108 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 65.2371 | 629.5392 | 0 | 0.05921 | 5.3111 | 0 | 0 | 0 | 2.0108 | off_peak | 629.5392 |  |  | 0.32 | 0 | 99.68 | 10.6793 | 0
2180 | 594.36 | 0 | 24.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 65.2371 | 594.36 | 0 | 0.05921 | 5.6201 | 0 | 0 | 0 | 0 | off_peak | 594.36 |  |  | 0 | 0 | 100 | 0 | 0
2181 | 636.1 | 0 | 23.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 65.2371 | 636.1 | 0 | 0.05921 | 5.908 | 0 | 0 | 0 | 0 | off_peak | 636.1 |  |  | 0 | 0 | 100 | 0 | 0
2182 | 594.19 | 0 | 22.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 65.2371 | 594.19 | 0 | 0.05921 | 6.1296 | 0 | 0 | 0 | 0 | off_peak | 594.19 |  |  | 0 | 0 | 100 | 0 | 0
2183 | 616.94 | 0 | 21.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 65.2371 | 616.94 | 0 | 0.05921 | 6.406 | 0 | 0 | 0 | 0 | off_peak | 616.94 |  |  | 0 | 0 | 100 | 0 | 0
2184 | 632.94 | 0 | 20.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 65.2371 | 632.94 | 0 | 0.05921 | 6.4197 | 0 | 0 | 0 | 0 | off_peak | 632.94 |  |  | 0 | 0 | 100 | 0 | 0
2185 | 622.15 | 0 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 65.2371 | 622.15 | 0 | 0.05921 | 6.3606 | 0 | 0 | 0 | 0 | off_peak | 622.15 |  |  | 0 | 0 | 100 | 0 | 0
2186 | 598.53 | 0 | 19.6 | 0 | 0 | 0 | 0 | 8.9371 | 8.9371 | 0 | 0 | 0 | 73.597 | 607.4671 | 0 | 0.05921 | 6.221 | 0 | 0 | 0 | 0 | off_peak | 598.53 | 0 | 100 | 0 | 0 | 100 | 0 | 0
2187 | 616.08 | 0 | 19.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 73.597 | 616.08 | 0 | 0.05921 | 5.8342 | 0 | 0 | 0 | 0 | off_peak | 616.08 |  |  | 0 | 0 | 100 | 0 | 0
2188 | 602.59 | 0 | 19.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 73.597 | 602.59 | 0 | 0.05921 | 5.3513 | 0 | 0 | 0 | 0 | off_peak | 602.59 |  |  | 0 | 0 | 100 | 0 | 0
2189 | 626.28 | 0 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 73.597 | 626.28 | 0 | 0.05921 | 4.785 | 0 | 0 | 0 | 0 | off_peak | 626.28 |  |  | 0 | 0 | 100 | 0 | 0
2190 | 721.05 | 0 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 73.597 | 721.05 | 0 | 0.05921 | 4.2223 | 0 | 0 | 0 | 0 | off_peak | 721.05 |  |  | 0 | 0 | 100 | 0 | 0
2191 | 814.5 | 29.9048 | 19.7 | 4.937 | 4.937 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 73.597 | 809.563 | 0 | 0.05921 | 3.6744 | 0 | 0 | 0 | 4.937 | off_peak | 809.563 |  |  | 0.61 | 0 | 99.39 | 18.1406 | 0
2192 | 826.39 | 214.183 | 20.8 | 35.2223 | 35.2223 | 0 | 0 | 0.57721 | 0.57721 | 0 | 0 | 0 | 74.137 | 791.7449 | 0 | 0.05921 | 3.4007 | 0 | 0 | 0 | 35.2223 | off_peak | 791.1677 | 0 | 100 | 4.26 | 0 | 95.74 | 119.7817 | 0
2193 | 799.19 | 429.948 | 21.9 | 70.4289 | 70.4289 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.137 | 728.7611 | 0 | 0.05921 | 3.1331 | 0 | 0 | 0 | 70.4289 | off_peak | 728.7611 |  |  | 8.81 | 0 | 91.19 | 220.6583 | 0
2194 | 781.79 | 624.857 | 23.2 | 101.8828 | 101.8828 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.137 | 679.9072 | 0 | 0.05921 | 2.9831 | 0 | 0 | 0 | 101.8828 | off_peak | 679.9072 |  |  | 13.03 | 0 | 86.97 | 303.9295 | 0
2195 | 750.3 | 775.241 | 24.2 | 125.9507 | 125.9507 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.137 | 624.3493 | 0 | 0.05921 | 2.9622 | 0 | 0 | 0 | 125.9507 | off_peak | 624.3493 |  |  | 16.79 | 0 | 83.21 | 373.0886 | 0
2196 | 787.66 | 866.565 | 25 | 140.3835 | 140.3835 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.137 | 647.2765 | 0 | 0.05921 | 3.0491 | 0 | 0 | 0 | 140.3835 | off_peak | 647.2765 |  |  | 17.82 | 0 | 82.18 | 428.0453 | 0
2197 | 721.57 | 891.587 | 25.5 | 144.1771 | 144.1771 | 0 | 0 | 0.037279 | 0.037279 | 0 | 0 | 0 | 74.1718 | 577.4302 | 0 | 0.05921 | 3.2174 | 0 | 0 | 0 | 144.1771 | off_peak | 577.3929 | 0 | 100 | 19.98 | 0 | 80.02 | 463.8817 | 0
2198 | 712.91 | 847.999 | 25.7 | 137.0297 | 137.0297 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1718 | 575.8803 | 0 | 0.05921 | 3.4949 | 0 | 0 | 0 | 137.0297 | off_peak | 575.8803 |  |  | 19.22 | 0 | 80.78 | 478.9005 | 0
2199 | 745.09 | 744.756 | 25.6 | 120.3899 | 120.3899 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1718 | 624.7001 | 0 | 0.05921 | 3.8043 | 0 | 0 | 0 | 120.3899 | off_peak | 624.7001 |  |  | 16.16 | 0 | 83.84 | 457.9997 | 0
2200 | 708.73 | 540.946 | 25.3 | 87.5386 | 87.5386 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1718 | 621.1914 | 0 | 0.05921 | 4.043 | 0 | 0 | 0 | 87.5386 | off_peak | 621.1914 |  |  | 12.35 | 0 | 87.65 | 353.9214 | 0
2201 | 735.83 | 387.932 | 24.8 | 62.8902 | 62.8902 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1718 | 672.9398 | 0 | 0.05921 | 4.3997 | 0 | 0 | 0 | 62.8902 | off_peak | 672.9398 |  |  | 8.55 | 0 | 91.45 | 276.7008 | 0
2202 | 660.11 | 179.827 | 23.9 | 29.2473 | 29.2473 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1718 | 630.8627 | 0 | 0.05921 | 4.8763 | 0 | 0 | 0 | 29.2473 | off_peak | 630.8627 |  |  | 4.43 | 0 | 95.57 | 142.6196 | 0
2203 | 593.42 | 10.4734 | 23.4 | 1.7065 | 1.7065 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1718 | 591.7135 | 0 | 0.05921 | 5.2988 | 0 | 0 | 0 | 1.7065 | off_peak | 591.7135 |  |  | 0.29 | 0 | 99.71 | 9.0423 | 0
2204 | 630.92 | 0 | 22.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1718 | 630.92 | 0 | 0.05921 | 5.7079 | 0 | 0 | 0 | 0 | off_peak | 630.92 |  |  | 0 | 0 | 100 | 0 | 0
2205 | 590.47 | 0 | 22.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1718 | 590.47 | 0 | 0.05921 | 5.8576 | 0 | 0 | 0 | 0 | off_peak | 590.47 |  |  | 0 | 0 | 100 | 0 | 0
2206 | 584.76 | 0 | 22.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1718 | 584.76 | 0 | 0.05921 | 6.277 | 0 | 0 | 0 | 0 | off_peak | 584.76 |  |  | 0 | 0 | 100 | 0 | 0
2207 | 575.27 | 0 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1718 | 575.27 | 0 | 0.05921 | 6.5253 | 0 | 0 | 0 | 0 | off_peak | 575.27 |  |  | 0 | 0 | 100 | 0 | 0
2208 | 604.68 | 0 | 21.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1718 | 604.68 | 0 | 0.05921 | 6.7138 | 0 | 0 | 0 | 0 | off_peak | 604.68 |  |  | 0 | 0 | 100 | 0 | 0
2209 | 583.05 | 0 | 21.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1718 | 583.05 | 0 | 0.05921 | 6.5851 | 0 | 0 | 0 | 0 | off_peak | 583.05 |  |  | 0 | 0 | 100 | 0 | 0
2210 | 589.49 | 0 | 21.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1718 | 589.49 | 0 | 0.05921 | 6.4484 | 0 | 0 | 0 | 0 | off_peak | 589.49 |  |  | 0 | 0 | 100 | 0 | 0
2211 | 552.91 | 0 | 21.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1718 | 552.91 | 0 | 0.05921 | 6.0652 | 0 | 0 | 0 | 0 | off_peak | 552.91 |  |  | 0 | 0 | 100 | 0 | 0
2212 | 582.56 | 0 | 21.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1718 | 582.56 | 0 | 0.05921 | 5.4616 | 0 | 0 | 0 | 0 | off_peak | 582.56 |  |  | 0 | 0 | 100 | 0 | 0
2213 | 579.9 | 0 | 21.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1718 | 579.9 | 0 | 0.05921 | 4.7032 | 0 | 0 | 0 | 0 | off_peak | 579.9 |  |  | 0 | 0 | 100 | 0 | 0
2214 | 676.74 | 0 | 21.4 | 0 | 0 | 0 | 0 | 0.0024077 | 0.0024077 | 0 | 0 | 0 | 74.1741 | 676.7424 | 0 | 0.05921 | 4.078 | 0 | 0 | 0 | 0 | off_peak | 676.74 | 0 | 100 | 0 | 0 | 100 | 0 | 0
2215 | 786.49 | 23.6622 | 22.1 | 3.8733 | 3.8733 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1741 | 782.6167 | 0 | 0.05921 | 3.6458 | 0 | 0 | 0 | 3.8733 | off_peak | 782.6167 |  |  | 0.49 | 0 | 99.51 | 14.1212 | 0
2216 | 808.33 | 171.16 | 23.1 | 27.9176 | 27.9176 | 0 | 0 | 0.0001555 | 0.0001555 | 0 | 0 | 0 | 74.1742 | 780.4126 | 0 | 0.05921 | 3.3243 | 0 | 0 | 0 | 27.9176 | off_peak | 780.4124 | 0 | 100 | 3.45 | 0 | 96.55 | 92.8069 | 0
2217 | 804.91 | 323.594 | 23.6 | 52.6864 | 52.6864 | 0 | 0 | 1.0737e-05 | 1.0737e-05 | 0 | 0 | 0 | 74.1743 | 752.2236 | 0 | 0.05921 | 3.1663 | 0 | 0 | 0 | 52.6864 | off_peak | 752.2236 | 0 | 100 | 6.55 | 0 | 93.45 | 166.8192 | 0
2218 | 842.98 | 283.812 | 24.1 | 46.1265 | 46.1265 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1743 | 796.8535 | 0 | 0.05921 | 3.148 | 0 | 0 | 0 | 46.1265 | off_peak | 796.8535 |  |  | 5.47 | 0 | 94.53 | 145.2075 | 0
2219 | 846.61 | 606.214 | 24.6 | 98.3481 | 98.3481 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1743 | 748.2619 | 0 | 0.05921 | 3.374 | 0 | 0 | 0 | 98.3481 | off_peak | 748.2619 |  |  | 11.62 | 0 | 88.38 | 331.8266 | 0
2220 | 897.95 | 827.245 | 25 | 134.0137 | 134.0137 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1743 | 763.9363 | 0 | 0.05921 | 3.7669 | 0 | 0 | 0 | 134.0137 | off_peak | 763.9363 |  |  | 14.92 | 0 | 85.08 | 504.8133 | 0
2221 | 870.46 | 641.216 | 25.2 | 103.8022 | 103.8022 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1743 | 766.6578 | 0 | 0.088511 | 4.0562 | 0 | 0 | 0 | 103.8022 | on_peak | 766.6578 |  |  | 11.92 | 0 | 88.08 | 421.0443 | 0
2222 | 965.63 | 600.514 | 25.3 | 97.1782 | 97.1782 | 0 | 0 | 0 | 0 | 62.4453 | 62.4453 | 0 | 7.4174 | 806.0065 | 0 | 0.088511 | 4.2361 | 0 | 0 | 0 | 97.1782 | on_peak | 806.0065 |  |  | 10.06 | 6.47 | 83.47 | 411.6537 | 0
2223 | 944.56 | 530.417 | 25.3 | 85.8348 | 85.8348 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 858.7252 | 0 | 0.088511 | 4.4587 | 0 | 0 | 0 | 85.8348 | on_peak | 858.7252 |  |  | 9.09 | 0 | 90.91 | 382.71 | 0
2224 | 892.73 | 381.839 | 25.1 | 61.8356 | 61.8356 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 830.8944 | 0 | 0.088511 | 4.7004 | 0 | 0 | 0 | 61.8356 | on_peak | 830.8944 |  |  | 6.93 | 0 | 93.07 | 290.6542 | 0
2225 | 912.39 | 148.879 | 24.8 | 24.1358 | 24.1358 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 888.2542 | 0 | 0.088511 | 4.9386 | 0 | 0 | 0 | 24.1358 | on_peak | 888.2542 |  |  | 2.65 | 0 | 97.35 | 119.1969 | 0
2226 | 884.45 | 35.3912 | 24.2 | 5.7499 | 5.7499 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 878.7001 | 0 | 0.088511 | 5.3577 | 0 | 0 | 0 | 5.7499 | on_peak | 878.7001 |  |  | 0.65 | 0 | 99.35 | 30.8061 | 0
2227 | 838.25 | 9.5 | 23.8 | 1.5456 | 1.5456 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 836.7044 | 0 | 0.088511 | 5.7818 | 0 | 0 | 0 | 1.5456 | on_peak | 836.7044 |  |  | 0.18 | 0 | 99.82 | 8.9366 | 0
2228 | 869.78 | 0 | 23.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 869.78 | 0 | 0.088511 | 6.1013 | 0 | 0 | 0 | 0 | on_peak | 869.78 |  |  | 0 | 0 | 100 | 0 | 0
2229 | 841.48 | 0 | 23.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 841.48 | 0 | 0.088511 | 6.4183 | 0 | 0 | 0 | 0 | on_peak | 841.48 |  |  | 0 | 0 | 100 | 0 | 0
2230 | 828.91 | 0 | 23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 828.91 | 0 | 0.05921 | 6.7141 | 0 | 0 | 0 | 0 | off_peak | 828.91 |  |  | 0 | 0 | 100 | 0 | 0
2231 | 864.52 | 0 | 22.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 864.52 | 0 | 0.05921 | 6.9707 | 0 | 0 | 0 | 0 | off_peak | 864.52 |  |  | 0 | 0 | 100 | 0 | 0
2232 | 824.67 | 0 | 22.8 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 18.9814 | 837.0324 | 0 | 0.05921 | 7.2093 | 0 | 0 | 0 | 0 | off_peak | 824.67 | 0 | 100 | 0 | 0 | 100 | 0 | 0
2233 | 794.03 | 0 | 22.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18.9814 | 794.03 | 0 | 0.05921 | 7.1956 | 0 | 0 | 0 | 0 | off_peak | 794.03 |  |  | 0 | 0 | 100 | 0 | 0
2234 | 708.39 | 0 | 22.6 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 30.5453 | 720.7524 | 0 | 0.05921 | 7.0516 | 0 | 0 | 0 | 0 | off_peak | 708.39 | 0 | 100 | 0 | 0 | 100 | 0 | 0
2235 | 606.21 | 0 | 22.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30.5453 | 606.21 | 0 | 0.05921 | 6.5042 | 0 | 0 | 0 | 0 | off_peak | 606.21 |  |  | 0 | 0 | 100 | 0 | 0
2236 | 596.4 | 0 | 22.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30.5453 | 596.4 | 0 | 0.05921 | 5.7911 | 0 | 0 | 0 | 0 | off_peak | 596.4 |  |  | 0 | 0 | 100 | 0 | 0
2237 | 646.03 | 0 | 22.3 | 0 | 0 | 0 | 0 | 8.7006 | 8.7006 | 0 | 0 | 0 | 38.684 | 654.7306 | 0 | 0.05921 | 4.8102 | 0 | 0 | 0 | 0 | off_peak | 646.03 | 0 | 100 | 0 | 0 | 100 | 0 | 0
2238 | 681.16 | 0 | 22.4 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 50.2479 | 693.5224 | 0 | 0.05921 | 4.451 | 0 | 0 | 0 | 0 | off_peak | 681.16 | 0 | 100 | 0 | 0 | 100 | 0 | 0
2239 | 763.22 | 32.381 | 23 | 5.2835 | 5.2835 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 61.8119 | 770.2989 | 0 | 0.05921 | 3.9341 | 0 | 0 | 0 | 5.2835 | off_peak | 757.9365 | 0 | 100 | 0.69 | 0 | 99.31 | 20.786 | 0
2240 | 803.85 | 216.696 | 24 | 35.2311 | 35.2311 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 73.3758 | 780.9812 | 0 | 0.05921 | 3.5258 | 0 | 0 | 0 | 35.2311 | off_peak | 768.6189 | 0 | 100 | 4.38 | 0 | 95.62 | 124.2177 | 0
2241 | 845.38 | 287.892 | 24.5 | 46.7225 | 46.7225 | 0 | 0 | 0.79843 | 0.79843 | 0 | 0 | 0 | 74.1227 | 799.456 | 0 | 0.05921 | 3.285 | 0 | 0 | 0 | 46.7225 | off_peak | 798.6575 | 0 | 100 | 5.53 | 0 | 94.47 | 153.4848 | 0
2242 | 846.94 | 620.744 | 25 | 100.5605 | 100.5605 | 0 | 0 | 0.051567 | 0.051567 | 0 | 0 | 0 | 74.1709 | 746.431 | 0 | 0.05921 | 3.2386 | 0 | 0 | 0 | 100.5605 | off_peak | 746.3795 | 0 | 100 | 11.87 | 0 | 88.13 | 325.6718 | 0
2243 | 865.84 | 55.1 | 25.4 | 8.9133 | 8.9133 | 0 | 0 | 0.0033305 | 0.0033305 | 0 | 0 | 0 | 74.174 | 856.93 | 0 | 0.05921 | 3.3771 | 0 | 0 | 0 | 8.9133 | off_peak | 856.9267 | 0 | 100 | 1.03 | 0 | 98.97 | 30.1009 | 0
2244 | 893.48 | 81.7 | 25.7 | 13.202 | 13.202 | 0 | 0 | 0.0002151 | 0.0002151 | 0 | 0 | 0 | 74.1742 | 880.2782 | 0 | 0.05921 | 3.8233 | 0 | 0 | 0 | 13.202 | off_peak | 880.278 | 0 | 100 | 1.48 | 0 | 98.52 | 50.4749 | 0
2245 | 907.18 | 120.65 | 25.9 | 19.482 | 19.482 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1742 | 887.698 | 0 | 0.088511 | 4.1595 | 0 | 0 | 0 | 19.482 | on_peak | 887.698 |  |  | 2.15 | 0 | 97.85 | 81.0344 | 0
2246 | 924.29 | 609.374 | 26 | 98.3632 | 98.3632 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1742 | 825.9268 | 0 | 0.088511 | 4.3584 | 0 | 0 | 0 | 98.3632 | on_peak | 825.9268 |  |  | 10.64 | 0 | 89.36 | 428.711 | 0
2247 | 987.05 | 691.877 | 26 | 111.6806 | 111.6806 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1742 | 875.3694 | 0 | 0.088511 | 4.5748 | 0 | 0 | 0 | 111.6806 | on_peak | 875.3694 |  |  | 11.31 | 0 | 88.69 | 510.9143 | 0
2248 | 925.05 | 64.2787 | 25.9 | 10.3794 | 10.3794 | 0 | 0 | 0 | 0 | 24.9051 | 24.9051 | 0 | 47.5495 | 889.7655 | 0 | 0.088511 | 4.8283 | 0 | 0 | 0 | 10.3794 | on_peak | 889.7655 |  |  | 1.12 | 2.69 | 96.19 | 50.1152 | 0
2249 | 908.3 | 34.2 | 25.5 | 5.5304 | 5.5304 | 0 | 0 | 0 | 0 | 30.3091 | 30.3091 | 0 | 15.1477 | 872.4605 | 0 | 0.088511 | 5.2035 | 0 | 0 | 0 | 5.5304 | on_peak | 872.4605 |  |  | 0.61 | 3.34 | 96.05 | 28.7778 | 0
2250 | 896.48 | 28.7428 | 24.9 | 4.658 | 4.658 | 0 | 0 | 0 | 0 | 2.0565 | 2.0565 | 0 | 12.9492 | 889.7655 | 0 | 0.088511 | 5.5684 | 0 | 0 | 0 | 4.658 | on_peak | 889.7655 |  |  | 0.52 | 0.23 | 99.25 | 25.9376 | 0
2251 | 860.84 | 9.5 | 24.5 | 1.5418 | 1.5418 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12.9492 | 859.2982 | 0 | 0.088511 | 6.0427 | 0 | 0 | 0 | 1.5418 | on_peak | 859.2982 |  |  | 0.18 | 0 | 99.82 | 9.3165 | 0
2252 | 894.94 | 0 | 24.1 | 0 | 0 | 0 | 0 | 0 | 0 | 5.1745 | 5.1745 | 0 | 7.4174 | 889.7655 | 0 | 0.088511 | 6.4067 | 0 | 0 | 0 | 0 | on_peak | 889.7655 |  |  | 0 | 0.58 | 99.42 | 0 | 0
2253 | 884.18 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 884.18 | 0 | 0.088511 | 6.7037 | 0 | 0 | 0 | 0 | on_peak | 884.18 |  |  | 0 | 0 | 100 | 0 | 0
2254 | 858.14 | 0 | 23.8 | 0 | 0 | 0 | 0 | 8.7006 | 8.7006 | 0 | 0 | 0 | 15.5561 | 866.8406 | 0 | 0.05921 | 7.0191 | 0 | 0 | 0 | 0 | off_peak | 858.14 | 0 | 100 | 0 | 0 | 100 | 0 | 0
2255 | 836.37 | 0 | 23.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15.5561 | 836.37 | 0 | 0.05921 | 7.2017 | 0 | 0 | 0 | 0 | off_peak | 836.37 |  |  | 0 | 0 | 100 | 0 | 0
2256 | 860.06 | 0 | 23.6 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 27.12 | 872.4224 | 0 | 0.05921 | 7.3645 | 0 | 0 | 0 | 0 | off_peak | 860.06 | 0 | 100 | 0 | 0 | 100 | 0 | 0
2257 | 819.36 | 0 | 23.6 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 38.684 | 831.7224 | 0 | 0.05921 | 7.2593 | 0 | 0 | 0 | 0 | off_peak | 819.36 | 0 | 100 | 0 | 0 | 100 | 0 | 0
2258 | 702.51 | 0 | 23.5 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 50.2479 | 714.8724 | 0 | 0.05921 | 7.0482 | 0 | 0 | 0 | 0 | off_peak | 702.51 | 0 | 100 | 0 | 0 | 100 | 0 | 0
2259 | 648.1 | 0 | 23.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50.2479 | 648.1 | 0 | 0.05921 | 6.6237 | 0 | 0 | 0 | 0 | off_peak | 648.1 |  |  | 0 | 0 | 100 | 0 | 0
2260 | 623.03 | 0 | 23.2 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 61.8119 | 635.3924 | 0 | 0.05921 | 6.0284 | 0 | 0 | 0 | 0 | off_peak | 623.03 | 0 | 100 | 0 | 0 | 100 | 0 | 0
2261 | 645.52 | 0 | 22.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 61.8119 | 645.52 | 0 | 0.05921 | 5.1186 | 0 | 0 | 0 | 0 | off_peak | 645.52 |  |  | 0 | 0 | 100 | 0 | 0
2262 | 731.57 | 0 | 22.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 61.8119 | 731.57 | 0 | 0.05921 | 4.5506 | 0 | 0 | 0 | 0 | off_peak | 731.57 |  |  | 0 | 0 | 100 | 0 | 0
2263 | 766.68 | 39.6343 | 23.1 | 6.4647 | 6.4647 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 73.3758 | 772.5777 | 0 | 0.05921 | 3.9995 | 0 | 0 | 0 | 6.4647 | off_peak | 760.2153 | 0 | 100 | 0.84 | 0 | 99.16 | 25.8553 | 0
2264 | 840.41 | 232.7 | 23.8 | 37.8603 | 37.8603 | 0 | 0 | 0.79843 | 0.79843 | 0 | 0 | 0 | 74.1227 | 803.3482 | 0 | 0.05921 | 3.653 | 0 | 0 | 0 | 37.8603 | off_peak | 802.5497 | 0 | 100 | 4.5 | 0 | 95.5 | 138.3032 | 0
2265 | 813.31 | 449.964 | 24.3 | 73.0779 | 73.0779 | 0 | 0 | 0.051567 | 0.051567 | 0 | 0 | 0 | 74.1709 | 740.2837 | 0 | 0.05921 | 3.4391 | 0 | 0 | 0 | 73.0779 | off_peak | 740.2321 | 0 | 100 | 8.99 | 0 | 91.01 | 251.3221 | 0
2266 | 860.12 | 638.471 | 24.8 | 103.5068 | 103.5068 | 0 | 0 | 0.0033305 | 0.0033305 | 0 | 0 | 0 | 74.174 | 756.6166 | 0 | 0.05921 | 3.3321 | 0 | 0 | 0 | 103.5068 | off_peak | 756.6132 | 0 | 100 | 12.03 | 0 | 87.97 | 344.8915 | 0
2267 | 818.14 | 792.866 | 25.3 | 128.3056 | 128.3056 | 0 | 0 | 0.0002151 | 0.0002151 | 0 | 0 | 0 | 74.1742 | 689.8346 | 0 | 0.05921 | 3.5149 | 0 | 0 | 0 | 128.3056 | off_peak | 689.8344 | 0 | 100 | 15.68 | 0 | 84.32 | 450.9817 | 0
2268 | 856.37 | 887.018 | 25.6 | 143.3865 | 143.3865 | 0 | 0 | 1.3893e-05 | 1.3893e-05 | 0 | 0 | 0 | 74.1743 | 712.9835 | 0 | 0.05921 | 3.9751 | 0 | 0 | 0 | 143.3865 | off_peak | 712.9835 | 0 | 100 | 16.74 | 0 | 83.26 | 569.9824 | 0
2269 | 862.66 | 859.503 | 25.8 | 138.8385 | 138.8385 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1743 | 723.8215 | 0 | 0.088511 | 4.3143 | 0 | 0 | 0 | 138.8385 | on_peak | 723.8215 |  |  | 16.09 | 0 | 83.91 | 598.9923 | 0
2270 | 900.52 | 854.905 | 25.9 | 138.0459 | 138.0459 | 0 | 0 | 8.9726e-07 | 8.9726e-07 | 0 | 0 | 0 | 74.1743 | 762.4741 | 0 | 0.088511 | 4.5065 | 0 | 0 | 0 | 138.0459 | on_peak | 762.4741 | 0 | 100 | 15.33 | 0 | 84.67 | 622.1068 | 0
2271 | 975.07 | 769.155 | 25.9 | 124.1994 | 124.1994 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1743 | 850.8706 | 0 | 0.088511 | 4.545 | 0 | 0 | 0 | 124.1994 | on_peak | 850.8706 |  |  | 12.74 | 0 | 87.26 | 564.4836 | 0
2272 | 982.28 | 606.807 | 25.7 | 98.055 | 98.055 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1743 | 884.225 | 0 | 0.088511 | 4.7488 | 0 | 0 | 0 | 98.055 | on_peak | 884.225 |  |  | 9.98 | 0 | 90.02 | 465.6468 | 0
2273 | 974.71 | 405.535 | 25.4 | 65.6021 | 65.6021 | 0 | 0 | 0 | 0 | 19.3425 | 19.3425 | 0 | 53.4963 | 889.7655 | 0 | 0.088511 | 4.9407 | 0 | 0 | 0 | 65.6021 | on_peak | 889.7655 |  |  | 6.73 | 1.98 | 91.29 | 324.1218 | 0
2274 | 945.35 | 188.692 | 24.8 | 30.5901 | 30.5901 | 0 | 0 | 0 | 0 | 24.9944 | 24.9944 | 0 | 26.7761 | 889.7655 | 0 | 0.088511 | 5.3181 | 0 | 0 | 0 | 30.5901 | on_peak | 889.7655 |  |  | 3.24 | 2.64 | 94.12 | 162.6826 | 0
2275 | 905.52 | 16.3494 | 24.5 | 2.6534 | 2.6534 | 0 | 0 | 0 | 0 | 13.1012 | 13.1012 | 0 | 12.7704 | 889.7655 | 0 | 0.088511 | 5.7227 | 0 | 0 | 0 | 2.6534 | on_peak | 889.7655 |  |  | 0.29 | 1.45 | 98.26 | 15.1843 | 0
2276 | 884.74 | 0 | 24 | 0 | 0 | 0 | 0 | 5.0255 | 5.0255 | 0 | 0 | 0 | 17.4713 | 889.7655 | 0 | 0.088511 | 6.0266 | 0 | 0 | 0 | 0 | on_peak | 884.74 | 0 | 100 | 0 | 0 | 100 | 0 | 0
2277 | 899.17 | 0 | 23.8 | 0 | 0 | 0 | 0 | 0 | 0 | 9.4045 | 9.4045 | 0 | 7.4174 | 889.7655 | 0 | 0.088511 | 6.1862 | 0 | 0 | 0 | 0 | on_peak | 889.7655 |  |  | 0 | 1.05 | 98.95 | 0 | 0
2278 | 864.22 | 0 | 23.7 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 18.9814 | 876.5824 | 0 | 0.05921 | 6.483 | 0 | 0 | 0 | 0 | off_peak | 864.22 | 0 | 100 | 0 | 0 | 100 | 0 | 0
2279 | 922.01 | 0 | 23.6 | 0 | 0 | 0 | 0 | 0 | 0 | 10.8171 | 10.8171 | 0 | 7.4174 | 911.1929 | 0 | 0.05921 | 6.7797 | 0 | 0 | 0 | 0 | off_peak | 911.1929 |  |  | 0 | 1.17 | 98.83 | 0 | 0
2280 | 910.32 | 0 | 23.5 | 0 | 0 | 0 | 0 | 0.87292 | 0.87292 | 0 | 0 | 0 | 8.234 | 911.1929 | 0 | 0.05921 | 6.9928 | 0 | 0 | 0 | 0 | off_peak | 910.32 | 0 | 100 | 0 | 0 | 100 | 0 | 0
2281 | 843.27 | 0 | 23.4 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 19.7979 | 855.6324 | 0 | 0.05921 | 6.9495 | 0 | 0 | 0 | 0 | off_peak | 843.27 | 0 | 100 | 0 | 0 | 100 | 0 | 0
2282 | 744.42 | 0 | 23.2 | 0 | 0 | 0 | 0 | 7.8277 | 7.8277 | 0 | 0 | 0 | 27.12 | 752.2477 | 0 | 0.05921 | 6.8292 | 0 | 0 | 0 | 0 | off_peak | 744.42 | 0 | 100 | 0 | 0 | 100 | 0 | 0
2283 | 703.51 | 0 | 23.1 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 38.684 | 715.8724 | 0 | 0.05921 | 6.4052 | 0 | 0 | 0 | 0 | off_peak | 703.51 | 0 | 100 | 0 | 0 | 100 | 0 | 0
2284 | 691.37 | 0 | 23 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 50.2479 | 703.7324 | 0 | 0.05921 | 5.8001 | 0 | 0 | 0 | 0 | off_peak | 691.37 | 0 | 100 | 0 | 0 | 100 | 0 | 0
2285 | 711.26 | 0 | 22.8 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 61.8119 | 723.6224 | 0 | 0.05921 | 5.0415 | 0 | 0 | 0 | 0 | off_peak | 711.26 | 0 | 100 | 0 | 0 | 100 | 0 | 0
2286 | 780.68 | 0 | 22.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 61.8119 | 780.68 | 0 | 0.05921 | 4.337 | 0 | 0 | 0 | 0 | off_peak | 780.68 |  |  | 0 | 0 | 100 | 0 | 0
2287 | 843.52 | 38.1885 | 23.2 | 6.2266 | 6.2266 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 61.8119 | 837.2934 | 0 | 0.05921 | 3.8635 | 0 | 0 | 0 | 6.2266 | off_peak | 837.2934 |  |  | 0.74 | 0 | 99.26 | 24.0566 | 0
2288 | 856.85 | 225.656 | 23.7 | 36.7274 | 36.7274 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 73.3758 | 832.485 | 0 | 0.05921 | 3.5656 | 0 | 0 | 0 | 36.7274 | off_peak | 820.1226 | 0 | 100 | 4.29 | 0 | 95.71 | 130.9546 | 0
2289 | 873.9 | 443.096 | 24.1 | 72.0141 | 72.0141 | 0 | 0 | 0.79843 | 0.79843 | 0 | 0 | 0 | 74.1227 | 802.6843 | 0 | 0.05921 | 3.3703 | 0 | 0 | 0 | 72.0141 | off_peak | 801.8859 | 0 | 100 | 8.24 | 0 | 91.76 | 242.7111 | 0
2290 | 893.97 | 635.581 | 24.6 | 103.1124 | 103.1124 | 0 | 0 | 0.051567 | 0.051567 | 0 | 0 | 0 | 74.1709 | 790.9092 | 0 | 0.05921 | 3.3205 | 0 | 0 | 0 | 103.1124 | off_peak | 790.8576 | 0 | 100 | 11.53 | 0 | 88.47 | 342.3883 | 0
2291 | 859.38 | 783.373 | 25 | 126.9064 | 126.9064 | 0 | 0 | 0.0033305 | 0.0033305 | 0 | 0 | 0 | 74.174 | 732.4769 | 0 | 0.05921 | 3.5362 | 0 | 0 | 0 | 126.9064 | off_peak | 732.4736 | 0 | 100 | 14.77 | 0 | 85.23 | 448.7689 | 0
2292 | 920.9 | 879.963 | 25.2 | 142.4514 | 142.4514 | 0 | 0 | 0.0002151 | 0.0002151 | 0 | 0 | 0 | 74.1742 | 778.4488 | 0 | 0.05921 | 3.9338 | 0 | 0 | 0 | 142.4514 | off_peak | 778.4486 | 0 | 100 | 15.47 | 0 | 84.53 | 560.3752 | 0
2293 | 880.91 | 907.584 | 25.3 | 146.8698 | 146.8698 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1742 | 734.0402 | 0 | 0.088511 | 4.0722 | 0 | 0 | 0 | 146.8698 | on_peak | 734.0402 |  |  | 16.67 | 0 | 83.33 | 598.0878 | 0
2294 | 895.12 | 764.44 | 25.2 | 123.7501 | 123.7501 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1742 | 771.3699 | 0 | 0.088511 | 4.1835 | 0 | 0 | 0 | 123.7501 | on_peak | 771.3699 |  |  | 13.82 | 0 | 86.18 | 517.7032 | 0
2295 | 963.43 | 753.22 | 25.1 | 121.9777 | 121.9777 | 0 | 0 | 0 | 0 | 62.4453 | 62.4453 | 0 | 7.4174 | 779.007 | 0 | 0.088511 | 4.3124 | 0 | 0 | 0 | 121.9777 | on_peak | 779.007 |  |  | 12.66 | 6.48 | 80.86 | 526.0138 | 0
2296 | 956.79 | 580.294 | 24.8 | 94.0753 | 94.0753 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 862.7147 | 0 | 0.088511 | 4.5048 | 0 | 0 | 0 | 94.0753 | on_peak | 862.7147 |  |  | 9.83 | 0 | 90.17 | 423.791 | 0
2297 | 878.84 | 397.654 | 24.6 | 64.5127 | 64.5127 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 814.3273 | 0 | 0.088511 | 4.8462 | 0 | 0 | 0 | 64.5127 | on_peak | 814.3273 |  |  | 7.34 | 0 | 92.66 | 312.6396 | 0
2298 | 913.88 | 183.13 | 24.2 | 29.7525 | 29.7525 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 884.1275 | 0 | 0.088511 | 5.1637 | 0 | 0 | 0 | 29.7525 | on_peak | 884.1275 |  |  | 3.26 | 0 | 96.74 | 153.6341 | 0
2299 | 829.58 | 14.8353 | 24 | 2.412 | 2.412 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 827.168 | 0 | 0.088511 | 5.5735 | 0 | 0 | 0 | 2.412 | on_peak | 827.168 |  |  | 0.29 | 0 | 99.71 | 13.443 | 0
2300 | 839.63 | 0 | 23.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 839.63 | 0 | 0.088511 | 5.9319 | 0 | 0 | 0 | 0 | on_peak | 839.63 |  |  | 0 | 0 | 100 | 0 | 0
2301 | 810.54 | 0 | 23.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 810.54 | 0 | 0.088511 | 6.1713 | 0 | 0 | 0 | 0 | on_peak | 810.54 |  |  | 0 | 0 | 100 | 0 | 0
2302 | 757.46 | 0 | 23.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 757.46 | 0 | 0.05921 | 6.441 | 0 | 0 | 0 | 0 | off_peak | 757.46 |  |  | 0 | 0 | 100 | 0 | 0
2303 | 826.51 | 0 | 23.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 826.51 | 0 | 0.05921 | 6.6986 | 0 | 0 | 0 | 0 | off_peak | 826.51 |  |  | 0 | 0 | 100 | 0 | 0
2304 | 787.17 | 0 | 23.6 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 18.9814 | 799.5324 | 0 | 0.05921 | 6.9214 | 0 | 0 | 0 | 0 | off_peak | 787.17 | 0 | 100 | 0 | 0 | 100 | 0 | 0
2305 | 757.57 | 0 | 23.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18.9814 | 757.57 | 0 | 0.05921 | 6.7986 | 0 | 0 | 0 | 0 | off_peak | 757.57 |  |  | 0 | 0 | 100 | 0 | 0
2306 | 679.44 | 0 | 23.5 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 30.5453 | 691.8024 | 0 | 0.05921 | 6.5808 | 0 | 0 | 0 | 0 | off_peak | 679.44 | 0 | 100 | 0 | 0 | 100 | 0 | 0
2307 | 669.89 | 0 | 23.5 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 42.1093 | 682.2524 | 0 | 0.05921 | 6.1111 | 0 | 0 | 0 | 0 | off_peak | 669.89 | 0 | 100 | 0 | 0 | 100 | 0 | 0
2308 | 610.83 | 0 | 23.4 | 0 | 0 | 0 | 0 | 8.7006 | 8.7006 | 0 | 0 | 0 | 50.2479 | 619.5306 | 0 | 0.05921 | 5.5949 | 0 | 0 | 0 | 0 | off_peak | 610.83 | 0 | 100 | 0 | 0 | 100 | 0 | 0
2309 | 664.21 | 0 | 23.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50.2479 | 664.21 | 0 | 0.05921 | 5.0769 | 0 | 0 | 0 | 0 | off_peak | 664.21 |  |  | 0 | 0 | 100 | 0 | 0
2310 | 708.34 | 0 | 23.4 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 61.8119 | 720.7024 | 0 | 0.05921 | 4.4587 | 0 | 0 | 0 | 0 | off_peak | 708.34 | 0 | 100 | 0 | 0 | 100 | 0 | 0
2311 | 775.53 | 41.8244 | 23.9 | 6.8024 | 6.8024 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 61.8119 | 768.7276 | 0 | 0.05921 | 4.0495 | 0 | 0 | 0 | 6.8024 | off_peak | 768.7276 |  |  | 0.88 | 0 | 99.12 | 27.5464 | 0
2312 | 828.92 | 232.582 | 24.5 | 37.7461 | 37.7461 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 73.3758 | 803.5363 | 0 | 0.05921 | 3.7456 | 0 | 0 | 0 | 37.7461 | off_peak | 791.1739 | 0 | 100 | 4.55 | 0 | 95.45 | 141.3833 | 0
2313 | 790.05 | 449.507 | 24.9 | 72.8463 | 72.8463 | 0 | 0 | 0.79843 | 0.79843 | 0 | 0 | 0 | 74.1227 | 718.0021 | 0 | 0.05921 | 3.5645 | 0 | 0 | 0 | 72.8463 | off_peak | 717.2037 | 0 | 100 | 9.22 | 0 | 90.78 | 259.6627 | 0
2314 | 807.7 | 645.758 | 25.3 | 104.4998 | 104.4998 | 0 | 0 | 0.051567 | 0.051567 | 0 | 0 | 0 | 74.1709 | 703.2518 | 0 | 0.05921 | 3.5666 | 0 | 0 | 0 | 104.4998 | off_peak | 703.2002 | 0 | 100 | 12.94 | 0 | 87.06 | 372.7131 | 0
2315 | 767.29 | 724.189 | 25.7 | 117.023 | 117.023 | 0 | 0 | 0.0033305 | 0.0033305 | 0 | 0 | 0 | 74.174 | 650.2704 | 0 | 0.05921 | 3.6927 | 0 | 0 | 0 | 117.023 | off_peak | 650.267 | 0 | 100 | 15.25 | 0 | 84.75 | 432.13 | 0
2316 | 856.97 | 463.243 | 26 | 74.7752 | 74.7752 | 0 | 0 | 0.0002151 | 0.0002151 | 0 | 0 | 0 | 74.1742 | 782.195 | 0 | 0.05921 | 4.0149 | 0 | 0 | 0 | 74.7752 | off_peak | 782.1948 | 0 | 100 | 8.73 | 0 | 91.27 | 300.2135 | 0
2317 | 762.9 | 441.716 | 26.1 | 71.2746 | 71.2746 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1742 | 691.6254 | 0 | 0.088511 | 4.1521 | 0 | 0 | 0 | 71.2746 | on_peak | 691.6254 |  |  | 9.34 | 0 | 90.66 | 295.9358 | 0
2318 | 879.14 | 668.863 | 26.1 | 107.9267 | 107.9267 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1742 | 771.2133 | 0 | 0.088511 | 4.444 | 0 | 0 | 0 | 107.9267 | on_peak | 771.2133 |  |  | 12.28 | 0 | 87.72 | 479.6242 | 0
2319 | 874.33 | 603.913 | 26.1 | 97.4465 | 97.4465 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1742 | 776.8835 | 0 | 0.088511 | 4.6273 | 0 | 0 | 0 | 97.4465 | on_peak | 776.8835 |  |  | 11.15 | 0 | 88.85 | 450.9119 | 0
2320 | 845.39 | 290.687 | 25.9 | 46.9387 | 46.9387 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1742 | 798.4513 | 0 | 0.088511 | 4.946 | 0 | 0 | 0 | 46.9387 | on_peak | 798.4513 |  |  | 5.55 | 0 | 94.45 | 232.1583 | 0
2321 | 845.87 | 299.835 | 25.6 | 48.4684 | 48.4684 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1742 | 797.4016 | 0 | 0.088511 | 5.2996 | 0 | 0 | 0 | 48.4684 | on_peak | 797.4016 |  |  | 5.73 | 0 | 94.27 | 256.8612 | 0
2322 | 846.52 | 148.922 | 25.1 | 24.1167 | 24.1167 | 0 | 0 | 0 | 0 | 62.4453 | 62.4453 | 0 | 7.4174 | 759.958 | 0 | 0.088511 | 5.5701 | 0 | 0 | 0 | 24.1167 | on_peak | 759.958 |  |  | 2.85 | 7.38 | 89.77 | 134.3319 | 0
2323 | 783.17 | 13.3311 | 24.8 | 2.1612 | 2.1612 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 781.0088 | 0 | 0.088511 | 5.8301 | 0 | 0 | 0 | 2.1612 | on_peak | 781.0088 |  |  | 0.28 | 0 | 99.72 | 12.6 | 0
2324 | 802.38 | 0 | 24.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 802.38 | 0 | 0.088511 | 6.1334 | 0 | 0 | 0 | 0 | on_peak | 802.38 |  |  | 0 | 0 | 100 | 0 | 0
2325 | 731.1 | 0 | 24.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 731.1 | 0 | 0.088511 | 6.4067 | 0 | 0 | 0 | 0 | on_peak | 731.1 |  |  | 0 | 0 | 100 | 0 | 0
2326 | 746.53 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 746.53 | 0 | 0.05921 | 6.6541 | 0 | 0 | 0 | 0 | off_peak | 746.53 |  |  | 0 | 0 | 100 | 0 | 0
2327 | 766.78 | 0 | 23.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 766.78 | 0 | 0.05921 | 6.8113 | 0 | 0 | 0 | 0 | off_peak | 766.78 |  |  | 0 | 0 | 100 | 0 | 0
2328 | 719.3 | 0 | 23.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 719.3 | 0 | 0.05921 | 7.0045 | 0 | 0 | 0 | 0 | off_peak | 719.3 |  |  | 0 | 0 | 100 | 0 | 0
2329 | 710.93 | 0 | 23.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 710.93 | 0 | 0.05921 | 6.8165 | 0 | 0 | 0 | 0 | off_peak | 710.93 |  |  | 0 | 0 | 100 | 0 | 0
2330 | 574.71 | 0 | 23.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 574.71 | 0 | 0.05921 | 6.6449 | 0 | 0 | 0 | 0 | off_peak | 574.71 |  |  | 0 | 0 | 100 | 0 | 0
2331 | 502.13 | 0 | 23.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 502.13 | 0 | 0.05921 | 6.2321 | 0 | 0 | 0 | 0 | off_peak | 502.13 |  |  | 0 | 0 | 100 | 0 | 0
2332 | 483.54 | 0 | 23.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 483.54 | 0 | 0.05921 | 5.674 | 0 | 0 | 0 | 0 | off_peak | 483.54 |  |  | 0 | 0 | 100 | 0 | 0
2333 | 521.29 | 0 | 23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 521.29 | 0 | 0.05921 | 5.1398 | 0 | 0 | 0 | 0 | off_peak | 521.29 |  |  | 0 | 0 | 100 | 0 | 0
2334 | 707.03 | 0 | 23.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 707.03 | 0 | 0.05921 | 4.6108 | 0 | 0 | 0 | 0 | off_peak | 707.03 |  |  | 0 | 0 | 100 | 0 | 0
2335 | 768.21 | 41.274 | 23.7 | 6.7177 | 6.7177 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 18.9814 | 773.8547 | 0 | 0.05921 | 4.1257 | 0 | 0 | 0 | 6.7177 | off_peak | 761.4923 | 0 | 100 | 0.87 | 0 | 99.13 | 27.7152 | 0
2336 | 717.23 | 233.62 | 24.4 | 37.9282 | 37.9282 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18.9814 | 679.3018 | 0 | 0.05921 | 3.7673 | 0 | 0 | 0 | 37.9282 | off_peak | 679.3018 |  |  | 5.29 | 0 | 94.71 | 142.8859 | 0
2337 | 773.17 | 449.476 | 24.9 | 72.8413 | 72.8413 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18.9814 | 700.3287 | 0 | 0.05921 | 3.5525 | 0 | 0 | 0 | 72.8413 | off_peak | 700.3287 |  |  | 9.42 | 0 | 90.58 | 258.7685 | 0
2338 | 719.95 | 637.961 | 25.3 | 103.2381 | 103.2381 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18.9814 | 616.7119 | 0 | 0.05921 | 3.4656 | 0 | 0 | 0 | 103.2381 | off_peak | 616.7119 |  |  | 14.34 | 0 | 85.66 | 357.7831 | 0
2339 | 698.57 | 752.035 | 25.7 | 121.5227 | 121.5227 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18.9814 | 577.0473 | 0 | 0.05921 | 3.4737 | 0 | 0 | 0 | 121.5227 | off_peak | 577.0473 |  |  | 17.4 | 0 | 82.6 | 422.1344 | 0
2340 | 775.17 | 874.009 | 25.9 | 141.1307 | 141.1307 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18.9814 | 634.0393 | 0 | 0.05921 | 3.6007 | 0 | 0 | 0 | 141.1307 | off_peak | 634.0393 |  |  | 18.21 | 0 | 81.79 | 508.1672 | 0
2341 | 702.05 | 897.767 | 26 | 144.9147 | 144.9147 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18.9814 | 557.1353 | 0 | 0.05921 | 3.779 | 0 | 0 | 0 | 144.9147 | off_peak | 557.1353 |  |  | 20.64 | 0 | 79.36 | 547.6307 | 0
2342 | 690.31 | 754.544 | 25.9 | 121.8401 | 121.8401 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18.9814 | 568.4699 | 0 | 0.05921 | 4.2222 | 0 | 0 | 0 | 121.8401 | off_peak | 568.4699 |  |  | 17.65 | 0 | 82.35 | 514.4313 | 0
2343 | 733.69 | 369.75 | 25.8 | 59.727 | 59.727 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18.9814 | 673.963 | 0 | 0.05921 | 4.6022 | 0 | 0 | 0 | 59.727 | off_peak | 673.963 |  |  | 8.14 | 0 | 91.86 | 274.876 | 0
2344 | 680.02 | 382.69 | 25.5 | 61.8842 | 61.8842 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 30.5453 | 630.4982 | 0 | 0.05921 | 5.0693 | 0 | 0 | 0 | 61.8842 | off_peak | 618.1358 | 0 | 100 | 9.1 | 0 | 90.9 | 313.7096 | 0
2345 | 672.63 | 358.943 | 25.1 | 58.1278 | 58.1278 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30.5453 | 614.5022 | 0 | 0.05921 | 5.5282 | 0 | 0 | 0 | 58.1278 | off_peak | 614.5022 |  |  | 8.64 | 0 | 91.36 | 321.3433 | 0
2346 | 615.84 | 180.675 | 24.6 | 29.3115 | 29.3115 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 42.1093 | 598.8909 | 0 | 0.05921 | 5.8652 | 0 | 0 | 0 | 29.3115 | off_peak | 586.5285 | 0 | 100 | 4.76 | 0 | 95.24 | 171.9173 | 0
2347 | 589.03 | 15.5582 | 24.2 | 2.5277 | 2.5277 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 42.1093 | 586.5023 | 0 | 0.05921 | 6.2432 | 0 | 0 | 0 | 2.5277 | off_peak | 586.5023 |  |  | 0.43 | 0 | 99.57 | 15.781 | 0
2348 | 526.95 | 0 | 23.6 | 0 | 0 | 0 | 0 | 8.7006 | 8.7006 | 0 | 0 | 0 | 50.2479 | 535.6506 | 0 | 0.05921 | 6.5123 | 0 | 0 | 0 | 0 | off_peak | 526.95 | 0 | 100 | 0 | 0 | 100 | 0 | 0
2349 | 552.16 | 0 | 23.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50.2479 | 552.16 | 0 | 0.05921 | 6.8984 | 0 | 0 | 0 | 0 | off_peak | 552.16 |  |  | 0 | 0 | 100 | 0 | 0
2350 | 547.73 | 0 | 23.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50.2479 | 547.73 | 0 | 0.05921 | 6.9997 | 0 | 0 | 0 | 0 | off_peak | 547.73 |  |  | 0 | 0 | 100 | 0 | 0
2351 | 546.36 | 0 | 23.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50.2479 | 546.36 | 0 | 0.05921 | 7.2246 | 0 | 0 | 0 | 0 | off_peak | 546.36 |  |  | 0 | 0 | 100 | 0 | 0
2352 | 540.75 | 0 | 23.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50.2479 | 540.75 | 0 | 0.05921 | 7.2605 | 0 | 0 | 0 | 0 | off_peak | 540.75 |  |  | 0 | 0 | 100 | 0 | 0
2353 | 545.53 | 0 | 22.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50.2479 | 545.53 | 0 | 0.05921 | 6.8999 | 0 | 0 | 0 | 0 | off_peak | 545.53 |  |  | 0 | 0 | 100 | 0 | 0
2354 | 538.73 | 0 | 22.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50.2479 | 538.73 | 0 | 0.05921 | 6.667 | 0 | 0 | 0 | 0 | off_peak | 538.73 |  |  | 0 | 0 | 100 | 0 | 0
2355 | 513.75 | 0 | 22.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50.2479 | 513.75 | 0 | 0.05921 | 6.2643 | 0 | 0 | 0 | 0 | off_peak | 513.75 |  |  | 0 | 0 | 100 | 0 | 0
2356 | 541.22 | 0 | 22.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50.2479 | 541.22 | 0 | 0.05921 | 5.8201 | 0 | 0 | 0 | 0 | off_peak | 541.22 |  |  | 0 | 0 | 100 | 0 | 0
2357 | 532.31 | 0 | 22.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50.2479 | 532.31 | 0 | 0.05921 | 5.197 | 0 | 0 | 0 | 0 | off_peak | 532.31 |  |  | 0 | 0 | 100 | 0 | 0
2358 | 635.15 | 0 | 22.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50.2479 | 635.15 | 0 | 0.05921 | 4.5247 | 0 | 0 | 0 | 0 | off_peak | 635.15 |  |  | 0 | 0 | 100 | 0 | 0
2359 | 693.85 | 49.0826 | 23.2 | 8.0029 | 8.0029 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50.2479 | 685.8471 | 0 | 0.05921 | 4.0663 | 0 | 0 | 0 | 8.0029 | off_peak | 685.8471 |  |  | 1.15 | 0 | 98.85 | 32.5425 | 0
2360 | 710.69 | 248.029 | 23.9 | 40.3398 | 40.3398 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50.2479 | 670.3502 | 0 | 0.05921 | 3.7257 | 0 | 0 | 0 | 40.3398 | off_peak | 670.3502 |  |  | 5.68 | 0 | 94.32 | 150.2947 | 0
2361 | 732 | 433.331 | 24.4 | 70.3513 | 70.3513 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50.2479 | 661.6487 | 0 | 0.05921 | 3.473 | 0 | 0 | 0 | 70.3513 | off_peak | 661.6487 |  |  | 9.61 | 0 | 90.39 | 244.3317 | 0
2362 | 697.41 | 671.021 | 25 | 108.7054 | 108.7054 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50.2479 | 588.7046 | 0 | 0.05921 | 3.3517 | 0 | 0 | 0 | 108.7054 | off_peak | 588.7046 |  |  | 15.59 | 0 | 84.41 | 364.3452 | 0
2363 | 706.42 | 826.017 | 25.5 | 133.5739 | 133.5739 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50.2479 | 572.8461 | 0 | 0.05921 | 3.3176 | 0 | 0 | 0 | 133.5739 | off_peak | 572.8461 |  |  | 18.91 | 0 | 81.09 | 443.1471 | 0
2364 | 765.55 | 769.372 | 25.9 | 124.2344 | 124.2344 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50.2479 | 641.3156 | 0 | 0.05921 | 3.4358 | 0 | 0 | 0 | 124.2344 | off_peak | 641.3156 |  |  | 16.23 | 0 | 83.77 | 426.8421 | 0
2365 | 696.84 | 901.053 | 26.2 | 145.34 | 145.34 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50.2479 | 551.5 | 0 | 0.05921 | 3.59 | 0 | 0 | 0 | 145.34 | off_peak | 551.5 |  |  | 20.86 | 0 | 79.14 | 521.7772 | 0
2366 | 657.32 | 832.687 | 26.3 | 134.264 | 134.264 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50.2479 | 523.056 | 0 | 0.05921 | 4.0183 | 0 | 0 | 0 | 134.264 | off_peak | 523.056 |  |  | 20.43 | 0 | 79.57 | 539.5163 | 0
2367 | 738.32 | 775.273 | 26.3 | 125.0064 | 125.0064 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50.2479 | 613.3136 | 0 | 0.05921 | 4.5834 | 0 | 0 | 0 | 125.0064 | off_peak | 613.3136 |  |  | 16.93 | 0 | 83.07 | 572.9579 | 0
2368 | 726.36 | 648.654 | 26.1 | 104.6658 | 104.6658 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50.2479 | 621.6942 | 0 | 0.05921 | 5.0475 | 0 | 0 | 0 | 104.6658 | off_peak | 621.6942 |  |  | 14.41 | 0 | 85.59 | 528.3024 | 0
2369 | 692.31 | 438.745 | 25.7 | 70.8976 | 70.8976 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50.2479 | 621.4124 | 0 | 0.05921 | 5.3311 | 0 | 0 | 0 | 70.8976 | off_peak | 621.4124 |  |  | 10.24 | 0 | 89.76 | 377.9655 | 0
2370 | 619.6 | 211.504 | 24.9 | 34.276 | 34.276 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50.2479 | 585.324 | 0 | 0.05921 | 5.5819 | 0 | 0 | 0 | 34.276 | off_peak | 585.324 |  |  | 5.53 | 0 | 94.47 | 191.3244 | 0
2371 | 578.95 | 21.8572 | 24.5 | 3.5472 | 3.5472 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50.2479 | 575.4028 | 0 | 0.05921 | 5.7209 | 0 | 0 | 0 | 3.5472 | off_peak | 575.4028 |  |  | 0.61 | 0 | 99.39 | 20.2936 | 0
2372 | 530.94 | 0 | 23.7 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 61.8119 | 543.3024 | 0 | 0.05921 | 5.8012 | 0 | 0 | 0 | 0 | off_peak | 530.94 | 0 | 100 | 0 | 0 | 100 | 0 | 0
2373 | 583.39 | 0 | 23.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 61.8119 | 583.39 | 0 | 0.05921 | 5.7892 | 0 | 0 | 0 | 0 | off_peak | 583.39 |  |  | 0 | 0 | 100 | 0 | 0
2374 | 547.06 | 0 | 23.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 61.8119 | 547.06 | 0 | 0.05921 | 5.6512 | 0 | 0 | 0 | 0 | off_peak | 547.06 |  |  | 0 | 0 | 100 | 0 | 0
2375 | 564.86 | 0 | 23.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 61.8119 | 564.86 | 0 | 0.05921 | 5.4576 | 0 | 0 | 0 | 0 | off_peak | 564.86 |  |  | 0 | 0 | 100 | 0 | 0
2376 | 532.69 | 0 | 23.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 61.8119 | 532.69 | 0 | 0.05921 | 5.445 | 0 | 0 | 0 | 0 | off_peak | 532.69 |  |  | 0 | 0 | 100 | 0 | 0
2377 | 563.43 | 0 | 23.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 61.8119 | 563.43 | 0 | 0.05921 | 5.4743 | 0 | 0 | 0 | 0 | off_peak | 563.43 |  |  | 0 | 0 | 100 | 0 | 0
2378 | 541.99 | 0 | 23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 61.8119 | 541.99 | 0 | 0.05921 | 5.5318 | 0 | 0 | 0 | 0 | off_peak | 541.99 |  |  | 0 | 0 | 100 | 0 | 0
2379 | 554.44 | 0 | 22.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 61.8119 | 554.44 | 0 | 0.05921 | 5.223 | 0 | 0 | 0 | 0 | off_peak | 554.44 |  |  | 0 | 0 | 100 | 0 | 0
2380 | 562.36 | 0 | 22.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 61.8119 | 562.36 | 0 | 0.05921 | 4.7371 | 0 | 0 | 0 | 0 | off_peak | 562.36 |  |  | 0 | 0 | 100 | 0 | 0
2381 | 566.02 | 0 | 22.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 61.8119 | 566.02 | 0 | 0.05921 | 4.1283 | 0 | 0 | 0 | 0 | off_peak | 566.02 |  |  | 0 | 0 | 100 | 0 | 0
2382 | 701.57 | 0 | 23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 61.8119 | 701.57 | 0 | 0.05921 | 3.5965 | 0 | 0 | 0 | 0 | off_peak | 701.57 |  |  | 0 | 0 | 100 | 0 | 0
2383 | 771.17 | 60.7795 | 23.5 | 9.8994 | 9.8994 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 61.8119 | 761.2706 | 0 | 0.05921 | 3.2446 | 0 | 0 | 0 | 9.8994 | off_peak | 761.2706 |  |  | 1.28 | 0 | 98.72 | 32.1195 | 0
2384 | 860.88 | 276 | 24.1 | 44.8569 | 44.8569 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 73.3758 | 828.3855 | 0 | 0.05921 | 3.0689 | 0 | 0 | 0 | 44.8569 | off_peak | 816.0231 | 0 | 100 | 5.21 | 0 | 94.79 | 137.6596 | 0
2385 | 827.65 | 507.802 | 24.7 | 82.3528 | 82.3528 | 0 | 0 | 0.79843 | 0.79843 | 0 | 0 | 0 | 74.1227 | 746.0957 | 0 | 0.05921 | 2.9581 | 0 | 0 | 0 | 82.3528 | off_peak | 745.2972 | 0 | 100 | 9.95 | 0 | 90.05 | 243.6062 | 0
2386 | 847.32 | 710.105 | 25.3 | 114.9128 | 114.9128 | 0 | 0 | 0.051567 | 0.051567 | 0 | 0 | 0 | 74.1709 | 732.4588 | 0 | 0.05921 | 2.9837 | 0 | 0 | 0 | 114.9128 | off_peak | 732.4072 | 0 | 100 | 13.56 | 0 | 86.44 | 342.8615 | 0
2387 | 807.93 | 864.48 | 25.9 | 139.592 | 139.592 | 0 | 0 | 0.0033305 | 0.0033305 | 0 | 0 | 0 | 74.174 | 668.3413 | 0 | 0.05921 | 3.2594 | 0 | 0 | 0 | 139.592 | off_peak | 668.338 | 0 | 100 | 17.28 | 0 | 82.72 | 454.9844 | 0
2388 | 938.37 | 957.743 | 26.4 | 154.3724 | 154.3724 | 0 | 0 | 0.0002151 | 0.0002151 | 0 | 0 | 0 | 74.1742 | 783.9978 | 0 | 0.05921 | 3.7213 | 0 | 0 | 0 | 154.3724 | off_peak | 783.9976 | 0 | 100 | 16.45 | 0 | 83.55 | 574.4607 | 0
2389 | 840.89 | 981.111 | 26.7 | 157.9673 | 157.9673 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1742 | 682.9227 | 0 | 0.088511 | 3.9991 | 0 | 0 | 0 | 157.9673 | on_peak | 682.9227 |  |  | 18.79 | 0 | 81.21 | 631.7321 | 0
2390 | 907.11 | 934.138 | 26.9 | 150.2953 | 150.2953 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1742 | 756.8147 | 0 | 0.088511 | 4.1509 | 0 | 0 | 0 | 150.2953 | on_peak | 756.8147 |  |  | 16.57 | 0 | 83.43 | 623.8546 | 0
2391 | 952.74 | 819.798 | 26.9 | 131.8989 | 131.8989 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1742 | 820.8411 | 0 | 0.088511 | 4.2494 | 0 | 0 | 0 | 131.8989 | on_peak | 820.8411 |  |  | 13.84 | 0 | 86.16 | 560.4867 | 0
2392 | 884.46 | 649.191 | 26.7 | 104.5253 | 104.5253 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1742 | 779.9347 | 0 | 0.088511 | 4.4526 | 0 | 0 | 0 | 104.5253 | on_peak | 779.9347 |  |  | 11.82 | 0 | 88.18 | 465.4123 | 0
2393 | 851.02 | 435.867 | 26.3 | 70.28 | 70.28 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1742 | 780.74 | 0 | 0.088511 | 4.5598 | 0 | 0 | 0 | 70.28 | on_peak | 780.74 |  |  | 8.26 | 0 | 91.74 | 320.4601 | 0
2394 | 867.55 | 208.367 | 25.5 | 33.6947 | 33.6947 | 0 | 0 | 0 | 0 | 62.4453 | 62.4453 | 0 | 7.4174 | 771.41 | 0 | 0.088511 | 4.6125 | 0 | 0 | 0 | 33.6947 | on_peak | 771.41 |  |  | 3.88 | 7.2 | 88.92 | 155.4175 | 0
2395 | 815.54 | 21.4965 | 25 | 3.4824 | 3.4824 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 812.0576 | 0 | 0.088511 | 4.5837 | 0 | 0 | 0 | 3.4824 | on_peak | 812.0576 |  |  | 0.43 | 0 | 99.57 | 15.9624 | 0
2396 | 826.71 | 0 | 24.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 826.71 | 0 | 0.088511 | 4.7287 | 0 | 0 | 0 | 0 | on_peak | 826.71 |  |  | 0 | 0 | 100 | 0 | 0
2397 | 830.73 | 0 | 23.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 830.73 | 0 | 0.088511 | 4.9755 | 0 | 0 | 0 | 0 | on_peak | 830.73 |  |  | 0 | 0 | 100 | 0 | 0
2398 | 779.63 | 0 | 23.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 779.63 | 0 | 0.05921 | 5.0247 | 0 | 0 | 0 | 0 | off_peak | 779.63 |  |  | 0 | 0 | 100 | 0 | 0
2399 | 802.36 | 0 | 23.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 802.36 | 0 | 0.05921 | 5.213 | 0 | 0 | 0 | 0 | off_peak | 802.36 |  |  | 0 | 0 | 100 | 0 | 0
2400 | 776.45 | 0 | 23.5 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 18.9814 | 788.8124 | 0 | 0.05921 | 5.3372 | 0 | 0 | 0 | 0 | off_peak | 776.45 | 0 | 100 | 0 | 0 | 100 | 0 | 0
2401 | 768.18 | 0 | 23.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18.9814 | 768.18 | 0 | 0.05921 | 5.4528 | 0 | 0 | 0 | 0 | off_peak | 768.18 |  |  | 0 | 0 | 100 | 0 | 0
2402 | 724.5 | 0 | 23.4 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 30.5453 | 736.8624 | 0 | 0.05921 | 5.4418 | 0 | 0 | 0 | 0 | off_peak | 724.5 | 0 | 100 | 0 | 0 | 100 | 0 | 0
2403 | 649.39 | 0 | 23.4 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 42.1093 | 661.7524 | 0 | 0.05921 | 5.1234 | 0 | 0 | 0 | 0 | off_peak | 649.39 | 0 | 100 | 0 | 0 | 100 | 0 | 0
2404 | 629.87 | 0 | 23.4 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 53.6732 | 642.2324 | 0 | 0.05921 | 4.6756 | 0 | 0 | 0 | 0 | off_peak | 629.87 | 0 | 100 | 0 | 0 | 100 | 0 | 0
2405 | 657.05 | 0 | 23.5 | 0 | 0 | 0 | 0 | 8.7006 | 8.7006 | 0 | 0 | 0 | 61.8119 | 665.7506 | 0 | 0.05921 | 3.9918 | 0 | 0 | 0 | 0 | off_peak | 657.05 | 0 | 100 | 0 | 0 | 100 | 0 | 0
2406 | 727.61 | 0 | 23.6 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 73.3758 | 739.9724 | 0 | 0.05921 | 3.4148 | 0 | 0 | 0 | 0 | off_peak | 727.61 | 0 | 100 | 0 | 0 | 100 | 0 | 0
2407 | 743.75 | 57.4715 | 24.4 | 9.3305 | 9.3305 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 73.3758 | 734.4195 | 0 | 0.05921 | 3.1246 | 0 | 0 | 0 | 9.3305 | off_peak | 734.4195 |  |  | 1.25 | 0 | 98.75 | 29.1542 | 0
2408 | 792.14 | 266.144 | 25.3 | 43.0688 | 43.0688 | 0 | 0 | 0.79843 | 0.79843 | 0 | 0 | 0 | 74.1227 | 749.8697 | 0 | 0.05921 | 2.9303 | 0 | 0 | 0 | 43.0688 | off_peak | 749.0712 | 0 | 100 | 5.44 | 0 | 94.56 | 126.2027 | 0
2409 | 845.56 | 444.36 | 25.8 | 71.779 | 71.779 | 0 | 0 | 0.051567 | 0.051567 | 0 | 0 | 0 | 74.1709 | 773.8326 | 0 | 0.05921 | 2.8139 | 0 | 0 | 0 | 71.779 | off_peak | 773.781 | 0 | 100 | 8.49 | 0 | 91.51 | 201.9817 | 0
2410 | 828.52 | 581.609 | 26.3 | 93.7797 | 93.7797 | 0 | 0 | 0.0033305 | 0.0033305 | 0 | 0 | 0 | 74.174 | 734.7436 | 0 | 0.05921 | 2.8497 | 0 | 0 | 0 | 93.7797 | off_peak | 734.7403 | 0 | 100 | 11.32 | 0 | 88.68 | 267.2409 | 0
2411 | 817.92 | 709.021 | 26.8 | 114.1171 | 114.1171 | 0 | 0 | 0.0002151 | 0.0002151 | 0 | 0 | 0 | 74.1742 | 703.8031 | 0 | 0.05921 | 3.1224 | 0 | 0 | 0 | 114.1171 | off_peak | 703.8029 | 0 | 100 | 13.95 | 0 | 86.05 | 356.3216 | 0
2412 | 957.79 | 845.486 | 27.2 | 135.8839 | 135.8839 | 0 | 0 | 1.3893e-05 | 1.3893e-05 | 0 | 0 | 0 | 74.1743 | 821.9061 | 0 | 0.05921 | 3.6686 | 0 | 0 | 0 | 135.8839 | off_peak | 821.9061 | 0 | 100 | 14.19 | 0 | 85.81 | 498.5004 | 0
2413 | 897.82 | 838.624 | 27.4 | 134.6833 | 134.6833 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1743 | 763.1367 | 0 | 0.088511 | 3.9741 | 0 | 0 | 0 | 134.6833 | on_peak | 763.1367 |  |  | 15 | 0 | 85 | 535.2435 | 0
2414 | 912.03 | 917.337 | 27.5 | 147.2711 | 147.2711 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1743 | 764.7589 | 0 | 0.088511 | 3.9034 | 0 | 0 | 0 | 147.2711 | on_peak | 764.7589 |  |  | 16.15 | 0 | 83.85 | 574.8557 | 0
2415 | 902.19 | 817.135 | 27.4 | 131.2321 | 131.2321 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1743 | 770.9579 | 0 | 0.088511 | 3.8867 | 0 | 0 | 0 | 131.2321 | on_peak | 770.9579 |  |  | 14.55 | 0 | 85.45 | 510.0571 | 0
2416 | 940.69 | 648.219 | 27.2 | 104.1798 | 104.1798 | 0 | 0 | 0 | 0 | 62.4453 | 62.4453 | 0 | 7.4174 | 774.0649 | 0 | 0.088511 | 3.9898 | 0 | 0 | 0 | 104.1798 | on_peak | 774.0649 |  |  | 11.07 | 6.64 | 82.29 | 415.6536 | 0
2417 | 883.34 | 437.511 | 26.8 | 70.4175 | 70.4175 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 812.9225 | 0 | 0.088511 | 4.1612 | 0 | 0 | 0 | 70.4175 | on_peak | 812.9225 |  |  | 7.97 | 0 | 92.03 | 293.0203 | 0
2418 | 902.99 | 208.869 | 26.3 | 33.6784 | 33.6784 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 869.3116 | 0 | 0.088511 | 4.2641 | 0 | 0 | 0 | 33.6784 | on_peak | 869.3116 |  |  | 3.73 | 0 | 96.27 | 143.6078 | 0
2419 | 839.26 | 23.1574 | 25.9 | 3.7393 | 3.7393 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 835.5207 | 0 | 0.088511 | 4.3009 | 0 | 0 | 0 | 3.7393 | on_peak | 835.5207 |  |  | 0.45 | 0 | 99.55 | 16.0826 | 0
2420 | 864.74 | 0 | 25.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 864.74 | 0 | 0.088511 | 4.4412 | 0 | 0 | 0 | 0 | on_peak | 864.74 |  |  | 0 | 0 | 100 | 0 | 0
2421 | 881.11 | 0 | 25.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 881.11 | 0 | 0.088511 | 4.5776 | 0 | 0 | 0 | 0 | on_peak | 881.11 |  |  | 0 | 0 | 100 | 0 | 0
2422 | 842.53 | 0 | 25.2 | 0 | 0 | 0 | 0 | 8.7006 | 8.7006 | 0 | 0 | 0 | 15.5561 | 851.2306 | 0 | 0.05921 | 4.8315 | 0 | 0 | 0 | 0 | off_peak | 842.53 | 0 | 100 | 0 | 0 | 100 | 0 | 0
2423 | 859.27 | 0 | 25.2 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 27.12 | 871.6324 | 0 | 0.05921 | 5.0286 | 0 | 0 | 0 | 0 | off_peak | 859.27 | 0 | 100 | 0 | 0 | 100 | 0 | 0
2424 | 811.26 | 0 | 25.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27.12 | 811.26 | 0 | 0.05921 | 5.2783 | 0 | 0 | 0 | 0 | off_peak | 811.26 |  |  | 0 | 0 | 100 | 0 | 0
2425 | 816.96 | 0 | 25.1 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 38.684 | 829.3224 | 0 | 0.05921 | 5.5411 | 0 | 0 | 0 | 0 | off_peak | 816.96 | 0 | 100 | 0 | 0 | 100 | 0 | 0
2426 | 723.74 | 0 | 24.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 38.684 | 723.74 | 0 | 0.05921 | 5.5665 | 0 | 0 | 0 | 0 | off_peak | 723.74 |  |  | 0 | 0 | 100 | 0 | 0
2427 | 702.4 | 0 | 24.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 38.684 | 702.4 | 0 | 0.05921 | 5.265 | 0 | 0 | 0 | 0 | off_peak | 702.4 |  |  | 0 | 0 | 100 | 0 | 0
2428 | 658.52 | 0 | 24.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 38.684 | 658.52 | 0 | 0.05921 | 4.7446 | 0 | 0 | 0 | 0 | off_peak | 658.52 |  |  | 0 | 0 | 100 | 0 | 0
2429 | 686.44 | 0 | 24.5 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 50.2479 | 698.8024 | 0 | 0.05921 | 3.9943 | 0 | 0 | 0 | 0 | off_peak | 686.44 | 0 | 100 | 0 | 0 | 100 | 0 | 0
2430 | 721.43 | 0 | 24.7 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 61.8119 | 733.7924 | 0 | 0.05921 | 3.4744 | 0 | 0 | 0 | 0 | off_peak | 721.43 | 0 | 100 | 0 | 0 | 100 | 0 | 0
2431 | 810.58 | 27.4527 | 25.3 | 4.4425 | 4.4425 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 73.3758 | 818.4998 | 0 | 0.05921 | 3.1767 | 0 | 0 | 0 | 4.4425 | off_peak | 806.1375 | 0 | 100 | 0.55 | 0 | 99.45 | 14.1127 | 0
2432 | 878.2 | 122.888 | 26.1 | 19.829 | 19.829 | 0 | 0 | 0.79843 | 0.79843 | 0 | 0 | 0 | 74.1227 | 859.1694 | 0 | 0.05921 | 3.0682 | 0 | 0 | 0 | 19.829 | off_peak | 858.371 | 0 | 100 | 2.26 | 0 | 97.74 | 60.8393 | 0
2433 | 854.68 | 320.282 | 26.5 | 51.6055 | 51.6055 | 0 | 0 | 0.051567 | 0.051567 | 0 | 0 | 0 | 74.1709 | 803.1261 | 0 | 0.05921 | 2.9871 | 0 | 0 | 0 | 51.6055 | off_peak | 803.0745 | 0 | 100 | 6.04 | 0 | 93.96 | 154.1514 | 0
2434 | 852.19 | 581.828 | 26.9 | 93.6114 | 93.6114 | 0 | 0 | 0.0033305 | 0.0033305 | 0 | 0 | 0 | 74.174 | 758.5819 | 0 | 0.05921 | 3.0524 | 0 | 0 | 0 | 93.6114 | off_peak | 758.5786 | 0 | 100 | 10.98 | 0 | 89.02 | 285.7438 | 0
2435 | 815.36 | 644.788 | 27.2 | 103.6284 | 103.6284 | 0 | 0 | 0.0002151 | 0.0002151 | 0 | 0 | 0 | 74.1742 | 711.7318 | 0 | 0.05921 | 3.3366 | 0 | 0 | 0 | 103.6284 | off_peak | 711.7316 | 0 | 100 | 12.71 | 0 | 87.29 | 345.7653 | 0
2436 | 863.24 | 679.158 | 27.5 | 109.0334 | 109.0334 | 0 | 0 | 1.3893e-05 | 1.3893e-05 | 0 | 0 | 0 | 74.1743 | 754.2066 | 0 | 0.05921 | 3.8156 | 0 | 0 | 0 | 109.0334 | off_peak | 754.2066 | 0 | 100 | 12.63 | 0 | 87.37 | 416.0285 | 0
2437 | 813.24 | 817.879 | 27.6 | 131.2562 | 131.2562 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1743 | 681.9838 | 0 | 0.088511 | 4.1184 | 0 | 0 | 0 | 131.2562 | on_peak | 681.9838 |  |  | 16.14 | 0 | 83.86 | 540.5626 | 0
2438 | 856.88 | 915.574 | 27.7 | 146.8813 | 146.8813 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1743 | 709.9987 | 0 | 0.088511 | 4.2454 | 0 | 0 | 0 | 146.8813 | on_peak | 709.9987 |  |  | 17.14 | 0 | 82.86 | 623.5724 | 0
2439 | 866.31 | 806.161 | 27.6 | 129.3757 | 129.3757 | 0 | 0 | 0 | 0 | 62.4453 | 62.4453 | 0 | 7.4174 | 674.489 | 0 | 0.088511 | 4.2787 | 0 | 0 | 0 | 129.3757 | on_peak | 674.489 |  |  | 14.93 | 7.21 | 77.86 | 553.554 | 0
2440 | 836.9 | 623.684 | 27.5 | 100.1275 | 100.1275 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 736.7725 | 0 | 0.088511 | 4.4074 | 0 | 0 | 0 | 100.1275 | on_peak | 736.7725 |  |  | 11.96 | 0 | 88.04 | 441.2981 | 0
2441 | 844.49 | 371.775 | 27.2 | 59.7505 | 59.7505 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 784.7395 | 0 | 0.088511 | 4.5136 | 0 | 0 | 0 | 59.7505 | on_peak | 784.7395 |  |  | 7.08 | 0 | 92.92 | 269.6908 | 0
2442 | 803.8 | 207.469 | 26.6 | 33.4164 | 33.4164 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 770.3836 | 0 | 0.088511 | 4.5071 | 0 | 0 | 0 | 33.4164 | on_peak | 770.3836 |  |  | 4.16 | 0 | 95.84 | 150.6119 | 0
2443 | 801.3 | 23.0567 | 26.3 | 3.7177 | 3.7177 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 797.5823 | 0 | 0.088511 | 4.7201 | 0 | 0 | 0 | 3.7177 | on_peak | 797.5823 |  |  | 0.46 | 0 | 99.54 | 17.5481 | 0
2444 | 773.15 | 0 | 25.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 773.15 | 0 | 0.088511 | 4.7434 | 0 | 0 | 0 | 0 | on_peak | 773.15 |  |  | 0 | 0 | 100 | 0 | 0
2445 | 803.43 | 0 | 25.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 803.43 | 0 | 0.088511 | 4.7344 | 0 | 0 | 0 | 0 | on_peak | 803.43 |  |  | 0 | 0 | 100 | 0 | 0
2446 | 762.26 | 0 | 25.3 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 18.9814 | 774.6224 | 0 | 0.05921 | 4.8321 | 0 | 0 | 0 | 0 | off_peak | 762.26 | 0 | 100 | 0 | 0 | 100 | 0 | 0
2447 | 797.55 | 0 | 25.3 | 0 | 0 | 0 | 0 | 8.7006 | 8.7006 | 0 | 0 | 0 | 27.12 | 806.2506 | 0 | 0.05921 | 4.9288 | 0 | 0 | 0 | 0 | off_peak | 797.55 | 0 | 100 | 0 | 0 | 100 | 0 | 0
2448 | 751.72 | 0 | 25.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27.12 | 751.72 | 0 | 0.05921 | 5.1431 | 0 | 0 | 0 | 0 | off_peak | 751.72 |  |  | 0 | 0 | 100 | 0 | 0
2449 | 707.62 | 0 | 25.2 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 38.684 | 719.9824 | 0 | 0.05921 | 5.2731 | 0 | 0 | 0 | 0 | off_peak | 707.62 | 0 | 100 | 0 | 0 | 100 | 0 | 0
2450 | 612.24 | 0 | 25.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 38.684 | 612.24 | 0 | 0.05921 | 5.3298 | 0 | 0 | 0 | 0 | off_peak | 612.24 |  |  | 0 | 0 | 100 | 0 | 0
2451 | 578.92 | 0 | 25 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 50.2479 | 591.2824 | 0 | 0.05921 | 5.0828 | 0 | 0 | 0 | 0 | off_peak | 578.92 | 0 | 100 | 0 | 0 | 100 | 0 | 0
2452 | 575.64 | 0 | 25 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 61.8119 | 588.0024 | 0 | 0.05921 | 4.639 | 0 | 0 | 0 | 0 | off_peak | 575.64 | 0 | 100 | 0 | 0 | 100 | 0 | 0
2453 | 590.47 | 0 | 24.9 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 73.3758 | 602.8324 | 0 | 0.05921 | 3.995 | 0 | 0 | 0 | 0 | off_peak | 590.47 | 0 | 100 | 0 | 0 | 100 | 0 | 0
2454 | 714.38 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 73.3758 | 714.38 | 0 | 0.05921 | 3.4343 | 0 | 0 | 0 | 0 | off_peak | 714.38 |  |  | 0 | 0 | 100 | 0 | 0
2455 | 773.33 | 60.4583 | 25.5 | 9.7766 | 9.7766 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 73.3758 | 763.5534 | 0 | 0.05921 | 3.1862 | 0 | 0 | 0 | 9.7766 | off_peak | 763.5534 |  |  | 1.26 | 0 | 98.74 | 31.1507 | 0
2456 | 782.34 | 241.608 | 26.1 | 38.9855 | 38.9855 | 0 | 0 | 0.79843 | 0.79843 | 0 | 0 | 0 | 74.1227 | 744.1529 | 0 | 0.05921 | 3.1016 | 0 | 0 | 0 | 38.9855 | off_peak | 743.3545 | 0 | 100 | 4.98 | 0 | 95.02 | 120.916 | 0
2457 | 872.69 | 488.042 | 26.6 | 78.6074 | 78.6074 | 0 | 0 | 0.051567 | 0.051567 | 0 | 0 | 0 | 74.1709 | 794.1342 | 0 | 0.05921 | 3.018 | 0 | 0 | 0 | 78.6074 | off_peak | 794.0826 | 0 | 100 | 9.01 | 0 | 90.99 | 237.2382 | 0
2458 | 851.15 | 493.601 | 27 | 79.3876 | 79.3876 | 0 | 0 | 0.0033305 | 0.0033305 | 0 | 0 | 0 | 74.174 | 771.7657 | 0 | 0.05921 | 3.038 | 0 | 0 | 0 | 79.3876 | off_peak | 771.7624 | 0 | 100 | 9.33 | 0 | 90.67 | 241.183 | 0
2459 | 796.87 | 377.83 | 27.5 | 60.6576 | 60.6576 | 0 | 0 | 0.0002151 | 0.0002151 | 0 | 0 | 0 | 74.1742 | 736.2126 | 0 | 0.05921 | 3.2946 | 0 | 0 | 0 | 60.6576 | off_peak | 736.2124 | 0 | 100 | 7.61 | 0 | 92.39 | 199.8396 | 0
2460 | 871.71 | 522.219 | 27.9 | 83.7163 | 83.7163 | 0 | 0 | 1.3893e-05 | 1.3893e-05 | 0 | 0 | 0 | 74.1743 | 787.9938 | 0 | 0.05921 | 3.7863 | 0 | 0 | 0 | 83.7163 | off_peak | 787.9937 | 0 | 100 | 9.6 | 0 | 90.4 | 316.9755 | 0
2461 | 829.93 | 662.746 | 28.2 | 106.128 | 106.128 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1743 | 723.802 | 0 | 0.088511 | 4.0758 | 0 | 0 | 0 | 106.128 | on_peak | 723.802 |  |  | 12.79 | 0 | 87.21 | 432.554 | 0
2462 | 851.41 | 599.597 | 28.4 | 95.9458 | 95.9458 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1743 | 755.4642 | 0 | 0.088511 | 4.2969 | 0 | 0 | 0 | 95.9458 | on_peak | 755.4642 |  |  | 11.27 | 0 | 88.73 | 412.267 | 0
2463 | 866.55 | 712.359 | 28.4 | 113.9896 | 113.9896 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1743 | 752.5604 | 0 | 0.088511 | 4.4812 | 0 | 0 | 0 | 113.9896 | on_peak | 752.5604 |  |  | 13.15 | 0 | 86.85 | 510.816 | 0
2464 | 882.03 | 544.365 | 28.3 | 87.1395 | 87.1395 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1743 | 794.8905 | 0 | 0.088511 | 4.5126 | 0 | 0 | 0 | 87.1395 | on_peak | 794.8905 |  |  | 9.88 | 0 | 90.12 | 393.2264 | 0
2465 | 833.72 | 359.068 | 28 | 57.5408 | 57.5408 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1743 | 776.1792 | 0 | 0.088511 | 4.8276 | 0 | 0 | 0 | 57.5408 | on_peak | 776.1792 |  |  | 6.9 | 0 | 93.1 | 277.7812 | 0
2466 | 811.65 | 184.857 | 27.4 | 29.6881 | 29.6881 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1743 | 781.9619 | 0 | 0.088511 | 5.166 | 0 | 0 | 0 | 29.6881 | on_peak | 781.9619 |  |  | 3.66 | 0 | 96.34 | 153.3698 | 0
2467 | 743.42 | 18.1311 | 27 | 2.9161 | 2.9161 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1743 | 740.5039 | 0 | 0.088511 | 5.5774 | 0 | 0 | 0 | 2.9161 | on_peak | 740.5039 |  |  | 0.39 | 0 | 99.61 | 16.2641 | 0
2468 | 787.93 | 0 | 26.1 | 0 | 0 | 0 | 0 | 0 | 0 | 62.4453 | 62.4453 | 0 | 7.4174 | 725.4847 | 0 | 0.088511 | 5.7291 | 0 | 0 | 0 | 0 | on_peak | 725.4847 |  |  | 0 | 7.93 | 92.07 | 0 | 0
2469 | 735.22 | 0 | 25.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 735.22 | 0 | 0.088511 | 5.9705 | 0 | 0 | 0 | 0 | on_peak | 735.22 |  |  | 0 | 0 | 100 | 0 | 0
2470 | 743.23 | 0 | 25.5 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 18.9814 | 755.5924 | 0 | 0.05921 | 6.1252 | 0 | 0 | 0 | 0 | off_peak | 743.23 | 0 | 100 | 0 | 0 | 100 | 0 | 0
2471 | 750.62 | 0 | 25.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18.9814 | 750.62 | 0 | 0.05921 | 5.9857 | 0 | 0 | 0 | 0 | off_peak | 750.62 |  |  | 0 | 0 | 100 | 0 | 0
2472 | 719.97 | 0 | 25.3 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 30.5453 | 732.3324 | 0 | 0.05921 | 6.0907 | 0 | 0 | 0 | 0 | off_peak | 719.97 | 0 | 100 | 0 | 0 | 100 | 0 | 0
2473 | 729.26 | 0 | 25.1 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 42.1093 | 741.6224 | 0 | 0.05921 | 6.1523 | 0 | 0 | 0 | 0 | off_peak | 729.26 | 0 | 100 | 0 | 0 | 100 | 0 | 0
2474 | 671.05 | 0 | 25.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 42.1093 | 671.05 | 0 | 0.05921 | 6.1258 | 0 | 0 | 0 | 0 | off_peak | 671.05 |  |  | 0 | 0 | 100 | 0 | 0
2475 | 578.91 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 42.1093 | 578.91 | 0 | 0.05921 | 5.8013 | 0 | 0 | 0 | 0 | off_peak | 578.91 |  |  | 0 | 0 | 100 | 0 | 0
2476 | 578.39 | 0 | 24.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 42.1093 | 578.39 | 0 | 0.05921 | 5.2421 | 0 | 0 | 0 | 0 | off_peak | 578.39 |  |  | 0 | 0 | 100 | 0 | 0
2477 | 595.1 | 0 | 24.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 42.1093 | 595.1 | 0 | 0.05921 | 4.4804 | 0 | 0 | 0 | 0 | off_peak | 595.1 |  |  | 0 | 0 | 100 | 0 | 0
2478 | 656.21 | 0 | 24.8 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 53.6732 | 668.5724 | 0 | 0.05921 | 3.8722 | 0 | 0 | 0 | 0 | off_peak | 656.21 | 0 | 100 | 0 | 0 | 100 | 0 | 0
2479 | 741.95 | 61.6075 | 25.2 | 9.9732 | 9.9732 | 0 | 0 | 8.7006 | 8.7006 | 0 | 0 | 0 | 61.8119 | 740.6774 | 0 | 0.05921 | 3.4342 | 0 | 0 | 0 | 9.9732 | off_peak | 731.9768 | 0 | 100 | 1.34 | 0 | 98.66 | 34.2501 | 0
2480 | 766.99 | 264.229 | 25.8 | 42.6818 | 42.6818 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 73.3758 | 736.6706 | 0 | 0.05921 | 3.2622 | 0 | 0 | 0 | 42.6818 | off_peak | 724.3082 | 0 | 100 | 5.56 | 0 | 94.44 | 139.2387 | 0
2481 | 815.99 | 463.229 | 26.5 | 74.6379 | 74.6379 | 0 | 0 | 0.79843 | 0.79843 | 0 | 0 | 0 | 74.1227 | 742.1506 | 0 | 0.05921 | 3.1453 | 0 | 0 | 0 | 74.6379 | off_peak | 741.3521 | 0 | 100 | 9.15 | 0 | 90.85 | 234.7595 | 0
2482 | 810.64 | 636.34 | 27.3 | 102.2335 | 102.2335 | 0 | 0 | 0.051567 | 0.051567 | 0 | 0 | 0 | 74.1709 | 708.458 | 0 | 0.05921 | 3.1317 | 0 | 0 | 0 | 102.2335 | off_peak | 708.4065 | 0 | 100 | 12.61 | 0 | 87.39 | 320.1691 | 0
2483 | 772.91 | 730.735 | 28.1 | 117.058 | 117.058 | 0 | 0 | 0.0033305 | 0.0033305 | 0 | 0 | 0 | 74.174 | 655.8554 | 0 | 0.05921 | 3.3095 | 0 | 0 | 0 | 117.058 | off_peak | 655.852 | 0 | 100 | 15.15 | 0 | 84.85 | 387.4041 | 0
2484 | 823.58 | 776.192 | 28.9 | 123.9777 | 123.9777 | 0 | 0 | 0.0002151 | 0.0002151 | 0 | 0 | 0 | 74.1742 | 699.6025 | 0 | 0.05921 | 3.7221 | 0 | 0 | 0 | 123.9777 | off_peak | 699.6023 | 0 | 100 | 15.05 | 0 | 84.95 | 461.4568 | 0
2485 | 797.09 | 939.417 | 29.5 | 149.7201 | 149.7201 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1742 | 647.3699 | 0 | 0.088511 | 4.023 | 0 | 0 | 0 | 149.7201 | on_peak | 647.3699 |  |  | 18.78 | 0 | 81.22 | 602.3263 | 0
2486 | 797.11 | 778.345 | 30 | 123.8222 | 123.8222 | 0 | 0 | 0 | 0 | 62.4453 | 62.4453 | 0 | 7.4174 | 610.8425 | 0 | 0.088511 | 4.2191 | 0 | 0 | 0 | 123.8222 | on_peak | 610.8425 |  |  | 15.53 | 7.83 | 76.63 | 522.4235 | 0
2487 | 831.99 | 704.381 | 30.1 | 112.0147 | 112.0147 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 719.9753 | 0 | 0.088511 | 4.4209 | 0 | 0 | 0 | 112.0147 | on_peak | 719.9753 |  |  | 13.46 | 0 | 86.54 | 495.2056 | 0
2488 | 815.01 | 403.727 | 29.9 | 64.2501 | 64.2501 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 750.7599 | 0 | 0.088511 | 4.6639 | 0 | 0 | 0 | 64.2501 | on_peak | 750.7599 |  |  | 7.88 | 0 | 92.12 | 299.6585 | 0
2489 | 784.85 | 312.462 | 29.4 | 49.817 | 49.817 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 735.033 | 0 | 0.088511 | 5.0644 | 0 | 0 | 0 | 49.817 | on_peak | 735.033 |  |  | 6.35 | 0 | 93.65 | 252.2938 | 0
2490 | 765.07 | 78.9043 | 28.5 | 12.6214 | 12.6214 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 752.4486 | 0 | 0.088511 | 5.4992 | 0 | 0 | 0 | 12.6214 | on_peak | 752.4486 |  |  | 1.65 | 0 | 98.35 | 69.4074 | 0
2491 | 717.29 | 14.2048 | 28 | 2.2763 | 2.2763 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 715.0137 | 0 | 0.088511 | 5.9818 | 0 | 0 | 0 | 2.2763 | on_peak | 715.0137 |  |  | 0.32 | 0 | 99.68 | 13.6165 | 0
2492 | 733.03 | 0 | 27.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 733.03 | 0 | 0.088511 | 6.2587 | 0 | 0 | 0 | 0 | on_peak | 733.03 |  |  | 0 | 0 | 100 | 0 | 0
2493 | 706.84 | 0 | 26.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 706.84 | 0 | 0.088511 | 6.4961 | 0 | 0 | 0 | 0 | on_peak | 706.84 |  |  | 0 | 0 | 100 | 0 | 0
2494 | 728.4 | 0 | 26.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 728.4 | 0 | 0.05921 | 6.5883 | 0 | 0 | 0 | 0 | off_peak | 728.4 |  |  | 0 | 0 | 100 | 0 | 0
2495 | 711.05 | 0 | 25.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 711.05 | 0 | 0.05921 | 6.6967 | 0 | 0 | 0 | 0 | off_peak | 711.05 |  |  | 0 | 0 | 100 | 0 | 0
2496 | 727.15 | 0 | 25.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 727.15 | 0 | 0.05921 | 6.7956 | 0 | 0 | 0 | 0 | off_peak | 727.15 |  |  | 0 | 0 | 100 | 0 | 0
2497 | 678.8 | 0 | 25.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 678.8 | 0 | 0.05921 | 6.9013 | 0 | 0 | 0 | 0 | off_peak | 678.8 |  |  | 0 | 0 | 100 | 0 | 0
2498 | 598.14 | 0 | 25.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 598.14 | 0 | 0.05921 | 6.7714 | 0 | 0 | 0 | 0 | off_peak | 598.14 |  |  | 0 | 0 | 100 | 0 | 0
2499 | 549.95 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 549.95 | 0 | 0.05921 | 6.2743 | 0 | 0 | 0 | 0 | off_peak | 549.95 |  |  | 0 | 0 | 100 | 0 | 0
2500 | 556.56 | 0 | 24.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 556.56 | 0 | 0.05921 | 5.6992 | 0 | 0 | 0 | 0 | off_peak | 556.56 |  |  | 0 | 0 | 100 | 0 | 0
2501 | 570.63 | 0 | 24.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 570.63 | 0 | 0.05921 | 4.8693 | 0 | 0 | 0 | 0 | off_peak | 570.63 |  |  | 0 | 0 | 100 | 0 | 0
2502 | 637.69 | 0 | 24.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 637.69 | 0 | 0.05921 | 4.3474 | 0 | 0 | 0 | 0 | off_peak | 637.69 |  |  | 0 | 0 | 100 | 0 | 0
2503 | 720.39 | 30.6102 | 25.1 | 4.9571 | 4.9571 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 18.9814 | 727.7953 | 0 | 0.05921 | 3.9221 | 0 | 0 | 0 | 4.9571 | off_peak | 715.4329 | 0 | 100 | 0.69 | 0 | 99.31 | 19.4421 | 0
2504 | 681.46 | 190.146 | 26 | 30.6928 | 30.6928 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 30.5453 | 663.1296 | 0 | 0.05921 | 3.6885 | 0 | 0 | 0 | 30.6928 | off_peak | 650.7672 | 0 | 100 | 4.5 | 0 | 95.5 | 113.2099 | 0
2505 | 702.71 | 323.641 | 27.1 | 52.0335 | 52.0335 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 42.1093 | 663.0389 | 0 | 0.05921 | 3.4966 | 0 | 0 | 0 | 52.0335 | off_peak | 650.6765 | 0 | 100 | 7.4 | 0 | 92.6 | 181.9425 | 0
2506 | 699.73 | 391.891 | 28 | 62.8007 | 62.8007 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 42.1093 | 636.9293 | 0 | 0.05921 | 3.3807 | 0 | 0 | 0 | 62.8007 | off_peak | 636.9293 |  |  | 8.97 | 0 | 91.03 | 212.3122 | 0
2507 | 694.38 | 466.863 | 28.7 | 74.6244 | 74.6244 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 42.1093 | 619.7556 | 0 | 0.05921 | 3.3708 | 0 | 0 | 0 | 74.6244 | off_peak | 619.7556 |  |  | 10.75 | 0 | 89.25 | 251.5448 | 0
2508 | 715.52 | 684.097 | 29.3 | 109.1082 | 109.1082 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 53.6732 | 618.7742 | 0 | 0.05921 | 3.5195 | 0 | 0 | 0 | 109.1082 | off_peak | 606.4118 | 0 | 100 | 15.25 | 0 | 84.75 | 384.0062 | 0
2509 | 661.14 | 767.339 | 29.7 | 122.2056 | 122.2056 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 53.6732 | 538.9344 | 0 | 0.05921 | 3.6783 | 0 | 0 | 0 | 122.2056 | off_peak | 538.9344 |  |  | 18.48 | 0 | 81.52 | 449.5059 | 0
2510 | 642.53 | 181.228 | 29.9 | 28.841 | 28.841 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 53.6732 | 613.689 | 0 | 0.05921 | 3.9948 | 0 | 0 | 0 | 28.841 | off_peak | 613.689 |  |  | 4.49 | 0 | 95.51 | 115.2143 | 0
2511 | 689.79 | 227.625 | 30 | 36.2115 | 36.2115 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 53.6732 | 653.5785 | 0 | 0.05921 | 4.3036 | 0 | 0 | 0 | 36.2115 | off_peak | 653.5785 |  |  | 5.25 | 0 | 94.75 | 155.8393 | 0
2512 | 662.83 | 500.496 | 29.9 | 79.6501 | 79.6501 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 53.6732 | 583.1799 | 0 | 0.05921 | 4.71 | 0 | 0 | 0 | 79.6501 | off_peak | 583.1799 |  |  | 12.02 | 0 | 87.98 | 375.1506 | 0
2513 | 670.66 | 81.6799 | 29.6 | 13.013 | 13.013 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 53.6732 | 657.647 | 0 | 0.05921 | 5.2421 | 0 | 0 | 0 | 13.013 | off_peak | 657.647 |  |  | 1.94 | 0 | 98.06 | 68.2157 | 0
2514 | 632.73 | 44.9093 | 29 | 7.1705 | 7.1705 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 65.2371 | 637.9218 | 0 | 0.05921 | 5.7883 | 0 | 0 | 0 | 7.1705 | off_peak | 625.5595 | 0 | 100 | 1.13 | 0 | 98.87 | 41.505 | 0
2515 | 608.01 | 7.6 | 28.6 | 1.2152 | 1.2152 | 0 | 0 | 8.9371 | 8.9371 | 0 | 0 | 0 | 73.597 | 615.7319 | 0 | 0.05921 | 6.2443 | 0 | 0 | 0 | 1.2152 | off_peak | 606.7948 | 0 | 100 | 0.2 | 0 | 99.8 | 7.5884 | 0
2516 | 608.31 | 0 | 27.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 73.597 | 608.31 | 0 | 0.05921 | 6.7467 | 0 | 0 | 0 | 0 | off_peak | 608.31 |  |  | 0 | 0 | 100 | 0 | 0
2517 | 594.57 | 0 | 26.9 | 0 | 0 | 0 | 0 | 0.57721 | 0.57721 | 0 | 0 | 0 | 74.137 | 595.1472 | 0 | 0.05921 | 7.101 | 0 | 0 | 0 | 0 | off_peak | 594.57 | 0 | 100 | 0 | 0 | 100 | 0 | 0
2518 | 543.93 | 0 | 26.1 | 0 | 0 | 0 | 0 | 0.037279 | 0.037279 | 0 | 0 | 0 | 74.1718 | 543.9673 | 0 | 0.05921 | 7.3343 | 0 | 0 | 0 | 0 | off_peak | 543.93 | 0 | 100 | 0 | 0 | 100 | 0 | 0
2519 | 529.49 | 0 | 25.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1718 | 529.49 | 0 | 0.05921 | 7.4876 | 0 | 0 | 0 | 0 | off_peak | 529.49 |  |  | 0 | 0 | 100 | 0 | 0
2520 | 545.3 | 0 | 24.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1718 | 545.3 | 0 | 0.05921 | 7.6233 | 0 | 0 | 0 | 0 | off_peak | 545.3 |  |  | 0 | 0 | 100 | 0 | 0
2521 | 492.5 | 0 | 24.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1718 | 492.5 | 0 | 0.05921 | 7.3131 | 0 | 0 | 0 | 0 | off_peak | 492.5 |  |  | 0 | 0 | 100 | 0 | 0
2522 | 542.13 | 0 | 23.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1718 | 542.13 | 0 | 0.05921 | 6.9723 | 0 | 0 | 0 | 0 | off_peak | 542.13 |  |  | 0 | 0 | 100 | 0 | 0
2523 | 503.65 | 0 | 23.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1718 | 503.65 | 0 | 0.05921 | 6.6138 | 0 | 0 | 0 | 0 | off_peak | 503.65 |  |  | 0 | 0 | 100 | 0 | 0
2524 | 547.75 | 0 | 23.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1718 | 547.75 | 0 | 0.05921 | 6.1346 | 0 | 0 | 0 | 0 | off_peak | 547.75 |  |  | 0 | 0 | 100 | 0 | 0
2525 | 516.96 | 0 | 23.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1718 | 516.96 | 0 | 0.05921 | 5.4552 | 0 | 0 | 0 | 0 | off_peak | 516.96 |  |  | 0 | 0 | 100 | 0 | 0
2526 | 605.96 | 0 | 23.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1718 | 605.96 | 0 | 0.05921 | 4.8246 | 0 | 0 | 0 | 0 | off_peak | 605.96 |  |  | 0 | 0 | 100 | 0 | 0
2527 | 658.94 | 67.1673 | 23.9 | 10.9242 | 10.9242 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1718 | 648.0158 | 0 | 0.05921 | 4.4158 | 0 | 0 | 0 | 10.9242 | off_peak | 648.0158 |  |  | 1.66 | 0 | 98.34 | 48.2391 | 0
2528 | 702.36 | 270.528 | 24.9 | 43.8413 | 43.8413 | 0 | 0 | 0.0024077 | 0.0024077 | 0 | 0 | 0 | 74.1741 | 658.5211 | 0 | 0.05921 | 4.0924 | 0 | 0 | 0 | 43.8413 | off_peak | 658.5187 | 0 | 100 | 6.24 | 0 | 93.76 | 179.4159 | 0
2529 | 676.1 | 487.683 | 25.8 | 78.7771 | 78.7771 | 0 | 0 | 0.0001555 | 0.0001555 | 0 | 0 | 0 | 74.1742 | 597.323 | 0 | 0.05921 | 3.8265 | 0 | 0 | 0 | 78.7771 | off_peak | 597.3229 | 0 | 100 | 11.65 | 0 | 88.35 | 301.4374 | 0
2530 | 680.98 | 610.91 | 26.8 | 98.3261 | 98.3261 | 0 | 0 | 1.0737e-05 | 1.0737e-05 | 0 | 0 | 0 | 74.1743 | 582.6539 | 0 | 0.05921 | 3.6645 | 0 | 0 | 0 | 98.3261 | off_peak | 582.6539 | 0 | 100 | 14.44 | 0 | 85.56 | 360.3164 | 0
2531 | 683.7 | 828.885 | 27.8 | 132.9258 | 132.9258 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1743 | 550.7742 | 0 | 0.05921 | 3.6005 | 0 | 0 | 0 | 132.9258 | off_peak | 550.7742 |  |  | 19.44 | 0 | 80.56 | 478.6012 | 0
2532 | 688 | 908.665 | 28.6 | 145.296 | 145.296 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1743 | 542.704 | 0 | 0.05921 | 3.6497 | 0 | 0 | 0 | 145.296 | off_peak | 542.704 |  |  | 21.12 | 0 | 78.88 | 530.2901 | 0
2533 | 694.46 | 882.516 | 29.1 | 140.8574 | 140.8574 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1743 | 553.6026 | 0 | 0.05921 | 3.7668 | 0 | 0 | 0 | 140.8574 | off_peak | 553.6026 |  |  | 20.28 | 0 | 79.72 | 530.5878 | 0
2534 | 634.59 | 900.782 | 29.5 | 143.5627 | 143.5627 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1743 | 491.0273 | 0 | 0.05921 | 4.1781 | 0 | 0 | 0 | 143.5627 | off_peak | 491.0273 |  |  | 22.62 | 0 | 77.38 | 599.8261 | 0
2535 | 676.7 | 790.116 | 29.5 | 125.9252 | 125.9252 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1743 | 550.7748 | 0 | 0.05921 | 4.7296 | 0 | 0 | 0 | 125.9252 | off_peak | 550.7748 |  |  | 18.61 | 0 | 81.39 | 595.5721 | 0
2536 | 672.58 | 626.502 | 29.4 | 99.8857 | 99.8857 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1743 | 572.6943 | 0 | 0.05921 | 5.0743 | 0 | 0 | 0 | 99.8857 | off_peak | 572.6943 |  |  | 14.85 | 0 | 85.15 | 506.8494 | 0
2537 | 704.19 | 422.725 | 29.1 | 67.4707 | 67.4707 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1743 | 636.7193 | 0 | 0.05921 | 5.5262 | 0 | 0 | 0 | 67.4707 | off_peak | 636.7193 |  |  | 9.58 | 0 | 90.42 | 372.8543 | 0
2538 | 609.11 | 204.361 | 28.7 | 32.6655 | 32.6655 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1743 | 576.4445 | 0 | 0.05921 | 6.0009 | 0 | 0 | 0 | 32.6655 | off_peak | 576.4445 |  |  | 5.36 | 0 | 94.64 | 196.0232 | 0
2539 | 579.58 | 22.546 | 28.4 | 3.6077 | 3.6077 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1743 | 575.9723 | 0 | 0.05921 | 6.5461 | 0 | 0 | 0 | 3.6077 | off_peak | 575.9723 |  |  | 0.62 | 0 | 99.38 | 23.6166 | 0
2540 | 540.12 | 0 | 27.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1743 | 540.12 | 0 | 0.05921 | 6.9299 | 0 | 0 | 0 | 0 | off_peak | 540.12 |  |  | 0 | 0 | 100 | 0 | 0
2541 | 523.27 | 0 | 27.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1743 | 523.27 | 0 | 0.05921 | 7.1424 | 0 | 0 | 0 | 0 | off_peak | 523.27 |  |  | 0 | 0 | 100 | 0 | 0
2542 | 499.71 | 0 | 26.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1743 | 499.71 | 0 | 0.05921 | 7.3416 | 0 | 0 | 0 | 0 | off_peak | 499.71 |  |  | 0 | 0 | 100 | 0 | 0
2543 | 506.68 | 0 | 26 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1743 | 506.68 | 0 | 0.05921 | 7.4461 | 0 | 0 | 0 | 0 | off_peak | 506.68 |  |  | 0 | 0 | 100 | 0 | 0
2544 | 513.47 | 0 | 25.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1743 | 513.47 | 0 | 0.05921 | 7.3655 | 0 | 0 | 0 | 0 | off_peak | 513.47 |  |  | 0 | 0 | 100 | 0 | 0
2545 | 500.03 | 0 | 24.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1743 | 500.03 | 0 | 0.05921 | 7.1996 | 0 | 0 | 0 | 0 | off_peak | 500.03 |  |  | 0 | 0 | 100 | 0 | 0
2546 | 518.96 | 0 | 24.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1743 | 518.96 | 0 | 0.05921 | 6.8494 | 0 | 0 | 0 | 0 | off_peak | 518.96 |  |  | 0 | 0 | 100 | 0 | 0
2547 | 492.38 | 0 | 23.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1743 | 492.38 | 0 | 0.05921 | 6.3041 | 0 | 0 | 0 | 0 | off_peak | 492.38 |  |  | 0 | 0 | 100 | 0 | 0
2548 | 502.36 | 0 | 23.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1743 | 502.36 | 0 | 0.05921 | 5.6733 | 0 | 0 | 0 | 0 | off_peak | 502.36 |  |  | 0 | 0 | 100 | 0 | 0
2549 | 538.02 | 0 | 23.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1743 | 538.02 | 0 | 0.05921 | 4.8751 | 0 | 0 | 0 | 0 | off_peak | 538.02 |  |  | 0 | 0 | 100 | 0 | 0
2550 | 608.5 | 0 | 23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1743 | 608.5 | 0 | 0.05921 | 4.1615 | 0 | 0 | 0 | 0 | off_peak | 608.5 |  |  | 0 | 0 | 100 | 0 | 0
2551 | 678.04 | 71.341 | 23.3 | 11.628 | 11.628 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1743 | 666.412 | 0 | 0.05921 | 3.8777 | 0 | 0 | 0 | 11.628 | off_peak | 666.412 |  |  | 1.71 | 0 | 98.29 | 45.0894 | 0
2552 | 730.1 | 277.644 | 24.1 | 45.1241 | 45.1241 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1743 | 684.9759 | 0 | 0.05921 | 3.6214 | 0 | 0 | 0 | 45.1241 | off_peak | 684.9759 |  |  | 6.18 | 0 | 93.82 | 163.4115 | 0
2553 | 783.61 | 497.059 | 25.2 | 80.4656 | 80.4656 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1743 | 703.1444 | 0 | 0.05921 | 3.4511 | 0 | 0 | 0 | 80.4656 | off_peak | 703.1444 |  |  | 10.27 | 0 | 89.73 | 277.6913 | 0
2554 | 765.53 | 690.397 | 26.2 | 111.3611 | 111.3611 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1743 | 654.1689 | 0 | 0.05921 | 3.4006 | 0 | 0 | 0 | 111.3611 | off_peak | 654.1689 |  |  | 14.55 | 0 | 85.45 | 378.6962 | 0
2555 | 743.87 | 839.222 | 27.1 | 134.9262 | 134.9262 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1743 | 608.9438 | 0 | 0.05921 | 3.5994 | 0 | 0 | 0 | 134.9262 | off_peak | 608.9438 |  |  | 18.14 | 0 | 81.86 | 485.6486 | 0
2556 | 804.47 | 927.606 | 27.9 | 148.7033 | 148.7033 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1743 | 655.7667 | 0 | 0.05921 | 4.0271 | 0 | 0 | 0 | 148.7033 | off_peak | 655.7667 |  |  | 18.48 | 0 | 81.52 | 598.8485 | 0
2557 | 753.46 | 948.502 | 28.6 | 151.6659 | 151.6659 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1743 | 601.7941 | 0 | 0.088511 | 4.3354 | 0 | 0 | 0 | 151.6659 | on_peak | 601.7941 |  |  | 20.13 | 0 | 79.87 | 657.5399 | 0
2558 | 820.09 | 902.941 | 29.1 | 144.1174 | 144.1174 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1743 | 675.9726 | 0 | 0.088511 | 4.467 | 0 | 0 | 0 | 144.1174 | on_peak | 675.9726 |  |  | 17.57 | 0 | 82.43 | 643.7787 | 0
2559 | 869.79 | 792.826 | 29.4 | 126.4034 | 126.4034 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1743 | 743.3866 | 0 | 0.088511 | 4.6037 | 0 | 0 | 0 | 126.4034 | on_peak | 743.3866 |  |  | 14.53 | 0 | 85.47 | 581.9189 | 0
2560 | 811.4 | 629.058 | 29.5 | 100.2565 | 100.2565 | 0 | 0 | 0 | 0 | 62.4453 | 62.4453 | 0 | 7.4174 | 648.6982 | 0 | 0.088511 | 4.7024 | 0 | 0 | 0 | 100.2565 | on_peak | 648.6982 |  |  | 12.36 | 7.7 | 79.95 | 471.4446 | 0
2561 | 852.78 | 399.046 | 29.2 | 63.668 | 63.668 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 789.112 | 0 | 0.088511 | 4.9192 | 0 | 0 | 0 | 63.668 | on_peak | 789.112 |  |  | 7.47 | 0 | 92.53 | 313.1986 | 0
2562 | 853.87 | 180.421 | 28.4 | 28.8704 | 28.8704 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 824.9996 | 0 | 0.088511 | 4.9309 | 0 | 0 | 0 | 28.8704 | on_peak | 824.9996 |  |  | 3.38 | 0 | 96.62 | 142.3562 | 0
2563 | 766.5 | 17.0003 | 27.9 | 2.7253 | 2.7253 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 763.7747 | 0 | 0.088511 | 4.7179 | 0 | 0 | 0 | 2.7253 | on_peak | 763.7747 |  |  | 0.36 | 0 | 99.64 | 12.8578 | 0
2564 | 815.05 | 0 | 26.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 815.05 | 0 | 0.088511 | 4.6502 | 0 | 0 | 0 | 0 | on_peak | 815.05 |  |  | 0 | 0 | 100 | 0 | 0
2565 | 820.96 | 0 | 26 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 820.96 | 0 | 0.088511 | 4.8674 | 0 | 0 | 0 | 0 | on_peak | 820.96 |  |  | 0 | 0 | 100 | 0 | 0
2566 | 712.62 | 0 | 25.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 712.62 | 0 | 0.05921 | 5.2589 | 0 | 0 | 0 | 0 | off_peak | 712.62 |  |  | 0 | 0 | 100 | 0 | 0
2567 | 803.32 | 0 | 24.7 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 18.9814 | 815.6824 | 0 | 0.05921 | 5.6452 | 0 | 0 | 0 | 0 | off_peak | 803.32 | 0 | 100 | 0 | 0 | 100 | 0 | 0
2568 | 773.42 | 0 | 24.1 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 30.5453 | 785.7824 | 0 | 0.05921 | 6.0349 | 0 | 0 | 0 | 0 | off_peak | 773.42 | 0 | 100 | 0 | 0 | 100 | 0 | 0
2569 | 725.89 | 0 | 23.6 | 0 | 0 | 0 | 0 | 8.7006 | 8.7006 | 0 | 0 | 0 | 38.684 | 734.5906 | 0 | 0.05921 | 6.179 | 0 | 0 | 0 | 0 | off_peak | 725.89 | 0 | 100 | 0 | 0 | 100 | 0 | 0
2570 | 645.9 | 0 | 23.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 38.684 | 645.9 | 0 | 0.05921 | 6.1386 | 0 | 0 | 0 | 0 | off_peak | 645.9 |  |  | 0 | 0 | 100 | 0 | 0
2571 | 596.3 | 0 | 22.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 38.684 | 596.3 | 0 | 0.05921 | 5.7347 | 0 | 0 | 0 | 0 | off_peak | 596.3 |  |  | 0 | 0 | 100 | 0 | 0
2572 | 587.87 | 0 | 21.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 38.684 | 587.87 | 0 | 0.05921 | 5.1506 | 0 | 0 | 0 | 0 | off_peak | 587.87 |  |  | 0 | 0 | 100 | 0 | 0
2573 | 551.97 | 0 | 21.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 38.684 | 551.97 | 0 | 0.05921 | 4.4078 | 0 | 0 | 0 | 0 | off_peak | 551.97 |  |  | 0 | 0 | 100 | 0 | 0
2574 | 642.82 | 0 | 20.5 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 50.2479 | 655.1824 | 0 | 0.05921 | 3.6095 | 0 | 0 | 0 | 0 | off_peak | 642.82 | 0 | 100 | 0 | 0 | 100 | 0 | 0
2575 | 663.51 | 67.2562 | 20.1 | 11.0877 | 11.0877 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 61.8119 | 664.7847 | 0 | 0.05921 | 3.2063 | 0 | 0 | 0 | 11.0877 | off_peak | 652.4223 | 0 | 100 | 1.67 | 0 | 98.33 | 35.5509 | 0
2576 | 773.6 | 264.669 | 20.4 | 43.5864 | 43.5864 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 73.3758 | 742.376 | 0 | 0.05921 | 2.9522 | 0 | 0 | 0 | 43.5864 | off_peak | 730.0136 | 0 | 100 | 5.63 | 0 | 94.37 | 128.6737 | 0
2577 | 725.61 | 481.026 | 21 | 79.0483 | 79.0483 | 0 | 0 | 0.79843 | 0.79843 | 0 | 0 | 0 | 74.1227 | 647.3601 | 0 | 0.05921 | 2.8306 | 0 | 0 | 0 | 79.0483 | off_peak | 646.5617 | 0 | 100 | 10.89 | 0 | 89.11 | 223.7542 | 0
2578 | 775.65 | 674.15 | 21.8 | 110.4704 | 110.4704 | 0 | 0 | 0.051567 | 0.051567 | 0 | 0 | 0 | 74.1709 | 665.2311 | 0 | 0.05921 | 2.7738 | 0 | 0 | 0 | 110.4704 | off_peak | 665.1796 | 0 | 100 | 14.24 | 0 | 85.76 | 306.4247 | 0
2579 | 756.75 | 743.829 | 22.5 | 121.5848 | 121.5848 | 0 | 0 | 0.0033305 | 0.0033305 | 0 | 0 | 0 | 74.174 | 635.1685 | 0 | 0.05921 | 2.8615 | 0 | 0 | 0 | 121.5848 | off_peak | 635.1652 | 0 | 100 | 16.07 | 0 | 83.93 | 347.9181 | 0
2580 | 774.67 | 586.612 | 23.1 | 95.6812 | 95.6812 | 0 | 0 | 0.0002151 | 0.0002151 | 0 | 0 | 0 | 74.1742 | 678.9891 | 0 | 0.05921 | 3.512 | 0 | 0 | 0 | 95.6812 | off_peak | 678.9888 | 0 | 100 | 12.35 | 0 | 87.65 | 336.0324 | 0
2581 | 754.92 | 900.866 | 23.5 | 146.7284 | 146.7284 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1742 | 608.1916 | 0 | 0.088511 | 3.722 | 0 | 0 | 0 | 146.7284 | on_peak | 608.1916 |  |  | 19.44 | 0 | 80.56 | 546.1191 | 0
2582 | 774.09 | 881.482 | 23.6 | 143.5198 | 143.5198 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1742 | 630.5702 | 0 | 0.088511 | 3.5685 | 0 | 0 | 0 | 143.5198 | on_peak | 630.5702 |  |  | 18.54 | 0 | 81.46 | 512.1487 | 0
2583 | 812.02 | 682.641 | 23.6 | 111.1452 | 111.1452 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1742 | 700.8748 | 0 | 0.088511 | 3.2724 | 0 | 0 | 0 | 111.1452 | on_peak | 700.8748 |  |  | 13.69 | 0 | 86.31 | 363.711 | 0
2584 | 777.86 | 522.992 | 23.3 | 85.2432 | 85.2432 | 0 | 0 | 0 | 0 | 62.4453 | 62.4453 | 0 | 7.4174 | 630.1715 | 0 | 0.088511 | 3.172 | 0 | 0 | 0 | 85.2432 | on_peak | 630.1715 |  |  | 10.96 | 8.03 | 81.01 | 270.3893 | 0
2585 | 789.19 | 86.7342 | 22.9 | 14.1572 | 14.1572 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 775.0328 | 0 | 0.088511 | 3.2868 | 0 | 0 | 0 | 14.1572 | on_peak | 775.0328 |  |  | 1.79 | 0 | 98.21 | 46.5312 | 0
2586 | 756.42 | 62.1655 | 22.1 | 10.176 | 10.176 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 746.244 | 0 | 0.088511 | 3.562 | 0 | 0 | 0 | 10.176 | on_peak | 746.244 |  |  | 1.35 | 0 | 98.65 | 36.2467 | 0
2587 | 715.23 | 13.3 | 21.6 | 2.181 | 2.181 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 713.049 | 0 | 0.088511 | 3.8727 | 0 | 0 | 0 | 2.181 | on_peak | 713.049 |  |  | 0.3 | 0 | 99.7 | 8.4462 | 0
2588 | 759.9 | 0 | 20.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 759.9 | 0 | 0.088511 | 4.1315 | 0 | 0 | 0 | 0 | on_peak | 759.9 |  |  | 0 | 0 | 100 | 0 | 0
2589 | 740.84 | 0 | 20.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 740.84 | 0 | 0.088511 | 4.4589 | 0 | 0 | 0 | 0 | on_peak | 740.84 |  |  | 0 | 0 | 100 | 0 | 0
2590 | 706.98 | 0 | 19.8 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 18.9814 | 719.3424 | 0 | 0.05921 | 4.9351 | 0 | 0 | 0 | 0 | off_peak | 706.98 | 0 | 100 | 0 | 0 | 100 | 0 | 0
2591 | 727.08 | 0 | 19.7 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 30.5453 | 739.4424 | 0 | 0.05921 | 5.497 | 0 | 0 | 0 | 0 | off_peak | 727.08 | 0 | 100 | 0 | 0 | 100 | 0 | 0
2592 | 699.09 | 0 | 19.7 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 42.1093 | 711.4524 | 0 | 0.05921 | 6.0801 | 0 | 0 | 0 | 0 | off_peak | 699.09 | 0 | 100 | 0 | 0 | 100 | 0 | 0
2593 | 656.28 | 0 | 19.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 42.1093 | 656.28 | 0 | 0.05921 | 6.2489 | 0 | 0 | 0 | 0 | off_peak | 656.28 |  |  | 0 | 0 | 100 | 0 | 0
2594 | 628.19 | 0 | 19.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 42.1093 | 628.19 | 0 | 0.05921 | 6.1388 | 0 | 0 | 0 | 0 | off_peak | 628.19 |  |  | 0 | 0 | 100 | 0 | 0
2595 | 585.51 | 0 | 19.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 42.1093 | 585.51 | 0 | 0.05921 | 5.7274 | 0 | 0 | 0 | 0 | off_peak | 585.51 |  |  | 0 | 0 | 100 | 0 | 0
2596 | 545.56 | 0 | 19.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 42.1093 | 545.56 | 0 | 0.05921 | 5.1162 | 0 | 0 | 0 | 0 | off_peak | 545.56 |  |  | 0 | 0 | 100 | 0 | 0
2597 | 565.9 | 0 | 19.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 42.1093 | 565.9 | 0 | 0.05921 | 4.339 | 0 | 0 | 0 | 0 | off_peak | 565.9 |  |  | 0 | 0 | 100 | 0 | 0
2598 | 646.86 | 0 | 19.9 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 53.6732 | 659.2224 | 0 | 0.05921 | 3.647 | 0 | 0 | 0 | 0 | off_peak | 646.86 | 0 | 100 | 0 | 0 | 100 | 0 | 0
2599 | 674.69 | 72.5201 | 20.5 | 11.9386 | 11.9386 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 65.2371 | 675.1138 | 0 | 0.05921 | 3.2575 | 0 | 0 | 0 | 11.9386 | off_peak | 662.7514 | 0 | 100 | 1.77 | 0 | 98.23 | 38.89 | 0
2600 | 732.21 | 277.483 | 21.2 | 45.5672 | 45.5672 | 0 | 0 | 8.9371 | 8.9371 | 0 | 0 | 0 | 73.597 | 695.5799 | 0 | 0.05921 | 3.0092 | 0 | 0 | 0 | 45.5672 | off_peak | 686.6428 | 0 | 100 | 6.22 | 0 | 93.78 | 137.1226 | 0
2601 | 759.57 | 499.31 | 21.7 | 81.8492 | 81.8492 | 0 | 0 | 0.57721 | 0.57721 | 0 | 0 | 0 | 74.137 | 678.298 | 0 | 0.05921 | 2.8781 | 0 | 0 | 0 | 81.8492 | off_peak | 677.7208 | 0 | 100 | 10.78 | 0 | 89.22 | 235.5697 | 0
2602 | 785.04 | 695.243 | 22.2 | 113.7647 | 113.7647 | 0 | 0 | 0.037279 | 0.037279 | 0 | 0 | 0 | 74.1718 | 671.3126 | 0 | 0.05921 | 2.8629 | 0 | 0 | 0 | 113.7647 | off_peak | 671.2753 | 0 | 100 | 14.49 | 0 | 85.51 | 325.698 | 0
2603 | 757.13 | 844.726 | 22.6 | 138.028 | 138.028 | 0 | 0 | 0.0024077 | 0.0024077 | 0 | 0 | 0 | 74.1741 | 619.1044 | 0 | 0.05921 | 3.1031 | 0 | 0 | 0 | 138.028 | off_peak | 619.102 | 0 | 100 | 18.23 | 0 | 81.77 | 428.3203 | 0
2604 | 818.07 | 625.592 | 22.9 | 102.1121 | 102.1121 | 0 | 0 | 0.0001555 | 0.0001555 | 0 | 0 | 0 | 74.1742 | 715.9581 | 0 | 0.05921 | 3.5635 | 0 | 0 | 0 | 102.1121 | off_peak | 715.9579 | 0 | 100 | 12.48 | 0 | 87.52 | 363.8801 | 0
2605 | 735.69 | 951.551 | 23.1 | 155.2057 | 155.2057 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1742 | 580.4843 | 0 | 0.088511 | 3.8124 | 0 | 0 | 0 | 155.2057 | on_peak | 580.4843 |  |  | 21.1 | 0 | 78.9 | 591.71 | 0
2606 | 789.82 | 902.437 | 23.2 | 147.1421 | 147.1421 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1742 | 642.6779 | 0 | 0.088511 | 3.7882 | 0 | 0 | 0 | 147.1421 | on_peak | 642.6779 |  |  | 18.63 | 0 | 81.37 | 557.4019 | 0
2607 | 828.05 | 715.672 | 23.2 | 116.6901 | 116.6901 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1742 | 711.3599 | 0 | 0.088511 | 3.6534 | 0 | 0 | 0 | 116.6901 | on_peak | 711.3599 |  |  | 14.09 | 0 | 85.91 | 426.3121 | 0
2608 | 795.11 | 620.844 | 23.1 | 101.2647 | 101.2647 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1742 | 693.8453 | 0 | 0.088511 | 3.662 | 0 | 0 | 0 | 101.2647 | on_peak | 693.8453 |  |  | 12.74 | 0 | 87.26 | 370.8272 | 0
2609 | 814.66 | 415.096 | 22.8 | 67.7781 | 67.7781 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1742 | 746.8819 | 0 | 0.088511 | 3.8644 | 0 | 0 | 0 | 67.7781 | on_peak | 746.8819 |  |  | 8.32 | 0 | 91.68 | 261.9228 | 0
2610 | 789.47 | 197.767 | 22.5 | 32.3266 | 32.3266 | 0 | 0 | 0 | 0 | 62.4453 | 62.4453 | 0 | 7.4174 | 694.6981 | 0 | 0.088511 | 4.0262 | 0 | 0 | 0 | 32.3266 | on_peak | 694.6981 |  |  | 4.09 | 7.91 | 88 | 130.1548 | 0
2611 | 764.73 | 22.3319 | 22.3 | 3.6529 | 3.6529 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 761.0771 | 0 | 0.088511 | 4.2951 | 0 | 0 | 0 | 3.6529 | on_peak | 761.0771 |  |  | 0.48 | 0 | 99.52 | 15.6895 | 0
2612 | 758.26 | 0 | 21.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 758.26 | 0 | 0.088511 | 4.5318 | 0 | 0 | 0 | 0 | on_peak | 758.26 |  |  | 0 | 0 | 100 | 0 | 0
2613 | 764.15 | 0 | 21.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 764.15 | 0 | 0.088511 | 4.88 | 0 | 0 | 0 | 0 | on_peak | 764.15 |  |  | 0 | 0 | 100 | 0 | 0
2614 | 704.84 | 0 | 21.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 704.84 | 0 | 0.05921 | 5.3628 | 0 | 0 | 0 | 0 | off_peak | 704.84 |  |  | 0 | 0 | 100 | 0 | 0
2615 | 725.59 | 0 | 21.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 725.59 | 0 | 0.05921 | 5.7525 | 0 | 0 | 0 | 0 | off_peak | 725.59 |  |  | 0 | 0 | 100 | 0 | 0
2616 | 734.97 | 0 | 21.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 734.97 | 0 | 0.05921 | 6.1863 | 0 | 0 | 0 | 0 | off_peak | 734.97 |  |  | 0 | 0 | 100 | 0 | 0
2617 | 693.34 | 0 | 21.8 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 18.9814 | 705.7024 | 0 | 0.05921 | 6.3904 | 0 | 0 | 0 | 0 | off_peak | 693.34 | 0 | 100 | 0 | 0 | 100 | 0 | 0
2618 | 639.66 | 0 | 21.8 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 30.5453 | 652.0224 | 0 | 0.05921 | 6.3206 | 0 | 0 | 0 | 0 | off_peak | 639.66 | 0 | 100 | 0 | 0 | 100 | 0 | 0
2619 | 588.34 | 0 | 21.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30.5453 | 588.34 | 0 | 0.05921 | 5.9353 | 0 | 0 | 0 | 0 | off_peak | 588.34 |  |  | 0 | 0 | 100 | 0 | 0
2620 | 557.03 | 0 | 21.8 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 42.1093 | 569.3924 | 0 | 0.05921 | 5.3462 | 0 | 0 | 0 | 0 | off_peak | 557.03 | 0 | 100 | 0 | 0 | 100 | 0 | 0
2621 | 582.98 | 0 | 21.8 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 53.6732 | 595.3424 | 0 | 0.05921 | 4.4911 | 0 | 0 | 0 | 0 | off_peak | 582.98 | 0 | 100 | 0 | 0 | 100 | 0 | 0
2622 | 636 | 0 | 21.9 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 65.2371 | 648.3624 | 0 | 0.05921 | 3.8093 | 0 | 0 | 0 | 0 | off_peak | 636 | 0 | 100 | 0 | 0 | 100 | 0 | 0
2623 | 728.97 | 72.2921 | 22.4 | 11.8209 | 11.8209 | 0 | 0 | 8.9371 | 8.9371 | 0 | 0 | 0 | 73.597 | 726.0862 | 0 | 0.05921 | 3.4277 | 0 | 0 | 0 | 11.8209 | off_peak | 717.1491 | 0 | 100 | 1.62 | 0 | 98.38 | 40.5184 | 0
2624 | 736.89 | 286.87 | 22.9 | 46.8243 | 46.8243 | 0 | 0 | 0.57721 | 0.57721 | 0 | 0 | 0 | 74.137 | 690.6429 | 0 | 0.05921 | 3.2005 | 0 | 0 | 0 | 46.8243 | off_peak | 690.0657 | 0 | 100 | 6.35 | 0 | 93.65 | 149.8606 | 0
2625 | 764.53 | 507.973 | 23.4 | 82.7656 | 82.7656 | 0 | 0 | 0.037279 | 0.037279 | 0 | 0 | 0 | 74.1718 | 681.8017 | 0 | 0.05921 | 3.0654 | 0 | 0 | 0 | 82.7656 | off_peak | 681.7644 | 0 | 100 | 10.83 | 0 | 89.17 | 253.71 | 0
2626 | 799.26 | 702.105 | 23.9 | 114.1914 | 114.1914 | 0 | 0 | 0.0024077 | 0.0024077 | 0 | 0 | 0 | 74.1741 | 685.071 | 0 | 0.05921 | 3.0701 | 0 | 0 | 0 | 114.1914 | off_peak | 685.0686 | 0 | 100 | 14.29 | 0 | 85.71 | 350.5758 | 0
2627 | 751.32 | 694.065 | 24.3 | 112.7219 | 112.7219 | 0 | 0 | 0.0001555 | 0.0001555 | 0 | 0 | 0 | 74.1742 | 638.5983 | 0 | 0.05921 | 3.3146 | 0 | 0 | 0 | 112.7219 | off_peak | 638.5981 | 0 | 100 | 15 | 0 | 85 | 373.6236 | 0
2628 | 819 | 938.19 | 24.6 | 152.2056 | 152.2056 | 0 | 0 | 1.0043e-05 | 1.0043e-05 | 0 | 0 | 0 | 74.1743 | 666.7944 | 0 | 0.05921 | 3.8337 | 0 | 0 | 0 | 152.2056 | off_peak | 666.7944 | 0 | 100 | 18.58 | 0 | 81.42 | 583.508 | 0
2629 | 740.19 | 884.843 | 24.7 | 143.4994 | 143.4994 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1743 | 596.6906 | 0 | 0.088511 | 4.0011 | 0 | 0 | 0 | 143.4994 | on_peak | 596.6906 |  |  | 19.39 | 0 | 80.61 | 574.1614 | 0
2630 | 794.76 | 776.271 | 24.7 | 125.8917 | 125.8917 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1743 | 668.8683 | 0 | 0.088511 | 3.9887 | 0 | 0 | 0 | 125.8917 | on_peak | 668.8683 |  |  | 15.84 | 0 | 84.16 | 502.1483 | 0
2631 | 804.37 | 688.945 | 24.5 | 111.81 | 111.81 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1743 | 692.56 | 0 | 0.088511 | 3.9489 | 0 | 0 | 0 | 111.81 | on_peak | 692.56 |  |  | 13.9 | 0 | 86.1 | 441.5295 | 0
2632 | 805.58 | 593.127 | 24.3 | 96.3287 | 96.3287 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1743 | 709.2513 | 0 | 0.088511 | 4.0655 | 0 | 0 | 0 | 96.3287 | on_peak | 709.2513 |  |  | 11.96 | 0 | 88.04 | 391.6286 | 0
2633 | 834.38 | 285.828 | 24 | 46.4708 | 46.4708 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1743 | 787.9092 | 0 | 0.088511 | 4.4911 | 0 | 0 | 0 | 46.4708 | on_peak | 787.9092 |  |  | 5.57 | 0 | 94.43 | 208.706 | 0
2634 | 818.15 | 104.943 | 23.6 | 17.0864 | 17.0864 | 0 | 0 | 0 | 0 | 62.4453 | 62.4453 | 0 | 7.4174 | 738.6183 | 0 | 0.088511 | 4.9188 | 0 | 0 | 0 | 17.0864 | on_peak | 738.6183 |  |  | 2.09 | 7.63 | 90.28 | 84.0454 | 0
2635 | 764.47 | 18.3967 | 23.4 | 2.9974 | 2.9974 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 761.4726 | 0 | 0.088511 | 5.1398 | 0 | 0 | 0 | 2.9974 | on_peak | 761.4726 |  |  | 0.39 | 0 | 99.61 | 15.4062 | 0
2636 | 792.24 | 0 | 23.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 792.24 | 0 | 0.088511 | 5.3769 | 0 | 0 | 0 | 0 | on_peak | 792.24 |  |  | 0 | 0 | 100 | 0 | 0
2637 | 745.63 | 0 | 23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 745.63 | 0 | 0.088511 | 5.7109 | 0 | 0 | 0 | 0 | on_peak | 745.63 |  |  | 0 | 0 | 100 | 0 | 0
2638 | 724.39 | 0 | 22.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 724.39 | 0 | 0.05921 | 5.987 | 0 | 0 | 0 | 0 | off_peak | 724.39 |  |  | 0 | 0 | 100 | 0 | 0
2639 | 716.29 | 0 | 22.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 716.29 | 0 | 0.05921 | 6.4292 | 0 | 0 | 0 | 0 | off_peak | 716.29 |  |  | 0 | 0 | 100 | 0 | 0
2640 | 731.39 | 0 | 22.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 731.39 | 0 | 0.05921 | 6.762 | 0 | 0 | 0 | 0 | off_peak | 731.39 |  |  | 0 | 0 | 100 | 0 | 0
2641 | 687.05 | 0 | 22.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 687.05 | 0 | 0.05921 | 6.9511 | 0 | 0 | 0 | 0 | off_peak | 687.05 |  |  | 0 | 0 | 100 | 0 | 0
2642 | 660.79 | 0 | 22.8 | 0 | 0 | 0 | 0 | 8.7006 | 8.7006 | 0 | 0 | 0 | 15.5561 | 669.4906 | 0 | 0.05921 | 6.8504 | 0 | 0 | 0 | 0 | off_peak | 660.79 | 0 | 100 | 0 | 0 | 100 | 0 | 0
2643 | 601.38 | 0 | 22.8 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 27.12 | 613.7424 | 0 | 0.05921 | 6.3696 | 0 | 0 | 0 | 0 | off_peak | 601.38 | 0 | 100 | 0 | 0 | 100 | 0 | 0
2644 | 613.41 | 0 | 22.8 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 38.684 | 625.7724 | 0 | 0.05921 | 5.7607 | 0 | 0 | 0 | 0 | off_peak | 613.41 | 0 | 100 | 0 | 0 | 100 | 0 | 0
2645 | 602.03 | 0 | 22.9 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 50.2479 | 614.3924 | 0 | 0.05921 | 4.9324 | 0 | 0 | 0 | 0 | off_peak | 602.03 | 0 | 100 | 0 | 0 | 100 | 0 | 0
2646 | 649.72 | 0 | 23 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 61.8119 | 662.0824 | 0 | 0.05921 | 4.2795 | 0 | 0 | 0 | 0 | off_peak | 649.72 | 0 | 100 | 0 | 0 | 100 | 0 | 0
2647 | 693.36 | 77.9539 | 23.4 | 12.7013 | 12.7013 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 61.8119 | 680.6587 | 0 | 0.05921 | 3.8344 | 0 | 0 | 0 | 12.7013 | off_peak | 680.6587 |  |  | 1.83 | 0 | 98.17 | 48.7023 | 0
2648 | 732.88 | 285.878 | 23.9 | 46.4956 | 46.4956 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 73.3758 | 698.7467 | 0 | 0.05921 | 3.5552 | 0 | 0 | 0 | 46.4956 | off_peak | 686.3844 | 0 | 100 | 6.34 | 0 | 93.66 | 165.3007 | 0
2649 | 773.8 | 506.202 | 24.4 | 82.1819 | 82.1819 | 0 | 0 | 0.79843 | 0.79843 | 0 | 0 | 0 | 74.1227 | 692.4166 | 0 | 0.05921 | 3.3757 | 0 | 0 | 0 | 82.1819 | off_peak | 691.6181 | 0 | 100 | 10.62 | 0 | 89.38 | 277.422 | 0
2650 | 772.82 | 699.744 | 24.9 | 113.3993 | 113.3993 | 0 | 0 | 0.051567 | 0.051567 | 0 | 0 | 0 | 74.1709 | 659.4722 | 0 | 0.05921 | 3.3158 | 0 | 0 | 0 | 113.3993 | off_peak | 659.4207 | 0 | 100 | 14.67 | 0 | 85.33 | 376.0105 | 0
2651 | 784.61 | 849.234 | 25.2 | 137.4769 | 137.4769 | 0 | 0 | 0.0033305 | 0.0033305 | 0 | 0 | 0 | 74.174 | 647.1365 | 0 | 0.05921 | 3.4775 | 0 | 0 | 0 | 137.4769 | off_peak | 647.1331 | 0 | 100 | 17.52 | 0 | 82.48 | 478.0782 | 0
2652 | 811.24 | 930.431 | 25.5 | 150.4585 | 150.4585 | 0 | 0 | 0.0002151 | 0.0002151 | 0 | 0 | 0 | 74.1742 | 660.7817 | 0 | 0.05921 | 3.8976 | 0 | 0 | 0 | 150.4585 | off_peak | 660.7815 | 0 | 100 | 18.55 | 0 | 81.45 | 586.428 | 0
2653 | 766.74 | 956.92 | 25.6 | 154.6862 | 154.6862 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1742 | 612.0538 | 0 | 0.088511 | 4.1473 | 0 | 0 | 0 | 154.6862 | on_peak | 612.0538 |  |  | 20.17 | 0 | 79.83 | 641.5364 | 0
2654 | 772.38 | 695.169 | 25.7 | 112.3336 | 112.3336 | 0 | 0 | 0 | 0 | 62.4453 | 62.4453 | 0 | 7.4174 | 597.6011 | 0 | 0.088511 | 4.1462 | 0 | 0 | 0 | 112.3336 | on_peak | 597.6011 |  |  | 14.54 | 8.08 | 77.37 | 465.763 | 0
2655 | 821.07 | 568.675 | 25.6 | 91.9264 | 91.9264 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 729.1436 | 0 | 0.088511 | 4.2306 | 0 | 0 | 0 | 91.9264 | on_peak | 729.1436 |  |  | 11.2 | 0 | 88.8 | 388.8995 | 0
2656 | 805.24 | 432.128 | 25.3 | 69.9291 | 69.9291 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 735.3109 | 0 | 0.088511 | 4.5508 | 0 | 0 | 0 | 69.9291 | on_peak | 735.3109 |  |  | 8.68 | 0 | 91.32 | 318.2319 | 0
2657 | 780.99 | 342.605 | 25 | 55.502 | 55.502 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 725.488 | 0 | 0.088511 | 5.0228 | 0 | 0 | 0 | 55.502 | on_peak | 725.488 |  |  | 7.11 | 0 | 92.89 | 278.7764 | 0
2658 | 766.03 | 191.96 | 24.7 | 31.1311 | 31.1311 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 734.8989 | 0 | 0.088511 | 5.3411 | 0 | 0 | 0 | 31.1311 | on_peak | 734.8989 |  |  | 4.06 | 0 | 95.94 | 166.2732 | 0
2659 | 775.06 | 17.9482 | 24.5 | 2.9128 | 2.9128 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 772.1472 | 0 | 0.088511 | 5.6494 | 0 | 0 | 0 | 2.9128 | on_peak | 772.1472 |  |  | 0.38 | 0 | 99.62 | 16.4558 | 0
2660 | 757.61 | 0 | 24.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 757.61 | 0 | 0.088511 | 6.0604 | 0 | 0 | 0 | 0 | on_peak | 757.61 |  |  | 0 | 0 | 100 | 0 | 0
2661 | 746.23 | 0 | 24.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 746.23 | 0 | 0.088511 | 6.3715 | 0 | 0 | 0 | 0 | on_peak | 746.23 |  |  | 0 | 0 | 100 | 0 | 0
2662 | 749.33 | 0 | 24.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 749.33 | 0 | 0.05921 | 6.7065 | 0 | 0 | 0 | 0 | off_peak | 749.33 |  |  | 0 | 0 | 100 | 0 | 0
2663 | 749.04 | 0 | 24.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 749.04 | 0 | 0.05921 | 7.0204 | 0 | 0 | 0 | 0 | off_peak | 749.04 |  |  | 0 | 0 | 100 | 0 | 0
2664 | 710.24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 710.24 | 0 | 0.05921 | 7.125 | 0 | 0 | 0 | 0 | off_peak | 710.24 |  |  | 0 | 0 | 100 | 0 | 0
2665 | 667.48 | 0 | 23.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 667.48 | 0 | 0.05921 | 6.86 | 0 | 0 | 0 | 0 | off_peak | 667.48 |  |  | 0 | 0 | 100 | 0 | 0
2666 | 638.1 | 0 | 23.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 638.1 | 0 | 0.05921 | 6.667 | 0 | 0 | 0 | 0 | off_peak | 638.1 |  |  | 0 | 0 | 100 | 0 | 0
2667 | 587.05 | 0 | 23.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 587.05 | 0 | 0.05921 | 6.2729 | 0 | 0 | 0 | 0 | off_peak | 587.05 |  |  | 0 | 0 | 100 | 0 | 0
2668 | 580.97 | 0 | 23.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 580.97 | 0 | 0.05921 | 5.8064 | 0 | 0 | 0 | 0 | off_peak | 580.97 |  |  | 0 | 0 | 100 | 0 | 0
2669 | 615.23 | 0 | 23.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 615.23 | 0 | 0.05921 | 5.1436 | 0 | 0 | 0 | 0 | off_peak | 615.23 |  |  | 0 | 0 | 100 | 0 | 0
2670 | 656.71 | 0 | 23.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 656.71 | 0 | 0.05921 | 4.4311 | 0 | 0 | 0 | 0 | off_peak | 656.71 |  |  | 0 | 0 | 100 | 0 | 0
2671 | 689.13 | 51.7504 | 24 | 8.4137 | 8.4137 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 680.7163 | 0 | 0.05921 | 4.0288 | 0 | 0 | 0 | 8.4137 | off_peak | 680.7163 |  |  | 1.22 | 0 | 98.78 | 33.8973 | 0
2672 | 711 | 270.603 | 24.6 | 43.9008 | 43.9008 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 667.0992 | 0 | 0.05921 | 3.7206 | 0 | 0 | 0 | 43.9008 | off_peak | 667.0992 |  |  | 6.17 | 0 | 93.83 | 163.3352 | 0
2673 | 758.58 | 493.201 | 25.2 | 79.841 | 79.841 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 678.739 | 0 | 0.05921 | 3.4598 | 0 | 0 | 0 | 79.841 | off_peak | 678.739 |  |  | 10.53 | 0 | 89.47 | 276.2373 | 0
2674 | 727.78 | 521.54 | 25.6 | 84.307 | 84.307 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 643.473 | 0 | 0.05921 | 3.3318 | 0 | 0 | 0 | 84.307 | off_peak | 643.473 |  |  | 11.58 | 0 | 88.42 | 280.8936 | 0
2675 | 731.54 | 604.586 | 25.9 | 97.6256 | 97.6256 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 633.9144 | 0 | 0.05921 | 3.3319 | 0 | 0 | 0 | 97.6256 | off_peak | 633.9144 |  |  | 13.35 | 0 | 86.65 | 325.2771 | 0
2676 | 751.08 | 509.589 | 26.1 | 82.2265 | 82.2265 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 668.8535 | 0 | 0.05921 | 3.4998 | 0 | 0 | 0 | 82.2265 | off_peak | 668.8535 |  |  | 10.95 | 0 | 89.05 | 287.775 | 0
2677 | 710.86 | 545.834 | 26.2 | 88.0431 | 88.0431 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 622.8169 | 0 | 0.05921 | 3.665 | 0 | 0 | 0 | 88.0431 | off_peak | 622.8169 |  |  | 12.39 | 0 | 87.61 | 322.6787 | 0
2678 | 647.35 | 655.45 | 26.2 | 105.7242 | 105.7242 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 541.6258 | 0 | 0.05921 | 3.8405 | 0 | 0 | 0 | 105.7242 | off_peak | 541.6258 |  |  | 16.33 | 0 | 83.67 | 406.0307 | 0
2679 | 653.74 | 518.092 | 26.1 | 83.5985 | 83.5985 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 570.1415 | 0 | 0.05921 | 4.0565 | 0 | 0 | 0 | 83.5985 | off_peak | 570.1415 |  |  | 12.79 | 0 | 87.21 | 339.1139 | 0
2680 | 609.06 | 451.546 | 25.9 | 72.9134 | 72.9134 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 536.1466 | 0 | 0.05921 | 4.4655 | 0 | 0 | 0 | 72.9134 | off_peak | 536.1466 |  |  | 11.97 | 0 | 88.03 | 325.5919 | 0
2681 | 621.52 | 278.992 | 25.6 | 45.0991 | 45.0991 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 576.4209 | 0 | 0.05921 | 4.8227 | 0 | 0 | 0 | 45.0991 | off_peak | 576.4209 |  |  | 7.26 | 0 | 92.74 | 217.4988 | 0
2682 | 591.02 | 186.393 | 25.1 | 30.1848 | 30.1848 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 560.8352 | 0 | 0.05921 | 5.322 | 0 | 0 | 0 | 30.1848 | off_peak | 560.8352 |  |  | 5.11 | 0 | 94.89 | 160.6433 | 0
2683 | 544.22 | 22.5199 | 24.9 | 3.6495 | 3.6495 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 540.5705 | 0 | 0.05921 | 5.7749 | 0 | 0 | 0 | 3.6495 | off_peak | 540.5705 |  |  | 0.67 | 0 | 99.33 | 21.0757 | 0
2684 | 573.62 | 0 | 24.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 573.62 | 0 | 0.05921 | 6.238 | 0 | 0 | 0 | 0 | off_peak | 573.62 |  |  | 0 | 0 | 100 | 0 | 0
2685 | 548.08 | 0 | 24.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 548.08 | 0 | 0.05921 | 6.5614 | 0 | 0 | 0 | 0 | off_peak | 548.08 |  |  | 0 | 0 | 100 | 0 | 0
2686 | 544.89 | 0 | 24.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 544.89 | 0 | 0.05921 | 6.6622 | 0 | 0 | 0 | 0 | off_peak | 544.89 |  |  | 0 | 0 | 100 | 0 | 0
2687 | 548.21 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 548.21 | 0 | 0.05921 | 6.8655 | 0 | 0 | 0 | 0 | off_peak | 548.21 |  |  | 0 | 0 | 100 | 0 | 0
2688 | 519.88 | 0 | 23.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 519.88 | 0 | 0.05921 | 6.8837 | 0 | 0 | 0 | 0 | off_peak | 519.88 |  |  | 0 | 0 | 100 | 0 | 0
2689 | 525.54 | 0 | 23.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 525.54 | 0 | 0.05921 | 6.7109 | 0 | 0 | 0 | 0 | off_peak | 525.54 |  |  | 0 | 0 | 100 | 0 | 0
2690 | 534.91 | 0 | 23.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 534.91 | 0 | 0.05921 | 6.5905 | 0 | 0 | 0 | 0 | off_peak | 534.91 |  |  | 0 | 0 | 100 | 0 | 0
2691 | 513.81 | 0 | 23.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 513.81 | 0 | 0.05921 | 6.1743 | 0 | 0 | 0 | 0 | off_peak | 513.81 |  |  | 0 | 0 | 100 | 0 | 0
2692 | 550.19 | 0 | 23.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 550.19 | 0 | 0.05921 | 5.5749 | 0 | 0 | 0 | 0 | off_peak | 550.19 |  |  | 0 | 0 | 100 | 0 | 0
2693 | 546.36 | 0 | 23.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 546.36 | 0 | 0.05921 | 5.1134 | 0 | 0 | 0 | 0 | off_peak | 546.36 |  |  | 0 | 0 | 100 | 0 | 0
2694 | 637.55 | 0 | 23.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 637.55 | 0 | 0.05921 | 4.4711 | 0 | 0 | 0 | 0 | off_peak | 637.55 |  |  | 0 | 0 | 100 | 0 | 0
2695 | 701.22 | 75.6388 | 24.3 | 12.2844 | 12.2844 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 688.9356 | 0 | 0.05921 | 4.0341 | 0 | 0 | 0 | 12.2844 | off_peak | 688.9356 |  |  | 1.75 | 0 | 98.25 | 49.5569 | 0
2696 | 708.19 | 253.648 | 24.9 | 41.1058 | 41.1058 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 667.0842 | 0 | 0.05921 | 3.7061 | 0 | 0 | 0 | 41.1058 | off_peak | 667.0842 |  |  | 5.8 | 0 | 94.2 | 152.3403 | 0
2697 | 676.59 | 445.336 | 25.4 | 72.0405 | 72.0405 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 604.5495 | 0 | 0.05921 | 3.4442 | 0 | 0 | 0 | 72.0405 | off_peak | 604.5495 |  |  | 10.65 | 0 | 89.35 | 248.1243 | 0
2698 | 694.3 | 703.558 | 25.8 | 113.6481 | 113.6481 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 580.6519 | 0 | 0.05921 | 3.315 | 0 | 0 | 0 | 113.6481 | off_peak | 580.6519 |  |  | 16.37 | 0 | 83.63 | 376.7389 | 0
2699 | 719.24 | 730.865 | 26.1 | 117.9313 | 117.9313 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 601.3087 | 0 | 0.05921 | 3.2766 | 0 | 0 | 0 | 117.9313 | off_peak | 601.3087 |  |  | 16.4 | 0 | 83.6 | 386.4145 | 0
2700 | 677.33 | 914.772 | 26.4 | 147.4462 | 147.4462 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 529.8838 | 0 | 0.05921 | 3.3499 | 0 | 0 | 0 | 147.4462 | off_peak | 529.8838 |  |  | 21.77 | 0 | 78.23 | 493.9278 | 0
2701 | 667.87 | 952.424 | 26.5 | 153.4595 | 153.4595 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 514.4105 | 0 | 0.05921 | 3.4376 | 0 | 0 | 0 | 153.4595 | off_peak | 514.4105 |  |  | 22.98 | 0 | 77.02 | 527.5387 | 0
2702 | 623.42 | 919.662 | 26.5 | 148.1807 | 148.1807 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 475.2393 | 0 | 0.05921 | 3.6849 | 0 | 0 | 0 | 148.1807 | off_peak | 475.2393 |  |  | 23.77 | 0 | 76.23 | 546.0274 | 0
2703 | 627.15 | 805.685 | 26.4 | 129.8631 | 129.8631 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 18.9814 | 509.6492 | 0 | 0.05921 | 3.8938 | 0 | 0 | 0 | 129.8631 | off_peak | 497.2869 | 0 | 100 | 20.71 | 0 | 79.29 | 505.6641 | 0
2704 | 642.23 | 644.413 | 26.2 | 103.9439 | 103.9439 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 30.5453 | 550.6485 | 0 | 0.05921 | 4.1402 | 0 | 0 | 0 | 103.9439 | off_peak | 538.2861 | 0 | 100 | 16.18 | 0 | 83.82 | 430.3462 | 0
2705 | 640.46 | 383.885 | 25.9 | 61.9879 | 61.9879 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 42.1093 | 590.8345 | 0 | 0.05921 | 4.453 | 0 | 0 | 0 | 61.9879 | off_peak | 578.4721 | 0 | 100 | 9.68 | 0 | 90.32 | 276.034 | 0
2706 | 599.75 | 218.512 | 25.5 | 35.3352 | 35.3352 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 53.6732 | 576.7771 | 0 | 0.05921 | 4.9242 | 0 | 0 | 0 | 35.3352 | off_peak | 564.4148 | 0 | 100 | 5.89 | 0 | 94.11 | 173.9988 | 0
2707 | 569.61 | 29.9448 | 25.3 | 4.8458 | 4.8458 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 53.6732 | 564.7642 | 0 | 0.05921 | 5.3735 | 0 | 0 | 0 | 4.8458 | off_peak | 564.7642 |  |  | 0.85 | 0 | 99.15 | 26.039 | 0
2708 | 509.76 | 0 | 24.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 53.6732 | 509.76 | 0 | 0.05921 | 5.8521 | 0 | 0 | 0 | 0 | off_peak | 509.76 |  |  | 0 | 0 | 100 | 0 | 0
2709 | 530.83 | 0 | 24.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 53.6732 | 530.83 | 0 | 0.05921 | 6.2474 | 0 | 0 | 0 | 0 | off_peak | 530.83 |  |  | 0 | 0 | 100 | 0 | 0
2710 | 532.98 | 0 | 24.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 53.6732 | 532.98 | 0 | 0.05921 | 6.5849 | 0 | 0 | 0 | 0 | off_peak | 532.98 |  |  | 0 | 0 | 100 | 0 | 0
2711 | 497.25 | 0 | 24.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 53.6732 | 497.25 | 0 | 0.05921 | 6.9215 | 0 | 0 | 0 | 0 | off_peak | 497.25 |  |  | 0 | 0 | 100 | 0 | 0
2712 | 487.61 | 0 | 24.3 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 65.2371 | 499.9724 | 0 | 0.05921 | 7.2687 | 0 | 0 | 0 | 0 | off_peak | 487.61 | 0 | 100 | 0 | 0 | 100 | 0 | 0
2713 | 515.59 | 0 | 24.1 | 0 | 0 | 0 | 0 | 8.9371 | 8.9371 | 0 | 0 | 0 | 73.597 | 524.5271 | 0 | 0.05921 | 7.173 | 0 | 0 | 0 | 0 | off_peak | 515.59 | 0 | 100 | 0 | 0 | 100 | 0 | 0
2714 | 517.03 | 0 | 23.9 | 0 | 0 | 0 | 0 | 0.57721 | 0.57721 | 0 | 0 | 0 | 74.137 | 517.6072 | 0 | 0.05921 | 7.017 | 0 | 0 | 0 | 0 | off_peak | 517.03 | 0 | 100 | 0 | 0 | 100 | 0 | 0
2715 | 505.08 | 0 | 23.7 | 0 | 0 | 0 | 0 | 0.037279 | 0.037279 | 0 | 0 | 0 | 74.1718 | 505.1173 | 0 | 0.05921 | 6.4851 | 0 | 0 | 0 | 0 | off_peak | 505.08 | 0 | 100 | 0 | 0 | 100 | 0 | 0
2716 | 529.47 | 0 | 23.5 | 0 | 0 | 0 | 0 | 0.0024077 | 0.0024077 | 0 | 0 | 0 | 74.1741 | 529.4724 | 0 | 0.05921 | 5.7719 | 0 | 0 | 0 | 0 | off_peak | 529.47 | 0 | 100 | 0 | 0 | 100 | 0 | 0
2717 | 535.72 | 0 | 23.4 | 0 | 0 | 0 | 0 | 0.0001555 | 0.0001555 | 0 | 0 | 0 | 74.1742 | 535.7202 | 0 | 0.05921 | 5.1368 | 0 | 0 | 0 | 0 | off_peak | 535.72 | 0 | 100 | 0 | 0 | 100 | 0 | 0
2718 | 643.78 | 0 | 23.5 | 0 | 0 | 0 | 0 | 1.0737e-05 | 1.0737e-05 | 0 | 0 | 0 | 74.1743 | 643.78 | 0 | 0.05921 | 4.4572 | 0 | 0 | 0 | 0 | off_peak | 643.78 | 0 | 100 | 0 | 0 | 100 | 0 | 0
2719 | 731.73 | 90.0975 | 24.2 | 14.6378 | 14.6378 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1743 | 717.0922 | 0 | 0.05921 | 4.0053 | 0 | 0 | 0 | 14.6378 | off_peak | 717.0922 |  |  | 2 | 0 | 98 | 58.6289 | 0
2720 | 770.43 | 303.235 | 24.9 | 49.1418 | 49.1418 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1743 | 721.2882 | 0 | 0.05921 | 3.6857 | 0 | 0 | 0 | 49.1418 | off_peak | 721.2882 |  |  | 6.38 | 0 | 93.62 | 181.122 | 0
2721 | 783.64 | 525.397 | 25.4 | 84.9917 | 84.9917 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1743 | 698.6483 | 0 | 0.05921 | 3.5204 | 0 | 0 | 0 | 84.9917 | off_peak | 698.6483 |  |  | 10.85 | 0 | 89.15 | 299.2029 | 0
2722 | 801.35 | 719.502 | 25.9 | 116.1817 | 116.1817 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1743 | 685.1683 | 0 | 0.05921 | 3.5327 | 0 | 0 | 0 | 116.1817 | off_peak | 685.1683 |  |  | 14.5 | 0 | 85.5 | 410.4389 | 0
2723 | 771.32 | 866.785 | 26.3 | 139.762 | 139.762 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1743 | 631.558 | 0 | 0.05921 | 3.7641 | 0 | 0 | 0 | 139.762 | off_peak | 631.558 |  |  | 18.12 | 0 | 81.88 | 526.0781 | 0
2724 | 820.73 | 892.718 | 26.6 | 143.7873 | 143.7873 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1743 | 676.9427 | 0 | 0.05921 | 4.1804 | 0 | 0 | 0 | 143.7873 | off_peak | 676.9427 |  |  | 17.52 | 0 | 82.48 | 601.0831 | 0
2725 | 761.82 | 947.76 | 26.7 | 152.5975 | 152.5975 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1743 | 609.2225 | 0 | 0.088511 | 4.3885 | 0 | 0 | 0 | 152.5975 | on_peak | 609.2225 |  |  | 20.03 | 0 | 79.97 | 669.6754 | 0
2726 | 784.31 | 814.594 | 26.7 | 131.1566 | 131.1566 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1743 | 653.1534 | 0 | 0.088511 | 4.6203 | 0 | 0 | 0 | 131.1566 | on_peak | 653.1534 |  |  | 16.72 | 0 | 83.28 | 605.9853 | 0
2727 | 820.12 | 421.143 | 26.6 | 67.8322 | 67.8322 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1743 | 752.2878 | 0 | 0.088511 | 4.8741 | 0 | 0 | 0 | 67.8322 | on_peak | 752.2878 |  |  | 8.27 | 0 | 91.73 | 330.6214 | 0
2728 | 808.87 | 423.547 | 26.4 | 68.2688 | 68.2688 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1743 | 740.6012 | 0 | 0.088511 | 4.9043 | 0 | 0 | 0 | 68.2688 | on_peak | 740.6012 |  |  | 8.44 | 0 | 91.56 | 334.8105 | 0
2729 | 793.51 | 333.124 | 26 | 53.7718 | 53.7718 | 0 | 0 | 0 | 0 | 62.4453 | 62.4453 | 0 | 7.4174 | 677.2929 | 0 | 0.088511 | 4.9146 | 0 | 0 | 0 | 53.7718 | on_peak | 677.2929 |  |  | 6.78 | 7.87 | 85.35 | 264.2664 | 0
2730 | 778.28 | 217.673 | 25.5 | 35.1996 | 35.1996 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 743.0804 | 0 | 0.088511 | 5.1022 | 0 | 0 | 0 | 35.1996 | on_peak | 743.0804 |  |  | 4.52 | 0 | 95.48 | 179.5969 | 0
2731 | 691.55 | 26.3459 | 25.2 | 4.265 | 4.265 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 687.285 | 0 | 0.088511 | 5.3279 | 0 | 0 | 0 | 4.265 | on_peak | 687.285 |  |  | 0.62 | 0 | 99.38 | 22.7233 | 0
2732 | 790.29 | 0 | 24.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 790.29 | 0 | 0.088511 | 5.7664 | 0 | 0 | 0 | 0 | on_peak | 790.29 |  |  | 0 | 0 | 100 | 0 | 0
2733 | 734.23 | 0 | 24.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 734.23 | 0 | 0.088511 | 6.0095 | 0 | 0 | 0 | 0 | on_peak | 734.23 |  |  | 0 | 0 | 100 | 0 | 0
2734 | 708.23 | 0 | 24.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 708.23 | 0 | 0.05921 | 6.4042 | 0 | 0 | 0 | 0 | off_peak | 708.23 |  |  | 0 | 0 | 100 | 0 | 0
2735 | 741.87 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 741.87 | 0 | 0.05921 | 6.5878 | 0 | 0 | 0 | 0 | off_peak | 741.87 |  |  | 0 | 0 | 100 | 0 | 0
2736 | 759.61 | 0 | 23.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 759.61 | 0 | 0.05921 | 6.6498 | 0 | 0 | 0 | 0 | off_peak | 759.61 |  |  | 0 | 0 | 100 | 0 | 0
2737 | 711.05 | 0 | 23.6 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 18.9814 | 723.4124 | 0 | 0.05921 | 6.4964 | 0 | 0 | 0 | 0 | off_peak | 711.05 | 0 | 100 | 0 | 0 | 100 | 0 | 0
2738 | 639.19 | 0 | 23.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18.9814 | 639.19 | 0 | 0.05921 | 6.4154 | 0 | 0 | 0 | 0 | off_peak | 639.19 |  |  | 0 | 0 | 100 | 0 | 0
2739 | 598.69 | 0 | 23.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18.9814 | 598.69 | 0 | 0.05921 | 6.0588 | 0 | 0 | 0 | 0 | off_peak | 598.69 |  |  | 0 | 0 | 100 | 0 | 0
2740 | 580.32 | 0 | 23.5 | 0 | 0 | 0 | 0 | 8.7006 | 8.7006 | 0 | 0 | 0 | 27.12 | 589.0206 | 0 | 0.05921 | 5.3624 | 0 | 0 | 0 | 0 | off_peak | 580.32 | 0 | 100 | 0 | 0 | 100 | 0 | 0
2741 | 568.08 | 0 | 23.6 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 38.684 | 580.4424 | 0 | 0.05921 | 4.6398 | 0 | 0 | 0 | 0 | off_peak | 568.08 | 0 | 100 | 0 | 0 | 100 | 0 | 0
2742 | 651.58 | 0 | 23.7 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 50.2479 | 663.9424 | 0 | 0.05921 | 3.9641 | 0 | 0 | 0 | 0 | off_peak | 651.58 | 0 | 100 | 0 | 0 | 100 | 0 | 0
2743 | 740.12 | 93.352 | 24.1 | 15.172 | 15.172 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 61.8119 | 737.3104 | 0 | 0.05921 | 3.5917 | 0 | 0 | 0 | 15.172 | off_peak | 724.948 | 0 | 100 | 2.05 | 0 | 97.95 | 54.4938 | 0
2744 | 733.58 | 305.604 | 24.5 | 49.597 | 49.597 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 73.3758 | 696.3454 | 0 | 0.05921 | 3.3802 | 0 | 0 | 0 | 49.597 | off_peak | 683.983 | 0 | 100 | 6.76 | 0 | 93.24 | 167.6501 | 0
2745 | 768.86 | 525.57 | 24.9 | 85.173 | 85.173 | 0 | 0 | 0.79843 | 0.79843 | 0 | 0 | 0 | 74.1227 | 684.4854 | 0 | 0.05921 | 3.2673 | 0 | 0 | 0 | 85.173 | off_peak | 683.687 | 0 | 100 | 11.08 | 0 | 88.92 | 278.282 | 0
2746 | 784.87 | 715.671 | 25.3 | 115.8135 | 115.8135 | 0 | 0 | 0.051567 | 0.051567 | 0 | 0 | 0 | 74.1709 | 669.1081 | 0 | 0.05921 | 3.3158 | 0 | 0 | 0 | 115.8135 | off_peak | 669.0565 | 0 | 100 | 14.76 | 0 | 85.24 | 384.0104 | 0
2747 | 736.42 | 859.989 | 25.9 | 138.8668 | 138.8668 | 0 | 0 | 0.0033305 | 0.0033305 | 0 | 0 | 0 | 74.174 | 597.5565 | 0 | 0.05921 | 3.5574 | 0 | 0 | 0 | 138.8668 | off_peak | 597.5532 | 0 | 100 | 18.86 | 0 | 81.14 | 494.0032 | 0
2748 | 769.87 | 947.38 | 26.4 | 152.702 | 152.702 | 0 | 0 | 0.0002151 | 0.0002151 | 0 | 0 | 0 | 74.1742 | 617.1682 | 0 | 0.05921 | 3.946 | 0 | 0 | 0 | 152.702 | off_peak | 617.168 | 0 | 100 | 19.83 | 0 | 80.17 | 602.5628 | 0
2749 | 731.21 | 923.517 | 26.8 | 148.6403 | 148.6403 | 0 | 0 | 0 | 0 | 62.4453 | 62.4453 | 0 | 7.4174 | 520.1244 | 0 | 0.088511 | 4.127 | 0 | 0 | 0 | 148.6403 | on_peak | 520.1244 |  |  | 20.33 | 8.54 | 71.13 | 613.4442 | 0
2750 | 805.67 | 921.048 | 26.9 | 148.1892 | 148.1892 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 657.4808 | 0 | 0.088511 | 4.1006 | 0 | 0 | 0 | 148.1892 | on_peak | 657.4808 |  |  | 18.39 | 0 | 81.61 | 607.6664 | 0
2751 | 804.61 | 809.297 | 26.9 | 130.2093 | 130.2093 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 674.4007 | 0 | 0.088511 | 4.0995 | 0 | 0 | 0 | 130.2093 | on_peak | 674.4007 |  |  | 16.18 | 0 | 83.82 | 533.7895 | 0
2752 | 830.75 | 644.368 | 26.7 | 103.7488 | 103.7488 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 727.0012 | 0 | 0.088511 | 4.3863 | 0 | 0 | 0 | 103.7488 | on_peak | 727.0012 |  |  | 12.49 | 0 | 87.51 | 455.0695 | 0
2753 | 809.42 | 441.292 | 26.4 | 71.129 | 71.129 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 738.291 | 0 | 0.088511 | 4.6928 | 0 | 0 | 0 | 71.129 | on_peak | 738.291 |  |  | 8.79 | 0 | 91.21 | 333.7927 | 0
2754 | 782.03 | 221.89 | 26 | 35.8168 | 35.8168 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 746.2132 | 0 | 0.088511 | 5.131 | 0 | 0 | 0 | 35.8168 | on_peak | 746.2132 |  |  | 4.58 | 0 | 95.42 | 183.7768 | 0
2755 | 711.41 | 32.8168 | 25.7 | 5.3029 | 5.3029 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 706.1071 | 0 | 0.088511 | 5.5106 | 0 | 0 | 0 | 5.3029 | on_peak | 706.1071 |  |  | 0.75 | 0 | 99.25 | 29.2225 | 0
2756 | 764.27 | 0 | 25.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 764.27 | 0 | 0.088511 | 5.8321 | 0 | 0 | 0 | 0 | on_peak | 764.27 |  |  | 0 | 0 | 100 | 0 | 0
2757 | 746.82 | 0 | 24.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 746.82 | 0 | 0.088511 | 6.1868 | 0 | 0 | 0 | 0 | on_peak | 746.82 |  |  | 0 | 0 | 100 | 0 | 0
2758 | 713.66 | 0 | 24.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 713.66 | 0 | 0.05921 | 6.8817 | 0 | 0 | 0 | 0 | off_peak | 713.66 |  |  | 0 | 0 | 100 | 0 | 0
2759 | 757.13 | 0 | 24.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 757.13 | 0 | 0.05921 | 7.2246 | 0 | 0 | 0 | 0 | off_peak | 757.13 |  |  | 0 | 0 | 100 | 0 | 0
2760 | 727.45 | 0 | 23.9 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 18.9814 | 739.8124 | 0 | 0.05921 | 7.2536 | 0 | 0 | 0 | 0 | off_peak | 727.45 | 0 | 100 | 0 | 0 | 100 | 0 | 0
2761 | 705.38 | 0 | 23.8 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 30.5453 | 717.7424 | 0 | 0.05921 | 7.136 | 0 | 0 | 0 | 0 | off_peak | 705.38 | 0 | 100 | 0 | 0 | 100 | 0 | 0
2762 | 607.39 | 0 | 23.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30.5453 | 607.39 | 0 | 0.05921 | 6.9883 | 0 | 0 | 0 | 0 | off_peak | 607.39 |  |  | 0 | 0 | 100 | 0 | 0
2763 | 524.57 | 0 | 23.5 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 42.1093 | 536.9324 | 0 | 0.05921 | 6.359 | 0 | 0 | 0 | 0 | off_peak | 524.57 | 0 | 100 | 0 | 0 | 100 | 0 | 0
2764 | 500.53 | 0 | 23.3 | 0 | 0 | 0 | 0 | 8.7006 | 8.7006 | 0 | 0 | 0 | 50.2479 | 509.2306 | 0 | 0.05921 | 5.6479 | 0 | 0 | 0 | 0 | off_peak | 500.53 | 0 | 100 | 0 | 0 | 100 | 0 | 0
2765 | 520.11 | 0 | 23.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50.2479 | 520.11 | 0 | 0.05921 | 4.8684 | 0 | 0 | 0 | 0 | off_peak | 520.11 |  |  | 0 | 0 | 100 | 0 | 0
2766 | 663.27 | 0 | 23.1 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 61.8119 | 675.6324 | 0 | 0.05921 | 4.1524 | 0 | 0 | 0 | 0 | off_peak | 663.27 | 0 | 100 | 0 | 0 | 100 | 0 | 0
2767 | 674.26 | 93.5085 | 23.5 | 15.2302 | 15.2302 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 61.8119 | 659.0298 | 0 | 0.05921 | 3.7064 | 0 | 0 | 0 | 15.2302 | off_peak | 659.0298 |  |  | 2.26 | 0 | 97.74 | 56.4487 | 0
2768 | 733.52 | 304.009 | 24.1 | 49.409 | 49.409 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 73.3758 | 696.4733 | 0 | 0.05921 | 3.4022 | 0 | 0 | 0 | 49.409 | off_peak | 684.111 | 0 | 100 | 6.74 | 0 | 93.26 | 168.0997 | 0
2769 | 770.9 | 522.591 | 24.9 | 84.6902 | 84.6902 | 0 | 0 | 0.79843 | 0.79843 | 0 | 0 | 0 | 74.1227 | 687.0082 | 0 | 0.05921 | 3.2381 | 0 | 0 | 0 | 84.6902 | off_peak | 686.2098 | 0 | 100 | 10.99 | 0 | 89.01 | 274.2387 | 0
2770 | 780.13 | 716.309 | 25.7 | 115.7496 | 115.7496 | 0 | 0 | 0.051567 | 0.051567 | 0 | 0 | 0 | 74.1709 | 664.4319 | 0 | 0.05921 | 3.206 | 0 | 0 | 0 | 115.7496 | off_peak | 664.3804 | 0 | 100 | 14.84 | 0 | 85.16 | 371.0987 | 0
2771 | 756.28 | 864.136 | 26.2 | 139.3853 | 139.3853 | 0 | 0 | 0.0033305 | 0.0033305 | 0 | 0 | 0 | 74.174 | 616.8981 | 0 | 0.05921 | 3.375 | 0 | 0 | 0 | 139.3853 | off_peak | 616.8947 | 0 | 100 | 18.43 | 0 | 81.57 | 470.4214 | 0
2772 | 737.76 | 952.902 | 26.5 | 153.5365 | 153.5365 | 0 | 0 | 0.0002151 | 0.0002151 | 0 | 0 | 0 | 74.1742 | 584.2237 | 0 | 0.05921 | 3.8116 | 0 | 0 | 0 | 153.5365 | off_peak | 584.2235 | 0 | 100 | 20.81 | 0 | 79.19 | 585.2241 | 0
2773 | 753.14 | 973.238 | 26.7 | 156.6996 | 156.6996 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1742 | 596.4404 | 0 | 0.088511 | 4.0073 | 0 | 0 | 0 | 156.6996 | on_peak | 596.4404 |  |  | 20.81 | 0 | 79.19 | 627.9367 | 0
2774 | 744.51 | 923.858 | 26.7 | 148.749 | 148.749 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1742 | 595.761 | 0 | 0.088511 | 4.0995 | 0 | 0 | 0 | 148.749 | on_peak | 595.761 |  |  | 19.98 | 0 | 80.02 | 609.8011 | 0
2775 | 822.75 | 813.351 | 26.4 | 131.0988 | 131.0988 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1742 | 691.6512 | 0 | 0.088511 | 4.2692 | 0 | 0 | 0 | 131.0988 | on_peak | 691.6512 |  |  | 15.93 | 0 | 84.07 | 559.6821 | 0
2776 | 799.25 | 647.871 | 26 | 104.5773 | 104.5773 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1742 | 694.6727 | 0 | 0.088511 | 4.6843 | 0 | 0 | 0 | 104.5773 | on_peak | 694.6727 |  |  | 13.08 | 0 | 86.92 | 489.8669 | 0
2777 | 801.74 | 443.622 | 25.3 | 71.7891 | 71.7891 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1742 | 729.9509 | 0 | 0.088511 | 5.0667 | 0 | 0 | 0 | 71.7891 | on_peak | 729.9509 |  |  | 8.95 | 0 | 91.05 | 363.7362 | 0
2778 | 796.3 | 223.503 | 24.6 | 36.2596 | 36.2596 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1742 | 760.0404 | 0 | 0.088511 | 5.5601 | 0 | 0 | 0 | 36.2596 | on_peak | 760.0404 |  |  | 4.55 | 0 | 95.45 | 201.6058 | 0
2779 | 732.16 | 32.9971 | 24.3 | 5.359 | 5.359 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1742 | 726.801 | 0 | 0.088511 | 6.08 | 0 | 0 | 0 | 5.359 | on_peak | 726.801 |  |  | 0.73 | 0 | 99.27 | 32.5828 | 0
2780 | 824.66 | 0 | 23.7 | 0 | 0 | 0 | 0 | 0 | 0 | 62.4453 | 62.4453 | 0 | 7.4174 | 762.2147 | 0 | 0.088511 | 6.4766 | 0 | 0 | 0 | 0 | on_peak | 762.2147 |  |  | 0 | 7.57 | 92.43 | 0 | 0
2781 | 792.38 | 0 | 23.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 792.38 | 0 | 0.088511 | 6.8744 | 0 | 0 | 0 | 0 | on_peak | 792.38 |  |  | 0 | 0 | 100 | 0 | 0
2782 | 792.29 | 0 | 23.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 792.29 | 0 | 0.05921 | 7.0904 | 0 | 0 | 0 | 0 | off_peak | 792.29 |  |  | 0 | 0 | 100 | 0 | 0
2783 | 783.82 | 0 | 23.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 783.82 | 0 | 0.05921 | 7.1101 | 0 | 0 | 0 | 0 | off_peak | 783.82 |  |  | 0 | 0 | 100 | 0 | 0
2784 | 794.49 | 0 | 23.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 794.49 | 0 | 0.05921 | 7.2007 | 0 | 0 | 0 | 0 | off_peak | 794.49 |  |  | 0 | 0 | 100 | 0 | 0
2785 | 742.63 | 0 | 23.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 742.63 | 0 | 0.05921 | 7.1179 | 0 | 0 | 0 | 0 | off_peak | 742.63 |  |  | 0 | 0 | 100 | 0 | 0
2786 | 653.53 | 0 | 22.9 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 18.9814 | 665.8924 | 0 | 0.05921 | 6.9813 | 0 | 0 | 0 | 0 | off_peak | 653.53 | 0 | 100 | 0 | 0 | 100 | 0 | 0
2787 | 621.49 | 0 | 22.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18.9814 | 621.49 | 0 | 0.05921 | 6.5526 | 0 | 0 | 0 | 0 | off_peak | 621.49 |  |  | 0 | 0 | 100 | 0 | 0
2788 | 575.42 | 0 | 22.8 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 30.5453 | 587.7824 | 0 | 0.05921 | 5.8735 | 0 | 0 | 0 | 0 | off_peak | 575.42 | 0 | 100 | 0 | 0 | 100 | 0 | 0
2789 | 644.53 | 0 | 22.7 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 42.1093 | 656.8924 | 0 | 0.05921 | 5.0274 | 0 | 0 | 0 | 0 | off_peak | 644.53 | 0 | 100 | 0 | 0 | 100 | 0 | 0
2790 | 692.45 | 0 | 22.7 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 53.6732 | 704.8124 | 0 | 0.05921 | 4.342 | 0 | 0 | 0 | 0 | off_peak | 692.45 | 0 | 100 | 0 | 0 | 100 | 0 | 0
2791 | 753.97 | 94.1219 | 23.1 | 15.352 | 15.352 | 0 | 0 | 8.7006 | 8.7006 | 0 | 0 | 0 | 61.8119 | 747.3186 | 0 | 0.05921 | 3.8877 | 0 | 0 | 0 | 15.352 | off_peak | 738.618 | 0 | 100 | 2.04 | 0 | 97.96 | 59.6843 | 0
2792 | 804.32 | 302.592 | 23.7 | 49.2493 | 49.2493 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 73.3758 | 767.4331 | 0 | 0.05921 | 3.5781 | 0 | 0 | 0 | 49.2493 | off_peak | 755.0707 | 0 | 100 | 6.12 | 0 | 93.88 | 176.2194 | 0
2793 | 804.33 | 519.552 | 24.3 | 84.3795 | 84.3795 | 0 | 0 | 0.79843 | 0.79843 | 0 | 0 | 0 | 74.1227 | 720.7489 | 0 | 0.05921 | 3.4045 | 0 | 0 | 0 | 84.3795 | off_peak | 719.9505 | 0 | 100 | 10.49 | 0 | 89.51 | 287.2743 | 0
2794 | 847.72 | 708.5 | 24.8 | 114.8596 | 114.8596 | 0 | 0 | 0.051567 | 0.051567 | 0 | 0 | 0 | 74.1709 | 732.9119 | 0 | 0.05921 | 3.3328 | 0 | 0 | 0 | 114.8596 | off_peak | 732.8604 | 0 | 100 | 13.55 | 0 | 86.45 | 382.8011 | 0
2795 | 851.86 | 850.73 | 25.2 | 137.719 | 137.719 | 0 | 0 | 0.0033305 | 0.0033305 | 0 | 0 | 0 | 74.174 | 714.1443 | 0 | 0.05921 | 3.4914 | 0 | 0 | 0 | 137.719 | off_peak | 714.141 | 0 | 100 | 16.17 | 0 | 83.83 | 480.8384 | 0
2796 | 892.37 | 880.741 | 25.4 | 142.4746 | 142.4746 | 0 | 0 | 0.0002151 | 0.0002151 | 0 | 0 | 0 | 74.1742 | 749.8956 | 0 | 0.05921 | 3.9561 | 0 | 0 | 0 | 142.4746 | off_peak | 749.8954 | 0 | 100 | 15.97 | 0 | 84.03 | 563.6448 | 0
2797 | 855.52 | 919.198 | 25.4 | 148.6956 | 148.6956 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1742 | 706.8244 | 0 | 0.088511 | 4.1893 | 0 | 0 | 0 | 148.6956 | on_peak | 706.8244 |  |  | 17.38 | 0 | 82.62 | 622.9376 | 0
2798 | 849.78 | 821.786 | 25.4 | 132.9376 | 132.9376 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1742 | 716.8424 | 0 | 0.088511 | 4.5083 | 0 | 0 | 0 | 132.9376 | on_peak | 716.8424 |  |  | 15.64 | 0 | 84.36 | 599.3283 | 0
2799 | 859.31 | 579.392 | 25.2 | 93.7939 | 93.7939 | 0 | 0 | 0 | 0 | 62.4453 | 62.4453 | 0 | 7.4174 | 703.0708 | 0 | 0.088511 | 4.8428 | 0 | 0 | 0 | 93.7939 | on_peak | 703.0708 |  |  | 10.92 | 7.27 | 81.82 | 454.2233 | 0
2800 | 851.97 | 356.558 | 24.9 | 57.7832 | 57.7832 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 794.1868 | 0 | 0.088511 | 5.247 | 0 | 0 | 0 | 57.7832 | on_peak | 794.1868 |  |  | 6.78 | 0 | 93.22 | 303.1888 | 0
2801 | 816.05 | 294.704 | 24.5 | 47.828 | 47.828 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 768.222 | 0 | 0.088511 | 5.6733 | 0 | 0 | 0 | 47.828 | on_peak | 768.222 |  |  | 5.86 | 0 | 94.14 | 271.3439 | 0
2802 | 873.29 | 193.805 | 24.2 | 31.4868 | 31.4868 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 841.8032 | 0 | 0.088511 | 6.1721 | 0 | 0 | 0 | 31.4868 | on_peak | 841.8032 |  |  | 3.61 | 0 | 96.39 | 194.34 | 0
2803 | 824.12 | 31.6524 | 24 | 5.1461 | 5.1461 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 818.9739 | 0 | 0.088511 | 6.6719 | 0 | 0 | 0 | 5.1461 | on_peak | 818.9739 |  |  | 0.62 | 0 | 99.38 | 34.3348 | 0
2804 | 814.08 | 0 | 23.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 814.08 | 0 | 0.088511 | 7.0598 | 0 | 0 | 0 | 0 | on_peak | 814.08 |  |  | 0 | 0 | 100 | 0 | 0
2805 | 810.68 | 0 | 23.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 810.68 | 0 | 0.088511 | 7.5463 | 0 | 0 | 0 | 0 | on_peak | 810.68 |  |  | 0 | 0 | 100 | 0 | 0
2806 | 775.51 | 0 | 23.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 775.51 | 0 | 0.05921 | 7.6788 | 0 | 0 | 0 | 0 | off_peak | 775.51 |  |  | 0 | 0 | 100 | 0 | 0
2807 | 814.96 | 0 | 23.6 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 18.9814 | 827.3224 | 0 | 0.05921 | 7.6576 | 0 | 0 | 0 | 0 | off_peak | 814.96 | 0 | 100 | 0 | 0 | 100 | 0 | 0
2808 | 754.25 | 0 | 23.4 | 0 | 0 | 0 | 0 | 8.7006 | 8.7006 | 0 | 0 | 0 | 27.12 | 762.9506 | 0 | 0.05921 | 7.7557 | 0 | 0 | 0 | 0 | off_peak | 754.25 | 0 | 100 | 0 | 0 | 100 | 0 | 0
2809 | 773.34 | 0 | 23.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27.12 | 773.34 | 0 | 0.05921 | 7.6586 | 0 | 0 | 0 | 0 | off_peak | 773.34 |  |  | 0 | 0 | 100 | 0 | 0
2810 | 675.2 | 0 | 23.2 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 38.684 | 687.5624 | 0 | 0.05921 | 7.4647 | 0 | 0 | 0 | 0 | off_peak | 675.2 | 0 | 100 | 0 | 0 | 100 | 0 | 0
2811 | 594.68 | 0 | 23.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 38.684 | 594.68 | 0 | 0.05921 | 7.0046 | 0 | 0 | 0 | 0 | off_peak | 594.68 |  |  | 0 | 0 | 100 | 0 | 0
2812 | 582.44 | 0 | 23 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 50.2479 | 594.8024 | 0 | 0.05921 | 6.3361 | 0 | 0 | 0 | 0 | off_peak | 582.44 | 0 | 100 | 0 | 0 | 100 | 0 | 0
2813 | 617.11 | 0 | 22.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50.2479 | 617.11 | 0 | 0.05921 | 5.455 | 0 | 0 | 0 | 0 | off_peak | 617.11 |  |  | 0 | 0 | 100 | 0 | 0
2814 | 677.85 | 0 | 23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50.2479 | 677.85 | 0 | 0.05921 | 4.7682 | 0 | 0 | 0 | 0 | off_peak | 677.85 |  |  | 0 | 0 | 100 | 0 | 0
2815 | 730.64 | 89.6793 | 23.5 | 14.6065 | 14.6065 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 61.8119 | 728.3959 | 0 | 0.05921 | 4.2456 | 0 | 0 | 0 | 14.6065 | off_peak | 716.0335 | 0 | 100 | 2 | 0 | 98 | 62.0132 | 0
2816 | 787.84 | 298.696 | 24 | 48.563 | 48.563 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 73.3758 | 751.6394 | 0 | 0.05921 | 3.9117 | 0 | 0 | 0 | 48.563 | off_peak | 739.277 | 0 | 100 | 6.16 | 0 | 93.84 | 189.9659 | 0
2817 | 819.79 | 515.907 | 24.4 | 83.7575 | 83.7575 | 0 | 0 | 0.79843 | 0.79843 | 0 | 0 | 0 | 74.1227 | 736.831 | 0 | 0.05921 | 3.6762 | 0 | 0 | 0 | 83.7575 | off_peak | 736.0325 | 0 | 100 | 10.22 | 0 | 89.78 | 307.9127 | 0
2818 | 829.21 | 706.302 | 24.7 | 114.5445 | 114.5445 | 0 | 0 | 0.051567 | 0.051567 | 0 | 0 | 0 | 74.1709 | 714.7171 | 0 | 0.05921 | 3.601 | 0 | 0 | 0 | 114.5445 | off_peak | 714.6655 | 0 | 100 | 13.81 | 0 | 86.19 | 412.4744 | 0
2819 | 793.04 | 850.106 | 24.9 | 137.7668 | 137.7668 | 0 | 0 | 0.0033305 | 0.0033305 | 0 | 0 | 0 | 74.174 | 655.2766 | 0 | 0.05921 | 3.7766 | 0 | 0 | 0 | 137.7668 | off_peak | 655.2732 | 0 | 100 | 17.37 | 0 | 82.63 | 520.2836 | 0
2820 | 877.87 | 787.485 | 25.1 | 127.5266 | 127.5266 | 0 | 0 | 0.0002151 | 0.0002151 | 0 | 0 | 0 | 74.1742 | 750.3436 | 0 | 0.05921 | 4.2087 | 0 | 0 | 0 | 127.5266 | off_peak | 750.3434 | 0 | 100 | 14.53 | 0 | 85.47 | 536.7162 | 0
2821 | 807.36 | 812.071 | 25 | 131.5555 | 131.5555 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1742 | 675.8045 | 0 | 0.088511 | 4.4144 | 0 | 0 | 0 | 131.5555 | on_peak | 675.8045 |  |  | 16.29 | 0 | 83.71 | 580.7434 | 0
2822 | 883.02 | 839.32 | 25 | 135.9698 | 135.9698 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1742 | 747.0502 | 0 | 0.088511 | 4.6779 | 0 | 0 | 0 | 135.9698 | on_peak | 747.0502 |  |  | 15.4 | 0 | 84.6 | 636.0534 | 0
2823 | 915.73 | 541.505 | 24.9 | 87.7554 | 87.7554 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1742 | 827.9746 | 0 | 0.088511 | 5.0064 | 0 | 0 | 0 | 87.7554 | on_peak | 827.9746 |  |  | 9.58 | 0 | 90.42 | 439.3366 | 0
2824 | 796.47 | 138.439 | 24.8 | 22.4433 | 22.4433 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1742 | 774.0267 | 0 | 0.088511 | 5.3451 | 0 | 0 | 0 | 22.4433 | on_peak | 774.0267 |  |  | 2.82 | 0 | 97.18 | 119.9623 | 0
2825 | 823.38 | 45.1313 | 24.6 | 7.3218 | 7.3218 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1742 | 816.0582 | 0 | 0.088511 | 5.5348 | 0 | 0 | 0 | 7.3218 | on_peak | 816.0582 |  |  | 0.89 | 0 | 99.11 | 40.525 | 0
2826 | 837.09 | 23.75 | 24.3 | 3.8572 | 3.8572 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1742 | 833.2328 | 0 | 0.088511 | 5.6497 | 0 | 0 | 0 | 3.8572 | on_peak | 833.2328 |  |  | 0.46 | 0 | 99.54 | 21.7922 | 0
2827 | 788.85 | 18.0472 | 24.2 | 2.9321 | 2.9321 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1742 | 785.9179 | 0 | 0.088511 | 5.8404 | 0 | 0 | 0 | 2.9321 | on_peak | 785.9179 |  |  | 0.37 | 0 | 99.63 | 17.1244 | 0
2828 | 837.9 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 62.4453 | 62.4453 | 0 | 7.4174 | 775.4547 | 0 | 0.088511 | 6.0447 | 0 | 0 | 0 | 0 | on_peak | 775.4547 |  |  | 0 | 7.45 | 92.55 | 0 | 0
2829 | 796.43 | 0 | 23.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 796.43 | 0 | 0.088511 | 6.5043 | 0 | 0 | 0 | 0 | on_peak | 796.43 |  |  | 0 | 0 | 100 | 0 | 0
2830 | 742.76 | 0 | 23.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 742.76 | 0 | 0.05921 | 7.0824 | 0 | 0 | 0 | 0 | off_peak | 742.76 |  |  | 0 | 0 | 100 | 0 | 0
2831 | 823.08 | 0 | 23.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 823.08 | 0 | 0.05921 | 7.4707 | 0 | 0 | 0 | 0 | off_peak | 823.08 |  |  | 0 | 0 | 100 | 0 | 0
2832 | 786.04 | 0 | 23.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 786.04 | 0 | 0.05921 | 7.5049 | 0 | 0 | 0 | 0 | off_peak | 786.04 |  |  | 0 | 0 | 100 | 0 | 0
2833 | 743.69 | 0 | 23.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 743.69 | 0 | 0.05921 | 7.3598 | 0 | 0 | 0 | 0 | off_peak | 743.69 |  |  | 0 | 0 | 100 | 0 | 0
2834 | 645.4 | 0 | 23.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 645.4 | 0 | 0.05921 | 7.2687 | 0 | 0 | 0 | 0 | off_peak | 645.4 |  |  | 0 | 0 | 100 | 0 | 0
2835 | 661.13 | 0 | 23.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 661.13 | 0 | 0.05921 | 6.7949 | 0 | 0 | 0 | 0 | off_peak | 661.13 |  |  | 0 | 0 | 100 | 0 | 0
2836 | 587.11 | 0 | 23.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 587.11 | 0 | 0.05921 | 6.216 | 0 | 0 | 0 | 0 | off_peak | 587.11 |  |  | 0 | 0 | 100 | 0 | 0
2837 | 612.99 | 0 | 23.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 612.99 | 0 | 0.05921 | 5.6832 | 0 | 0 | 0 | 0 | off_peak | 612.99 |  |  | 0 | 0 | 100 | 0 | 0
2838 | 703.27 | 0 | 23.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 703.27 | 0 | 0.05921 | 4.9328 | 0 | 0 | 0 | 0 | off_peak | 703.27 |  |  | 0 | 0 | 100 | 0 | 0
2839 | 722.61 | 23.75 | 23.5 | 3.8683 | 3.8683 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 718.7417 | 0 | 0.05921 | 4.4492 | 0 | 0 | 0 | 3.8683 | off_peak | 718.7417 |  |  | 0.54 | 0 | 99.46 | 17.2107 | 0
2840 | 836.96 | 171.644 | 23.5 | 27.9565 | 27.9565 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 809.0035 | 0 | 0.05921 | 4.1671 | 0 | 0 | 0 | 27.9565 | off_peak | 809.0035 |  |  | 3.34 | 0 | 96.66 | 116.4986 | 0
2841 | 806.43 | 245.922 | 23.4 | 40.0688 | 40.0688 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 766.3612 | 0 | 0.05921 | 3.9518 | 0 | 0 | 0 | 40.0688 | off_peak | 766.3612 |  |  | 4.97 | 0 | 95.03 | 158.346 | 0
2842 | 792.84 | 614.365 | 23.4 | 100.1004 | 100.1004 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 692.7396 | 0 | 0.05921 | 3.8474 | 0 | 0 | 0 | 100.1004 | off_peak | 692.7396 |  |  | 12.63 | 0 | 87.37 | 385.1253 | 0
2843 | 790.3 | 746.915 | 23.4 | 121.6972 | 121.6972 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 668.6028 | 0 | 0.05921 | 3.8474 | 0 | 0 | 0 | 121.6972 | off_peak | 668.6028 |  |  | 15.4 | 0 | 84.6 | 468.2166 | 0
2844 | 778.13 | 523.68 | 23.4 | 85.3248 | 85.3248 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 692.8052 | 0 | 0.05921 | 3.9559 | 0 | 0 | 0 | 85.3248 | off_peak | 692.8052 |  |  | 10.97 | 0 | 89.03 | 337.5339 | 0
2845 | 750.36 | 780.477 | 23.3 | 127.2111 | 127.2111 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 623.1489 | 0 | 0.05921 | 4.1292 | 0 | 0 | 0 | 127.2111 | off_peak | 623.1489 |  |  | 16.95 | 0 | 83.05 | 525.281 | 0
2846 | 729.92 | 229.828 | 23.3 | 37.46 | 37.46 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 692.46 | 0 | 0.05921 | 4.5235 | 0 | 0 | 0 | 37.46 | off_peak | 692.46 |  |  | 5.13 | 0 | 94.87 | 169.4487 | 0
2847 | 752.69 | 238.34 | 23.1 | 38.8752 | 38.8752 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 713.8148 | 0 | 0.05921 | 5.0033 | 0 | 0 | 0 | 38.8752 | off_peak | 713.8148 |  |  | 5.16 | 0 | 94.84 | 194.5034 | 0
2848 | 746.97 | 278.732 | 22.8 | 45.5122 | 45.5122 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 18.9814 | 713.8202 | 0 | 0.05921 | 5.5862 | 0 | 0 | 0 | 45.5122 | off_peak | 701.4578 | 0 | 100 | 6.09 | 0 | 93.91 | 254.242 | 0
2849 | 723.46 | 375.331 | 22.6 | 61.329 | 61.329 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18.9814 | 662.131 | 0 | 0.05921 | 6.1305 | 0 | 0 | 0 | 61.329 | off_peak | 662.131 |  |  | 8.48 | 0 | 91.52 | 375.9792 | 0
2850 | 712.59 | 155.826 | 22.4 | 25.4801 | 25.4801 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18.9814 | 687.1099 | 0 | 0.05921 | 6.7208 | 0 | 0 | 0 | 25.4801 | off_peak | 687.1099 |  |  | 3.58 | 0 | 96.42 | 171.2478 | 0
2851 | 646.02 | 23.6764 | 22.3 | 3.8729 | 3.8729 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18.9814 | 642.1471 | 0 | 0.05921 | 7.1564 | 0 | 0 | 0 | 3.8729 | off_peak | 642.1471 |  |  | 0.6 | 0 | 99.4 | 27.7157 | 0
2852 | 684.9 | 0 | 22.3 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 30.5453 | 697.2624 | 0 | 0.05921 | 7.6033 | 0 | 0 | 0 | 0 | off_peak | 684.9 | 0 | 100 | 0 | 0 | 100 | 0 | 0
2853 | 637.76 | 0 | 22.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30.5453 | 637.76 | 0 | 0.05921 | 7.7675 | 0 | 0 | 0 | 0 | off_peak | 637.76 |  |  | 0 | 0 | 100 | 0 | 0
2854 | 660.22 | 0 | 22.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30.5453 | 660.22 | 0 | 0.05921 | 7.6443 | 0 | 0 | 0 | 0 | off_peak | 660.22 |  |  | 0 | 0 | 100 | 0 | 0
2855 | 561.97 | 0 | 22.5 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 42.1093 | 574.3324 | 0 | 0.05921 | 7.4046 | 0 | 0 | 0 | 0 | off_peak | 561.97 | 0 | 100 | 0 | 0 | 100 | 0 | 0
2856 | 605.37 | 0 | 22.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 42.1093 | 605.37 | 0 | 0.05921 | 7.0627 | 0 | 0 | 0 | 0 | off_peak | 605.37 |  |  | 0 | 0 | 100 | 0 | 0
2857 | 589.44 | 0 | 22.6 | 0 | 0 | 0 | 0 | 8.7006 | 8.7006 | 0 | 0 | 0 | 50.2479 | 598.1406 | 0 | 0.05921 | 6.8721 | 0 | 0 | 0 | 0 | off_peak | 589.44 | 0 | 100 | 0 | 0 | 100 | 0 | 0
2858 | 570.08 | 0 | 22.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50.2479 | 570.08 | 0 | 0.05921 | 6.7885 | 0 | 0 | 0 | 0 | off_peak | 570.08 |  |  | 0 | 0 | 100 | 0 | 0
2859 | 585.27 | 0 | 22.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50.2479 | 585.27 | 0 | 0.05921 | 6.4028 | 0 | 0 | 0 | 0 | off_peak | 585.27 |  |  | 0 | 0 | 100 | 0 | 0
2860 | 584.4 | 0 | 22.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50.2479 | 584.4 | 0 | 0.05921 | 5.9243 | 0 | 0 | 0 | 0 | off_peak | 584.4 |  |  | 0 | 0 | 100 | 0 | 0
2861 | 594.35 | 0 | 22.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50.2479 | 594.35 | 0 | 0.05921 | 5.4815 | 0 | 0 | 0 | 0 | off_peak | 594.35 |  |  | 0 | 0 | 100 | 0 | 0
2862 | 668.37 | 0 | 22.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50.2479 | 668.37 | 0 | 0.05921 | 5.0032 | 0 | 0 | 0 | 0 | off_peak | 668.37 |  |  | 0 | 0 | 100 | 0 | 0
2863 | 728.12 | 55.3733 | 23 | 9.0351 | 9.0351 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50.2479 | 719.0849 | 0 | 0.05921 | 4.5916 | 0 | 0 | 0 | 9.0351 | off_peak | 719.0849 |  |  | 1.24 | 0 | 98.76 | 41.4854 | 0
2864 | 716.31 | 152.933 | 23.2 | 24.9357 | 24.9357 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50.2479 | 691.3743 | 0 | 0.05921 | 4.2711 | 0 | 0 | 0 | 24.9357 | off_peak | 691.3743 |  |  | 3.48 | 0 | 96.52 | 106.5029 | 0
2865 | 794.54 | 423.047 | 23.5 | 68.9037 | 68.9037 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 61.8119 | 737.9987 | 0 | 0.05921 | 4.0922 | 0 | 0 | 0 | 68.9037 | off_peak | 725.6363 | 0 | 100 | 8.67 | 0 | 91.33 | 281.967 | 0
2866 | 781.68 | 274.747 | 23.7 | 44.7173 | 44.7173 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 73.3758 | 749.3251 | 0 | 0.05921 | 4.0303 | 0 | 0 | 0 | 44.7173 | off_peak | 736.9627 | 0 | 100 | 5.72 | 0 | 94.28 | 180.2247 | 0
2867 | 784.05 | 675.974 | 23.9 | 109.9414 | 109.9414 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 73.3758 | 674.1086 | 0 | 0.05921 | 4.0852 | 0 | 0 | 0 | 109.9414 | off_peak | 674.1086 |  |  | 14.02 | 0 | 85.98 | 449.1327 | 0
2868 | 737.53 | 909.756 | 24.2 | 147.8049 | 147.8049 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 73.3758 | 589.7251 | 0 | 0.05921 | 4.2109 | 0 | 0 | 0 | 147.8049 | off_peak | 589.7251 |  |  | 20.04 | 0 | 79.96 | 622.3939 | 0
2869 | 739.49 | 739.763 | 24.4 | 120.1005 | 120.1005 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 73.3758 | 619.3895 | 0 | 0.05921 | 4.3788 | 0 | 0 | 0 | 120.1005 | off_peak | 619.3895 |  |  | 16.24 | 0 | 83.76 | 525.8918 | 0
2870 | 726.4 | 713.48 | 24.5 | 115.7918 | 115.7918 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 73.3758 | 610.6082 | 0 | 0.05921 | 4.6344 | 0 | 0 | 0 | 115.7918 | off_peak | 610.6082 |  |  | 15.94 | 0 | 84.06 | 536.6312 | 0
2871 | 679.85 | 781.2 | 24.5 | 126.7822 | 126.7822 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 73.3758 | 553.0678 | 0 | 0.05921 | 4.8875 | 0 | 0 | 0 | 126.7822 | off_peak | 553.0678 |  |  | 18.65 | 0 | 81.35 | 619.6441 | 0
2872 | 716.54 | 578.989 | 24.4 | 93.9988 | 93.9988 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 73.3758 | 622.5412 | 0 | 0.05921 | 4.9352 | 0 | 0 | 0 | 93.9988 | off_peak | 622.5412 |  |  | 13.12 | 0 | 86.88 | 463.9013 | 0
2873 | 683.62 | 419.958 | 24.1 | 68.2536 | 68.2536 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 73.3758 | 615.3664 | 0 | 0.05921 | 4.8299 | 0 | 0 | 0 | 68.2536 | off_peak | 615.3664 |  |  | 9.98 | 0 | 90.02 | 329.6562 | 0
2874 | 680.35 | 89.3322 | 23.8 | 14.5343 | 14.5343 | 0 | 0 | 0.79843 | 0.79843 | 0 | 0 | 0 | 74.1227 | 666.6141 | 0 | 0.05921 | 4.7272 | 0 | 0 | 0 | 14.5343 | off_peak | 665.8157 | 0 | 100 | 2.14 | 0 | 97.86 | 68.7071 | 0
2875 | 591.66 | 14.25 | 23.6 | 2.3201 | 2.3201 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1227 | 589.3399 | 0 | 0.05921 | 4.7975 | 0 | 0 | 0 | 2.3201 | off_peak | 589.3399 |  |  | 0.39 | 0 | 99.61 | 11.1309 | 0
2876 | 577.36 | 0 | 22.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1227 | 577.36 | 0 | 0.05921 | 4.9324 | 0 | 0 | 0 | 0 | off_peak | 577.36 |  |  | 0 | 0 | 100 | 0 | 0
2877 | 589.25 | 0 | 22.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1227 | 589.25 | 0 | 0.05921 | 5.1128 | 0 | 0 | 0 | 0 | off_peak | 589.25 |  |  | 0 | 0 | 100 | 0 | 0
2878 | 591.34 | 0 | 22.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1227 | 591.34 | 0 | 0.05921 | 5.4154 | 0 | 0 | 0 | 0 | off_peak | 591.34 |  |  | 0 | 0 | 100 | 0 | 0
2879 | 554.2 | 0 | 22.4 | 0 | 0 | 0 | 0 | 0.051567 | 0.051567 | 0 | 0 | 0 | 74.1709 | 554.2516 | 0 | 0.05921 | 5.7363 | 0 | 0 | 0 | 0 | off_peak | 554.2 | 0 | 100 | 0 | 0 | 100 | 0 | 0
2880 | 571.5 | 0 | 22.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1709 | 571.5 | 0 | 0.05921 | 6.1091 | 0 | 0 | 0 | 0 | off_peak | 571.5 |  |  | 0 | 0 | 100 | 0 | 0
2881 | 569.12 | 0 | 22.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1709 | 569.12 | 0 | 0.05921 | 6.2649 | 0 | 0 | 0 | 0 | off_peak | 569.12 |  |  | 0 | 0 | 100 | 0 | 0
2882 | 556.12 | 0 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1709 | 556.12 | 0 | 0.05921 | 6.1887 | 0 | 0 | 0 | 0 | off_peak | 556.12 |  |  | 0 | 0 | 100 | 0 | 0
2883 | 546.7 | 0 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1709 | 546.7 | 0 | 0.05921 | 5.8471 | 0 | 0 | 0 | 0 | off_peak | 546.7 |  |  | 0 | 0 | 100 | 0 | 0
2884 | 558.7 | 0 | 21.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1709 | 558.7 | 0 | 0.05921 | 5.2127 | 0 | 0 | 0 | 0 | off_peak | 558.7 |  |  | 0 | 0 | 100 | 0 | 0
2885 | 580.46 | 0 | 21.8 | 0 | 0 | 0 | 0 | 0.0033305 | 0.0033305 | 0 | 0 | 0 | 74.174 | 580.4633 | 0 | 0.05921 | 4.481 | 0 | 0 | 0 | 0 | off_peak | 580.46 | 0 | 100 | 0 | 0 | 100 | 0 | 0
2886 | 661.12 | 0 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.174 | 661.12 | 0 | 0.05921 | 3.9187 | 0 | 0 | 0 | 0 | off_peak | 661.12 |  |  | 0 | 0 | 100 | 0 | 0
2887 | 740.59 | 96.8793 | 22.6 | 15.83 | 15.83 | 0 | 0 | 0.0002151 | 0.0002151 | 0 | 0 | 0 | 74.1742 | 724.7602 | 0 | 0.05921 | 3.4633 | 0 | 0 | 0 | 15.83 | off_peak | 724.76 | 0 | 100 | 2.14 | 0 | 97.86 | 54.8235 | 0
2888 | 783.69 | 304.035 | 23.3 | 49.5551 | 49.5551 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1742 | 734.1349 | 0 | 0.05921 | 3.1644 | 0 | 0 | 0 | 49.5551 | off_peak | 734.1349 |  |  | 6.32 | 0 | 93.68 | 156.8114 | 0
2889 | 785.25 | 515.318 | 23.9 | 83.8121 | 83.8121 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1742 | 701.4379 | 0 | 0.05921 | 3.0063 | 0 | 0 | 0 | 83.8121 | off_peak | 701.4379 |  |  | 10.67 | 0 | 89.33 | 251.9658 | 0
2890 | 785.88 | 703.435 | 24.6 | 114.1206 | 114.1206 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1742 | 671.7594 | 0 | 0.05921 | 3.0424 | 0 | 0 | 0 | 114.1206 | off_peak | 671.7594 |  |  | 14.52 | 0 | 85.48 | 347.2028 | 0
2891 | 772.97 | 848.878 | 25.2 | 137.4192 | 137.4192 | 0 | 0 | 1.4852e-05 | 1.4852e-05 | 0 | 0 | 0 | 74.1743 | 635.5508 | 0 | 0.05921 | 3.2865 | 0 | 0 | 0 | 137.4192 | off_peak | 635.5508 | 0 | 100 | 17.78 | 0 | 82.22 | 451.6333 | 0
2892 | 812.8 | 935.555 | 25.6 | 151.2325 | 151.2325 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1743 | 661.5675 | 0 | 0.05921 | 3.7268 | 0 | 0 | 0 | 151.2325 | off_peak | 661.5675 |  |  | 18.61 | 0 | 81.39 | 563.6111 | 0
2893 | 791.66 | 954.667 | 25.9 | 154.155 | 154.155 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1743 | 637.505 | 0 | 0.088511 | 3.928 | 0 | 0 | 0 | 154.155 | on_peak | 637.505 |  |  | 19.47 | 0 | 80.53 | 605.5149 | 0
2894 | 810.58 | 908.484 | 26.1 | 146.5916 | 146.5916 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1743 | 663.9884 | 0 | 0.088511 | 3.8931 | 0 | 0 | 0 | 146.5916 | on_peak | 663.9884 |  |  | 18.08 | 0 | 81.92 | 570.7013 | 0
2895 | 890.07 | 799.786 | 26.2 | 129.0056 | 129.0056 | 0 | 0 | 0 | 0 | 62.4453 | 62.4453 | 0 | 7.4174 | 698.6191 | 0 | 0.088511 | 3.8408 | 0 | 0 | 0 | 129.0056 | on_peak | 698.6191 |  |  | 14.49 | 7.02 | 78.49 | 495.4897 | 0
2896 | 886.03 | 487.256 | 26 | 78.6513 | 78.6513 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 807.3787 | 0 | 0.088511 | 3.8689 | 0 | 0 | 0 | 78.6513 | on_peak | 807.3787 |  |  | 8.88 | 0 | 91.12 | 304.2919 | 0
2897 | 872.97 | 376.005 | 25.7 | 60.7593 | 60.7593 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 812.2107 | 0 | 0.088511 | 4.056 | 0 | 0 | 0 | 60.7593 | on_peak | 812.2107 |  |  | 6.96 | 0 | 93.04 | 246.4398 | 0
2898 | 859.47 | 222.419 | 25 | 36.0319 | 36.0319 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 823.4381 | 0 | 0.088511 | 4.3854 | 0 | 0 | 0 | 36.0319 | on_peak | 823.4381 |  |  | 4.19 | 0 | 95.81 | 158.0139 | 0
2899 | 790.12 | 37.8942 | 24.7 | 6.1455 | 6.1455 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 783.9745 | 0 | 0.088511 | 4.7928 | 0 | 0 | 0 | 6.1455 | on_peak | 783.9745 |  |  | 0.78 | 0 | 99.22 | 29.4538 | 0
2900 | 812.73 | 0 | 23.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 812.73 | 0 | 0.088511 | 5.2066 | 0 | 0 | 0 | 0 | on_peak | 812.73 |  |  | 0 | 0 | 100 | 0 | 0
2901 | 795.1 | 0 | 23.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 795.1 | 0 | 0.088511 | 5.5947 | 0 | 0 | 0 | 0 | on_peak | 795.1 |  |  | 0 | 0 | 100 | 0 | 0
2902 | 776.16 | 0 | 22.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 776.16 | 0 | 0.05921 | 6.0325 | 0 | 0 | 0 | 0 | off_peak | 776.16 |  |  | 0 | 0 | 100 | 0 | 0
2903 | 780.95 | 0 | 22.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 780.95 | 0 | 0.05921 | 6.4529 | 0 | 0 | 0 | 0 | off_peak | 780.95 |  |  | 0 | 0 | 100 | 0 | 0
2904 | 773.25 | 0 | 22.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 773.25 | 0 | 0.05921 | 6.7591 | 0 | 0 | 0 | 0 | off_peak | 773.25 |  |  | 0 | 0 | 100 | 0 | 0
2905 | 705.41 | 0 | 22.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 705.41 | 0 | 0.05921 | 6.8807 | 0 | 0 | 0 | 0 | off_peak | 705.41 |  |  | 0 | 0 | 100 | 0 | 0
2906 | 664.77 | 0 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 664.77 | 0 | 0.05921 | 6.7393 | 0 | 0 | 0 | 0 | off_peak | 664.77 |  |  | 0 | 0 | 100 | 0 | 0
2907 | 638.85 | 0 | 22 | 0 | 0 | 0 | 0 | 8.7006 | 8.7006 | 0 | 0 | 0 | 15.5561 | 647.5506 | 0 | 0.05921 | 6.2395 | 0 | 0 | 0 | 0 | off_peak | 638.85 | 0 | 100 | 0 | 0 | 100 | 0 | 0
2908 | 582.92 | 0 | 21.9 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 27.12 | 595.2824 | 0 | 0.05921 | 5.5137 | 0 | 0 | 0 | 0 | off_peak | 582.92 | 0 | 100 | 0 | 0 | 100 | 0 | 0
2909 | 631.39 | 0 | 21.8 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 38.684 | 643.7524 | 0 | 0.05921 | 4.6711 | 0 | 0 | 0 | 0 | off_peak | 631.39 | 0 | 100 | 0 | 0 | 100 | 0 | 0
2910 | 718.52 | 0 | 22 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 50.2479 | 730.8824 | 0 | 0.05921 | 4.0093 | 0 | 0 | 0 | 0 | off_peak | 718.52 | 0 | 100 | 0 | 0 | 100 | 0 | 0
2911 | 739.19 | 101.381 | 22.6 | 16.5656 | 16.5656 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 61.8119 | 734.9868 | 0 | 0.05921 | 3.5747 | 0 | 0 | 0 | 16.5656 | off_peak | 722.6244 | 0 | 100 | 2.24 | 0 | 97.76 | 59.2175 | 0
2912 | 767.59 | 306.249 | 23.4 | 49.8981 | 49.8981 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 73.3758 | 730.0543 | 0 | 0.05921 | 3.3383 | 0 | 0 | 0 | 49.8981 | off_peak | 717.6919 | 0 | 100 | 6.5 | 0 | 93.5 | 166.5736 | 0
2913 | 801.91 | 518.191 | 24 | 84.2492 | 84.2492 | 0 | 0 | 0.79843 | 0.79843 | 0 | 0 | 0 | 74.1227 | 718.4593 | 0 | 0.05921 | 3.1529 | 0 | 0 | 0 | 84.2492 | off_peak | 717.6608 | 0 | 100 | 10.51 | 0 | 89.49 | 265.6265 | 0
2914 | 807.42 | 703.456 | 24.7 | 114.0829 | 114.0829 | 0 | 0 | 0.051567 | 0.051567 | 0 | 0 | 0 | 74.1709 | 693.3886 | 0 | 0.05921 | 3.0988 | 0 | 0 | 0 | 114.0829 | off_peak | 693.3371 | 0 | 100 | 14.13 | 0 | 85.87 | 353.5204 | 0
2915 | 815.62 | 844.219 | 25.3 | 136.6158 | 136.6158 | 0 | 0 | 0.0033305 | 0.0033305 | 0 | 0 | 0 | 74.174 | 679.0076 | 0 | 0.05921 | 3.254 | 0 | 0 | 0 | 136.6158 | off_peak | 679.0042 | 0 | 100 | 16.75 | 0 | 83.25 | 444.5478 | 0
2916 | 835.82 | 925.063 | 25.7 | 149.4826 | 149.4826 | 0 | 0 | 0.0002151 | 0.0002151 | 0 | 0 | 0 | 74.1742 | 686.3377 | 0 | 0.05921 | 3.6966 | 0 | 0 | 0 | 149.4826 | off_peak | 686.3374 | 0 | 100 | 17.88 | 0 | 82.12 | 552.5772 | 0
2917 | 825.4 | 943.646 | 26.1 | 152.2653 | 152.2653 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1742 | 673.1347 | 0 | 0.088511 | 3.9237 | 0 | 0 | 0 | 152.2653 | on_peak | 673.1347 |  |  | 18.45 | 0 | 81.55 | 597.4413 | 0
2918 | 821.64 | 896.105 | 26.3 | 144.4896 | 144.4896 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1742 | 677.1504 | 0 | 0.088511 | 3.9614 | 0 | 0 | 0 | 144.4896 | on_peak | 677.1504 |  |  | 17.59 | 0 | 82.41 | 572.3873 | 0
2919 | 903.18 | 784.591 | 26.4 | 126.4631 | 126.4631 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1742 | 776.7169 | 0 | 0.088511 | 3.961 | 0 | 0 | 0 | 126.4631 | on_peak | 776.7169 |  |  | 14 | 0 | 86 | 500.9179 | 0
2920 | 887.15 | 624.343 | 26.3 | 100.6702 | 100.6702 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1742 | 786.4798 | 0 | 0.088511 | 4.1193 | 0 | 0 | 0 | 100.6702 | on_peak | 786.4798 |  |  | 11.35 | 0 | 88.65 | 414.6929 | 0
2921 | 907.78 | 428.655 | 26 | 69.1921 | 69.1921 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1742 | 838.5879 | 0 | 0.088511 | 4.3554 | 0 | 0 | 0 | 69.1921 | on_peak | 838.5879 |  |  | 7.62 | 0 | 92.38 | 301.3583 | 0
2922 | 894.7 | 218.384 | 25.4 | 35.3273 | 35.3273 | 0 | 0 | 0 | 0 | 4.4305 | 4.4305 | 0 | 69.4378 | 854.9422 | 0 | 0.088511 | 4.7485 | 0 | 0 | 0 | 35.3273 | on_peak | 854.9422 |  |  | 3.95 | 0.5 | 95.56 | 167.7524 | 0
2923 | 814.4 | 34.289 | 24.9 | 5.5568 | 5.5568 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 69.4378 | 808.8432 | 0 | 0.088511 | 5.1986 | 0 | 0 | 0 | 5.5568 | on_peak | 808.8432 |  |  | 0.68 | 0 | 99.32 | 28.8874 | 0
2924 | 893.12 | 0 | 23.8 | 0 | 0 | 0 | 0 | 0 | 0 | 58.0147 | 58.0147 | 0 | 7.4174 | 835.1053 | 0 | 0.088511 | 5.6316 | 0 | 0 | 0 | 0 | on_peak | 835.1053 |  |  | 0 | 6.5 | 93.5 | 0 | 0
2925 | 851.08 | 0 | 23.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 851.08 | 0 | 0.088511 | 5.9993 | 0 | 0 | 0 | 0 | on_peak | 851.08 |  |  | 0 | 0 | 100 | 0 | 0
2926 | 773.75 | 0 | 23.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 773.75 | 0 | 0.05921 | 6.4949 | 0 | 0 | 0 | 0 | off_peak | 773.75 |  |  | 0 | 0 | 100 | 0 | 0
2927 | 813.69 | 0 | 22.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 813.69 | 0 | 0.05921 | 6.8912 | 0 | 0 | 0 | 0 | off_peak | 813.69 |  |  | 0 | 0 | 100 | 0 | 0
2928 | 813.48 | 0 | 22.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 813.48 | 0 | 0.05921 | 7.2316 | 0 | 0 | 0 | 0 | off_peak | 813.48 |  |  | 0 | 0 | 100 | 0 | 0
2929 | 718.35 | 0 | 22.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 718.35 | 0 | 0.05921 | 7.3255 | 0 | 0 | 0 | 0 | off_peak | 718.35 |  |  | 0 | 0 | 100 | 0 | 0
2930 | 563.84 | 0 | 22.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 563.84 | 0 | 0.05921 | 7.1506 | 0 | 0 | 0 | 0 | off_peak | 563.84 |  |  | 0 | 0 | 100 | 0 | 0
2931 | 529.81 | 0 | 22.4 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 18.9814 | 542.1724 | 0 | 0.05921 | 6.5846 | 0 | 0 | 0 | 0 | off_peak | 529.81 | 0 | 100 | 0 | 0 | 100 | 0 | 0
2932 | 500.84 | 0 | 22.3 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 30.5453 | 513.2024 | 0 | 0.05921 | 5.8092 | 0 | 0 | 0 | 0 | off_peak | 500.84 | 0 | 100 | 0 | 0 | 100 | 0 | 0
2933 | 535.74 | 0 | 22.1 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 42.1093 | 548.1024 | 0 | 0.05921 | 4.9587 | 0 | 0 | 0 | 0 | off_peak | 535.74 | 0 | 100 | 0 | 0 | 100 | 0 | 0
2934 | 711.06 | 0 | 22.4 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 53.6732 | 723.4224 | 0 | 0.05921 | 4.212 | 0 | 0 | 0 | 0 | off_peak | 711.06 | 0 | 100 | 0 | 0 | 100 | 0 | 0
2935 | 726.3 | 103.821 | 23.2 | 16.928 | 16.928 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 65.2371 | 721.7344 | 0 | 0.05921 | 3.7811 | 0 | 0 | 0 | 16.928 | off_peak | 709.372 | 0 | 100 | 2.33 | 0 | 97.67 | 64.0073 | 0
2936 | 777.28 | 277.582 | 24 | 45.1302 | 45.1302 | 0 | 0 | 8.9371 | 8.9371 | 0 | 0 | 0 | 73.597 | 741.0869 | 0 | 0.05921 | 3.5071 | 0 | 0 | 0 | 45.1302 | off_peak | 732.1498 | 0 | 100 | 5.81 | 0 | 94.19 | 158.2776 | 0
2937 | 815.17 | 423.137 | 24.7 | 68.6222 | 68.6222 | 0 | 0 | 0.57721 | 0.57721 | 0 | 0 | 0 | 74.137 | 747.125 | 0 | 0.05921 | 3.3311 | 0 | 0 | 0 | 68.6222 | off_peak | 746.5478 | 0 | 100 | 8.42 | 0 | 91.58 | 228.5886 | 0
2938 | 795.03 | 640.256 | 25.3 | 103.6095 | 103.5722 | 0 | 0.037279 | 0.037279 | 0 | 0 | 0 | 0 | 74.1718 | 691.4578 | 0 | 0.05921 | 3.2834 | 0 | 0 | 0.034872 | 103.5722 | off_peak | 691.4578 | 100 | 0 | 13.03 | 0 | 86.97 | 340.0676 | 0
2939 | 796.43 | 818.188 | 25.9 | 132.117 | 132.1146 | 0 | 0.0024077 | 0.0024077 | 0 | 0 | 0 | 0 | 74.1741 | 664.3154 | 0 | 0.05921 | 3.4849 | 0 | 0 | 0.037124 | 132.1146 | off_peak | 664.3154 | 100 | 0 | 16.59 | 0 | 83.41 | 460.4024 | 0
2940 | 868.83 | 907.304 | 26.3 | 146.2954 | 146.2954 | 0 | 0 | 0.0001555 | 0.0001555 | 0 | 0 | 0 | 74.1742 | 722.5348 | 0 | 0.05921 | 3.9311 | 0 | 0 | 0.037124 | 146.2954 | off_peak | 722.5346 | 0 | 100 | 16.84 | 0 | 83.16 | 575.1046 | 0
2941 | 819.49 | 809.286 | 26.7 | 130.302 | 130.302 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1742 | 689.188 | 0 | 0.088511 | 4.1135 | 0 | 0 | 0.037124 | 130.302 | on_peak | 689.188 |  |  | 15.9 | 0 | 84.1 | 535.9921 | 0
2942 | 849.86 | 805.152 | 26.9 | 129.5425 | 129.5425 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1742 | 720.3175 | 0 | 0.088511 | 4.1373 | 0 | 0 | 0.037124 | 129.5425 | on_peak | 720.3175 |  |  | 15.24 | 0 | 84.76 | 535.9526 | 0
2943 | 908.8 | 770.334 | 26.9 | 123.9405 | 123.9405 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1742 | 784.8595 | 0 | 0.088511 | 4.1773 | 0 | 0 | 0.037124 | 123.9405 | on_peak | 784.8595 |  |  | 13.64 | 0 | 86.36 | 517.7382 | 0
2944 | 903.54 | 477.687 | 26.7 | 76.9117 | 76.9117 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1742 | 826.6283 | 0 | 0.088511 | 4.247 | 0 | 0 | 0.037124 | 76.9117 | on_peak | 826.6283 |  |  | 8.51 | 0 | 91.49 | 326.6462 | 0
2945 | 893.79 | 376.891 | 26.4 | 60.7486 | 60.7486 | 0 | 0 | 0 | 0 | 36.8197 | 36.8197 | 0 | 34.8123 | 796.2217 | 0 | 0.088511 | 4.3855 | 0.034726 | 0 | 0 | 60.7833 | on_peak | 796.2217 |  |  | 6.8 | 4.12 | 89.08 | 266.5661 | 0
2946 | 878.74 | 209.42 | 25.7 | 33.8405 | 33.8405 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 34.8123 | 844.8995 | 0 | 0.088511 | 4.6583 | 0 | 0 | 0 | 33.8405 | on_peak | 844.8995 |  |  | 3.85 | 0 | 96.15 | 157.6407 | 0
2947 | 835.03 | 35.1914 | 25.2 | 5.6969 | 5.6969 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 34.8123 | 829.3331 | 0 | 0.088511 | 5.0567 | 0 | 0 | 0 | 5.6969 | on_peak | 829.3331 |  |  | 0.68 | 0 | 99.32 | 28.8078 | 0
2948 | 876.43 | 0 | 24.1 | 0 | 0 | 0 | 0 | 0 | 0 | 21.4878 | 21.4878 | 0 | 11.8409 | 854.9422 | 0 | 0.088511 | 5.4214 | 0 | 0 | 0 | 0 | on_peak | 854.9422 |  |  | 0 | 2.45 | 97.55 | 0 | 0
2949 | 859.08 | 0 | 23.9 | 0 | 0 | 0 | 0 | 0 | 0 | 4.1378 | 4.1378 | 0 | 7.4174 | 854.9422 | 0 | 0.088511 | 5.7971 | 0 | 0 | 0 | 0 | on_peak | 854.9422 |  |  | 0 | 0.48 | 99.52 | 0 | 0
2950 | 751.38 | 0 | 23.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 751.38 | 0 | 0.05921 | 6.3501 | 0 | 0 | 0 | 0 | off_peak | 751.38 |  |  | 0 | 0 | 100 | 0 | 0
2951 | 789.36 | 0 | 23.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 789.36 | 0 | 0.05921 | 6.7912 | 0 | 0 | 0 | 0 | off_peak | 789.36 |  |  | 0 | 0 | 100 | 0 | 0
2952 | 736.57 | 0 | 23.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 736.57 | 0 | 0.05921 | 7.138 | 0 | 0 | 0 | 0 | off_peak | 736.57 |  |  | 0 | 0 | 100 | 0 | 0
2953 | 720.64 | 0 | 23.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 720.64 | 0 | 0.05921 | 7.2332 | 0 | 0 | 0 | 0 | off_peak | 720.64 |  |  | 0 | 0 | 100 | 0 | 0
2954 | 652.45 | 0 | 23.4 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 18.9814 | 664.8124 | 0 | 0.05921 | 7.0618 | 0 | 0 | 0 | 0 | off_peak | 652.45 | 0 | 100 | 0 | 0 | 100 | 0 | 0
2955 | 620.21 | 0 | 23.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18.9814 | 620.21 | 0 | 0.05921 | 6.4713 | 0 | 0 | 0 | 0 | off_peak | 620.21 |  |  | 0 | 0 | 100 | 0 | 0
2956 | 582.57 | 0 | 23 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 30.5453 | 594.9324 | 0 | 0.05921 | 5.7161 | 0 | 0 | 0 | 0 | off_peak | 582.57 | 0 | 100 | 0 | 0 | 100 | 0 | 0
2957 | 594.07 | 0 | 22.7 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 42.1093 | 606.4324 | 0 | 0.05921 | 4.7751 | 0 | 0 | 0 | 0 | off_peak | 594.07 | 0 | 100 | 0 | 0 | 100 | 0 | 0
2958 | 694.77 | 0 | 22.7 | 0 | 0 | 0 | 0 | 8.7006 | 8.7006 | 0 | 0 | 0 | 50.2479 | 703.4706 | 0 | 0.05921 | 4.0103 | 0 | 0 | 0 | 0 | off_peak | 694.77 | 0 | 100 | 0 | 0 | 100 | 0 | 0
2959 | 754.74 | 102.764 | 23.3 | 16.7497 | 16.7497 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 61.8119 | 750.3527 | 0 | 0.05921 | 3.5254 | 0 | 0 | 0 | 16.7497 | off_peak | 737.9903 | 0 | 100 | 2.22 | 0 | 97.78 | 59.0496 | 0
2960 | 792.23 | 307.97 | 24.3 | 50.0169 | 50.0169 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 73.3758 | 754.5755 | 0 | 0.05921 | 3.3156 | 0 | 0 | 0 | 50.0169 | off_peak | 742.2131 | 0 | 100 | 6.31 | 0 | 93.69 | 165.837 | 0
2961 | 781.8 | 518.838 | 25.3 | 83.961 | 83.961 | 0 | 0 | 0.79843 | 0.79843 | 0 | 0 | 0 | 74.1227 | 698.6375 | 0 | 0.05921 | 3.1461 | 0 | 0 | 0 | 83.961 | off_peak | 697.839 | 0 | 100 | 10.74 | 0 | 89.26 | 264.1456 | 0
2962 | 821.14 | 704.72 | 26.4 | 113.5893 | 113.5377 | 0 | 0.051567 | 0.051567 | 0 | 0 | 0 | 0 | 74.1709 | 707.6023 | 0 | 0.05921 | 3.0936 | 0 | 0 | 0.048237 | 113.5377 | off_peak | 707.6023 | 100 | 0 | 13.83 | 0 | 86.17 | 351.2368 | 0
2963 | 798.59 | 845.905 | 27.4 | 135.8526 | 135.8526 | 0 | 0 | 0.0033305 | 0.0033305 | 0 | 0 | 0 | 74.174 | 662.7407 | 0 | 0.05921 | 3.3459 | 0 | 0 | 0.048237 | 135.8526 | off_peak | 662.7374 | 0 | 100 | 17.01 | 0 | 82.99 | 454.5462 | 0
2964 | 856.49 | 930.411 | 28.2 | 148.9902 | 148.9902 | 0 | 0 | 0.0002151 | 0.0002151 | 0 | 0 | 0 | 74.1742 | 707.5 | 0 | 0.05921 | 3.7309 | 0 | 0 | 0.048237 | 148.9902 | off_peak | 707.4998 | 0 | 100 | 17.4 | 0 | 82.6 | 555.8694 | 0
2965 | 755.27 | 944.201 | 28.8 | 150.8681 | 150.8681 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1742 | 604.4019 | 0 | 0.088511 | 3.8334 | 0 | 0 | 0.048237 | 150.8681 | on_peak | 604.4019 |  |  | 19.98 | 0 | 80.02 | 578.3407 | 0
2966 | 801.68 | 892.899 | 29.1 | 142.5146 | 142.5146 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1742 | 659.1654 | 0 | 0.088511 | 3.8157 | 0 | 0 | 0.048237 | 142.5146 | on_peak | 659.1654 |  |  | 17.78 | 0 | 82.22 | 543.7897 | 0
2967 | 916.44 | 787.094 | 29.3 | 125.5354 | 125.5354 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1742 | 790.9046 | 0 | 0.088511 | 3.7508 | 0 | 0 | 0.048237 | 125.5354 | on_peak | 790.9046 |  |  | 13.7 | 0 | 86.3 | 470.8533 | 0
2968 | 895.37 | 626.728 | 29.2 | 99.9948 | 99.9948 | 0 | 0 | 0 | 0 | 0.045121 | 0.045121 | 0 | 74.126 | 795.3301 | 0 | 0.088511 | 3.7981 | 0.045121 | 0 | 0 | 100.0399 | on_peak | 795.3301 |  |  | 11.17 | 0.01 | 88.83 | 379.9628 | 0
2969 | 877.93 | 431.158 | 28.8 | 68.8921 | 68.8921 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.126 | 809.0379 | 0 | 0.088511 | 3.9897 | 0 | 0 | 0 | 68.8921 | on_peak | 809.0379 |  |  | 7.85 | 0 | 92.15 | 274.8609 | 0
2970 | 901.64 | 221.868 | 28 | 35.5544 | 35.5544 | 0 | 0 | 0 | 0 | 38.9024 | 38.9024 | 0 | 32.5376 | 827.1832 | 0 | 0.088511 | 4.3449 | 0 | 0 | 0 | 35.5544 | on_peak | 827.1832 |  |  | 3.94 | 4.31 | 91.74 | 154.4788 | 0
2971 | 822.82 | 32.4252 | 27.4 | 5.2075 | 5.2075 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 32.5376 | 817.6125 | 0 | 0.088511 | 4.829 | 0 | 0 | 0 | 5.2075 | on_peak | 817.6125 |  |  | 0.63 | 0 | 99.37 | 25.1472 | 0
2972 | 878.44 | 0 | 26.1 | 0 | 0 | 0 | 0 | 0 | 0 | 23.4978 | 23.4978 | 0 | 7.4174 | 854.9422 | 0 | 0.088511 | 5.2617 | 0 | 0 | 0 | 0 | on_peak | 854.9422 |  |  | 0 | 2.67 | 97.33 | 0 | 0
2973 | 817.62 | 0 | 25.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 817.62 | 0 | 0.088511 | 5.6455 | 0 | 0 | 0 | 0 | on_peak | 817.62 |  |  | 0 | 0 | 100 | 0 | 0
2974 | 767 | 0 | 25.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 767 | 0 | 0.05921 | 6.1147 | 0 | 0 | 0 | 0 | off_peak | 767 |  |  | 0 | 0 | 100 | 0 | 0
2975 | 796.29 | 0 | 25.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 796.29 | 0 | 0.05921 | 6.5873 | 0 | 0 | 0 | 0 | off_peak | 796.29 |  |  | 0 | 0 | 100 | 0 | 0
2976 | 782.01 | 0 | 24.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 782.01 | 0 | 0.05921 | 6.9155 | 0 | 0 | 0 | 0 | off_peak | 782.01 |  |  | 0 | 0 | 100 | 0 | 0
2977 | 746.71 | 0 | 24.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 746.71 | 0 | 0.05921 | 6.8316 | 0 | 0 | 0 | 0 | off_peak | 746.71 |  |  | 0 | 0 | 100 | 0 | 0
2978 | 694.19 | 0 | 23.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 694.19 | 0 | 0.05921 | 6.748 | 0 | 0 | 0 | 0 | off_peak | 694.19 |  |  | 0 | 0 | 100 | 0 | 0
2979 | 671.64 | 0 | 23.6 | 0 | 0 | 0 | 0 | 8.7006 | 8.7006 | 0 | 0 | 0 | 15.5561 | 680.3406 | 0 | 0.05921 | 6.2503 | 0 | 0 | 0 | 0 | off_peak | 671.64 | 0 | 100 | 0 | 0 | 100 | 0 | 0
2980 | 596.4 | 0 | 23.3 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 27.12 | 608.7624 | 0 | 0.05921 | 5.5407 | 0 | 0 | 0 | 0 | off_peak | 596.4 | 0 | 100 | 0 | 0 | 100 | 0 | 0
2981 | 644.53 | 0 | 23.1 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 38.684 | 656.8924 | 0 | 0.05921 | 4.7183 | 0 | 0 | 0 | 0 | off_peak | 644.53 | 0 | 100 | 0 | 0 | 100 | 0 | 0
2982 | 693.3 | 0 | 23.2 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 50.2479 | 705.6624 | 0 | 0.05921 | 4.0081 | 0 | 0 | 0 | 0 | off_peak | 693.3 | 0 | 100 | 0 | 0 | 100 | 0 | 0
2983 | 782.11 | 106.5 | 23.9 | 17.3213 | 17.3213 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 61.8119 | 777.1511 | 0 | 0.05921 | 3.5698 | 0 | 0 | 0 | 17.3213 | off_peak | 764.7887 | 0 | 100 | 2.21 | 0 | 97.79 | 61.833 | 0
2984 | 818.09 | 312.857 | 25 | 50.6828 | 50.6828 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 73.3758 | 779.7695 | 0 | 0.05921 | 3.4454 | 0 | 0 | 0 | 50.6828 | off_peak | 767.4072 | 0 | 100 | 6.2 | 0 | 93.8 | 174.6232 | 0
2985 | 806.55 | 377.729 | 26.2 | 60.9277 | 60.9277 | 0 | 0 | 0.79843 | 0.79843 | 0 | 0 | 0 | 74.1227 | 746.4207 | 0 | 0.05921 | 3.2768 | 0 | 0 | 0 | 60.9277 | off_peak | 745.6223 | 0 | 100 | 7.55 | 0 | 92.45 | 199.65 | 0
2986 | 813.48 | 707.985 | 27.4 | 113.7026 | 113.7026 | 0 | 0 | 0.051567 | 0.051567 | 0 | 0 | 0 | 74.1709 | 699.8289 | 0 | 0.05921 | 3.2125 | 0 | 0 | 0 | 113.7026 | off_peak | 699.7774 | 0 | 100 | 13.98 | 0 | 86.02 | 365.2739 | 0
2987 | 795.94 | 847.943 | 28.3 | 135.7348 | 135.7315 | 0 | 0.0033305 | 0.0033305 | 0 | 0 | 0 | 0 | 74.174 | 660.2085 | 0 | 0.05921 | 3.3841 | 0 | 0 | 0.0031154 | 135.7315 | off_peak | 660.2085 | 100 | 0 | 17.05 | 0 | 82.95 | 459.3232 | 0
2988 | 855.11 | 932.051 | 29 | 148.818 | 148.818 | 0 | 0 | 0.0002151 | 0.0002151 | 0 | 0 | 0 | 74.1742 | 706.2922 | 0 | 0.05921 | 3.7989 | 0 | 0 | 0.0031154 | 148.818 | off_peak | 706.292 | 0 | 100 | 17.4 | 0 | 82.6 | 565.3453 | 0
2989 | 795.69 | 953.978 | 29.4 | 152.0965 | 152.0965 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1742 | 643.5935 | 0 | 0.088511 | 4.0556 | 0 | 0 | 0.0031154 | 152.0965 | on_peak | 643.5935 |  |  | 19.12 | 0 | 80.88 | 616.8497 | 0
2990 | 858.07 | 910.282 | 29.7 | 144.9706 | 144.9706 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1742 | 713.0994 | 0 | 0.088511 | 4.2532 | 0 | 0 | 0.0031154 | 144.9706 | on_peak | 713.0994 |  |  | 16.89 | 0 | 83.11 | 616.584 | 0
2991 | 935.42 | 803.439 | 29.8 | 127.908 | 127.908 | 0 | 0 | 0 | 0 | 0.0029142 | 0.0029142 | 0 | 74.1711 | 807.5091 | 0 | 0.088511 | 4.4019 | 0.0029142 | 0 | 0 | 127.9109 | on_peak | 807.5091 |  |  | 13.67 | 0 | 86.33 | 563.0462 | 0
2992 | 885 | 644.505 | 29.7 | 102.6432 | 102.6432 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1711 | 782.3568 | 0 | 0.088511 | 4.6844 | 0 | 0 | 0 | 102.6432 | on_peak | 782.3568 |  |  | 11.6 | 0 | 88.4 | 480.8222 | 0
2993 | 887.68 | 445.304 | 29.3 | 71.0225 | 71.0225 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1711 | 816.6575 | 0 | 0.088511 | 5.1016 | 0 | 0 | 0 | 71.0225 | on_peak | 816.6575 |  |  | 8 | 0 | 92 | 362.3315 | 0
2994 | 903.47 | 231.186 | 28.6 | 36.9668 | 36.9668 | 0 | 0 | 0 | 0 | 11.561 | 11.561 | 0 | 61.8118 | 854.9422 | 0 | 0.088511 | 5.476 | 0 | 0 | 0 | 36.9668 | on_peak | 854.9422 |  |  | 4.09 | 1.28 | 94.63 | 202.4287 | 0
2995 | 838.34 | 39.6236 | 28.2 | 6.3451 | 6.3451 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 61.8118 | 831.9949 | 0 | 0.088511 | 5.8178 | 0 | 0 | 0 | 6.3451 | on_peak | 831.9949 |  |  | 0.76 | 0 | 99.24 | 36.9145 | 0
2996 | 825.57 | 0 | 27 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 61.8118 | 825.57 | 0 | 0.088511 | 6.1539 | 0 | 0 | 0 | 0 | on_peak | 825.57 |  |  | 0 | 0 | 100 | 0 | 0
2997 | 804.53 | 0 | 26.4 | 0 | 0 | 0 | 0 | 0 | 0 | 50.8813 | 50.8813 | 0 | 7.4174 | 753.6487 | 0 | 0.088511 | 6.4419 | 0 | 0 | 0 | 0 | on_peak | 753.6487 |  |  | 0 | 6.32 | 93.68 | 0 | 0
2998 | 779.28 | 0 | 25.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 779.28 | 0 | 0.05921 | 6.7589 | 0 | 0 | 0 | 0 | off_peak | 779.28 |  |  | 0 | 0 | 100 | 0 | 0
2999 | 777.75 | 0 | 25.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 777.75 | 0 | 0.05921 | 6.9257 | 0 | 0 | 0 | 0 | off_peak | 777.75 |  |  | 0 | 0 | 100 | 0 | 0
3000 | 760.51 | 0 | 24.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 760.51 | 0 | 0.05921 | 6.9351 | 0 | 0 | 0 | 0 | off_peak | 760.51 |  |  | 0 | 0 | 100 | 0 | 0
3001 | 765.17 | 0 | 24.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 765.17 | 0 | 0.05921 | 6.7464 | 0 | 0 | 0 | 0 | off_peak | 765.17 |  |  | 0 | 0 | 100 | 0 | 0
3002 | 682.07 | 0 | 24.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 682.07 | 0 | 0.05921 | 6.6125 | 0 | 0 | 0 | 0 | off_peak | 682.07 |  |  | 0 | 0 | 100 | 0 | 0
3003 | 630.16 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 630.16 | 0 | 0.05921 | 6.2284 | 0 | 0 | 0 | 0 | off_peak | 630.16 |  |  | 0 | 0 | 100 | 0 | 0
3004 | 614.91 | 0 | 23.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 614.91 | 0 | 0.05921 | 5.7437 | 0 | 0 | 0 | 0 | off_peak | 614.91 |  |  | 0 | 0 | 100 | 0 | 0
3005 | 618.43 | 0 | 23.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 618.43 | 0 | 0.05921 | 5.0555 | 0 | 0 | 0 | 0 | off_peak | 618.43 |  |  | 0 | 0 | 100 | 0 | 0
3006 | 722.04 | 0 | 23.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 722.04 | 0 | 0.05921 | 4.3709 | 0 | 0 | 0 | 0 | off_peak | 722.04 |  |  | 0 | 0 | 100 | 0 | 0
3007 | 735.15 | 113.334 | 24.6 | 18.3865 | 18.3865 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 716.7635 | 0 | 0.05921 | 3.998 | 0 | 0 | 0 | 18.3865 | off_peak | 716.7635 |  |  | 2.5 | 0 | 97.5 | 73.5095 | 0
3008 | 743.08 | 320.061 | 25.5 | 51.7566 | 51.7566 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 691.3234 | 0 | 0.05921 | 3.8255 | 0 | 0 | 0 | 51.7566 | off_peak | 691.3234 |  |  | 6.97 | 0 | 93.03 | 197.9945 | 0
3009 | 784.11 | 531.07 | 26.3 | 85.6307 | 85.6307 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 698.4793 | 0 | 0.05921 | 3.5955 | 0 | 0 | 0 | 85.6307 | off_peak | 698.4793 |  |  | 10.92 | 0 | 89.08 | 307.8884 | 0
3010 | 729.85 | 717.709 | 27.2 | 115.348 | 115.348 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 614.502 | 0 | 0.05921 | 3.4806 | 0 | 0 | 0 | 115.348 | off_peak | 614.502 |  |  | 15.8 | 0 | 84.2 | 401.4749 | 0
3011 | 719.27 | 859.24 | 27.9 | 137.7437 | 137.7437 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 581.5263 | 0 | 0.05921 | 3.485 | 0 | 0 | 0 | 137.7437 | off_peak | 581.5263 |  |  | 19.15 | 0 | 80.85 | 480.0328 | 0
3012 | 764.83 | 815.187 | 28.6 | 130.3488 | 130.3488 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 634.4812 | 0 | 0.05921 | 3.5678 | 0 | 0 | 0 | 130.3488 | off_peak | 634.4812 |  |  | 17.04 | 0 | 82.96 | 465.0554 | 0
3013 | 739.99 | 940.012 | 29.1 | 150.0343 | 150.0343 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 589.9557 | 0 | 0.05921 | 3.7384 | 0 | 0 | 0 | 150.0343 | off_peak | 589.9557 |  |  | 20.28 | 0 | 79.72 | 560.8904 | 0
3014 | 734.93 | 909.328 | 29.4 | 144.9777 | 144.9777 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 589.9523 | 0 | 0.05921 | 4.1517 | 0 | 0 | 0 | 144.9777 | off_peak | 589.9523 |  |  | 19.73 | 0 | 80.27 | 601.9069 | 0
3015 | 751.71 | 773.127 | 29.5 | 123.2176 | 123.2176 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 18.9814 | 640.8548 | 0 | 0.05921 | 4.6521 | 0 | 0 | 0 | 123.2176 | off_peak | 628.4924 | 0 | 100 | 16.39 | 0 | 83.61 | 573.2189 | 0
3016 | 734.83 | 636.863 | 29.4 | 101.5376 | 101.5376 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 30.5453 | 645.6548 | 0 | 0.05921 | 5.0066 | 0 | 0 | 0 | 101.5376 | off_peak | 633.2924 | 0 | 100 | 13.82 | 0 | 86.18 | 508.3587 | 0
3017 | 761.54 | 383.358 | 29.1 | 61.1873 | 61.1873 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30.5453 | 700.3527 | 0 | 0.05921 | 5.3898 | 0 | 0 | 0 | 61.1873 | off_peak | 700.3527 |  |  | 8.03 | 0 | 91.97 | 329.7872 | 0
3018 | 653.2 | 63.6235 | 28.4 | 10.1808 | 10.1808 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30.5453 | 643.0192 | 0 | 0.05921 | 5.7765 | 0 | 0 | 0 | 10.1808 | off_peak | 643.0192 |  |  | 1.56 | 0 | 98.44 | 58.81 | 0
3019 | 585.11 | 19 | 28 | 3.0448 | 3.0448 | 0 | 0 | 8.7006 | 8.7006 | 0 | 0 | 0 | 38.684 | 590.7659 | 0 | 0.05921 | 6.1393 | 0 | 0 | 0 | 3.0448 | off_peak | 582.0652 | 0 | 100 | 0.52 | 0 | 99.48 | 18.6926 | 0
3020 | 602.65 | 0 | 26.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 38.684 | 602.65 | 0 | 0.05921 | 6.4132 | 0 | 0 | 0 | 0 | off_peak | 602.65 |  |  | 0 | 0 | 100 | 0 | 0
3021 | 596.96 | 0 | 26.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 38.684 | 596.96 | 0 | 0.05921 | 6.614 | 0 | 0 | 0 | 0 | off_peak | 596.96 |  |  | 0 | 0 | 100 | 0 | 0
3022 | 578.77 | 0 | 25.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 38.684 | 578.77 | 0 | 0.05921 | 6.6928 | 0 | 0 | 0 | 0 | off_peak | 578.77 |  |  | 0 | 0 | 100 | 0 | 0
3023 | 620.27 | 0 | 25.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 38.684 | 620.27 | 0 | 0.05921 | 6.7481 | 0 | 0 | 0 | 0 | off_peak | 620.27 |  |  | 0 | 0 | 100 | 0 | 0
3024 | 556.98 | 0 | 25.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 38.684 | 556.98 | 0 | 0.05921 | 6.6628 | 0 | 0 | 0 | 0 | off_peak | 556.98 |  |  | 0 | 0 | 100 | 0 | 0
3025 | 589.16 | 0 | 24.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 38.684 | 589.16 | 0 | 0.05921 | 6.5371 | 0 | 0 | 0 | 0 | off_peak | 589.16 |  |  | 0 | 0 | 100 | 0 | 0
3026 | 577.93 | 0 | 24.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 38.684 | 577.93 | 0 | 0.05921 | 6.5512 | 0 | 0 | 0 | 0 | off_peak | 577.93 |  |  | 0 | 0 | 100 | 0 | 0
3027 | 577.3 | 0 | 24.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 38.684 | 577.3 | 0 | 0.05921 | 6.1563 | 0 | 0 | 0 | 0 | off_peak | 577.3 |  |  | 0 | 0 | 100 | 0 | 0
3028 | 576.62 | 0 | 24.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 38.684 | 576.62 | 0 | 0.05921 | 5.6545 | 0 | 0 | 0 | 0 | off_peak | 576.62 |  |  | 0 | 0 | 100 | 0 | 0
3029 | 571.71 | 0 | 24.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 38.684 | 571.71 | 0 | 0.05921 | 4.9942 | 0 | 0 | 0 | 0 | off_peak | 571.71 |  |  | 0 | 0 | 100 | 0 | 0
3030 | 677.93 | 0 | 24.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 38.684 | 677.93 | 0 | 0.05921 | 4.3806 | 0 | 0 | 0 | 0 | off_peak | 677.93 |  |  | 0 | 0 | 100 | 0 | 0
3031 | 716.43 | 100.462 | 25.5 | 16.2455 | 16.2455 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 38.684 | 700.1845 | 0 | 0.05921 | 4.0057 | 0 | 0 | 0 | 16.2455 | off_peak | 700.1845 |  |  | 2.27 | 0 | 97.73 | 65.0753 | 0
3032 | 738.98 | 312.014 | 26.2 | 50.3279 | 50.3279 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 50.2479 | 701.0145 | 0 | 0.05921 | 3.8515 | 0 | 0 | 0 | 50.3279 | off_peak | 688.6521 | 0 | 100 | 6.81 | 0 | 93.19 | 193.8379 | 0
3033 | 710.6 | 525.425 | 26.9 | 84.5366 | 84.5366 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50.2479 | 626.0634 | 0 | 0.05921 | 3.6551 | 0 | 0 | 0 | 84.5366 | off_peak | 626.0634 |  |  | 11.9 | 0 | 88.1 | 308.9902 | 0
3034 | 783.49 | 708.44 | 27.6 | 113.6931 | 113.6931 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50.2479 | 669.7969 | 0 | 0.05921 | 3.5354 | 0 | 0 | 0 | 113.6931 | off_peak | 669.7969 |  |  | 14.51 | 0 | 85.49 | 401.9463 | 0
3035 | 781.68 | 847.93 | 28.2 | 135.7822 | 135.7822 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50.2479 | 645.8978 | 0 | 0.05921 | 3.5062 | 0 | 0 | 0 | 135.7822 | off_peak | 645.8978 |  |  | 17.37 | 0 | 82.63 | 476.0861 | 0
3036 | 733.25 | 929.647 | 28.7 | 148.5968 | 148.5968 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50.2479 | 584.6532 | 0 | 0.05921 | 3.5623 | 0 | 0 | 0 | 148.5968 | off_peak | 584.6532 |  |  | 20.27 | 0 | 79.73 | 529.3531 | 0
3037 | 781.51 | 945.985 | 29 | 151.0428 | 151.0428 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50.2479 | 630.4672 | 0 | 0.05921 | 3.6659 | 0 | 0 | 0 | 151.0428 | off_peak | 630.4672 |  |  | 19.33 | 0 | 80.67 | 553.7121 | 0
3038 | 736.93 | 842.973 | 29.1 | 134.546 | 122.1836 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 0 | 61.8119 | 614.7464 | 0 | 0.05921 | 3.9282 | 0 | 0 | 11.5639 | 122.1836 | off_peak | 614.7464 | 100 | 0 | 16.58 | 0 | 83.42 | 479.967 | 0
3039 | 776.11 | 568.986 | 29 | 90.8484 | 90.8484 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 61.8119 | 685.2616 | 0 | 0.05921 | 4.2488 | 0 | 0 | 11.5639 | 90.8484 | off_peak | 685.2616 |  |  | 11.71 | 0 | 88.29 | 385.9937 | 0
3040 | 724.67 | 289.65 | 28.7 | 46.2983 | 46.2983 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 61.8119 | 678.3717 | 0 | 0.05921 | 4.5 | 0 | 0 | 11.5639 | 46.2983 | off_peak | 678.3717 |  |  | 6.39 | 0 | 93.61 | 208.3423 | 0
3041 | 690.2 | 327.692 | 28.3 | 52.4554 | 40.0931 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 0 | 73.3758 | 650.1069 | 0 | 0.05921 | 4.822 | 0 | 0 | 23.1279 | 40.0931 | off_peak | 650.1069 | 100 | 0 | 5.81 | 0 | 94.19 | 193.3291 | 0
3042 | 641.18 | 129.315 | 27.6 | 20.7529 | 19.9545 | 0 | 0.79843 | 0.79843 | 0 | 0 | 0 | 0 | 74.1227 | 621.2255 | 0 | 0.05921 | 5.2387 | 0 | 0 | 23.8748 | 19.9545 | off_peak | 621.2255 | 100 | 0 | 3.11 | 0 | 96.89 | 104.5366 | 0
3043 | 591.15 | 29.5794 | 27.2 | 4.7539 | 4.7023 | 0 | 0.051567 | 0.051567 | 0 | 0 | 0 | 0 | 74.1709 | 586.4477 | 0 | 0.05921 | 5.5362 | 0 | 0 | 23.923 | 4.7023 | off_peak | 586.4477 | 100 | 0 | 0.8 | 0 | 99.2 | 26.0332 | 0
3044 | 585.28 | 0 | 26.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1709 | 585.28 | 0 | 0.05921 | 5.7493 | 0 | 0 | 23.923 | 0 | off_peak | 585.28 |  |  | 0 | 0 | 100 | 0 | 0
3045 | 599.58 | 0 | 25.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1709 | 599.58 | 0 | 0.05921 | 5.9013 | 0 | 0 | 23.923 | 0 | off_peak | 599.58 |  |  | 0 | 0 | 100 | 0 | 0
3046 | 569.16 | 0 | 25.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1709 | 569.16 | 0 | 0.05921 | 6.0488 | 0 | 0 | 23.923 | 0 | off_peak | 569.16 |  |  | 0 | 0 | 100 | 0 | 0
3047 | 552.43 | 0 | 25.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1709 | 552.43 | 0 | 0.05921 | 6.3181 | 0 | 0 | 23.923 | 0 | off_peak | 552.43 |  |  | 0 | 0 | 100 | 0 | 0
3048 | 561.77 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1709 | 561.77 | 0 | 0.05921 | 6.4242 | 0 | 0 | 23.923 | 0 | off_peak | 561.77 |  |  | 0 | 0 | 100 | 0 | 0
3049 | 581.54 | 0 | 24.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1709 | 581.54 | 0 | 0.05921 | 6.4903 | 0 | 0 | 23.923 | 0 | off_peak | 581.54 |  |  | 0 | 0 | 100 | 0 | 0
3050 | 547.8 | 0 | 24.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1709 | 547.8 | 0 | 0.05921 | 6.4485 | 0 | 0 | 23.923 | 0 | off_peak | 547.8 |  |  | 0 | 0 | 100 | 0 | 0
3051 | 557.4 | 0 | 24.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1709 | 557.4 | 0 | 0.05921 | 6.0565 | 0 | 0 | 23.923 | 0 | off_peak | 557.4 |  |  | 0 | 0 | 100 | 0 | 0
3052 | 590.22 | 0 | 24.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1709 | 590.22 | 0 | 0.05921 | 5.3915 | 0 | 0 | 23.923 | 0 | off_peak | 590.22 |  |  | 0 | 0 | 100 | 0 | 0
3053 | 599.15 | 0 | 24.7 | 0 | 0 | 0 | 0 | 0.0033305 | 0.0033305 | 0 | 0 | 0 | 74.174 | 599.1533 | 0 | 0.05921 | 4.5704 | 0 | 0 | 23.923 | 0 | off_peak | 599.15 | 0 | 100 | 0 | 0 | 100 | 0 | 0
3054 | 659.13 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.174 | 659.13 | 0 | 0.05921 | 3.8864 | 0 | 0 | 23.923 | 0 | off_peak | 659.13 |  |  | 0 | 0 | 100 | 0 | 0
3055 | 715.43 | 107.902 | 25.8 | 17.4298 | 17.4298 | 0 | 0 | 0.0002151 | 0.0002151 | 0 | 0 | 0 | 74.1742 | 698.0004 | 0 | 0.05921 | 3.4944 | 0 | 0 | 23.923 | 17.4298 | off_peak | 698.0002 | 0 | 100 | 2.44 | 0 | 97.56 | 60.906 | 0
3056 | 821.23 | 311.842 | 26.5 | 50.2456 | 50.2456 | 0 | 0 | 1.4852e-05 | 1.4852e-05 | 0 | 0 | 0 | 74.1743 | 770.9844 | 0 | 0.05921 | 3.268 | 0 | 0 | 23.923 | 50.2456 | off_peak | 770.9844 | 0 | 100 | 6.12 | 0 | 93.88 | 164.2044 | 0
3057 | 832.76 | 499.455 | 27.1 | 80.3 | 80.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1743 | 752.46 | 0 | 0.05921 | 3.1113 | 0 | 0 | 23.923 | 80.3 | off_peak | 752.46 |  |  | 9.64 | 0 | 90.36 | 249.8373 | 0
3058 | 813.33 | 619.099 | 27.7 | 99.3192 | 99.3192 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1743 | 714.0108 | 0 | 0.05921 | 3.0763 | 0 | 0 | 23.923 | 99.3192 | off_peak | 714.0108 |  |  | 12.21 | 0 | 87.79 | 305.5358 | 0
3059 | 806.04 | 537.056 | 28.3 | 85.9695 | 85.9695 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1743 | 720.0705 | 0 | 0.05921 | 3.218 | 0 | 0 | 23.923 | 85.9695 | off_peak | 720.0705 |  |  | 10.67 | 0 | 89.33 | 276.6491 | 0
3060 | 865.8 | 493.023 | 28.8 | 78.7771 | 78.7771 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1743 | 787.0229 | 0 | 0.05921 | 3.5404 | 0 | 0 | 23.923 | 78.7771 | off_peak | 787.0229 |  |  | 9.1 | 0 | 90.9 | 278.8998 | 0
3061 | 804.08 | 948.683 | 29.1 | 151.4182 | 151.4182 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1743 | 652.6618 | 0 | 0.088511 | 3.7862 | 0 | 0 | 23.923 | 151.4182 | on_peak | 652.6618 |  |  | 18.83 | 0 | 81.17 | 573.2987 | 0
3062 | 834.9 | 809.335 | 29.4 | 129.0355 | 129.0355 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1743 | 705.8645 | 0 | 0.088511 | 3.957 | 0 | 0 | 23.923 | 129.0355 | on_peak | 705.8645 |  |  | 15.46 | 0 | 84.54 | 510.5963 | 0
3063 | 885.79 | 793.958 | 29.4 | 126.5838 | 126.5838 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1743 | 759.2062 | 0 | 0.088511 | 4.0983 | 0 | 0 | 23.923 | 126.5838 | on_peak | 759.2062 |  |  | 14.29 | 0 | 85.71 | 518.7825 | 0
3064 | 878.53 | 418.909 | 29.2 | 66.8372 | 66.8372 | 0 | 0 | 0 | 0 | 40.0674 | 40.0674 | 0 | 31.3404 | 771.6254 | 0 | 0.088511 | 4.2597 | 0 | 0 | 23.923 | 66.8372 | on_peak | 771.6254 |  |  | 7.61 | 4.56 | 87.83 | 284.7041 | 0
3065 | 842.72 | 443.04 | 28.8 | 70.7906 | 70.7906 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 31.3404 | 771.9294 | 0 | 0.088511 | 4.4727 | 0 | 0 | 23.923 | 70.7906 | on_peak | 771.9294 |  |  | 8.4 | 0 | 91.6 | 316.6268 | 0
3066 | 848.51 | 229.848 | 28.1 | 36.8198 | 36.8198 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 31.3404 | 811.6902 | 0 | 0.088511 | 4.8666 | 0 | 0 | 23.923 | 36.8198 | on_peak | 811.6902 |  |  | 4.34 | 0 | 95.66 | 179.1874 | 0
3067 | 808.26 | 45.4202 | 27.7 | 7.2866 | 7.2866 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 31.3404 | 800.9734 | 0 | 0.088511 | 5.4553 | 0 | 0 | 23.923 | 7.2866 | on_peak | 800.9734 |  |  | 0.9 | 0 | 99.1 | 39.7506 | 0
3068 | 810.31 | 0 | 26.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 31.3404 | 810.31 | 0 | 0.088511 | 5.8826 | 0 | 0 | 23.923 | 0 | on_peak | 810.31 |  |  | 0 | 0 | 100 | 0 | 0
3069 | 811.56 | 0 | 26.3 | 0 | 0 | 0 | 0 | 0 | 0 | 22.3779 | 22.3779 | 0 | 7.4174 | 789.1821 | 0 | 0.088511 | 6.185 | 22.3779 | 0 | 0 | 22.3779 | on_peak | 789.1821 |  |  | 0 | 2.76 | 97.24 | 138.4075 | 0
3070 | 779.3 | 0 | 26 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 779.3 | 0 | 0.05921 | 6.6534 | 0 | 0 | 0 | 0 | off_peak | 779.3 |  |  | 0 | 0 | 100 | 0 | 0
3071 | 801.42 | 0 | 25.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 801.42 | 0 | 0.05921 | 6.8498 | 0 | 0 | 0 | 0 | off_peak | 801.42 |  |  | 0 | 0 | 100 | 0 | 0
3072 | 803.55 | 0 | 25.5 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 18.9814 | 815.9124 | 0 | 0.05921 | 7.0903 | 0 | 0 | 0 | 0 | off_peak | 803.55 | 0 | 100 | 0 | 0 | 100 | 0 | 0
3073 | 760.57 | 0 | 25.4 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 30.5453 | 772.9324 | 0 | 0.05921 | 7.1266 | 0 | 0 | 0 | 0 | off_peak | 760.57 | 0 | 100 | 0 | 0 | 100 | 0 | 0
3074 | 677.38 | 0 | 25.2 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 42.1093 | 689.7424 | 0 | 0.05921 | 6.8506 | 0 | 0 | 0 | 0 | off_peak | 677.38 | 0 | 100 | 0 | 0 | 100 | 0 | 0
3075 | 604.95 | 0 | 25.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 42.1093 | 604.95 | 0 | 0.05921 | 6.3781 | 0 | 0 | 0 | 0 | off_peak | 604.95 |  |  | 0 | 0 | 100 | 0 | 0
3076 | 604.77 | 0 | 25.1 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 53.6732 | 617.1324 | 0 | 0.05921 | 5.6298 | 0 | 0 | 0 | 0 | off_peak | 604.77 | 0 | 100 | 0 | 0 | 100 | 0 | 0
3077 | 610.84 | 0 | 25.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 53.6732 | 610.84 | 0 | 0.05921 | 4.8066 | 0 | 0 | 0 | 0 | off_peak | 610.84 |  |  | 0 | 0 | 100 | 0 | 0
3078 | 692.31 | 0 | 25.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 53.6732 | 692.31 | 0 | 0.05921 | 4.1204 | 0 | 0 | 0 | 0 | off_peak | 692.31 |  |  | 0 | 0 | 100 | 0 | 0
3079 | 705.59 | 113.221 | 25.9 | 18.2824 | 18.2824 | 0 | 0 | 8.7006 | 8.7006 | 0 | 0 | 0 | 61.8119 | 696.0082 | 0 | 0.05921 | 3.7362 | 0 | 0 | 0 | 18.2824 | off_peak | 687.3076 | 0 | 100 | 2.59 | 0 | 97.41 | 68.3066 | 0
3080 | 808.87 | 317.419 | 26.4 | 51.1627 | 51.1627 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 73.3758 | 770.0697 | 0 | 0.05921 | 3.4319 | 0 | 0 | 0 | 51.1627 | off_peak | 757.7073 | 0 | 100 | 6.33 | 0 | 93.67 | 175.585 | 0
3081 | 793.31 | 498.186 | 26.9 | 80.1541 | 80.1541 | 0 | 0 | 0.79843 | 0.79843 | 0 | 0 | 0 | 74.1227 | 713.9543 | 0 | 0.05921 | 3.2181 | 0 | 0 | 0 | 80.1541 | off_peak | 713.1559 | 0 | 100 | 10.1 | 0 | 89.9 | 257.9415 | 0
3082 | 807.97 | 426.635 | 27.4 | 68.5177 | 68.5177 | 0 | 0 | 0.051567 | 0.051567 | 0 | 0 | 0 | 74.1709 | 739.5038 | 0 | 0.05921 | 3.1675 | 0 | 0 | 0 | 68.5177 | off_peak | 739.4523 | 0 | 100 | 8.48 | 0 | 91.52 | 217.0271 | 0
3083 | 825.51 | 299.939 | 28.1 | 48.0479 | 48.0479 | 0 | 0 | 0.0033305 | 0.0033305 | 0 | 0 | 0 | 74.174 | 777.4655 | 0 | 0.05921 | 3.3431 | 0 | 0 | 0 | 48.0479 | off_peak | 777.4621 | 0 | 100 | 5.82 | 0 | 94.18 | 160.627 | 0
3084 | 864.05 | 769.861 | 28.6 | 123.1011 | 123.1011 | 0 | 0 | 0.0002151 | 0.0002151 | 0 | 0 | 0 | 74.1742 | 740.9491 | 0 | 0.05921 | 3.7174 | 0 | 0 | 0 | 123.1011 | off_peak | 740.9489 | 0 | 100 | 14.25 | 0 | 85.75 | 457.615 | 0
3085 | 823.56 | 814.632 | 29 | 130.07 | 130.07 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1742 | 693.49 | 0 | 0.088511 | 4.0246 | 0 | 0 | 0 | 130.07 | on_peak | 693.49 |  |  | 15.79 | 0 | 84.21 | 523.4846 | 0
3086 | 810.31 | 652.121 | 29.2 | 104.0463 | 104.0463 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1742 | 706.2637 | 0 | 0.088511 | 4.3275 | 0 | 0 | 0 | 104.0463 | on_peak | 706.2637 |  |  | 12.84 | 0 | 87.16 | 450.2569 | 0
3087 | 883.05 | 537.774 | 29.2 | 85.8021 | 85.8021 | 0 | 0 | 0 | 0 | 62.4453 | 62.4453 | 0 | 7.4174 | 734.8026 | 0 | 0.088511 | 4.6727 | 0 | 0 | 0 | 85.8021 | on_peak | 734.8026 |  |  | 9.72 | 7.07 | 83.21 | 400.9269 | 0
3088 | 860.82 | 488.815 | 29.1 | 78.0192 | 78.0192 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 782.8008 | 0 | 0.088511 | 4.9042 | 0 | 0 | 0 | 78.0192 | on_peak | 782.8008 |  |  | 9.06 | 0 | 90.94 | 382.6193 | 0
3089 | 822.32 | 430.675 | 28.9 | 68.7898 | 68.7898 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 753.5302 | 0 | 0.088511 | 5.2349 | 0 | 0 | 0 | 68.7898 | on_peak | 753.5302 |  |  | 8.37 | 0 | 91.63 | 360.1096 | 0
3090 | 831.33 | 209.846 | 28.6 | 33.5545 | 33.5545 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 797.7755 | 0 | 0.088511 | 5.5838 | 0 | 0 | 0 | 33.5545 | on_peak | 797.7755 |  |  | 4.04 | 0 | 95.96 | 187.3607 | 0
3091 | 779.06 | 34.5359 | 28.4 | 5.5263 | 5.5263 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 773.5337 | 0 | 0.088511 | 6.0599 | 0 | 0 | 0 | 5.5263 | on_peak | 773.5337 |  |  | 0.71 | 0 | 99.29 | 33.4889 | 0
3092 | 785.8 | 0 | 27.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 785.8 | 0 | 0.088511 | 6.4529 | 0 | 0 | 0 | 0 | on_peak | 785.8 |  |  | 0 | 0 | 100 | 0 | 0
3093 | 783.26 | 0 | 27.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 783.26 | 0 | 0.088511 | 6.7584 | 0 | 0 | 0 | 0 | on_peak | 783.26 |  |  | 0 | 0 | 100 | 0 | 0
3094 | 763.48 | 0 | 26.9 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 18.9814 | 775.8424 | 0 | 0.05921 | 7.0715 | 0 | 0 | 0 | 0 | off_peak | 763.48 | 0 | 100 | 0 | 0 | 100 | 0 | 0
3095 | 751.54 | 0 | 26.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18.9814 | 751.54 | 0 | 0.05921 | 7.3269 | 0 | 0 | 0 | 0 | off_peak | 751.54 |  |  | 0 | 0 | 100 | 0 | 0
3096 | 789.39 | 0 | 26.2 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 30.5453 | 801.7524 | 0 | 0.05921 | 7.4564 | 0 | 0 | 0 | 0 | off_peak | 789.39 | 0 | 100 | 0 | 0 | 100 | 0 | 0
3097 | 773.6 | 0 | 25.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30.5453 | 773.6 | 0 | 0.05921 | 7.4158 | 0 | 0 | 0 | 0 | off_peak | 773.6 |  |  | 0 | 0 | 100 | 0 | 0
3098 | 633.02 | 0 | 25.7 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 42.1093 | 645.3824 | 0 | 0.05921 | 7.1857 | 0 | 0 | 0 | 0 | off_peak | 633.02 | 0 | 100 | 0 | 0 | 100 | 0 | 0
3099 | 578.89 | 0 | 25.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 42.1093 | 578.89 | 0 | 0.05921 | 6.8539 | 0 | 0 | 0 | 0 | off_peak | 578.89 |  |  | 0 | 0 | 100 | 0 | 0
3100 | 581.62 | 0 | 25.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 42.1093 | 581.62 | 0 | 0.05921 | 6.0099 | 0 | 0 | 0 | 0 | off_peak | 581.62 |  |  | 0 | 0 | 100 | 0 | 0
3101 | 605.42 | 0 | 25.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 42.1093 | 605.42 | 0 | 0.05921 | 5.1828 | 0 | 0 | 0 | 0 | off_peak | 605.42 |  |  | 0 | 0 | 100 | 0 | 0
3102 | 667.53 | 0 | 25.4 | 0 | 0 | 0 | 0 | 8.7006 | 8.7006 | 0 | 0 | 0 | 50.2479 | 676.2306 | 0 | 0.05921 | 4.5311 | 0 | 0 | 0 | 0 | off_peak | 667.53 | 0 | 100 | 0 | 0 | 100 | 0 | 0
3103 | 722.03 | 116.521 | 26 | 18.8084 | 18.8084 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 61.8119 | 715.5839 | 0 | 0.05921 | 3.9765 | 0 | 0 | 0 | 18.8084 | off_peak | 703.2216 | 0 | 100 | 2.6 | 0 | 97.4 | 74.7915 | 0
3104 | 792.69 | 188.85 | 26.9 | 30.3844 | 30.3844 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 73.3758 | 774.6679 | 0 | 0.05921 | 3.6781 | 0 | 0 | 0 | 30.3844 | off_peak | 762.3056 | 0 | 100 | 3.83 | 0 | 96.17 | 111.7559 | 0
3105 | 793.79 | 215.098 | 27.7 | 34.5072 | 34.5072 | 0 | 0 | 0.79843 | 0.79843 | 0 | 0 | 0 | 74.1227 | 760.0813 | 0 | 0.05921 | 3.483 | 0 | 0 | 0 | 34.5072 | off_peak | 759.2828 | 0 | 100 | 4.35 | 0 | 95.65 | 120.1897 | 0
3106 | 823.73 | 714.609 | 28.4 | 114.3497 | 114.3497 | 0 | 0 | 0.051567 | 0.051567 | 0 | 0 | 0 | 74.1709 | 709.4319 | 0 | 0.05921 | 3.3999 | 0 | 0 | 0 | 114.3497 | off_peak | 709.3803 | 0 | 100 | 13.88 | 0 | 86.12 | 388.7747 | 0
3107 | 802.2 | 565.18 | 28.9 | 90.2737 | 90.2703 | 0 | 0.0033305 | 0.0033305 | 0 | 0 | 0 | 0 | 74.174 | 711.9297 | 0 | 0.05921 | 3.5434 | 0 | 0 | 0.0031154 | 90.2703 | off_peak | 711.9297 | 100 | 0 | 11.25 | 0 | 88.75 | 319.8611 | 0
3108 | 880.82 | 934.248 | 29.4 | 148.9508 | 148.9508 | 0 | 0 | 0.0002151 | 0.0002151 | 0 | 0 | 0 | 74.1742 | 731.8694 | 0 | 0.05921 | 3.9172 | 0 | 0 | 0.0031154 | 148.9508 | off_peak | 731.8692 | 0 | 100 | 16.91 | 0 | 83.09 | 583.4681 | 0
3109 | 828.43 | 952.211 | 29.8 | 151.5926 | 151.5926 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1742 | 676.8374 | 0 | 0.088511 | 4.1201 | 0 | 0 | 0.0031154 | 151.5926 | on_peak | 676.8374 |  |  | 18.3 | 0 | 81.7 | 624.5719 | 0
3110 | 816.89 | 875.768 | 30.2 | 139.2185 | 139.2185 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1742 | 677.6715 | 0 | 0.088511 | 4.3545 | 0 | 0 | 0.0031154 | 139.2185 | on_peak | 677.6715 |  |  | 17.04 | 0 | 82.96 | 606.2254 | 0
3111 | 849.42 | 636.069 | 30.5 | 101.0029 | 101.0029 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1742 | 748.4171 | 0 | 0.088511 | 4.55 | 0 | 0 | 0.0031154 | 101.0029 | on_peak | 748.4171 |  |  | 11.89 | 0 | 88.11 | 459.5643 | 0
3112 | 841.9 | 631.052 | 30.5 | 100.2063 | 100.2063 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1742 | 741.6937 | 0 | 0.088511 | 4.9059 | 0 | 0 | 0.0031154 | 100.2063 | on_peak | 741.6937 |  |  | 11.9 | 0 | 88.1 | 491.6028 | 0
3113 | 892.25 | 320.132 | 30.2 | 50.8905 | 50.8905 | 0 | 0 | 0 | 0 | 62.4453 | 62.4453 | 0 | 7.4174 | 778.9142 | 0 | 0.088511 | 5.4429 | 0 | 0 | 0.0031154 | 50.8905 | on_peak | 778.9142 |  |  | 5.7 | 7 | 87.3 | 276.9905 | 0
3114 | 840.81 | 232.563 | 29.6 | 37.0513 | 37.0513 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 803.7587 | 0 | 0.088511 | 6.0953 | 0 | 0 | 0.0031154 | 37.0513 | on_peak | 803.7587 |  |  | 4.41 | 0 | 95.59 | 225.8392 | 0
3115 | 826.33 | 44.0601 | 29.2 | 7.0298 | 7.0298 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 819.3002 | 0 | 0.088511 | 6.6444 | 0 | 0 | 0.0031154 | 7.0298 | on_peak | 819.3002 |  |  | 0.85 | 0 | 99.15 | 46.7089 | 0
3116 | 810.17 | 0 | 28.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 810.17 | 0 | 0.088511 | 6.9942 | 0 | 0 | 0.0031154 | 0 | on_peak | 810.17 |  |  | 0 | 0 | 100 | 0 | 0
3117 | 818.4 | 0 | 27.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 818.4 | 0 | 0.088511 | 7.3363 | 0 | 0 | 0.0031154 | 0 | on_peak | 818.4 |  |  | 0 | 0 | 100 | 0 | 0
3118 | 775.87 | 0 | 27.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 775.87 | 0 | 0.05921 | 7.5276 | 0 | 0 | 0.0031154 | 0 | off_peak | 775.87 |  |  | 0 | 0 | 100 | 0 | 0
3119 | 814.46 | 0 | 26.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 814.46 | 0 | 0.05921 | 7.7264 | 0 | 0 | 0.0031154 | 0 | off_peak | 814.46 |  |  | 0 | 0 | 100 | 0 | 0
3120 | 764.3 | 0 | 26.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 764.3 | 0 | 0.05921 | 7.8292 | 0 | 0 | 0.0031154 | 0 | off_peak | 764.3 |  |  | 0 | 0 | 100 | 0 | 0
3121 | 747.01 | 0 | 26.4 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 18.9814 | 759.3724 | 0 | 0.05921 | 7.6548 | 0 | 0 | 0.0031154 | 0 | off_peak | 747.01 | 0 | 100 | 0 | 0 | 100 | 0 | 0
3122 | 653.94 | 0 | 26.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18.9814 | 653.94 | 0 | 0.05921 | 7.473 | 0 | 0 | 0.0031154 | 0 | off_peak | 653.94 |  |  | 0 | 0 | 100 | 0 | 0
3123 | 592.12 | 0 | 26.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18.9814 | 592.12 | 0 | 0.05921 | 6.9423 | 0 | 0 | 0.0031154 | 0 | off_peak | 592.12 |  |  | 0 | 0 | 100 | 0 | 0
3124 | 615.67 | 0 | 26 | 0 | 0 | 0 | 0 | 8.7006 | 8.7006 | 0 | 0 | 0 | 27.12 | 624.3706 | 0 | 0.05921 | 6.3365 | 0 | 0 | 0.0031154 | 0 | off_peak | 615.67 | 0 | 100 | 0 | 0 | 100 | 0 | 0
3125 | 614.44 | 0 | 26 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 38.684 | 626.8024 | 0 | 0.05921 | 5.5598 | 0 | 0 | 0.0031154 | 0 | off_peak | 614.44 | 0 | 100 | 0 | 0 | 100 | 0 | 0
3126 | 727.85 | 0 | 26.2 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 50.2479 | 740.2124 | 0 | 0.05921 | 4.8132 | 0 | 0 | 0.0031154 | 0 | off_peak | 727.85 | 0 | 100 | 0 | 0 | 100 | 0 | 0
3127 | 750.08 | 120.14 | 26.7 | 19.3436 | 19.3436 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 61.8119 | 743.0988 | 0 | 0.05921 | 4.3613 | 0 | 0 | 0.0031154 | 19.3436 | off_peak | 730.7364 | 0 | 100 | 2.58 | 0 | 97.42 | 84.3637 | 0
3128 | 790.6 | 325.928 | 27.2 | 52.3822 | 52.3822 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 73.3758 | 750.5802 | 0 | 0.05921 | 3.9752 | 0 | 0 | 0.0031154 | 52.3822 | off_peak | 738.2178 | 0 | 100 | 6.63 | 0 | 93.37 | 208.2288 | 0
3129 | 859.95 | 534.848 | 27.8 | 85.772 | 85.772 | 0 | 0 | 0.79843 | 0.79843 | 0 | 0 | 0 | 74.1227 | 774.9764 | 0 | 0.05921 | 3.7506 | 0 | 0 | 0.0031154 | 85.772 | off_peak | 774.178 | 0 | 100 | 9.97 | 0 | 90.03 | 321.6952 | 0
3130 | 829.84 | 716.884 | 28.3 | 114.7555 | 114.7555 | 0 | 0 | 0.051567 | 0.051567 | 0 | 0 | 0 | 74.1709 | 715.136 | 0 | 0.05921 | 3.63 | 0 | 0 | 0.0031154 | 114.7555 | off_peak | 715.0845 | 0 | 100 | 13.83 | 0 | 86.17 | 416.5629 | 0
3131 | 780.51 | 818.386 | 28.8 | 130.7649 | 130.7649 | 0 | 0 | 0.0033305 | 0.0033305 | 0 | 0 | 0 | 74.174 | 649.7485 | 0 | 0.05921 | 3.8043 | 0 | 0 | 0.0031154 | 130.7649 | off_peak | 649.7451 | 0 | 100 | 16.75 | 0 | 83.25 | 497.4682 | 0
3132 | 859.91 | 934.741 | 29.3 | 149.0839 | 149.0839 | 0 | 0 | 0.0002151 | 0.0002151 | 0 | 0 | 0 | 74.1742 | 710.8263 | 0 | 0.05921 | 4.247 | 0 | 0 | 0.0031154 | 149.0839 | off_peak | 710.8261 | 0 | 100 | 17.34 | 0 | 82.66 | 633.1613 | 0
3133 | 813.66 | 952.708 | 29.7 | 151.7273 | 151.7273 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1742 | 661.9327 | 0 | 0.088511 | 4.3808 | 0 | 0 | 0.0031154 | 151.7273 | on_peak | 661.9327 |  |  | 18.65 | 0 | 81.35 | 664.6815 | 0
3134 | 856.74 | 904.511 | 30 | 143.8932 | 143.8932 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1742 | 712.8468 | 0 | 0.088511 | 4.728 | 0 | 0 | 0.0031154 | 143.8932 | on_peak | 712.8468 |  |  | 16.8 | 0 | 83.2 | 680.3302 | 0
3135 | 917.17 | 797.293 | 30.2 | 126.7436 | 126.7436 | 0 | 0 | 0 | 0 | 62.4453 | 62.4453 | 0 | 7.4174 | 727.9812 | 0 | 0.088511 | 4.9848 | 0 | 0 | 0.0031154 | 126.7436 | on_peak | 727.9812 |  |  | 13.82 | 6.81 | 79.37 | 631.7895 | 0
3136 | 871.77 | 626.299 | 30.2 | 99.5611 | 99.5611 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 772.2089 | 0 | 0.088511 | 5.3188 | 0 | 0 | 0.0031154 | 99.5611 | on_peak | 772.2089 |  |  | 11.42 | 0 | 88.58 | 529.5455 | 0
3137 | 829.59 | 376.658 | 30 | 59.9203 | 59.9203 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 769.6697 | 0 | 0.088511 | 5.5586 | 0 | 0 | 0.0031154 | 59.9203 | on_peak | 769.6697 |  |  | 7.22 | 0 | 92.78 | 333.0746 | 0
3138 | 821.53 | 149.775 | 29.6 | 23.8617 | 23.8617 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 797.6683 | 0 | 0.088511 | 5.9492 | 0 | 0 | 0.0031154 | 23.8617 | on_peak | 797.6683 |  |  | 2.9 | 0 | 97.1 | 141.9577 | 0
3139 | 774.75 | 43.4611 | 29.4 | 6.9292 | 6.9292 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 767.8208 | 0 | 0.088511 | 6.3228 | 0 | 0 | 0.0031154 | 6.9292 | on_peak | 767.8208 |  |  | 0.89 | 0 | 99.11 | 43.8117 | 0
3140 | 796.11 | 0 | 28.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 796.11 | 0 | 0.088511 | 6.703 | 0 | 0 | 0.0031154 | 0 | on_peak | 796.11 |  |  | 0 | 0 | 100 | 0 | 0
3141 | 812.82 | 0 | 27.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 812.82 | 0 | 0.088511 | 6.9743 | 0 | 0 | 0.0031154 | 0 | on_peak | 812.82 |  |  | 0 | 0 | 100 | 0 | 0
3142 | 762.3 | 0 | 27.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 762.3 | 0 | 0.05921 | 7.2672 | 0 | 0 | 0.0031154 | 0 | off_peak | 762.3 |  |  | 0 | 0 | 100 | 0 | 0
3143 | 793.54 | 0 | 26.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 793.54 | 0 | 0.05921 | 7.518 | 0 | 0 | 0.0031154 | 0 | off_peak | 793.54 |  |  | 0 | 0 | 100 | 0 | 0
3144 | 768.32 | 0 | 26.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 768.32 | 0 | 0.05921 | 7.6716 | 0 | 0 | 0.0031154 | 0 | off_peak | 768.32 |  |  | 0 | 0 | 100 | 0 | 0
3145 | 707.53 | 0 | 26.2 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 18.9814 | 719.8924 | 0 | 0.05921 | 7.594 | 0 | 0 | 0.0031154 | 0 | off_peak | 707.53 | 0 | 100 | 0 | 0 | 100 | 0 | 0
3146 | 677.94 | 0 | 26 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 30.5453 | 690.3024 | 0 | 0.05921 | 7.3961 | 0 | 0 | 0.0031154 | 0 | off_peak | 677.94 | 0 | 100 | 0 | 0 | 100 | 0 | 0
3147 | 608.93 | 0 | 25.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30.5453 | 608.93 | 0 | 0.05921 | 6.9099 | 0 | 0 | 0.0031154 | 0 | off_peak | 608.93 |  |  | 0 | 0 | 100 | 0 | 0
3148 | 600.99 | 0 | 25.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30.5453 | 600.99 | 0 | 0.05921 | 6.1808 | 0 | 0 | 0.0031154 | 0 | off_peak | 600.99 |  |  | 0 | 0 | 100 | 0 | 0
3149 | 579.14 | 0 | 25.5 | 0 | 0 | 0 | 0 | 8.7006 | 8.7006 | 0 | 0 | 0 | 38.684 | 587.8406 | 0 | 0.05921 | 5.4181 | 0 | 0 | 0.0031154 | 0 | off_peak | 579.14 | 0 | 100 | 0 | 0 | 100 | 0 | 0
3150 | 708.65 | 0 | 25.5 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 50.2479 | 721.0124 | 0 | 0.05921 | 4.648 | 0 | 0 | 0.0031154 | 0 | off_peak | 708.65 | 0 | 100 | 0 | 0 | 100 | 0 | 0
3151 | 763.87 | 116.632 | 25.7 | 18.8468 | 18.8468 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 61.8119 | 757.3856 | 0 | 0.05921 | 4.2697 | 0 | 0 | 0.0031154 | 18.8468 | off_peak | 745.0232 | 0 | 100 | 2.47 | 0 | 97.53 | 80.4707 | 0
3152 | 817.54 | 322.76 | 25.9 | 52.1177 | 52.1177 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 73.3758 | 777.7847 | 0 | 0.05921 | 4.0205 | 0 | 0 | 0.0031154 | 52.1177 | off_peak | 765.4223 | 0 | 100 | 6.37 | 0 | 93.63 | 209.5386 | 0
3153 | 848.27 | 527.977 | 26.3 | 85.132 | 85.132 | 0 | 0 | 0.79843 | 0.79843 | 0 | 0 | 0 | 74.1227 | 763.9364 | 0 | 0.05921 | 3.7666 | 0 | 0 | 0.0031154 | 85.132 | off_peak | 763.138 | 0 | 100 | 10.04 | 0 | 89.96 | 320.6556 | 0
3154 | 818.81 | 704.999 | 26.9 | 113.4286 | 113.4286 | 0 | 0 | 0.051567 | 0.051567 | 0 | 0 | 0 | 74.1709 | 705.4329 | 0 | 0.05921 | 3.6701 | 0 | 0 | 0.0031154 | 113.4286 | off_peak | 705.3814 | 0 | 100 | 13.85 | 0 | 86.15 | 416.2913 | 0
3155 | 770.36 | 790.895 | 27.5 | 126.9719 | 126.9685 | 0 | 0.0033305 | 0.0033305 | 0 | 0 | 0 | 0 | 74.174 | 643.3915 | 0 | 0.05921 | 3.8514 | 0 | 0 | 0.0062308 | 126.9685 | off_peak | 643.3915 | 100 | 0 | 16.48 | 0 | 83.52 | 489.0074 | 0
3156 | 853.49 | 756.919 | 28.1 | 121.2524 | 121.2524 | 0 | 0 | 0.0002151 | 0.0002151 | 0 | 0 | 0 | 74.1742 | 732.2378 | 0 | 0.05921 | 4.1596 | 0 | 0 | 0.0062308 | 121.2524 | off_peak | 732.2376 | 0 | 100 | 14.21 | 0 | 85.79 | 504.3674 | 0
3157 | 815.1 | 446.662 | 28.7 | 71.3954 | 71.3954 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1742 | 743.7046 | 0 | 0.088511 | 4.3509 | 0 | 0 | 0.0062308 | 71.3954 | on_peak | 743.7046 |  |  | 8.76 | 0 | 91.24 | 310.633 | 0
3158 | 819.36 | 855.975 | 29.1 | 136.6212 | 136.6212 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1742 | 682.7388 | 0 | 0.088511 | 4.6399 | 0 | 0 | 0.0062308 | 136.6212 | on_peak | 682.7388 |  |  | 16.67 | 0 | 83.33 | 633.9124 | 0
3159 | 926.8 | 788.245 | 29.4 | 125.673 | 125.673 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1742 | 801.127 | 0 | 0.088511 | 4.9864 | 0 | 0 | 0.0062308 | 125.673 | on_peak | 801.127 |  |  | 13.56 | 0 | 86.44 | 626.66 | 0
3160 | 911.15 | 606.054 | 29.5 | 96.5902 | 96.5902 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1742 | 814.5598 | 0 | 0.088511 | 5.3195 | 0 | 0 | 0.0062308 | 96.5902 | on_peak | 814.5598 |  |  | 10.6 | 0 | 89.4 | 513.8161 | 0
3161 | 882.26 | 387.262 | 29.1 | 61.8105 | 61.8105 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1742 | 820.4495 | 0 | 0.088511 | 5.6543 | 0 | 0 | 0.0062308 | 61.8105 | on_peak | 820.4495 |  |  | 7.01 | 0 | 92.99 | 349.4935 | 0
3162 | 888.38 | 179.987 | 28.4 | 28.801 | 28.801 | 0 | 0 | 0 | 0 | 62.4395 | 62.4395 | 0 | 7.4237 | 797.1395 | 0 | 0.088511 | 5.9544 | 0 | 0 | 0.0062308 | 28.801 | on_peak | 797.1395 |  |  | 3.24 | 7.03 | 89.73 | 171.4923 | 0
3163 | 839.94 | 42.3043 | 27.9 | 6.7817 | 6.7817 | 0 | 0 | 0 | 0 | 0.0058284 | 0.0058284 | 0 | 7.4174 | 833.1524 | 0 | 0.088511 | 6.4551 | 0.0058284 | 0 | 0 | 6.7876 | on_peak | 833.1524 |  |  | 0.81 | 0 | 99.19 | 43.8146 | 0
3164 | 832.61 | 0 | 26.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 832.61 | 0 | 0.088511 | 6.8037 | 0 | 0 | 0 | 0 | on_peak | 832.61 |  |  | 0 | 0 | 100 | 0 | 0
3165 | 831.52 | 0 | 25.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 831.52 | 0 | 0.088511 | 7.0781 | 0 | 0 | 0 | 0 | on_peak | 831.52 |  |  | 0 | 0 | 100 | 0 | 0
3166 | 784.49 | 0 | 25.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 784.49 | 0 | 0.05921 | 7.3085 | 0 | 0 | 0 | 0 | off_peak | 784.49 |  |  | 0 | 0 | 100 | 0 | 0
3167 | 771.24 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 771.24 | 0 | 0.05921 | 7.4673 | 0 | 0 | 0 | 0 | off_peak | 771.24 |  |  | 0 | 0 | 100 | 0 | 0
3168 | 776.62 | 0 | 24.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 776.62 | 0 | 0.05921 | 7.5392 | 0 | 0 | 0 | 0 | off_peak | 776.62 |  |  | 0 | 0 | 100 | 0 | 0
3169 | 768.33 | 0 | 24.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 768.33 | 0 | 0.05921 | 7.5204 | 0 | 0 | 0 | 0 | off_peak | 768.33 |  |  | 0 | 0 | 100 | 0 | 0
3170 | 637.9 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 637.9 | 0 | 0.05921 | 7.143 | 0 | 0 | 0 | 0 | off_peak | 637.9 |  |  | 0 | 0 | 100 | 0 | 0
3171 | 601.46 | 0 | 23.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 601.46 | 0 | 0.05921 | 6.7156 | 0 | 0 | 0 | 0 | off_peak | 601.46 |  |  | 0 | 0 | 100 | 0 | 0
3172 | 613.2 | 0 | 23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 613.2 | 0 | 0.05921 | 6.0881 | 0 | 0 | 0 | 0 | off_peak | 613.2 |  |  | 0 | 0 | 100 | 0 | 0
3173 | 586.36 | 0 | 22.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 586.36 | 0 | 0.05921 | 5.4843 | 0 | 0 | 0 | 0 | off_peak | 586.36 |  |  | 0 | 0 | 100 | 0 | 0
3174 | 794.43 | 0 | 22.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 794.43 | 0 | 0.05921 | 4.8979 | 0 | 0 | 0 | 0 | off_peak | 794.43 |  |  | 0 | 0 | 100 | 0 | 0
3175 | 799.59 | 69.3941 | 22.7 | 11.3349 | 11.3349 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 788.2551 | 0 | 0.05921 | 4.3954 | 0 | 0 | 0 | 11.3349 | off_peak | 788.2551 |  |  | 1.42 | 0 | 98.58 | 49.8221 | 0
3176 | 775.71 | 312.03 | 23.6 | 50.8036 | 50.8036 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 724.9064 | 0 | 0.05921 | 4.0617 | 0 | 0 | 0 | 50.8036 | off_peak | 724.9064 |  |  | 6.55 | 0 | 93.45 | 206.3488 | 0
3177 | 859.94 | 491.562 | 24.6 | 79.7477 | 79.7477 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 780.1923 | 0 | 0.05921 | 3.7043 | 0 | 0 | 0 | 79.7477 | off_peak | 780.1923 |  |  | 9.27 | 0 | 90.73 | 295.413 | 0
3178 | 805.74 | 549.061 | 25.6 | 88.7558 | 88.7558 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 716.9842 | 0 | 0.05921 | 3.5409 | 0 | 0 | 0 | 88.7558 | off_peak | 716.9842 |  |  | 11.02 | 0 | 88.98 | 314.2767 | 0
3179 | 760.67 | 727.148 | 26.5 | 117.1619 | 117.1619 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 643.5081 | 0 | 0.05921 | 3.5137 | 0 | 0 | 0 | 117.1619 | off_peak | 643.5081 |  |  | 15.4 | 0 | 84.6 | 411.6689 | 0
3180 | 810.78 | 870.699 | 27.1 | 139.9869 | 139.9869 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 670.7931 | 0 | 0.05921 | 3.5294 | 0 | 0 | 0 | 139.9869 | off_peak | 670.7931 |  |  | 17.27 | 0 | 82.73 | 494.0711 | 0
3181 | 772.58 | 884.475 | 27.6 | 141.9438 | 141.9438 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 630.6362 | 0 | 0.05921 | 3.7185 | 0 | 0 | 0 | 141.9438 | off_peak | 630.6362 |  |  | 18.37 | 0 | 81.63 | 527.8122 | 0
3182 | 708.3 | 696.861 | 28 | 111.6723 | 111.6723 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 18.9814 | 608.9901 | 0 | 0.05921 | 4.1838 | 0 | 0 | 0 | 111.6723 | off_peak | 596.6277 | 0 | 100 | 15.77 | 0 | 84.23 | 467.2116 | 0
3183 | 696.42 | 529.86 | 28.2 | 84.8485 | 84.8485 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18.9814 | 611.5715 | 0 | 0.05921 | 4.4757 | 0 | 0 | 0 | 84.8485 | off_peak | 611.5715 |  |  | 12.18 | 0 | 87.82 | 379.7602 | 0
3184 | 709.2 | 344.623 | 28.2 | 55.1858 | 55.1858 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 30.5453 | 666.3766 | 0 | 0.05921 | 4.6931 | 0 | 0 | 0 | 55.1858 | off_peak | 654.0142 | 0 | 100 | 7.78 | 0 | 92.22 | 258.9949 | 0
3185 | 701.78 | 225.986 | 28 | 36.2143 | 36.2143 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30.5453 | 665.5657 | 0 | 0.05921 | 5.1422 | 0 | 0 | 0 | 36.2143 | off_peak | 665.5657 |  |  | 5.16 | 0 | 94.84 | 186.2227 | 0
3186 | 611.8 | 97.192 | 27.4 | 15.6091 | 15.6091 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30.5453 | 596.1909 | 0 | 0.05921 | 5.6311 | 0 | 0 | 0 | 15.6091 | off_peak | 596.1909 |  |  | 2.55 | 0 | 97.45 | 87.897 | 0
3187 | 594.32 | 19 | 26.9 | 3.0569 | 3.0569 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30.5453 | 591.2631 | 0 | 0.05921 | 6.0481 | 0 | 0 | 0 | 3.0569 | off_peak | 591.2631 |  |  | 0.51 | 0 | 99.49 | 18.4887 | 0
3188 | 564.94 | 0 | 25.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30.5453 | 564.94 | 0 | 0.05921 | 6.216 | 0 | 0 | 0 | 0 | off_peak | 564.94 |  |  | 0 | 0 | 100 | 0 | 0
3189 | 578.34 | 0 | 25.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30.5453 | 578.34 | 0 | 0.05921 | 6.3832 | 0 | 0 | 0 | 0 | off_peak | 578.34 |  |  | 0 | 0 | 100 | 0 | 0
3190 | 550.18 | 0 | 25.1 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 42.1093 | 562.5424 | 0 | 0.05921 | 6.638 | 0 | 0 | 0 | 0 | off_peak | 550.18 | 0 | 100 | 0 | 0 | 100 | 0 | 0
3191 | 566.25 | 0 | 24.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 42.1093 | 566.25 | 0 | 0.05921 | 6.8704 | 0 | 0 | 0 | 0 | off_peak | 566.25 |  |  | 0 | 0 | 100 | 0 | 0
3192 | 515.95 | 0 | 24.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 42.1093 | 515.95 | 0 | 0.05921 | 6.9215 | 0 | 0 | 0 | 0 | off_peak | 515.95 |  |  | 0 | 0 | 100 | 0 | 0
3193 | 564.58 | 0 | 24.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 42.1093 | 564.58 | 0 | 0.05921 | 6.7709 | 0 | 0 | 0 | 0 | off_peak | 564.58 |  |  | 0 | 0 | 100 | 0 | 0
3194 | 554.47 | 0 | 24.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 42.1093 | 554.47 | 0 | 0.05921 | 6.683 | 0 | 0 | 0 | 0 | off_peak | 554.47 |  |  | 0 | 0 | 100 | 0 | 0
3195 | 538.81 | 0 | 24.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 42.1093 | 538.81 | 0 | 0.05921 | 6.3035 | 0 | 0 | 0 | 0 | off_peak | 538.81 |  |  | 0 | 0 | 100 | 0 | 0
3196 | 537.76 | 0 | 24.6 | 0 | 0 | 0 | 0 | 8.7006 | 8.7006 | 0 | 0 | 0 | 50.2479 | 546.4606 | 0 | 0.05921 | 5.6367 | 0 | 0 | 0 | 0 | off_peak | 537.76 | 0 | 100 | 0 | 0 | 100 | 0 | 0
3197 | 569.54 | 0 | 24.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50.2479 | 569.54 | 0 | 0.05921 | 5.0146 | 0 | 0 | 0 | 0 | off_peak | 569.54 |  |  | 0 | 0 | 100 | 0 | 0
3198 | 689.26 | 0 | 24.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50.2479 | 689.26 | 0 | 0.05921 | 4.4131 | 0 | 0 | 0 | 0 | off_peak | 689.26 |  |  | 0 | 0 | 100 | 0 | 0
3199 | 717.35 | 69.0549 | 25 | 11.1869 | 11.1869 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50.2479 | 706.1631 | 0 | 0.05921 | 3.9587 | 0 | 0 | 0 | 11.1869 | off_peak | 706.1631 |  |  | 1.56 | 0 | 98.44 | 44.2851 | 0
3200 | 775.4 | 141.863 | 25.7 | 22.9239 | 22.9239 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50.2479 | 752.4761 | 0 | 0.05921 | 3.5879 | 0 | 0 | 0 | 22.9239 | off_peak | 752.4761 |  |  | 2.96 | 0 | 97.04 | 82.2493 | 0
3201 | 760.49 | 260.037 | 26.6 | 41.8833 | 41.8833 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50.2479 | 718.6067 | 0 | 0.05921 | 3.3254 | 0 | 0 | 0 | 41.8833 | off_peak | 718.6067 |  |  | 5.51 | 0 | 94.49 | 139.2797 | 0
3202 | 775.4 | 352.243 | 27.3 | 56.5909 | 56.5909 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 61.8119 | 731.1715 | 0 | 0.05921 | 3.1818 | 0 | 0 | 0 | 56.5909 | off_peak | 718.8091 | 0 | 100 | 7.3 | 0 | 92.7 | 180.0614 | 0
3203 | 749.61 | 395.31 | 27.9 | 63.3716 | 63.3716 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 61.8119 | 686.2384 | 0 | 0.05921 | 3.1479 | 0 | 0 | 0 | 63.3716 | off_peak | 686.2384 |  |  | 8.45 | 0 | 91.55 | 199.4845 | 0
3204 | 756.77 | 612.803 | 28.4 | 98.059 | 98.059 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 73.3758 | 671.0734 | 0 | 0.05921 | 3.159 | 0 | 0 | 0 | 98.059 | off_peak | 658.711 | 0 | 100 | 12.96 | 0 | 87.04 | 309.7685 | 0
3205 | 728.74 | 652.285 | 28.8 | 104.2246 | 104.2246 | 0 | 0 | 0.79843 | 0.79843 | 0 | 0 | 0 | 74.1227 | 625.3138 | 0 | 0.05921 | 3.3331 | 0 | 0 | 0 | 104.2246 | off_peak | 624.5154 | 0 | 100 | 14.3 | 0 | 85.7 | 347.393 | 0
3206 | 681.22 | 661.631 | 28.9 | 105.6794 | 105.6794 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1227 | 575.5406 | 0 | 0.05921 | 3.6926 | 0 | 0 | 0 | 105.6794 | off_peak | 575.5406 |  |  | 15.51 | 0 | 84.49 | 390.233 | 0
3207 | 741.41 | 530.324 | 28.8 | 84.7372 | 84.7372 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1227 | 656.6728 | 0 | 0.05921 | 4.0849 | 0 | 0 | 0 | 84.7372 | off_peak | 656.6728 |  |  | 11.43 | 0 | 88.57 | 346.145 | 0
3208 | 732.99 | 350.951 | 28.6 | 56.1172 | 56.1172 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1227 | 676.8728 | 0 | 0.05921 | 4.4426 | 0 | 0 | 0 | 56.1172 | off_peak | 676.8728 |  |  | 7.66 | 0 | 92.34 | 249.3055 | 0
3209 | 716.79 | 354.204 | 28.2 | 56.72 | 56.72 | 0 | 0 | 0.051567 | 0.051567 | 0 | 0 | 0 | 74.1709 | 660.1215 | 0 | 0.05921 | 4.9397 | 0 | 0 | 0 | 56.72 | off_peak | 660.07 | 0 | 100 | 7.91 | 0 | 92.09 | 280.1797 | 0
3210 | 653.94 | 199.799 | 27.6 | 32.0645 | 32.0645 | 0 | 0 | 0.0033305 | 0.0033305 | 0 | 0 | 0 | 74.174 | 621.8789 | 0 | 0.05921 | 5.4746 | 0 | 0 | 0 | 32.0645 | off_peak | 621.8755 | 0 | 100 | 4.9 | 0 | 95.1 | 175.5405 | 0
3211 | 591.24 | 46.4542 | 27.3 | 7.4633 | 7.4633 | 0 | 0 | 0.0002151 | 0.0002151 | 0 | 0 | 0 | 74.1742 | 583.7769 | 0 | 0.05921 | 5.8204 | 0 | 0 | 0 | 7.4633 | off_peak | 583.7767 | 0 | 100 | 1.26 | 0 | 98.74 | 43.4396 | 0
3212 | 583.75 | 0 | 26.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1742 | 583.75 | 0 | 0.05921 | 6.1442 | 0 | 0 | 0 | 0 | off_peak | 583.75 |  |  | 0 | 0 | 100 | 0 | 0
3213 | 566.98 | 0 | 26 | 0 | 0 | 0 | 0 | 1.4852e-05 | 1.4852e-05 | 0 | 0 | 0 | 74.1743 | 566.98 | 0 | 0.05921 | 6.3077 | 0 | 0 | 0 | 0 | off_peak | 566.98 | 0 | 100 | 0 | 0 | 100 | 0 | 0
3214 | 588.04 | 0 | 25.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1743 | 588.04 | 0 | 0.05921 | 6.4769 | 0 | 0 | 0 | 0 | off_peak | 588.04 |  |  | 0 | 0 | 100 | 0 | 0
3215 | 591.02 | 0 | 25.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1743 | 591.02 | 0 | 0.05921 | 6.5172 | 0 | 0 | 0 | 0 | off_peak | 591.02 |  |  | 0 | 0 | 100 | 0 | 0
3216 | 573.8 | 0 | 25.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1743 | 573.8 | 0 | 0.05921 | 6.6471 | 0 | 0 | 0 | 0 | off_peak | 573.8 |  |  | 0 | 0 | 100 | 0 | 0
3217 | 574.56 | 0 | 25.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1743 | 574.56 | 0 | 0.05921 | 6.7959 | 0 | 0 | 0 | 0 | off_peak | 574.56 |  |  | 0 | 0 | 100 | 0 | 0
3218 | 572.23 | 0 | 25.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1743 | 572.23 | 0 | 0.05921 | 6.7883 | 0 | 0 | 0 | 0 | off_peak | 572.23 |  |  | 0 | 0 | 100 | 0 | 0
3219 | 587.2 | 0 | 25.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1743 | 587.2 | 0 | 0.05921 | 6.4403 | 0 | 0 | 0 | 0 | off_peak | 587.2 |  |  | 0 | 0 | 100 | 0 | 0
3220 | 574.87 | 0 | 25.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1743 | 574.87 | 0 | 0.05921 | 5.8736 | 0 | 0 | 0 | 0 | off_peak | 574.87 |  |  | 0 | 0 | 100 | 0 | 0
3221 | 604.49 | 0 | 25.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1743 | 604.49 | 0 | 0.05921 | 4.9454 | 0 | 0 | 0 | 0 | off_peak | 604.49 |  |  | 0 | 0 | 100 | 0 | 0
3222 | 700.51 | 0 | 25.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1743 | 700.51 | 0 | 0.05921 | 4.3177 | 0 | 0 | 0 | 0 | off_peak | 700.51 |  |  | 0 | 0 | 100 | 0 | 0
3223 | 773.2 | 124.281 | 26.2 | 20.0465 | 20.0465 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1743 | 753.1535 | 0 | 0.05921 | 3.8618 | 0 | 0 | 0 | 20.0465 | off_peak | 753.1535 |  |  | 2.59 | 0 | 97.41 | 77.4156 | 0
3224 | 784.6 | 330.047 | 26.8 | 53.1211 | 53.1211 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1743 | 731.4789 | 0 | 0.05921 | 3.5801 | 0 | 0 | 0 | 53.1211 | off_peak | 731.4789 |  |  | 6.77 | 0 | 93.23 | 190.1789 | 0
3225 | 815.65 | 539.728 | 27.1 | 86.7749 | 86.7749 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1743 | 728.8751 | 0 | 0.05921 | 3.4029 | 0 | 0 | 0 | 86.7749 | off_peak | 728.8751 |  |  | 10.64 | 0 | 89.36 | 295.2865 | 0
3226 | 813.52 | 723.598 | 27.3 | 116.2523 | 116.2523 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1743 | 697.2677 | 0 | 0.05921 | 3.3682 | 0 | 0 | 0 | 116.2523 | off_peak | 697.2677 |  |  | 14.29 | 0 | 85.71 | 391.5649 | 0
3227 | 827.52 | 561.389 | 27.5 | 90.1265 | 90.1265 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1743 | 737.3935 | 0 | 0.05921 | 3.5185 | 0 | 0 | 0 | 90.1265 | off_peak | 737.3935 |  |  | 10.89 | 0 | 89.11 | 317.1115 | 0
3228 | 872.93 | 654.762 | 27.7 | 105.0404 | 105.0404 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1743 | 767.8896 | 0 | 0.05921 | 3.8564 | 0 | 0 | 0 | 105.0404 | off_peak | 767.8896 |  |  | 12.03 | 0 | 87.97 | 405.0818 | 0
3229 | 827.42 | 553.144 | 27.7 | 88.7383 | 88.7383 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1743 | 738.6817 | 0 | 0.088511 | 4.0819 | 0 | 0 | 0 | 88.7383 | on_peak | 738.6817 |  |  | 10.72 | 0 | 89.28 | 362.2214 | 0
3230 | 860.59 | 881.909 | 27.7 | 141.4806 | 141.4806 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1743 | 719.1094 | 0 | 0.088511 | 4.2781 | 0 | 0 | 0 | 141.4806 | on_peak | 719.1094 |  |  | 16.44 | 0 | 83.56 | 605.2661 | 0
3231 | 862.61 | 806.497 | 27.6 | 129.4296 | 129.4296 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1743 | 733.1804 | 0 | 0.088511 | 4.4802 | 0 | 0 | 0 | 129.4296 | on_peak | 733.1804 |  |  | 15 | 0 | 85 | 579.866 | 0
3232 | 878.08 | 512.044 | 27.4 | 82.2344 | 82.2344 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1743 | 795.8456 | 0 | 0.088511 | 4.8492 | 0 | 0 | 0 | 82.2344 | on_peak | 795.8456 |  |  | 9.37 | 0 | 90.63 | 398.7689 | 0
3233 | 826.23 | 448.611 | 27.1 | 72.1256 | 72.1256 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1743 | 754.1044 | 0 | 0.088511 | 5.246 | 0 | 0 | 0 | 72.1256 | on_peak | 754.1044 |  |  | 8.73 | 0 | 91.27 | 378.372 | 0
3234 | 882.47 | 234.403 | 26.7 | 37.7409 | 37.7409 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1743 | 844.7291 | 0 | 0.088511 | 5.7726 | 0 | 0 | 0 | 37.7409 | on_peak | 844.7291 |  |  | 4.28 | 0 | 95.72 | 217.8615 | 0
3235 | 781.5 | 44.8892 | 26.4 | 7.2354 | 7.2354 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1743 | 774.2646 | 0 | 0.088511 | 6.2002 | 0 | 0 | 0 | 7.2354 | on_peak | 774.2646 |  |  | 0.93 | 0 | 99.07 | 44.861 | 0
3236 | 807.07 | 0 | 26 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1743 | 807.07 | 0 | 0.088511 | 6.5536 | 0 | 0 | 0 | 0 | on_peak | 807.07 |  |  | 0 | 0 | 100 | 0 | 0
3237 | 809.11 | 0 | 26 | 0 | 0 | 0 | 0 | 0 | 0 | 62.4453 | 62.4453 | 0 | 7.4174 | 746.6647 | 0 | 0.088511 | 6.9193 | 0 | 0 | 0 | 0 | on_peak | 746.6647 |  |  | 0 | 7.72 | 92.28 | 0 | 0
3238 | 792.48 | 0 | 26 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 792.48 | 0 | 0.05921 | 7.2747 | 0 | 0 | 0 | 0 | off_peak | 792.48 |  |  | 0 | 0 | 100 | 0 | 0
3239 | 772.9 | 0 | 26.1 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 18.9814 | 785.2624 | 0 | 0.05921 | 7.4464 | 0 | 0 | 0 | 0 | off_peak | 772.9 | 0 | 100 | 0 | 0 | 100 | 0 | 0
3240 | 755.06 | 0 | 26 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 30.5453 | 767.4224 | 0 | 0.05921 | 7.6134 | 0 | 0 | 0 | 0 | off_peak | 755.06 | 0 | 100 | 0 | 0 | 100 | 0 | 0
3241 | 738.31 | 0 | 25.8 | 0 | 0 | 0 | 0 | 8.7006 | 8.7006 | 0 | 0 | 0 | 38.684 | 747.0106 | 0 | 0.05921 | 7.5055 | 0 | 0 | 0 | 0 | off_peak | 738.31 | 0 | 100 | 0 | 0 | 100 | 0 | 0
3242 | 685.73 | 0 | 25.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 38.684 | 685.73 | 0 | 0.05921 | 7.2608 | 0 | 0 | 0 | 0 | off_peak | 685.73 |  |  | 0 | 0 | 100 | 0 | 0
3243 | 641.41 | 0 | 25.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 38.684 | 641.41 | 0 | 0.05921 | 6.8057 | 0 | 0 | 0 | 0 | off_peak | 641.41 |  |  | 0 | 0 | 100 | 0 | 0
3244 | 621.9 | 0 | 25.4 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 50.2479 | 634.2624 | 0 | 0.05921 | 6.0598 | 0 | 0 | 0 | 0 | off_peak | 621.9 | 0 | 100 | 0 | 0 | 100 | 0 | 0
3245 | 639.71 | 0 | 25.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50.2479 | 639.71 | 0 | 0.05921 | 5.126 | 0 | 0 | 0 | 0 | off_peak | 639.71 |  |  | 0 | 0 | 100 | 0 | 0
3246 | 693.6 | 0 | 25.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50.2479 | 693.6 | 0 | 0.05921 | 4.376 | 0 | 0 | 0 | 0 | off_peak | 693.6 |  |  | 0 | 0 | 100 | 0 | 0
3247 | 759.21 | 102.977 | 25.7 | 16.6402 | 16.6402 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 61.8119 | 754.9321 | 0 | 0.05921 | 3.9259 | 0 | 0 | 0 | 16.6402 | off_peak | 742.5698 | 0 | 100 | 2.19 | 0 | 97.81 | 65.3286 | 0
3248 | 854.01 | 290.878 | 25.7 | 47.0035 | 47.0035 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 73.3758 | 819.3689 | 0 | 0.05921 | 3.5722 | 0 | 0 | 0 | 47.0035 | off_peak | 807.0065 | 0 | 100 | 5.5 | 0 | 94.5 | 167.906 | 0
3249 | 864.2 | 460.606 | 25.5 | 74.4839 | 74.4839 | 0 | 0 | 0.79843 | 0.79843 | 0 | 0 | 0 | 74.1227 | 790.5146 | 0 | 0.05921 | 3.3685 | 0 | 0 | 0 | 74.4839 | off_peak | 789.7161 | 0 | 100 | 8.62 | 0 | 91.38 | 250.8977 | 0
3250 | 814.51 | 642.421 | 25.3 | 103.9598 | 103.9082 | 0 | 0.051567 | 0.051567 | 0 | 0 | 0 | 0 | 74.1709 | 710.6018 | 0 | 0.05921 | 3.2834 | 0 | 0 | 0.048237 | 103.9082 | off_peak | 710.6018 | 100 | 0 | 12.76 | 0 | 87.24 | 341.1701 | 0
3251 | 819.71 | 759.138 | 25 | 122.9804 | 122.977 | 0 | 0.0033305 | 0.0033305 | 0 | 0 | 0 | 0 | 74.174 | 696.733 | 0 | 0.05921 | 3.4161 | 0 | 0 | 0.051352 | 122.977 | off_peak | 696.733 | 100 | 0 | 15 | 0 | 85 | 420.1069 | 0
3252 | 873.82 | 897.594 | 24.6 | 145.6196 | 145.6194 | 0 | 0.0002151 | 0.0002151 | 0 | 0 | 0 | 0 | 74.1742 | 728.2006 | 0 | 0.05921 | 3.8073 | 0 | 0 | 0.051553 | 145.6194 | off_peak | 728.2006 | 100 | 0 | 16.66 | 0 | 83.34 | 554.4159 | 0
3253 | 880.4 | 867.342 | 24.4 | 140.8129 | 140.8129 | 0 | 1.3893e-05 | 1.3893e-05 | 0 | 0 | 0 | 0 | 74.1743 | 739.5871 | 0 | 0.088511 | 4.1348 | 0 | 0 | 0.051566 | 140.8129 | on_peak | 739.5871 | 100 | 0 | 15.99 | 0 | 84.01 | 582.2282 | 0
3254 | 897.78 | 830.755 | 24.1 | 135.0184 | 135.0184 | 0 | 8.9726e-07 | 8.9726e-07 | 0 | 0 | 0 | 0 | 74.1743 | 762.7616 | 0 | 0.088511 | 4.4151 | 0 | 0 | 0.051567 | 135.0184 | on_peak | 762.7616 | 100 | 0 | 15.04 | 0 | 84.96 | 596.1193 | 0
3255 | 911.92 | 735.43 | 23.7 | 119.6972 | 119.6972 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1743 | 792.2228 | 0 | 0.088511 | 4.688 | 0 | 0 | 0.051567 | 119.6972 | on_peak | 792.2228 |  |  | 13.13 | 0 | 86.87 | 561.1378 | 0
3256 | 939.3 | 341.564 | 23.4 | 55.6521 | 55.6521 | 0 | 0 | 0 | 0 | 28.7057 | 28.7057 | 0 | 43.4866 | 854.9422 | 0 | 0.088511 | 4.9597 | 0 | 0 | 0.051567 | 55.6521 | on_peak | 854.9422 |  |  | 5.92 | 3.06 | 91.02 | 276.0151 | 0
3257 | 912.97 | 376.172 | 23.3 | 61.3128 | 58.0278 | 0 | 3.285 | 3.285 | 0 | 0 | 0 | 0 | 46.5594 | 854.9422 | 0 | 0.088511 | 5.4232 | 0 | 0 | 3.1244 | 58.0278 | on_peak | 854.9422 | 100 | 0 | 6.36 | 0 | 93.64 | 314.6946 | 0
3258 | 921.29 | 182.491 | 23.4 | 29.7338 | 29.7338 | 0 | 0 | 0 | 0 | 36.614 | 36.614 | 0 | 7.4174 | 854.9422 | 0 | 0.088511 | 6.0307 | 2.9226 | 0 | 0 | 32.6565 | on_peak | 854.9422 |  |  | 3.23 | 3.97 | 92.8 | 196.9427 | 0
3259 | 827.41 | 54.3843 | 23.4 | 8.861 | 8.861 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 818.549 | 0 | 0.088511 | 6.6201 | 0 | 0 | 0 | 8.861 | on_peak | 818.549 |  |  | 1.07 | 0 | 98.93 | 58.6609 | 0
3260 | 841.05 | 0 | 23.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 841.05 | 0 | 0.088511 | 7.2021 | 0 | 0 | 0 | 0 | on_peak | 841.05 |  |  | 0 | 0 | 100 | 0 | 0
3261 | 825.89 | 0 | 23.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 825.89 | 0 | 0.088511 | 7.5088 | 0 | 0 | 0 | 0 | on_peak | 825.89 |  |  | 0 | 0 | 100 | 0 | 0
3262 | 802.35 | 0 | 23.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 802.35 | 0 | 0.05921 | 7.5994 | 0 | 0 | 0 | 0 | off_peak | 802.35 |  |  | 0 | 0 | 100 | 0 | 0
3263 | 812.43 | 0 | 23.4 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 18.9814 | 824.7924 | 0 | 0.05921 | 7.6903 | 0 | 0 | 0 | 0 | off_peak | 812.43 | 0 | 100 | 0 | 0 | 100 | 0 | 0
3264 | 794.01 | 0 | 23.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18.9814 | 794.01 | 0 | 0.05921 | 7.8245 | 0 | 0 | 0 | 0 | off_peak | 794.01 |  |  | 0 | 0 | 100 | 0 | 0
3265 | 735.42 | 0 | 23.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18.9814 | 735.42 | 0 | 0.05921 | 7.7372 | 0 | 0 | 0 | 0 | off_peak | 735.42 |  |  | 0 | 0 | 100 | 0 | 0
3266 | 694.08 | 0 | 23.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18.9814 | 694.08 | 0 | 0.05921 | 7.6534 | 0 | 0 | 0 | 0 | off_peak | 694.08 |  |  | 0 | 0 | 100 | 0 | 0
3267 | 558.46 | 0 | 23.2 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 30.5453 | 570.8224 | 0 | 0.05921 | 7.2368 | 0 | 0 | 0 | 0 | off_peak | 558.46 | 0 | 100 | 0 | 0 | 100 | 0 | 0
3268 | 493.17 | 0 | 23.1 | 0 | 0 | 0 | 0 | 8.7006 | 8.7006 | 0 | 0 | 0 | 38.684 | 501.8706 | 0 | 0.05921 | 6.3683 | 0 | 0 | 0 | 0 | off_peak | 493.17 | 0 | 100 | 0 | 0 | 100 | 0 | 0
3269 | 523.08 | 0 | 23.1 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 50.2479 | 535.4424 | 0 | 0.05921 | 5.4233 | 0 | 0 | 0 | 0 | off_peak | 523.08 | 0 | 100 | 0 | 0 | 100 | 0 | 0
3270 | 738.02 | 0 | 23.1 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 61.8119 | 750.3824 | 0 | 0.05921 | 4.7337 | 0 | 0 | 0 | 0 | off_peak | 738.02 | 0 | 100 | 0 | 0 | 100 | 0 | 0
3271 | 773.11 | 130.889 | 23.1 | 21.3491 | 21.3491 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 73.3758 | 764.1233 | 0 | 0.05921 | 4.3251 | 0 | 0 | 0 | 21.3491 | off_peak | 751.7609 | 0 | 100 | 2.76 | 0 | 97.24 | 92.3363 | 0
3272 | 819.62 | 341.374 | 23.3 | 55.641 | 55.641 | 0 | 0 | 0.79843 | 0.79843 | 0 | 0 | 0 | 74.1227 | 764.7774 | 0 | 0.05921 | 3.9711 | 0 | 0 | 0 | 55.641 | off_peak | 763.979 | 0 | 100 | 6.79 | 0 | 93.21 | 220.9534 | 0
3273 | 887.25 | 552.782 | 23.6 | 90.002 | 90.002 | 0 | 0 | 0.051567 | 0.051567 | 0 | 0 | 0 | 74.1709 | 797.2995 | 0 | 0.05921 | 3.7407 | 0 | 0 | 0 | 90.002 | off_peak | 797.248 | 0 | 100 | 10.14 | 0 | 89.86 | 336.668 | 0
3274 | 861.1 | 736.821 | 24.1 | 119.7517 | 119.7484 | 0 | 0.0033305 | 0.0033305 | 0 | 0 | 0 | 0 | 74.174 | 741.3516 | 0 | 0.05921 | 3.6527 | 0 | 0 | 0.0031154 | 119.7484 | off_peak | 741.3516 | 100 | 0 | 13.91 | 0 | 86.09 | 437.4069 | 0
3275 | 810.65 | 769.51 | 24.7 | 124.7953 | 124.7953 | 0 | 0 | 0.0002151 | 0.0002151 | 0 | 0 | 0 | 74.1742 | 685.855 | 0 | 0.05921 | 3.7985 | 0 | 0 | 0.0031154 | 124.7953 | off_peak | 685.8547 | 0 | 100 | 15.39 | 0 | 84.61 | 474.0391 | 0
3276 | 867.37 | 864.138 | 25.2 | 139.8896 | 139.8895 | 0 | 1.3893e-05 | 1.3893e-05 | 0 | 0 | 0 | 0 | 74.1743 | 727.4805 | 0 | 0.05921 | 4.2177 | 0 | 0 | 0.0031284 | 139.8895 | off_peak | 727.4805 | 100 | 0 | 16.13 | 0 | 83.87 | 590.0184 | 0
3277 | 860.53 | 639.379 | 25.5 | 103.393 | 103.393 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1743 | 757.137 | 0 | 0.088511 | 4.4452 | 0 | 0 | 0.0031284 | 103.393 | on_peak | 757.137 |  |  | 12.02 | 0 | 87.98 | 459.6025 | 0
3278 | 881.81 | 573.389 | 25.8 | 92.6215 | 92.6215 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1743 | 789.1885 | 0 | 0.088511 | 4.6832 | 0 | 0 | 0.0031284 | 92.6215 | on_peak | 789.1885 |  |  | 10.5 | 0 | 89.5 | 433.7655 | 0
3279 | 938.44 | 730.112 | 26.1 | 117.8098 | 117.8098 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1743 | 820.6302 | 0 | 0.088511 | 5.0405 | 0 | 0 | 0.0031284 | 117.8098 | on_peak | 820.6302 |  |  | 12.55 | 0 | 87.45 | 593.8228 | 0
3280 | 900.67 | 644.72 | 26.2 | 103.9934 | 103.9934 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1743 | 796.6766 | 0 | 0.088511 | 5.4407 | 0 | 0 | 0.0031284 | 103.9934 | on_peak | 796.6766 |  |  | 11.55 | 0 | 88.45 | 565.802 | 0
3281 | 867.92 | 461.775 | 26.2 | 74.4844 | 74.4844 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1743 | 793.4356 | 0 | 0.088511 | 5.9824 | 0 | 0 | 0.0031284 | 74.4844 | on_peak | 793.4356 |  |  | 8.58 | 0 | 91.42 | 445.5942 | 0
3282 | 861.94 | 225.962 | 25.8 | 36.5004 | 36.5004 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1743 | 825.4396 | 0 | 0.088511 | 6.5351 | 0 | 0 | 0.0031284 | 36.5004 | on_peak | 825.4396 |  |  | 4.23 | 0 | 95.77 | 238.5321 | 0
3283 | 814.91 | 53.5205 | 25.4 | 8.6578 | 8.6578 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1743 | 806.2522 | 0 | 0.088511 | 7.0378 | 0 | 0 | 0.0031284 | 8.6578 | on_peak | 806.2522 |  |  | 1.06 | 0 | 98.94 | 60.9317 | 0
3284 | 836.23 | 0 | 24.4 | 0 | 0 | 0 | 0 | 0 | 0 | 62.4424 | 62.4424 | 0 | 7.4206 | 773.7876 | 0 | 0.088511 | 7.1889 | 0 | 0 | 0.0031284 | 0 | on_peak | 773.7876 |  |  | 0 | 7.47 | 92.53 | 0 | 0
3285 | 814.57 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0029263 | 0.0029263 | 0 | 7.4174 | 814.5671 | 0 | 0.088511 | 7.0405 | 0.0029263 | 0 | 0 | 0.0029263 | on_peak | 814.5671 |  |  | 0 | 0 | 100 | 0.020603 | 0
3286 | 786.05 | 0 | 23.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 786.05 | 0 | 0.05921 | 6.9926 | 0 | 0 | 0 | 0 | off_peak | 786.05 |  |  | 0 | 0 | 100 | 0 | 0
3287 | 776.26 | 0 | 23.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 776.26 | 0 | 0.05921 | 7.1452 | 0 | 0 | 0 | 0 | off_peak | 776.26 |  |  | 0 | 0 | 100 | 0 | 0
3288 | 796.71 | 0 | 23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 796.71 | 0 | 0.05921 | 7.2513 | 0 | 0 | 0 | 0 | off_peak | 796.71 |  |  | 0 | 0 | 100 | 0 | 0
3289 | 704.24 | 0 | 22.7 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 18.9814 | 716.6024 | 0 | 0.05921 | 7.2244 | 0 | 0 | 0 | 0 | off_peak | 704.24 | 0 | 100 | 0 | 0 | 100 | 0 | 0
3290 | 717.82 | 0 | 22.4 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 30.5453 | 730.1824 | 0 | 0.05921 | 7.0584 | 0 | 0 | 0 | 0 | off_peak | 717.82 | 0 | 100 | 0 | 0 | 100 | 0 | 0
3291 | 645.35 | 0 | 22.1 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 42.1093 | 657.7124 | 0 | 0.05921 | 6.7285 | 0 | 0 | 0 | 0 | off_peak | 645.35 | 0 | 100 | 0 | 0 | 100 | 0 | 0
3292 | 618.02 | 0 | 21.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 42.1093 | 618.02 | 0 | 0.05921 | 6.0259 | 0 | 0 | 0 | 0 | off_peak | 618.02 |  |  | 0 | 0 | 100 | 0 | 0
3293 | 618.91 | 0 | 21.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 42.1093 | 618.91 | 0 | 0.05921 | 5.2332 | 0 | 0 | 0 | 0 | off_peak | 618.91 |  |  | 0 | 0 | 100 | 0 | 0
3294 | 671.69 | 0 | 21.6 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 53.6732 | 684.0524 | 0 | 0.05921 | 4.4288 | 0 | 0 | 0 | 0 | off_peak | 671.69 | 0 | 100 | 0 | 0 | 100 | 0 | 0
3295 | 784.43 | 109.714 | 22.2 | 17.9528 | 17.9528 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 65.2371 | 778.8395 | 0 | 0.05921 | 3.9549 | 0 | 0 | 0 | 17.9528 | off_peak | 766.4772 | 0 | 100 | 2.29 | 0 | 97.71 | 71.0023 | 0
3296 | 872.93 | 205.622 | 23.1 | 33.5386 | 33.5386 | 0 | 0 | 8.9371 | 8.9371 | 0 | 0 | 0 | 73.597 | 848.3285 | 0 | 0.05921 | 3.5938 | 0 | 0 | 0 | 33.5386 | off_peak | 839.3914 | 0 | 100 | 3.84 | 0 | 96.16 | 120.5301 | 0
3297 | 885.68 | 469.36 | 24 | 76.3101 | 76.3101 | 0 | 0 | 0.57721 | 0.57721 | 0 | 0 | 0 | 74.137 | 809.9472 | 0 | 0.05921 | 3.3528 | 0 | 0 | 0 | 76.3101 | off_peak | 809.3699 | 0 | 100 | 8.62 | 0 | 91.38 | 255.8542 | 0
3298 | 869.43 | 462.377 | 24.8 | 74.959 | 74.959 | 0 | 0 | 0.037279 | 0.037279 | 0 | 0 | 0 | 74.1718 | 794.5083 | 0 | 0.05921 | 3.2637 | 0 | 0 | 0 | 74.959 | off_peak | 794.471 | 0 | 100 | 8.62 | 0 | 91.38 | 244.6461 | 0
3299 | 823.32 | 659.436 | 25.5 | 106.6363 | 106.6363 | 0 | 0 | 0.0024077 | 0.0024077 | 0 | 0 | 0 | 74.1741 | 716.6861 | 0 | 0.05921 | 3.4273 | 0 | 0 | 0 | 106.6363 | off_peak | 716.6837 | 0 | 100 | 12.95 | 0 | 87.05 | 365.4724 | 0
3300 | 896.5 | 672.264 | 26.1 | 108.4755 | 108.4755 | 0 | 0 | 0.0001555 | 0.0001555 | 0 | 0 | 0 | 74.1742 | 788.0247 | 0 | 0.05921 | 3.8278 | 0 | 0 | 0 | 108.4755 | off_peak | 788.0245 | 0 | 100 | 12.1 | 0 | 87.9 | 415.223 | 0
3301 | 859.19 | 563.461 | 26.6 | 90.7549 | 90.7549 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1742 | 768.4351 | 0 | 0.088511 | 4.1254 | 0 | 0 | 0 | 90.7549 | on_peak | 768.4351 |  |  | 10.56 | 0 | 89.44 | 374.3973 | 0
3302 | 922.67 | 761.769 | 27 | 122.5181 | 122.5181 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1742 | 800.1519 | 0 | 0.088511 | 4.4173 | 0 | 0 | 0 | 122.5181 | on_peak | 800.1519 |  |  | 13.28 | 0 | 86.72 | 541.1974 | 0
3303 | 956.16 | 811.39 | 27.2 | 130.4041 | 130.4041 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1742 | 825.7559 | 0 | 0.088511 | 4.6711 | 0 | 0 | 0 | 130.4041 | on_peak | 825.7559 |  |  | 13.64 | 0 | 86.36 | 609.1281 | 0
3304 | 875.11 | 653.602 | 27.1 | 105.083 | 105.083 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1742 | 770.027 | 0 | 0.088511 | 5.1159 | 0 | 0 | 0 | 105.083 | on_peak | 770.027 |  |  | 12.01 | 0 | 87.99 | 537.5987 | 0
3305 | 933.87 | 457.75 | 26.9 | 73.6483 | 73.6483 | 0 | 0 | 0 | 0 | 60.2775 | 60.2775 | 0 | 9.7349 | 799.9442 | 0 | 0.088511 | 5.6353 | 0 | 0 | 0 | 73.6483 | on_peak | 799.9442 |  |  | 7.89 | 6.45 | 85.66 | 415.0265 | 0
3306 | 888.69 | 240.927 | 26.5 | 38.8194 | 38.8194 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9.7349 | 849.8706 | 0 | 0.088511 | 6.1492 | 0 | 0 | 0 | 38.8194 | on_peak | 849.8706 |  |  | 4.37 | 0 | 95.63 | 238.7079 | 0
3307 | 830.48 | 58.1645 | 26.2 | 9.3819 | 9.3819 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9.7349 | 821.0981 | 0 | 0.088511 | 6.696 | 0 | 0 | 0 | 9.3819 | on_peak | 821.0981 |  |  | 1.13 | 0 | 98.87 | 62.8212 | 0
3308 | 857.11 | 0 | 25.3 | 0 | 0 | 0 | 0 | 0 | 0 | 2.1678 | 2.1678 | 0 | 7.4174 | 854.9422 | 0 | 0.088511 | 7.08 | 0 | 0 | 0 | 0 | on_peak | 854.9422 |  |  | 0 | 0.25 | 99.75 | 0 | 0
3309 | 844.3 | 0 | 24.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 844.3 | 0 | 0.088511 | 7.3036 | 0 | 0 | 0 | 0 | on_peak | 844.3 |  |  | 0 | 0 | 100 | 0 | 0
3310 | 796.8 | 0 | 24.6 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 18.9814 | 809.1624 | 0 | 0.05921 | 7.4434 | 0 | 0 | 0 | 0 | off_peak | 796.8 | 0 | 100 | 0 | 0 | 100 | 0 | 0
3311 | 832.99 | 0 | 24.2 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 30.5453 | 845.3524 | 0 | 0.05921 | 7.4157 | 0 | 0 | 0 | 0 | off_peak | 832.99 | 0 | 100 | 0 | 0 | 100 | 0 | 0
3312 | 803.42 | 0 | 23.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30.5453 | 803.42 | 0 | 0.05921 | 7.1216 | 0 | 0 | 0 | 0 | off_peak | 803.42 |  |  | 0 | 0 | 100 | 0 | 0
3313 | 787.96 | 0 | 23.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30.5453 | 787.96 | 0 | 0.05921 | 6.9501 | 0 | 0 | 0 | 0 | off_peak | 787.96 |  |  | 0 | 0 | 100 | 0 | 0
3314 | 742.77 | 0 | 23 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 42.1093 | 755.1324 | 0 | 0.05921 | 6.8523 | 0 | 0 | 0 | 0 | off_peak | 742.77 | 0 | 100 | 0 | 0 | 100 | 0 | 0
3315 | 703 | 0 | 22.7 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 53.6732 | 715.3624 | 0 | 0.05921 | 6.5009 | 0 | 0 | 0 | 0 | off_peak | 703 | 0 | 100 | 0 | 0 | 100 | 0 | 0
3316 | 675.56 | 0 | 22.4 | 0 | 0 | 0 | 0 | 8.7006 | 8.7006 | 0 | 0 | 0 | 61.8119 | 684.2606 | 0 | 0.05921 | 5.8855 | 0 | 0 | 0 | 0 | off_peak | 675.56 | 0 | 100 | 0 | 0 | 100 | 0 | 0
3317 | 682.35 | 0 | 22.1 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 73.3758 | 694.7124 | 0 | 0.05921 | 5.1289 | 0 | 0 | 0 | 0 | off_peak | 682.35 | 0 | 100 | 0 | 0 | 100 | 0 | 0
3318 | 735.75 | 0 | 22.3 | 0 | 0 | 0 | 0 | 0.79843 | 0.79843 | 0 | 0 | 0 | 74.1227 | 736.5484 | 0 | 0.05921 | 4.4101 | 0 | 0 | 0 | 0 | off_peak | 735.75 | 0 | 100 | 0 | 0 | 100 | 0 | 0
3319 | 771.7 | 76.7798 | 23 | 12.5279 | 12.5279 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1227 | 759.1721 | 0 | 0.05921 | 4.0476 | 0 | 0 | 0 | 12.5279 | off_peak | 759.1721 |  |  | 1.62 | 0 | 98.38 | 50.7073 | 0
3320 | 849.08 | 179.361 | 23.8 | 29.182 | 29.182 | 0 | 0 | 0.051567 | 0.051567 | 0 | 0 | 0 | 74.1709 | 819.9496 | 0 | 0.05921 | 3.7282 | 0 | 0 | 0 | 29.182 | off_peak | 819.898 | 0 | 100 | 3.44 | 0 | 96.56 | 108.7949 | 0
3321 | 873.15 | 364.468 | 24.6 | 59.1288 | 59.1288 | 0 | 0 | 0.0033305 | 0.0033305 | 0 | 0 | 0 | 74.174 | 814.0245 | 0 | 0.05921 | 3.5345 | 0 | 0 | 0 | 59.1288 | off_peak | 814.0212 | 0 | 100 | 6.77 | 0 | 93.23 | 208.9889 | 0
3322 | 856.91 | 494.172 | 25.3 | 79.9694 | 79.9694 | 0 | 0 | 0.0002151 | 0.0002151 | 0 | 0 | 0 | 74.1742 | 776.9408 | 0 | 0.05921 | 3.4825 | 0 | 0 | 0 | 79.9694 | off_peak | 776.9406 | 0 | 100 | 9.33 | 0 | 90.67 | 278.4904 | 0
3323 | 775.74 | 635.302 | 26 | 102.5484 | 102.5484 | 0 | 0 | 1.3893e-05 | 1.3893e-05 | 0 | 0 | 0 | 74.1743 | 673.1916 | 0 | 0.05921 | 3.6573 | 0 | 0 | 0 | 102.5484 | off_peak | 673.1916 | 0 | 100 | 13.22 | 0 | 86.78 | 375.0478 | 0
3324 | 820.78 | 717.436 | 26.7 | 115.5133 | 115.5133 | 0 | 0 | 8.9726e-07 | 8.9726e-07 | 0 | 0 | 0 | 74.1743 | 705.2667 | 0 | 0.05921 | 4.0319 | 0 | 0 | 0 | 115.5133 | off_peak | 705.2667 | 0 | 100 | 14.07 | 0 | 85.93 | 465.7336 | 0
3325 | 870.95 | 627.363 | 27.3 | 100.7913 | 100.7913 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1743 | 770.1587 | 0 | 0.088511 | 4.2978 | 0 | 0 | 0 | 100.7913 | on_peak | 770.1587 |  |  | 11.57 | 0 | 88.43 | 433.176 | 0
3326 | 914.74 | 761.073 | 27.7 | 122.0954 | 122.0954 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1743 | 792.6446 | 0 | 0.088511 | 4.6578 | 0 | 0 | 0 | 122.0954 | on_peak | 792.6446 |  |  | 13.35 | 0 | 86.65 | 568.691 | 0
3327 | 914.26 | 657.007 | 28.1 | 105.2473 | 105.2473 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1743 | 809.0127 | 0 | 0.088511 | 5.0006 | 0 | 0 | 0 | 105.2473 | on_peak | 809.0127 |  |  | 11.51 | 0 | 88.49 | 526.3012 | 0
3328 | 908.19 | 498.612 | 28.2 | 79.8446 | 79.8446 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1743 | 828.3454 | 0 | 0.088511 | 5.3841 | 0 | 0 | 0 | 79.8446 | on_peak | 828.3454 |  |  | 8.79 | 0 | 91.21 | 429.8949 | 0
3329 | 873.57 | 251.695 | 27.9 | 40.3489 | 40.3489 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1743 | 833.2211 | 0 | 0.088511 | 5.8028 | 0 | 0 | 0 | 40.3489 | on_peak | 833.2211 |  |  | 4.62 | 0 | 95.38 | 234.1366 | 0
3330 | 832.89 | 125.559 | 27.3 | 20.1721 | 20.1721 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1743 | 812.7179 | 0 | 0.088511 | 6.3086 | 0 | 0 | 0 | 20.1721 | on_peak | 812.7179 |  |  | 2.42 | 0 | 97.58 | 127.2584 | 0
3331 | 836.84 | 45.831 | 26.8 | 7.3765 | 7.3765 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1743 | 829.4635 | 0 | 0.088511 | 6.675 | 0 | 0 | 0 | 7.3765 | on_peak | 829.4635 |  |  | 0.88 | 0 | 99.12 | 49.2382 | 0
3332 | 828.58 | 0 | 25.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1743 | 828.58 | 0 | 0.088511 | 6.8366 | 0 | 0 | 0 | 0 | on_peak | 828.58 |  |  | 0 | 0 | 100 | 0 | 0
3333 | 842.14 | 0 | 25.6 | 0 | 0 | 0 | 0 | 0 | 0 | 62.4453 | 62.4453 | 0 | 7.4174 | 779.6947 | 0 | 0.088511 | 6.7662 | 0 | 0 | 0 | 0 | on_peak | 779.6947 |  |  | 0 | 7.42 | 92.58 | 0 | 0
3334 | 803.54 | 0 | 25.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 803.54 | 0 | 0.05921 | 7.0882 | 0 | 0 | 0 | 0 | off_peak | 803.54 |  |  | 0 | 0 | 100 | 0 | 0
3335 | 800.54 | 0 | 24.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 800.54 | 0 | 0.05921 | 7.3244 | 0 | 0 | 0 | 0 | off_peak | 800.54 |  |  | 0 | 0 | 100 | 0 | 0
3336 | 776.8 | 0 | 24.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 776.8 | 0 | 0.05921 | 7.3211 | 0 | 0 | 0 | 0 | off_peak | 776.8 |  |  | 0 | 0 | 100 | 0 | 0
3337 | 776.24 | 0 | 24.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 776.24 | 0 | 0.05921 | 7.3005 | 0 | 0 | 0 | 0 | off_peak | 776.24 |  |  | 0 | 0 | 100 | 0 | 0
3338 | 698.46 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 698.46 | 0 | 0.05921 | 7.0806 | 0 | 0 | 0 | 0 | off_peak | 698.46 |  |  | 0 | 0 | 100 | 0 | 0
3339 | 634.08 | 0 | 23.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 634.08 | 0 | 0.05921 | 6.7695 | 0 | 0 | 0 | 0 | off_peak | 634.08 |  |  | 0 | 0 | 100 | 0 | 0
3340 | 646.48 | 0 | 23.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 646.48 | 0 | 0.05921 | 6.0665 | 0 | 0 | 0 | 0 | off_peak | 646.48 |  |  | 0 | 0 | 100 | 0 | 0
3341 | 681.43 | 0 | 23.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 681.43 | 0 | 0.05921 | 5.4649 | 0 | 0 | 0 | 0 | off_peak | 681.43 |  |  | 0 | 0 | 100 | 0 | 0
3342 | 730.1 | 0 | 23.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 730.1 | 0 | 0.05921 | 4.6988 | 0 | 0 | 0 | 0 | off_peak | 730.1 |  |  | 0 | 0 | 100 | 0 | 0
3343 | 800.89 | 102.248 | 24.1 | 16.6178 | 16.6178 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 784.2722 | 0 | 0.05921 | 4.2965 | 0 | 0 | 0 | 16.6178 | off_peak | 784.2722 |  |  | 2.07 | 0 | 97.93 | 71.3987 | 0
3344 | 876.51 | 241.294 | 24.9 | 39.1037 | 39.1037 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 837.4063 | 0 | 0.05921 | 3.9487 | 0 | 0 | 0 | 39.1037 | off_peak | 837.4063 |  |  | 4.46 | 0 | 95.54 | 154.4089 | 0
3345 | 879.14 | 359.783 | 25.7 | 58.138 | 58.138 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 821.002 | 0 | 0.05921 | 3.7028 | 0 | 0 | 0 | 58.138 | off_peak | 821.002 |  |  | 6.61 | 0 | 93.39 | 215.274 | 0
3346 | 867.28 | 478.481 | 26.5 | 77.0953 | 77.0953 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 790.1847 | 0 | 0.05921 | 3.5643 | 0 | 0 | 0 | 77.0953 | off_peak | 790.1847 |  |  | 8.89 | 0 | 91.11 | 274.7947 | 0
3347 | 835.95 | 536.765 | 27.3 | 86.2359 | 86.2359 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 749.7141 | 0 | 0.05921 | 3.5375 | 0 | 0 | 0 | 86.2359 | off_peak | 749.7141 |  |  | 10.32 | 0 | 89.68 | 305.0582 | 0
3348 | 872.72 | 737.035 | 28 | 118.1102 | 118.1102 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 754.6098 | 0 | 0.05921 | 3.5873 | 0 | 0 | 0 | 118.1102 | off_peak | 754.6098 |  |  | 13.53 | 0 | 86.47 | 423.7017 | 0
3349 | 831.02 | 775.165 | 28.4 | 124.0397 | 124.0397 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 706.9803 | 0 | 0.05921 | 3.8259 | 0 | 0 | 0 | 124.0397 | off_peak | 706.9803 |  |  | 14.93 | 0 | 85.07 | 474.5658 | 0
3350 | 869.03 | 742.01 | 28.7 | 118.6045 | 118.6045 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 750.4255 | 0 | 0.05921 | 4.3016 | 0 | 0 | 0 | 118.6045 | off_peak | 750.4255 |  |  | 13.65 | 0 | 86.35 | 510.1939 | 0
3351 | 855.87 | 562.194 | 28.8 | 89.8295 | 89.8295 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 766.0405 | 0 | 0.05921 | 4.6258 | 0 | 0 | 0 | 89.8295 | off_peak | 766.0405 |  |  | 10.5 | 0 | 89.5 | 415.5309 | 0
3352 | 843.28 | 481.64 | 28.7 | 76.9864 | 76.9864 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 766.2936 | 0 | 0.05921 | 5.0917 | 0 | 0 | 0 | 76.9864 | off_peak | 766.2936 |  |  | 9.13 | 0 | 90.87 | 391.9878 | 0
3353 | 811.47 | 396.871 | 28.2 | 63.5524 | 63.5524 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 747.9176 | 0 | 0.05921 | 5.7471 | 0 | 0 | 0 | 63.5524 | off_peak | 747.9176 |  |  | 7.83 | 0 | 92.17 | 365.2438 | 0
3354 | 788.53 | 142.993 | 27.4 | 22.9647 | 22.9647 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 765.5653 | 0 | 0.05921 | 6.5803 | 0 | 0 | 0 | 22.9647 | off_peak | 765.5653 |  |  | 2.91 | 0 | 97.09 | 151.1142 | 0
3355 | 730.12 | 49.0363 | 27 | 7.8867 | 7.8867 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 722.2333 | 0 | 0.05921 | 7.0998 | 0 | 0 | 0 | 7.8867 | off_peak | 722.2333 |  |  | 1.08 | 0 | 98.92 | 55.9942 | 0
3356 | 663.54 | 0 | 26 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 663.54 | 0 | 0.05921 | 7.3812 | 0 | 0 | 0 | 0 | off_peak | 663.54 |  |  | 0 | 0 | 100 | 0 | 0
3357 | 674.58 | 0 | 25.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 674.58 | 0 | 0.05921 | 7.5025 | 0 | 0 | 0 | 0 | off_peak | 674.58 |  |  | 0 | 0 | 100 | 0 | 0
3358 | 683.56 | 0 | 25.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 683.56 | 0 | 0.05921 | 7.4856 | 0 | 0 | 0 | 0 | off_peak | 683.56 |  |  | 0 | 0 | 100 | 0 | 0
3359 | 664.14 | 0 | 25.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 664.14 | 0 | 0.05921 | 7.4037 | 0 | 0 | 0 | 0 | off_peak | 664.14 |  |  | 0 | 0 | 100 | 0 | 0
3360 | 655.91 | 0 | 25.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 655.91 | 0 | 0.05921 | 7.4058 | 0 | 0 | 0 | 0 | off_peak | 655.91 |  |  | 0 | 0 | 100 | 0 | 0
3361 | 670.9 | 0 | 25.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 670.9 | 0 | 0.05921 | 7.219 | 0 | 0 | 0 | 0 | off_peak | 670.9 |  |  | 0 | 0 | 100 | 0 | 0
3362 | 641.03 | 0 | 25.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 641.03 | 0 | 0.05921 | 7.0103 | 0 | 0 | 0 | 0 | off_peak | 641.03 |  |  | 0 | 0 | 100 | 0 | 0
3363 | 689.16 | 0 | 25.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 689.16 | 0 | 0.05921 | 6.6193 | 0 | 0 | 0 | 0 | off_peak | 689.16 |  |  | 0 | 0 | 100 | 0 | 0
3364 | 678.85 | 0 | 25.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 678.85 | 0 | 0.05921 | 5.96 | 0 | 0 | 0 | 0 | off_peak | 678.85 |  |  | 0 | 0 | 100 | 0 | 0
3365 | 677.34 | 0 | 25.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 677.34 | 0 | 0.05921 | 5.3067 | 0 | 0 | 0 | 0 | off_peak | 677.34 |  |  | 0 | 0 | 100 | 0 | 0
3366 | 713.12 | 0 | 25.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 713.12 | 0 | 0.05921 | 4.7275 | 0 | 0 | 0 | 0 | off_peak | 713.12 |  |  | 0 | 0 | 100 | 0 | 0
3367 | 788.01 | 124.203 | 25.7 | 20.0702 | 20.0702 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 767.9398 | 0 | 0.05921 | 4.3646 | 0 | 0 | 0 | 20.0702 | off_peak | 767.9398 |  |  | 2.55 | 0 | 97.45 | 87.5979 | 0
3368 | 783.02 | 326.475 | 26.2 | 52.6605 | 52.6605 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 730.3595 | 0 | 0.05921 | 4.0453 | 0 | 0 | 0 | 52.6605 | off_peak | 730.3595 |  |  | 6.73 | 0 | 93.27 | 213.0259 | 0
3369 | 762.29 | 547.419 | 26.7 | 88.1391 | 88.1391 | 0 | 0 | 8.7006 | 8.7006 | 0 | 0 | 0 | 15.5561 | 682.8515 | 0 | 0.05921 | 3.7421 | 0 | 0 | 0 | 88.1391 | off_peak | 674.1509 | 0 | 100 | 11.56 | 0 | 88.44 | 329.8233 | 0
3370 | 787.61 | 571.422 | 27.2 | 91.8372 | 91.8372 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15.5561 | 695.7728 | 0 | 0.05921 | 3.5877 | 0 | 0 | 0 | 91.8372 | off_peak | 695.7728 |  |  | 11.66 | 0 | 88.34 | 329.4841 | 0
3371 | 772.71 | 530.051 | 27.8 | 85.0027 | 85.0027 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15.5561 | 687.7073 | 0 | 0.05921 | 3.5149 | 0 | 0 | 0 | 85.0027 | off_peak | 687.7073 |  |  | 11 | 0 | 89 | 298.7745 | 0
3372 | 783.34 | 837.414 | 28.3 | 134.0494 | 134.0494 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 27.12 | 661.653 | 0 | 0.05921 | 3.476 | 0 | 0 | 0 | 134.0494 | off_peak | 649.2906 | 0 | 100 | 17.11 | 0 | 82.89 | 465.9622 | 0
3373 | 757.18 | 939.12 | 28.6 | 150.1657 | 150.1657 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27.12 | 607.0143 | 0 | 0.05921 | 3.662 | 0 | 0 | 0 | 150.1657 | off_peak | 607.0143 |  |  | 19.83 | 0 | 80.17 | 549.9024 | 0
3374 | 773.26 | 899.931 | 28.8 | 143.7944 | 143.7944 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27.12 | 629.4656 | 0 | 0.05921 | 4.1339 | 0 | 0 | 0 | 143.7944 | off_peak | 629.4656 |  |  | 18.6 | 0 | 81.4 | 594.4324 | 0
3375 | 785.2 | 756.523 | 28.8 | 120.8801 | 108.5178 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 0 | 38.684 | 676.6822 | 0 | 0.05921 | 4.6883 | 0 | 0 | 11.5639 | 108.5178 | off_peak | 676.6822 | 100 | 0 | 13.82 | 0 | 86.18 | 508.7632 | 0
3376 | 783.58 | 493.84 | 28.7 | 78.9365 | 66.5741 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 0 | 50.2479 | 717.0059 | 0 | 0.05921 | 5.3011 | 0 | 0 | 23.1279 | 66.5741 | off_peak | 717.0059 | 100 | 0 | 8.5 | 0 | 91.5 | 352.917 | 0
3377 | 747.64 | 456.463 | 28.3 | 73.0685 | 60.7061 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 0 | 61.8119 | 686.9339 | 0 | 0.05921 | 5.8957 | 0 | 0 | 34.6918 | 60.7061 | off_peak | 686.9339 | 100 | 0 | 8.12 | 0 | 91.88 | 357.9072 | 0
3378 | 692.5 | 249.625 | 27.8 | 40.0316 | 27.6692 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 0 | 73.3758 | 664.8308 | 0 | 0.05921 | 6.4259 | 0 | 0 | 46.2558 | 27.6692 | off_peak | 664.8308 | 100 | 0 | 4 | 0 | 96 | 177.7988 | 0
3379 | 613.63 | 59.7095 | 27.4 | 9.5894 | 9.5894 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 73.3758 | 604.0406 | 0 | 0.05921 | 6.7343 | 0 | 0 | 46.2558 | 9.5894 | off_peak | 604.0406 |  |  | 1.56 | 0 | 98.44 | 64.5774 | 0
3380 | 590.53 | 0 | 26.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 73.3758 | 590.53 | 0 | 0.05921 | 6.8842 | 0 | 0 | 46.2558 | 0 | off_peak | 590.53 |  |  | 0 | 0 | 100 | 0 | 0
3381 | 562.98 | 0 | 26.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 73.3758 | 562.98 | 0 | 0.05921 | 7.0257 | 0 | 0 | 46.2558 | 0 | off_peak | 562.98 |  |  | 0 | 0 | 100 | 0 | 0
3382 | 550.14 | 0 | 26.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 73.3758 | 550.14 | 0 | 0.05921 | 7.2506 | 0 | 0 | 46.2558 | 0 | off_peak | 550.14 |  |  | 0 | 0 | 100 | 0 | 0
3383 | 588.76 | 0 | 26 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 73.3758 | 588.76 | 0 | 0.05921 | 7.2369 | 0 | 0 | 46.2558 | 0 | off_peak | 588.76 |  |  | 0 | 0 | 100 | 0 | 0
3384 | 523.32 | 0 | 26 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 73.3758 | 523.32 | 0 | 0.05921 | 7.2617 | 0 | 0 | 46.2558 | 0 | off_peak | 523.32 |  |  | 0 | 0 | 100 | 0 | 0
3385 | 565.13 | 0 | 25.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 73.3758 | 565.13 | 0 | 0.05921 | 7.2396 | 0 | 0 | 46.2558 | 0 | off_peak | 565.13 |  |  | 0 | 0 | 100 | 0 | 0
3386 | 561.79 | 0 | 26 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 73.3758 | 561.79 | 0 | 0.05921 | 7.1485 | 0 | 0 | 46.2558 | 0 | off_peak | 561.79 |  |  | 0 | 0 | 100 | 0 | 0
3387 | 536.84 | 0 | 26.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 73.3758 | 536.84 | 0 | 0.05921 | 6.7468 | 0 | 0 | 46.2558 | 0 | off_peak | 536.84 |  |  | 0 | 0 | 100 | 0 | 0
3388 | 551.46 | 0 | 26.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 73.3758 | 551.46 | 0 | 0.05921 | 5.9773 | 0 | 0 | 46.2558 | 0 | off_peak | 551.46 |  |  | 0 | 0 | 100 | 0 | 0
3389 | 557.28 | 0 | 26.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 73.3758 | 557.28 | 0 | 0.05921 | 5.2884 | 0 | 0 | 46.2558 | 0 | off_peak | 557.28 |  |  | 0 | 0 | 100 | 0 | 0
3390 | 689.76 | 0 | 26.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 73.3758 | 689.76 | 0 | 0.05921 | 4.6806 | 0 | 0 | 46.2558 | 0 | off_peak | 689.76 |  |  | 0 | 0 | 100 | 0 | 0
3391 | 833.03 | 134.443 | 26.6 | 21.6543 | 20.8559 | 0 | 0.79843 | 0.79843 | 0 | 0 | 0 | 0 | 74.1227 | 812.1741 | 0 | 0.05921 | 4.2597 | 0 | 0 | 47.0026 | 20.8559 | off_peak | 812.1741 | 100 | 0 | 2.5 | 0 | 97.5 | 88.8396 | 0
3392 | 888.92 | 343.427 | 26.9 | 55.2546 | 55.2031 | 0 | 0.051567 | 0.051567 | 0 | 0 | 0 | 0 | 74.1709 | 833.7169 | 0 | 0.05921 | 3.9445 | 0 | 0 | 47.0509 | 55.2031 | off_peak | 833.7169 | 100 | 0 | 6.21 | 0 | 93.79 | 217.751 | 0
3393 | 865.2 | 410.059 | 27.2 | 65.9034 | 65.9001 | 0 | 0.0033305 | 0.0033305 | 0 | 0 | 0 | 0 | 74.174 | 799.2999 | 0 | 0.05921 | 3.7716 | 0 | 0 | 47.054 | 65.9001 | off_peak | 799.2999 | 100 | 0 | 7.62 | 0 | 92.38 | 248.5464 | 0
3394 | 871.98 | 611.709 | 27.5 | 98.205 | 98.2048 | 0 | 0.0002151 | 0.0002151 | 0 | 0 | 0 | 0 | 74.1742 | 773.7752 | 0 | 0.05921 | 3.7059 | 0 | 0 | 47.0542 | 98.2048 | off_peak | 773.7752 | 100 | 0 | 11.26 | 0 | 88.74 | 363.9324 | 0
3395 | 849.16 | 876.834 | 27.9 | 140.5641 | 140.5641 | 0 | 0 | 1.3893e-05 | 1.3893e-05 | 0 | 0 | 0 | 74.1743 | 708.5959 | 0 | 0.05921 | 3.8708 | 0 | 0 | 47.0542 | 140.5641 | off_peak | 708.5959 | 0 | 100 | 16.55 | 0 | 83.45 | 544.1015 | 0
3396 | 899.45 | 880.754 | 28.3 | 140.9871 | 140.9871 | 0 | 8.9726e-07 | 8.9726e-07 | 0 | 0 | 0 | 0 | 74.1743 | 758.4629 | 0 | 0.05921 | 4.2025 | 0 | 0 | 47.0542 | 140.9871 | off_peak | 758.4629 | 100 | 0 | 15.67 | 0 | 84.33 | 592.4944 | 0
3397 | 911.92 | 967.351 | 28.6 | 154.6799 | 154.6799 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1743 | 757.2401 | 0 | 0.088511 | 4.4399 | 0 | 0 | 47.0542 | 154.6799 | on_peak | 757.2401 |  |  | 16.96 | 0 | 83.04 | 686.7644 | 0
3398 | 923.53 | 907.744 | 28.8 | 145.0428 | 145.0428 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1743 | 778.4872 | 0 | 0.088511 | 4.7563 | 0 | 0 | 47.0542 | 145.0428 | on_peak | 778.4872 |  |  | 15.71 | 0 | 84.29 | 689.8739 | 0
3399 | 929.8 | 823.275 | 28.9 | 131.498 | 131.498 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1743 | 798.302 | 0 | 0.088511 | 5.1111 | 0 | 0 | 47.0542 | 131.498 | on_peak | 798.302 |  |  | 14.14 | 0 | 85.86 | 672.1017 | 0
3400 | 918.92 | 661.838 | 28.9 | 105.7124 | 105.7124 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1743 | 813.2076 | 0 | 0.088511 | 5.5495 | 0 | 0 | 47.0542 | 105.7124 | on_peak | 813.2076 |  |  | 11.5 | 0 | 88.5 | 586.6532 | 0
3401 | 918.74 | 465.899 | 28.7 | 74.4703 | 74.4703 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1743 | 844.2697 | 0 | 0.088511 | 5.9481 | 0 | 0 | 47.0542 | 74.4703 | on_peak | 844.2697 |  |  | 8.11 | 0 | 91.89 | 442.9598 | 0
3402 | 892.26 | 251.453 | 28.3 | 40.2514 | 40.2514 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1743 | 852.0086 | 0 | 0.088511 | 6.6276 | 0 | 0 | 47.0542 | 40.2514 | on_peak | 852.0086 |  |  | 4.51 | 0 | 95.49 | 266.7719 | 0
3403 | 888.08 | 61.7687 | 27.9 | 9.9021 | 9.9021 | 0 | 0 | 0 | 0 | 23.2357 | 23.2357 | 0 | 49.3342 | 854.9422 | 0 | 0.088511 | 6.8956 | 0 | 0 | 47.0542 | 9.9021 | on_peak | 854.9422 |  |  | 1.11 | 2.62 | 96.27 | 68.2805 | 0
3404 | 841.99 | 0 | 27.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 49.3342 | 841.99 | 0 | 0.088511 | 7.1702 | 0 | 0 | 47.0542 | 0 | on_peak | 841.99 |  |  | 0 | 0 | 100 | 0 | 0
3405 | 862.8 | 0 | 26.9 | 0 | 0 | 0 | 0 | 0 | 0 | 13.181 | 13.181 | 0 | 35.2431 | 849.619 | 0 | 0.088511 | 7.58 | 0 | 0 | 47.0542 | 0 | on_peak | 849.619 |  |  | 0 | 1.53 | 98.47 | 0 | 0
3406 | 813.2 | 0 | 26.7 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 46.807 | 825.5624 | 0 | 0.05921 | 7.8608 | 0 | 0 | 47.0542 | 0 | off_peak | 813.2 | 0 | 100 | 0 | 0 | 100 | 0 | 0
3407 | 869.11 | 0 | 26.6 | 0 | 0 | 0 | 0 | 0 | 0 | 14.1678 | 14.1678 | 0 | 31.661 | 854.9422 | 0 | 0.05921 | 7.9315 | 0 | 0 | 47.0542 | 0 | off_peak | 854.9422 |  |  | 0 | 1.63 | 98.37 | 0 | 0
3408 | 877.62 | 0 | 26.6 | 0 | 0 | 0 | 0 | 0 | 0 | 22.6778 | 22.6778 | 0 | 7.4174 | 854.9422 | 0 | 0.05921 | 7.8755 | 0 | 0 | 47.0542 | 0 | off_peak | 854.9422 |  |  | 0 | 2.58 | 97.42 | 0 | 0
3409 | 788.49 | 0 | 26.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 788.49 | 0 | 0.05921 | 7.6794 | 0 | 0 | 47.0542 | 0 | off_peak | 788.49 |  |  | 0 | 0 | 100 | 0 | 0
3410 | 716.84 | 0 | 26.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 716.84 | 0 | 0.05921 | 7.4221 | 0 | 0 | 47.0542 | 0 | off_peak | 716.84 |  |  | 0 | 0 | 100 | 0 | 0
3411 | 648.1 | 0 | 26.6 | 0 | 0 | 0 | 0 | 8.7006 | 8.7006 | 0 | 0 | 0 | 15.5561 | 656.8006 | 0 | 0.05921 | 6.9525 | 0 | 0 | 47.0542 | 0 | off_peak | 648.1 | 0 | 100 | 0 | 0 | 100 | 0 | 0
3412 | 638.07 | 0 | 26.6 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 27.12 | 650.4324 | 0 | 0.05921 | 6.125 | 0 | 0 | 47.0542 | 0 | off_peak | 638.07 | 0 | 100 | 0 | 0 | 100 | 0 | 0
3413 | 624.7 | 0 | 26.6 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 38.684 | 637.0624 | 0 | 0.05921 | 5.1729 | 0 | 0 | 47.0542 | 0 | off_peak | 624.7 | 0 | 100 | 0 | 0 | 100 | 0 | 0
3414 | 708.63 | 0 | 26.6 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 50.2479 | 720.9924 | 0 | 0.05921 | 4.5369 | 0 | 0 | 47.0542 | 0 | off_peak | 708.63 | 0 | 100 | 0 | 0 | 100 | 0 | 0
3415 | 753.25 | 137.846 | 26.8 | 22.1863 | 9.824 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 0 | 61.8119 | 743.426 | 0 | 0.05921 | 4.136 | 0 | 0 | 58.6181 | 9.824 | off_peak | 743.426 | 100 | 0 | 1.3 | 0 | 98.7 | 40.6323 | 0
3416 | 872.57 | 346.532 | 27.2 | 55.6936 | 55.6936 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 73.3758 | 829.2388 | 0 | 0.05921 | 3.8018 | 0 | 0 | 58.6181 | 55.6936 | off_peak | 816.8764 | 0 | 100 | 6.38 | 0 | 93.62 | 211.7365 | 0
3417 | 819.51 | 557.064 | 27.5 | 89.4322 | 89.4322 | 0 | 0 | 0.79843 | 0.79843 | 0 | 0 | 0 | 74.1227 | 730.8763 | 0 | 0.05921 | 3.5966 | 0 | 0 | 58.6181 | 89.4322 | off_peak | 730.0778 | 0 | 100 | 10.91 | 0 | 89.09 | 321.6545 | 0
3418 | 863.6 | 613.916 | 28.1 | 98.3445 | 98.3445 | 0 | 0 | 0.051567 | 0.051567 | 0 | 0 | 0 | 74.1709 | 765.3071 | 0 | 0.05921 | 3.5182 | 0 | 0 | 58.6181 | 98.3445 | off_peak | 765.2555 | 0 | 100 | 11.39 | 0 | 88.61 | 345.9992 | 0
3419 | 844.43 | 747.188 | 28.6 | 119.4757 | 119.4724 | 0 | 0.0033305 | 0.0033305 | 0 | 0 | 0 | 0 | 74.174 | 724.9576 | 0 | 0.05921 | 3.6814 | 0 | 0 | 58.6213 | 119.4724 | off_peak | 724.9576 | 100 | 0 | 14.15 | 0 | 85.85 | 439.8299 | 0
3420 | 921.2 | 950.584 | 29 | 151.7771 | 151.7771 | 0 | 0 | 0.0002151 | 0.0002151 | 0 | 0 | 0 | 74.1742 | 769.4231 | 0 | 0.05921 | 4.0731 | 0 | 0 | 58.6213 | 151.7771 | off_peak | 769.4229 | 0 | 100 | 16.48 | 0 | 83.52 | 618.2062 | 0
3421 | 863.1 | 970.458 | 29.3 | 154.7805 | 154.7805 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1742 | 708.3195 | 0 | 0.088511 | 4.3539 | 0 | 0 | 58.6213 | 154.7805 | on_peak | 708.3195 |  |  | 17.93 | 0 | 82.07 | 673.893 | 0
3422 | 911.5 | 923.131 | 29.5 | 147.1246 | 147.1246 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1742 | 764.3754 | 0 | 0.088511 | 4.616 | 0 | 0 | 58.6213 | 147.1246 | on_peak | 764.3754 |  |  | 16.14 | 0 | 83.86 | 679.1326 | 0
3423 | 953.41 | 819.127 | 29.7 | 130.4533 | 130.4533 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1742 | 822.9567 | 0 | 0.088511 | 4.9309 | 0 | 0 | 58.6213 | 130.4533 | on_peak | 822.9567 |  |  | 13.68 | 0 | 86.32 | 643.2479 | 0
3424 | 932.26 | 662.762 | 29.8 | 105.5121 | 105.5121 | 0 | 0 | 0 | 0 | 7.4719 | 7.4719 | 0 | 66.1865 | 819.276 | 0 | 0.088511 | 5.3028 | 6.4996 | 0 | 51.6729 | 112.0117 | on_peak | 819.276 |  |  | 11.32 | 0.8 | 87.88 | 593.9753 | 0
3425 | 921.82 | 468.168 | 29.6 | 74.5873 | 74.5873 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 66.1865 | 847.2327 | 0 | 0.088511 | 5.7021 | 0 | 0 | 51.6729 | 74.5873 | on_peak | 847.2327 |  |  | 8.09 | 0 | 91.91 | 425.3008 | 0
3426 | 890.8 | 257.755 | 29 | 41.155 | 41.155 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 66.1865 | 849.645 | 0 | 0.088511 | 6.0557 | 0 | 0 | 51.6729 | 41.155 | on_peak | 849.645 |  |  | 4.62 | 0 | 95.38 | 249.2235 | 0
3427 | 850.67 | 64.905 | 28.6 | 10.3783 | 10.3783 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 66.1865 | 840.2917 | 0 | 0.088511 | 6.2829 | 0 | 0 | 51.6729 | 10.3783 | on_peak | 840.2917 |  |  | 1.22 | 0 | 98.78 | 65.2064 | 0
3428 | 890.81 | 0 | 27.6 | 0 | 0 | 0 | 0 | 0 | 0 | 35.8678 | 35.8678 | 0 | 27.8422 | 854.9422 | 0 | 0.088511 | 6.4869 | 35.8678 | 0 | 13.3286 | 35.8678 | on_peak | 854.9422 |  |  | 0 | 4.03 | 95.97 | 232.6704 | 0
3429 | 854.51 | 0 | 27.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27.8422 | 854.51 | 0 | 0.088511 | 6.5726 | 0 | 0 | 13.3286 | 0 | on_peak | 854.51 |  |  | 0 | 0 | 100 | 0 | 0
3430 | 867.41 | 0 | 26.8 | 0 | 0 | 0 | 0 | 0 | 0 | 12.4678 | 12.4678 | 0 | 14.5135 | 854.9422 | 0 | 0.05921 | 6.8537 | 12.4678 | 0 | 0 | 12.4678 | off_peak | 854.9422 |  |  | 0 | 1.44 | 98.56 | 85.4509 | 0
3431 | 861.58 | 0 | 26.5 | 0 | 0 | 0 | 0 | 0 | 0 | 6.6378 | 6.6378 | 0 | 7.4174 | 854.9422 | 0 | 0.05921 | 7.1511 | 0 | 0 | 0 | 0 | off_peak | 854.9422 |  |  | 0 | 0.77 | 99.23 | 0 | 0
3432 | 824.34 | 0 | 26.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 824.34 | 0 | 0.05921 | 7.0298 | 0 | 0 | 0 | 0 | off_peak | 824.34 |  |  | 0 | 0 | 100 | 0 | 0
3433 | 810.41 | 0 | 26.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 810.41 | 0 | 0.05921 | 6.7951 | 0 | 0 | 0 | 0 | off_peak | 810.41 |  |  | 0 | 0 | 100 | 0 | 0
3434 | 756.85 | 0 | 26.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 756.85 | 0 | 0.05921 | 6.6942 | 0 | 0 | 0 | 0 | off_peak | 756.85 |  |  | 0 | 0 | 100 | 0 | 0
3435 | 701.69 | 0 | 26.1 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 18.9814 | 714.0524 | 0 | 0.05921 | 6.2757 | 0 | 0 | 0 | 0 | off_peak | 701.69 | 0 | 100 | 0 | 0 | 100 | 0 | 0
3436 | 660.69 | 0 | 26.2 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 30.5453 | 673.0524 | 0 | 0.05921 | 5.5422 | 0 | 0 | 0 | 0 | off_peak | 660.69 | 0 | 100 | 0 | 0 | 100 | 0 | 0
3437 | 685.03 | 0 | 26.2 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 42.1093 | 697.3924 | 0 | 0.05921 | 4.839 | 0 | 0 | 0 | 0 | off_peak | 685.03 | 0 | 100 | 0 | 0 | 100 | 0 | 0
3438 | 739.38 | 0 | 26.4 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 53.6732 | 751.7424 | 0 | 0.05921 | 4.1093 | 0 | 0 | 0 | 0 | off_peak | 739.38 | 0 | 100 | 0 | 0 | 100 | 0 | 0
3439 | 794.19 | 129.657 | 26.8 | 20.8683 | 20.8683 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 65.2371 | 785.684 | 0 | 0.05921 | 3.7473 | 0 | 0 | 0 | 20.8683 | off_peak | 773.3217 | 0 | 100 | 2.63 | 0 | 97.37 | 78.1988 | 0
3440 | 803.83 | 333.711 | 27.1 | 53.6525 | 53.6525 | 0 | 0 | 8.9371 | 8.9371 | 0 | 0 | 0 | 73.597 | 759.1146 | 0 | 0.05921 | 3.4203 | 0 | 0 | 0 | 53.6525 | off_peak | 750.1775 | 0 | 100 | 6.67 | 0 | 93.33 | 183.5068 | 0
3441 | 912.91 | 541.942 | 27.5 | 87.0045 | 86.4272 | 0 | 0.57721 | 0.57721 | 0 | 0 | 0 | 0 | 74.137 | 826.4828 | 0 | 0.05921 | 3.2585 | 0 | 0 | 0.53993 | 86.4272 | off_peak | 826.4828 | 100 | 0 | 9.47 | 0 | 90.53 | 281.6258 | 0
3442 | 871.4 | 726.007 | 27.9 | 116.3853 | 116.348 | 0 | 0.037279 | 0.037279 | 0 | 0 | 0 | 0 | 74.1718 | 755.052 | 0 | 0.05921 | 3.2357 | 0 | 0 | 0.5748 | 116.348 | off_peak | 755.052 | 100 | 0 | 13.35 | 0 | 86.65 | 376.4642 | 0
3443 | 858.65 | 865.2 | 28.3 | 138.4973 | 138.4949 | 0 | 0.0024077 | 0.0024077 | 0 | 0 | 0 | 0 | 74.1741 | 720.1551 | 0 | 0.05921 | 3.0643 | 0 | 0 | 0.57705 | 138.4949 | off_peak | 720.1551 | 100 | 0 | 16.13 | 0 | 83.87 | 424.3941 | 0
3444 | 936.07 | 948.201 | 28.6 | 151.6178 | 151.6178 | 0 | 0 | 0.0001555 | 0.0001555 | 0 | 0 | 0 | 74.1742 | 784.4524 | 0 | 0.05921 | 3.8115 | 0 | 0 | 0.57705 | 151.6178 | off_peak | 784.4522 | 0 | 100 | 16.2 | 0 | 83.8 | 577.885 | 0
3445 | 860.51 | 968.815 | 28.8 | 154.801 | 154.801 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1742 | 705.709 | 0 | 0.088511 | 4.1311 | 0 | 0 | 0.57705 | 154.801 | on_peak | 705.709 |  |  | 17.99 | 0 | 82.01 | 639.4914 | 0
3446 | 902.63 | 926.602 | 28.8 | 148.056 | 148.056 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1742 | 754.574 | 0 | 0.088511 | 4.4398 | 0 | 0 | 0.57705 | 148.056 | on_peak | 754.574 |  |  | 16.4 | 0 | 83.6 | 657.34 | 0
3447 | 942.38 | 820.202 | 28.6 | 131.1507 | 131.1507 | 0 | 0 | 0 | 0 | 33.8575 | 33.8575 | 0 | 37.9791 | 777.3718 | 0 | 0.088511 | 4.742 | 0.53978 | 0 | 0 | 131.6905 | on_peak | 777.3718 |  |  | 13.92 | 3.59 | 82.49 | 624.4802 | 0
3448 | 916.42 | 662.612 | 28.3 | 106.0679 | 106.0679 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 37.9791 | 810.3521 | 0 | 0.088511 | 5.1431 | 0 | 0 | 0 | 106.0679 | on_peak | 810.3521 |  |  | 11.57 | 0 | 88.43 | 545.5184 | 0
3449 | 890.19 | 467.332 | 28 | 74.8901 | 74.8901 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 37.9791 | 815.2999 | 0 | 0.088511 | 5.6107 | 0 | 0 | 0 | 74.8901 | on_peak | 815.2999 |  |  | 8.41 | 0 | 91.59 | 420.1855 | 0
3450 | 862.63 | 255.682 | 27.5 | 41.0477 | 41.0477 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 37.9791 | 821.5823 | 0 | 0.088511 | 5.9015 | 0 | 0 | 0 | 41.0477 | on_peak | 821.5823 |  |  | 4.76 | 0 | 95.24 | 242.2414 | 0
3451 | 852.9 | 64.1992 | 27.3 | 10.3142 | 10.3142 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 37.9791 | 842.5858 | 0 | 0.088511 | 6.1622 | 0 | 0 | 0 | 10.3142 | on_peak | 842.5858 |  |  | 1.21 | 0 | 98.79 | 63.5584 | 0
3452 | 883.53 | 0 | 26.6 | 0 | 0 | 0 | 0 | 0 | 0 | 28.5878 | 28.5878 | 0 | 7.4174 | 854.9422 | 0 | 0.088511 | 6.3552 | 0 | 0 | 0 | 0 | on_peak | 854.9422 |  |  | 0 | 3.24 | 96.76 | 0 | 0
3453 | 832.13 | 0 | 26.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 832.13 | 0 | 0.088511 | 6.2093 | 0 | 0 | 0 | 0 | on_peak | 832.13 |  |  | 0 | 0 | 100 | 0 | 0
3454 | 831.92 | 0 | 26.3 | 0 | 0 | 0 | 0 | 8.7006 | 8.7006 | 0 | 0 | 0 | 15.5561 | 840.6206 | 0 | 0.05921 | 6.1437 | 0 | 0 | 0 | 0 | off_peak | 831.92 | 0 | 100 | 0 | 0 | 100 | 0 | 0
3455 | 826.21 | 0 | 26.2 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 27.12 | 838.5724 | 0 | 0.05921 | 6.131 | 0 | 0 | 0 | 0 | off_peak | 826.21 | 0 | 100 | 0 | 0 | 100 | 0 | 0
3456 | 834.01 | 0 | 26.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27.12 | 834.01 | 0 | 0.05921 | 5.9685 | 0 | 0 | 0 | 0 | off_peak | 834.01 |  |  | 0 | 0 | 100 | 0 | 0
3457 | 794.47 | 0 | 26 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27.12 | 794.47 | 0 | 0.05921 | 5.7383 | 0 | 0 | 0 | 0 | off_peak | 794.47 |  |  | 0 | 0 | 100 | 0 | 0
3458 | 770.63 | 0 | 26 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27.12 | 770.63 | 0 | 0.05921 | 5.6328 | 0 | 0 | 0 | 0 | off_peak | 770.63 |  |  | 0 | 0 | 100 | 0 | 0
3459 | 685.52 | 0 | 25.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27.12 | 685.52 | 0 | 0.05921 | 5.3525 | 0 | 0 | 0 | 0 | off_peak | 685.52 |  |  | 0 | 0 | 100 | 0 | 0
3460 | 688.13 | 0 | 25.9 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 38.684 | 700.4924 | 0 | 0.05921 | 4.7751 | 0 | 0 | 0 | 0 | off_peak | 688.13 | 0 | 100 | 0 | 0 | 100 | 0 | 0
3461 | 660.47 | 0 | 26 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 50.2479 | 672.8324 | 0 | 0.05921 | 4.1437 | 0 | 0 | 0 | 0 | off_peak | 660.47 | 0 | 100 | 0 | 0 | 100 | 0 | 0
3462 | 765.51 | 0 | 26.2 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 61.8119 | 777.8724 | 0 | 0.05921 | 3.5905 | 0 | 0 | 0 | 0 | off_peak | 765.51 | 0 | 100 | 0 | 0 | 100 | 0 | 0
3463 | 805.67 | 135.309 | 26.7 | 21.7859 | 21.7859 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 61.8119 | 783.8841 | 0 | 0.05921 | 3.428 | 0 | 0 | 0 | 21.7859 | off_peak | 783.8841 |  |  | 2.7 | 0 | 97.3 | 74.6821 | 0
3464 | 837.21 | 341.141 | 27 | 54.8669 | 54.8669 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 73.3758 | 794.7054 | 0 | 0.05921 | 3.1421 | 0 | 0 | 0 | 54.8669 | off_peak | 782.3431 | 0 | 100 | 6.55 | 0 | 93.45 | 172.3998 | 0
3465 | 865.79 | 549.03 | 27.1 | 88.2705 | 88.2705 | 0 | 0 | 0.79843 | 0.79843 | 0 | 0 | 0 | 74.1227 | 778.318 | 0 | 0.05921 | 2.9964 | 0 | 0 | 0 | 88.2705 | off_peak | 777.5195 | 0 | 100 | 10.2 | 0 | 89.8 | 264.4897 | 0
3466 | 872.47 | 729.667 | 26.9 | 117.3975 | 117.3975 | 0 | 0 | 0.051567 | 0.051567 | 0 | 0 | 0 | 74.1709 | 755.124 | 0 | 0.05921 | 2.9951 | 0 | 0 | 0 | 117.3975 | off_peak | 755.0725 | 0 | 100 | 13.46 | 0 | 86.54 | 351.613 | 0
3467 | 838.44 | 865.815 | 26.6 | 139.4541 | 139.4541 | 0 | 0 | 0.0033305 | 0.0033305 | 0 | 0 | 0 | 74.174 | 698.9892 | 0 | 0.05921 | 2.9154 | 0 | 0 | 0 | 139.4541 | off_peak | 698.9859 | 0 | 100 | 16.63 | 0 | 83.37 | 406.5592 | 0
3468 | 844.88 | 948.903 | 26.2 | 153.0582 | 153.0582 | 0 | 0 | 0.0002151 | 0.0002151 | 0 | 0 | 0 | 74.1742 | 691.822 | 0 | 0.05921 | 3.6139 | 0 | 0 | 0 | 153.0582 | off_peak | 691.8218 | 0 | 100 | 18.12 | 0 | 81.88 | 553.1369 | 0
3469 | 844.13 | 967.125 | 25.9 | 156.1666 | 156.1666 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1742 | 687.9634 | 0 | 0.088511 | 3.9087 | 0 | 0 | 0 | 156.1666 | on_peak | 687.9634 |  |  | 18.5 | 0 | 81.5 | 610.4016 | 0
3470 | 902.75 | 920.889 | 25.5 | 148.9155 | 148.9155 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1742 | 753.8345 | 0 | 0.088511 | 4.0395 | 0 | 0 | 0 | 148.9155 | on_peak | 753.8345 |  |  | 16.5 | 0 | 83.5 | 601.5396 | 0
3471 | 916.99 | 818.667 | 25.3 | 132.4808 | 132.4808 | 0 | 0 | 0 | 0 | 62.4453 | 62.4453 | 0 | 7.4174 | 722.0639 | 0 | 0.088511 | 4.2401 | 0 | 0 | 0 | 132.4808 | on_peak | 722.0639 |  |  | 14.45 | 6.81 | 78.74 | 561.732 | 0
3472 | 877.14 | 664.282 | 25.2 | 107.5362 | 107.5362 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 769.6038 | 0 | 0.088511 | 4.6025 | 0 | 0 | 0 | 107.5362 | on_peak | 769.6038 |  |  | 12.26 | 0 | 87.74 | 494.9393 | 0
3473 | 859.45 | 472.499 | 25.2 | 76.4897 | 76.4897 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 782.9603 | 0 | 0.088511 | 4.9711 | 0 | 0 | 0 | 76.4897 | on_peak | 782.9603 |  |  | 8.9 | 0 | 91.1 | 380.2396 | 0
3474 | 817.32 | 254.529 | 25.3 | 41.1892 | 41.1892 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 776.1308 | 0 | 0.088511 | 5.3698 | 0 | 0 | 0 | 41.1892 | on_peak | 776.1308 |  |  | 5.04 | 0 | 94.96 | 221.1794 | 0
3475 | 825.46 | 61.672 | 25.3 | 9.9801 | 9.9801 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 815.4799 | 0 | 0.088511 | 5.4363 | 0 | 0 | 0 | 9.9801 | on_peak | 815.4799 |  |  | 1.21 | 0 | 98.79 | 54.2543 | 0
3476 | 834.84 | 0 | 25.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 834.84 | 0 | 0.088511 | 5.4518 | 0 | 0 | 0 | 0 | on_peak | 834.84 |  |  | 0 | 0 | 100 | 0 | 0
3477 | 819.6 | 0 | 25.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 819.6 | 0 | 0.088511 | 5.618 | 0 | 0 | 0 | 0 | on_peak | 819.6 |  |  | 0 | 0 | 100 | 0 | 0
3478 | 784.14 | 0 | 25.8 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 18.9814 | 796.5024 | 0 | 0.05921 | 5.776 | 0 | 0 | 0 | 0 | off_peak | 784.14 | 0 | 100 | 0 | 0 | 100 | 0 | 0
3479 | 842.7 | 0 | 25.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18.9814 | 842.7 | 0 | 0.05921 | 5.9829 | 0 | 0 | 0 | 0 | off_peak | 842.7 |  |  | 0 | 0 | 100 | 0 | 0
3480 | 818.29 | 0 | 25.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18.9814 | 818.29 | 0 | 0.05921 | 6.0055 | 0 | 0 | 0 | 0 | off_peak | 818.29 |  |  | 0 | 0 | 100 | 0 | 0
3481 | 796.12 | 0 | 25.7 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 30.5453 | 808.4824 | 0 | 0.05921 | 6.0313 | 0 | 0 | 0 | 0 | off_peak | 796.12 | 0 | 100 | 0 | 0 | 100 | 0 | 0
3482 | 724.01 | 0 | 25.7 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 42.1093 | 736.3724 | 0 | 0.05921 | 5.9783 | 0 | 0 | 0 | 0 | off_peak | 724.01 | 0 | 100 | 0 | 0 | 100 | 0 | 0
3483 | 682.21 | 0 | 25.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 42.1093 | 682.21 | 0 | 0.05921 | 5.6661 | 0 | 0 | 0 | 0 | off_peak | 682.21 |  |  | 0 | 0 | 100 | 0 | 0
3484 | 654.58 | 0 | 25.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 42.1093 | 654.58 | 0 | 0.05921 | 5.1715 | 0 | 0 | 0 | 0 | off_peak | 654.58 |  |  | 0 | 0 | 100 | 0 | 0
3485 | 626.64 | 0 | 25.9 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 53.6732 | 639.0024 | 0 | 0.05921 | 4.4092 | 0 | 0 | 0 | 0 | off_peak | 626.64 | 0 | 100 | 0 | 0 | 100 | 0 | 0
3486 | 703.94 | 0 | 26.1 | 0 | 0 | 0 | 0 | 8.7006 | 8.7006 | 0 | 0 | 0 | 61.8119 | 712.6406 | 0 | 0.05921 | 3.8671 | 0 | 0 | 0 | 0 | off_peak | 703.94 | 0 | 100 | 0 | 0 | 100 | 0 | 0
3487 | 744.83 | 133.847 | 26.5 | 21.5661 | 21.5661 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 73.3758 | 735.6263 | 0 | 0.05921 | 3.4381 | 0 | 0 | 0 | 21.5661 | off_peak | 723.2639 | 0 | 100 | 2.9 | 0 | 97.1 | 74.1472 | 0
3488 | 854.82 | 340.997 | 26.8 | 54.8835 | 54.8835 | 0 | 0 | 0.79843 | 0.79843 | 0 | 0 | 0 | 74.1227 | 800.7349 | 0 | 0.05921 | 3.1585 | 0 | 0 | 0 | 54.8835 | off_peak | 799.9365 | 0 | 100 | 6.42 | 0 | 93.58 | 173.3516 | 0
3489 | 898.57 | 548.639 | 27.1 | 88.2076 | 88.2076 | 0 | 0 | 0.051567 | 0.051567 | 0 | 0 | 0 | 74.1709 | 810.414 | 0 | 0.05921 | 3.0061 | 0 | 0 | 0 | 88.2076 | off_peak | 810.3624 | 0 | 100 | 9.82 | 0 | 90.18 | 265.1586 | 0
3490 | 839.49 | 730.59 | 27.3 | 117.3756 | 117.3756 | 0 | 0 | 0.0033305 | 0.0033305 | 0 | 0 | 0 | 74.174 | 722.1177 | 0 | 0.05921 | 2.9923 | 0 | 0 | 0 | 117.3756 | off_peak | 722.1144 | 0 | 100 | 13.98 | 0 | 86.02 | 351.2197 | 0
3491 | 838.55 | 868.761 | 27.4 | 139.5233 | 139.5233 | 0 | 0 | 0.0002151 | 0.0002151 | 0 | 0 | 0 | 74.1742 | 699.0269 | 0 | 0.05921 | 3.2064 | 0 | 0 | 0 | 139.5233 | off_peak | 699.0267 | 0 | 100 | 16.64 | 0 | 83.36 | 447.3612 | 0
3492 | 890.83 | 953.661 | 27.5 | 153.1026 | 153.1026 | 0 | 0 | 1.3893e-05 | 1.3893e-05 | 0 | 0 | 0 | 74.1743 | 737.7274 | 0 | 0.05921 | 3.6104 | 0 | 0 | 0 | 153.1026 | off_peak | 737.7274 | 0 | 100 | 17.19 | 0 | 82.81 | 552.7675 | 0
3493 | 858.52 | 974.875 | 27.6 | 156.4515 | 156.4515 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1743 | 702.0685 | 0 | 0.088511 | 3.8295 | 0 | 0 | 0 | 156.4515 | on_peak | 702.0685 |  |  | 18.22 | 0 | 81.78 | 599.1303 | 0
3494 | 848.29 | 932.239 | 27.5 | 149.6635 | 149.6635 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1743 | 698.6265 | 0 | 0.088511 | 4.034 | 0 | 0 | 0 | 149.6635 | on_peak | 698.6265 |  |  | 17.64 | 0 | 82.36 | 603.7362 | 0
3495 | 864.62 | 828.76 | 27.4 | 133.0991 | 133.0991 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1743 | 731.5209 | 0 | 0.088511 | 4.2522 | 0 | 0 | 0 | 133.0991 | on_peak | 731.5209 |  |  | 15.39 | 0 | 84.61 | 565.9615 | 0
3496 | 848.56 | 673.458 | 27.2 | 108.2361 | 108.2361 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1743 | 740.3239 | 0 | 0.088511 | 4.5757 | 0 | 0 | 0 | 108.2361 | on_peak | 740.3239 |  |  | 12.76 | 0 | 87.24 | 495.2614 | 0
3497 | 868.59 | 479.085 | 26.9 | 77.0809 | 77.0809 | 0 | 0 | 0 | 0 | 62.4453 | 62.4453 | 0 | 7.4174 | 729.0638 | 0 | 0.088511 | 4.9409 | 0 | 0 | 0 | 77.0809 | on_peak | 729.0638 |  |  | 8.87 | 7.19 | 83.94 | 380.8511 | 0
3498 | 771.2 | 265.766 | 26.5 | 42.8216 | 42.8216 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 728.3784 | 0 | 0.088511 | 5.3112 | 0 | 0 | 0 | 42.8216 | on_peak | 728.3784 |  |  | 5.55 | 0 | 94.45 | 227.4327 | 0
3499 | 780.15 | 71.3606 | 26.3 | 11.5063 | 11.5063 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 768.6437 | 0 | 0.088511 | 5.4478 | 0 | 0 | 0 | 11.5063 | on_peak | 768.6437 |  |  | 1.47 | 0 | 98.53 | 62.6842 | 0
3500 | 769.74 | 0 | 26 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 769.74 | 0 | 0.088511 | 5.5862 | 0 | 0 | 0 | 0 | on_peak | 769.74 |  |  | 0 | 0 | 100 | 0 | 0
3501 | 793.18 | 0 | 25.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 793.18 | 0 | 0.088511 | 5.8023 | 0 | 0 | 0 | 0 | on_peak | 793.18 |  |  | 0 | 0 | 100 | 0 | 0
3502 | 756.1 | 0 | 25.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 756.1 | 0 | 0.05921 | 5.8173 | 0 | 0 | 0 | 0 | off_peak | 756.1 |  |  | 0 | 0 | 100 | 0 | 0
3503 | 800.02 | 0 | 25.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 800.02 | 0 | 0.05921 | 5.7525 | 0 | 0 | 0 | 0 | off_peak | 800.02 |  |  | 0 | 0 | 100 | 0 | 0
3504 | 726.45 | 0 | 25.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 726.45 | 0 | 0.05921 | 5.7299 | 0 | 0 | 0 | 0 | off_peak | 726.45 |  |  | 0 | 0 | 100 | 0 | 0
3505 | 754.45 | 0 | 25.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 754.45 | 0 | 0.05921 | 5.61 | 0 | 0 | 0 | 0 | off_peak | 754.45 |  |  | 0 | 0 | 100 | 0 | 0
3506 | 660.09 | 0 | 25.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 660.09 | 0 | 0.05921 | 5.5184 | 0 | 0 | 0 | 0 | off_peak | 660.09 |  |  | 0 | 0 | 100 | 0 | 0
3507 | 621.26 | 0 | 25.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 621.26 | 0 | 0.05921 | 5.2776 | 0 | 0 | 0 | 0 | off_peak | 621.26 |  |  | 0 | 0 | 100 | 0 | 0
3508 | 580.7 | 0 | 25.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 580.7 | 0 | 0.05921 | 4.8366 | 0 | 0 | 0 | 0 | off_peak | 580.7 |  |  | 0 | 0 | 100 | 0 | 0
3509 | 610.11 | 0 | 25.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 610.11 | 0 | 0.05921 | 4.2847 | 0 | 0 | 0 | 0 | off_peak | 610.11 |  |  | 0 | 0 | 100 | 0 | 0
3510 | 705.83 | 0 | 25.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 705.83 | 0 | 0.05921 | 3.7197 | 0 | 0 | 0 | 0 | off_peak | 705.83 |  |  | 0 | 0 | 100 | 0 | 0
3511 | 703.92 | 101.959 | 26.2 | 16.446 | 16.446 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 687.474 | 0 | 0.05921 | 3.2975 | 0 | 0 | 0 | 16.446 | off_peak | 687.474 |  |  | 2.34 | 0 | 97.66 | 54.23 | 0
3512 | 764.14 | 338.671 | 26.5 | 54.5684 | 54.5684 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 18.9814 | 721.9339 | 0 | 0.05921 | 3.0263 | 0 | 0 | 0 | 54.5684 | off_peak | 709.5716 | 0 | 100 | 7.14 | 0 | 92.86 | 165.1429 | 0
3513 | 776.81 | 542.954 | 26.6 | 87.4519 | 87.4519 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18.9814 | 689.3581 | 0 | 0.05921 | 2.8734 | 0 | 0 | 0 | 87.4519 | off_peak | 689.3581 |  |  | 11.26 | 0 | 88.74 | 251.2829 | 0
3514 | 754.13 | 717.333 | 26.9 | 115.4131 | 115.4131 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18.9814 | 638.7169 | 0 | 0.05921 | 2.7852 | 0 | 0 | 0 | 115.4131 | off_peak | 638.7169 |  |  | 15.3 | 0 | 84.7 | 321.4525 | 0
3515 | 741.37 | 849.955 | 27.3 | 136.5526 | 136.5526 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18.9814 | 604.8174 | 0 | 0.05921 | 2.7395 | 0 | 0 | 0 | 136.5526 | off_peak | 604.8174 |  |  | 18.42 | 0 | 81.58 | 374.0806 | 0
3516 | 818.03 | 850.717 | 27.8 | 136.427 | 136.427 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18.9814 | 681.603 | 0 | 0.05921 | 2.8225 | 0 | 0 | 0 | 136.427 | off_peak | 681.603 |  |  | 16.68 | 0 | 83.32 | 385.0696 | 0
3517 | 737.56 | 849.707 | 28.3 | 136.0172 | 136.0172 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18.9814 | 601.5428 | 0 | 0.05921 | 2.9493 | 0 | 0 | 0 | 136.0172 | off_peak | 601.5428 |  |  | 18.44 | 0 | 81.56 | 401.1587 | 0
3518 | 764.47 | 744.309 | 28.6 | 119.0154 | 119.0154 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18.9814 | 645.4546 | 0 | 0.05921 | 3.2 | 0 | 0 | 0 | 119.0154 | off_peak | 645.4546 |  |  | 15.57 | 0 | 84.43 | 380.8475 | 0
3519 | 738.67 | 611.234 | 28.9 | 97.6297 | 97.6297 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18.9814 | 641.0403 | 0 | 0.05921 | 3.458 | 0 | 0 | 0 | 97.6297 | off_peak | 641.0403 |  |  | 13.22 | 0 | 86.78 | 337.6039 | 0
3520 | 751.34 | 660.172 | 28.9 | 105.4463 | 105.4463 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18.9814 | 645.8937 | 0 | 0.05921 | 3.6395 | 0 | 0 | 0 | 105.4463 | off_peak | 645.8937 |  |  | 14.03 | 0 | 85.97 | 383.7685 | 0
3521 | 746.61 | 470.426 | 28.8 | 75.1665 | 75.1665 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18.9814 | 671.4435 | 0 | 0.05921 | 3.8943 | 0 | 0 | 0 | 75.1665 | off_peak | 671.4435 |  |  | 10.07 | 0 | 89.93 | 292.7245 | 0
3522 | 666.68 | 261.737 | 28.5 | 41.8671 | 41.8671 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18.9814 | 624.8129 | 0 | 0.05921 | 4.278 | 0 | 0 | 0 | 41.8671 | off_peak | 624.8129 |  |  | 6.28 | 0 | 93.72 | 179.1077 | 0
3523 | 606.79 | 62.9168 | 28.4 | 10.0678 | 10.0678 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 30.5453 | 609.0846 | 0 | 0.05921 | 4.6191 | 0 | 0 | 0 | 10.0678 | off_peak | 596.7222 | 0 | 100 | 1.66 | 0 | 98.34 | 46.5037 | 0
3524 | 601.01 | 0 | 27.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30.5453 | 601.01 | 0 | 0.05921 | 4.9398 | 0 | 0 | 0 | 0 | off_peak | 601.01 |  |  | 0 | 0 | 100 | 0 | 0
3525 | 618.7 | 0 | 27.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30.5453 | 618.7 | 0 | 0.05921 | 5.2398 | 0 | 0 | 0 | 0 | off_peak | 618.7 |  |  | 0 | 0 | 100 | 0 | 0
3526 | 577.71 | 0 | 27 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30.5453 | 577.71 | 0 | 0.05921 | 5.685 | 0 | 0 | 0 | 0 | off_peak | 577.71 |  |  | 0 | 0 | 100 | 0 | 0
3527 | 598.15 | 0 | 26.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30.5453 | 598.15 | 0 | 0.05921 | 6.0608 | 0 | 0 | 0 | 0 | off_peak | 598.15 |  |  | 0 | 0 | 100 | 0 | 0
3528 | 597.49 | 0 | 26.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30.5453 | 597.49 | 0 | 0.05921 | 6.2563 | 0 | 0 | 0 | 0 | off_peak | 597.49 |  |  | 0 | 0 | 100 | 0 | 0
3529 | 589.85 | 0 | 26.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30.5453 | 589.85 | 0 | 0.05921 | 6.3699 | 0 | 0 | 0 | 0 | off_peak | 589.85 |  |  | 0 | 0 | 100 | 0 | 0
3530 | 603.8 | 0 | 26.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30.5453 | 603.8 | 0 | 0.05921 | 6.1583 | 0 | 0 | 0 | 0 | off_peak | 603.8 |  |  | 0 | 0 | 100 | 0 | 0
3531 | 607.58 | 0 | 25.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30.5453 | 607.58 | 0 | 0.05921 | 5.7943 | 0 | 0 | 0 | 0 | off_peak | 607.58 |  |  | 0 | 0 | 100 | 0 | 0
3532 | 582.93 | 0 | 25.7 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 42.1093 | 595.2924 | 0 | 0.05921 | 5.2526 | 0 | 0 | 0 | 0 | off_peak | 582.93 | 0 | 100 | 0 | 0 | 100 | 0 | 0
3533 | 609.03 | 0 | 25.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 42.1093 | 609.03 | 0 | 0.05921 | 4.7162 | 0 | 0 | 0 | 0 | off_peak | 609.03 |  |  | 0 | 0 | 100 | 0 | 0
3534 | 690.29 | 0 | 25.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 42.1093 | 690.29 | 0 | 0.05921 | 4.2062 | 0 | 0 | 0 | 0 | off_peak | 690.29 |  |  | 0 | 0 | 100 | 0 | 0
3535 | 753.99 | 138.139 | 25.9 | 22.306 | 22.306 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 42.1093 | 731.684 | 0 | 0.05921 | 3.7238 | 0 | 0 | 0 | 22.306 | off_peak | 731.684 |  |  | 2.96 | 0 | 97.04 | 83.063 | 0
3536 | 730.72 | 343.947 | 26.6 | 55.3985 | 55.3985 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 53.6732 | 687.6839 | 0 | 0.05921 | 3.3215 | 0 | 0 | 0 | 55.3985 | off_peak | 675.3215 | 0 | 100 | 7.58 | 0 | 92.42 | 184.0074 | 0
3537 | 798.56 | 550.113 | 27.6 | 88.2842 | 88.2842 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 53.6732 | 710.2758 | 0 | 0.05921 | 3.1614 | 0 | 0 | 0 | 88.2842 | off_peak | 710.2758 |  |  | 11.06 | 0 | 88.94 | 279.1 | 0
3538 | 777.42 | 720.168 | 28.5 | 115.1972 | 115.1972 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 53.6732 | 662.2228 | 0 | 0.05921 | 3.0294 | 0 | 0 | 0 | 115.1972 | off_peak | 662.2228 |  |  | 14.82 | 0 | 85.18 | 348.9817 | 0
3539 | 765.15 | 827.584 | 29.2 | 132.0415 | 132.0415 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 65.2371 | 645.4709 | 0 | 0.05921 | 2.9863 | 0 | 0 | 0 | 132.0415 | off_peak | 633.1085 | 0 | 100 | 17.26 | 0 | 82.74 | 394.3136 | 0
3540 | 769.75 | 904.609 | 29.7 | 144.0671 | 144.0671 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 65.2371 | 625.6829 | 0 | 0.05921 | 2.9861 | 0 | 0 | 0 | 144.0671 | off_peak | 625.6829 |  |  | 18.72 | 0 | 81.28 | 430.2044 | 0
3541 | 758.31 | 921.496 | 30 | 146.5953 | 146.5953 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 65.2371 | 611.7147 | 0 | 0.05921 | 3.1506 | 0 | 0 | 0 | 146.5953 | off_peak | 611.7147 |  |  | 19.33 | 0 | 80.67 | 461.8678 | 0
3542 | 759.32 | 925.225 | 30.1 | 147.1345 | 147.1345 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 65.2371 | 612.1855 | 0 | 0.05921 | 3.5258 | 0 | 0 | 0 | 147.1345 | off_peak | 612.1855 |  |  | 19.38 | 0 | 80.62 | 518.7601 | 0
3543 | 708.82 | 821.201 | 30.1 | 130.592 | 130.592 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 65.2371 | 578.228 | 0 | 0.05921 | 3.8517 | 0 | 0 | 0 | 130.592 | off_peak | 578.228 |  |  | 18.42 | 0 | 81.58 | 503.0001 | 0
3544 | 755.72 | 666.607 | 29.9 | 106.0854 | 106.0854 | 0 | 0 | 8.7324 | 8.7324 | 0 | 0 | 0 | 73.4056 | 658.367 | 0 | 0.05921 | 4.2187 | 0 | 0 | 0 | 106.0854 | off_peak | 649.6346 | 0 | 100 | 14.04 | 0 | 85.96 | 447.5431 | 0
3545 | 730.21 | 474.728 | 29.6 | 75.6324 | 75.6324 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 73.4056 | 654.5776 | 0 | 0.05921 | 4.6675 | 0 | 0 | 0 | 75.6324 | off_peak | 654.5776 |  |  | 10.36 | 0 | 89.64 | 353.0111 | 0
3546 | 704.49 | 265.14 | 29 | 42.3342 | 42.3342 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 73.4056 | 662.1558 | 0 | 0.05921 | 5.1781 | 0 | 0 | 0 | 42.3342 | off_peak | 662.1558 |  |  | 6.01 | 0 | 93.99 | 219.2109 | 0
3547 | 651.05 | 72.5796 | 28.7 | 11.6013 | 11.6013 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 73.4056 | 639.4487 | 0 | 0.05921 | 5.53 | 0 | 0 | 0 | 11.6013 | off_peak | 639.4487 |  |  | 1.78 | 0 | 98.22 | 64.1556 | 0
3548 | 614.49 | 0 | 27.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 73.4056 | 614.49 | 0 | 0.05921 | 5.8919 | 0 | 0 | 0 | 0 | off_peak | 614.49 |  |  | 0 | 0 | 100 | 0 | 0
3549 | 597.85 | 0 | 27.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 73.4056 | 597.85 | 0 | 0.05921 | 6.271 | 0 | 0 | 0 | 0 | off_peak | 597.85 |  |  | 0 | 0 | 100 | 0 | 0
3550 | 617.29 | 0 | 27.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 73.4056 | 617.29 | 0 | 0.05921 | 6.5476 | 0 | 0 | 0 | 0 | off_peak | 617.29 |  |  | 0 | 0 | 100 | 0 | 0
3551 | 596.92 | 0 | 27.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 73.4056 | 596.92 | 0 | 0.05921 | 6.8445 | 0 | 0 | 0 | 0 | off_peak | 596.92 |  |  | 0 | 0 | 100 | 0 | 0
3552 | 599.48 | 0 | 27.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 73.4056 | 599.48 | 0 | 0.05921 | 6.9166 | 0 | 0 | 0 | 0 | off_peak | 599.48 |  |  | 0 | 0 | 100 | 0 | 0
3553 | 586.87 | 0 | 26.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 73.4056 | 586.87 | 0 | 0.05921 | 6.9498 | 0 | 0 | 0 | 0 | off_peak | 586.87 |  |  | 0 | 0 | 100 | 0 | 0
3554 | 595.96 | 0 | 26.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 73.4056 | 595.96 | 0 | 0.05921 | 6.7833 | 0 | 0 | 0 | 0 | off_peak | 595.96 |  |  | 0 | 0 | 100 | 0 | 0
3555 | 579.89 | 0 | 26.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 73.4056 | 579.89 | 0 | 0.05921 | 6.3995 | 0 | 0 | 0 | 0 | off_peak | 579.89 |  |  | 0 | 0 | 100 | 0 | 0
3556 | 623.13 | 0 | 26.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 73.4056 | 623.13 | 0 | 0.05921 | 5.8089 | 0 | 0 | 0 | 0 | off_peak | 623.13 |  |  | 0 | 0 | 100 | 0 | 0
3557 | 591.54 | 0 | 26.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 73.4056 | 591.54 | 0 | 0.05921 | 5.1101 | 0 | 0 | 0 | 0 | off_peak | 591.54 |  |  | 0 | 0 | 100 | 0 | 0
3558 | 685.61 | 0 | 26.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 73.4056 | 685.61 | 0 | 0.05921 | 4.4805 | 0 | 0 | 0 | 0 | off_peak | 685.61 |  |  | 0 | 0 | 100 | 0 | 0
3559 | 733.2 | 141.738 | 26.8 | 22.8128 | 22.8128 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 73.4056 | 710.3872 | 0 | 0.05921 | 3.9823 | 0 | 0 | 0 | 22.8128 | off_peak | 710.3872 |  |  | 3.11 | 0 | 96.89 | 90.8465 | 0
3560 | 772.36 | 349.834 | 27.2 | 56.2243 | 56.2243 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 73.4056 | 716.1357 | 0 | 0.05921 | 3.5608 | 0 | 0 | 0 | 56.2243 | off_peak | 716.1357 |  |  | 7.28 | 0 | 92.72 | 200.2024 | 0
3561 | 807.06 | 556.32 | 27.9 | 89.1829 | 89.1829 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 73.4056 | 717.8771 | 0 | 0.05921 | 3.2833 | 0 | 0 | 0 | 89.1829 | off_peak | 717.8771 |  |  | 11.05 | 0 | 88.95 | 292.8153 | 0
3562 | 797.73 | 737.523 | 28.6 | 117.9303 | 117.9303 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 73.4056 | 679.7997 | 0 | 0.05921 | 3.1506 | 0 | 0 | 0 | 117.9303 | off_peak | 679.7997 |  |  | 14.78 | 0 | 85.22 | 371.5531 | 0
3563 | 773.62 | 875.283 | 29.2 | 139.6519 | 139.6519 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 73.4056 | 633.9681 | 0 | 0.05921 | 3.1377 | 0 | 0 | 0 | 139.6519 | off_peak | 633.9681 |  |  | 18.05 | 0 | 81.95 | 438.1817 | 0
3564 | 801.33 | 687.401 | 29.5 | 109.5549 | 109.5549 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 73.4056 | 691.7751 | 0 | 0.05921 | 3.188 | 0 | 0 | 0 | 109.5549 | off_peak | 691.7751 |  |  | 13.67 | 0 | 86.33 | 349.2582 | 0
3565 | 773.07 | 971.614 | 29.7 | 154.7382 | 154.7382 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 73.4056 | 618.3318 | 0 | 0.05921 | 3.2653 | 0 | 0 | 0 | 154.7382 | on_peak | 618.3318 |  |  | 20.02 | 0 | 79.98 | 505.2602 | 0
3566 | 791.84 | 923.185 | 29.8 | 146.9716 | 146.9716 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 73.4056 | 644.8684 | 0 | 0.05921 | 3.5606 | 0 | 0 | 0 | 146.9716 | on_peak | 644.8684 |  |  | 18.56 | 0 | 81.44 | 523.3065 | 0
3567 | 829.65 | 819.181 | 29.7 | 130.4619 | 130.4619 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 73.4056 | 699.1881 | 0 | 0.05921 | 4.0209 | 0 | 0 | 0 | 130.4619 | on_peak | 699.1881 |  |  | 15.72 | 0 | 84.28 | 524.5703 | 0
3568 | 808.16 | 662.921 | 29.5 | 105.6534 | 105.6534 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 73.4056 | 702.5066 | 0 | 0.05921 | 4.5024 | 0 | 0 | 0 | 105.6534 | on_peak | 702.5066 |  |  | 13.07 | 0 | 86.93 | 475.6979 | 0
3569 | 805.14 | 470.11 | 29.1 | 75.0337 | 75.0337 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 73.4056 | 730.1063 | 0 | 0.05921 | 4.9985 | 0 | 0 | 0 | 75.0337 | on_peak | 730.1063 |  |  | 9.32 | 0 | 90.68 | 375.0543 | 0
3570 | 778.15 | 260.945 | 28.5 | 41.7404 | 41.7404 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 73.4056 | 736.4096 | 0 | 0.05921 | 5.3999 | 0 | 0 | 0 | 41.7404 | on_peak | 736.4096 |  |  | 5.36 | 0 | 94.64 | 225.394 | 0
3571 | 784.37 | 69.9687 | 28.1 | 11.2084 | 11.2084 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 73.4056 | 773.1616 | 0 | 0.05921 | 5.9129 | 0 | 0 | 0 | 11.2084 | on_peak | 773.1616 |  |  | 1.43 | 0 | 98.57 | 66.2748 | 0
3572 | 733.26 | 0 | 27.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 73.4056 | 733.26 | 0 | 0.05921 | 6.1526 | 0 | 0 | 0 | 0 | on_peak | 733.26 |  |  | 0 | 0 | 100 | 0 | 0
3573 | 679.45 | 0 | 26.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 73.4056 | 679.45 | 0 | 0.05921 | 6.4859 | 0 | 0 | 0 | 0 | on_peak | 679.45 |  |  | 0 | 0 | 100 | 0 | 0
3574 | 597.01 | 0 | 26.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 73.4056 | 597.01 | 0 | 0.05921 | 6.7407 | 0 | 0 | 0 | 0 | off_peak | 597.01 |  |  | 0 | 0 | 100 | 0 | 0
3575 | 643.05 | 0 | 26 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 73.4056 | 643.05 | 0 | 0.05921 | 7.0471 | 0 | 0 | 0 | 0 | off_peak | 643.05 |  |  | 0 | 0 | 100 | 0 | 0
3576 | 623.04 | 0 | 25.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 73.4056 | 623.04 | 0 | 0.05921 | 7.074 | 0 | 0 | 0 | 0 | off_peak | 623.04 |  |  | 0 | 0 | 100 | 0 | 0
3577 | 571.95 | 0 | 25.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 73.4056 | 571.95 | 0 | 0.05921 | 7.165 | 0 | 0 | 0 | 0 | off_peak | 571.95 |  |  | 0 | 0 | 100 | 0 | 0
3578 | 541.23 | 0 | 25.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 73.4056 | 541.23 | 0 | 0.05921 | 6.9613 | 0 | 0 | 0 | 0 | off_peak | 541.23 |  |  | 0 | 0 | 100 | 0 | 0
3579 | 544.05 | 0 | 25.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 73.4056 | 544.05 | 0 | 0.05921 | 6.5482 | 0 | 0 | 0 | 0 | off_peak | 544.05 |  |  | 0 | 0 | 100 | 0 | 0
3580 | 562.73 | 0 | 25.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 73.4056 | 562.73 | 0 | 0.05921 | 5.8867 | 0 | 0 | 0 | 0 | off_peak | 562.73 |  |  | 0 | 0 | 100 | 0 | 0
3581 | 587.01 | 0 | 25.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 73.4056 | 587.01 | 0 | 0.05921 | 5.1819 | 0 | 0 | 0 | 0 | off_peak | 587.01 |  |  | 0 | 0 | 100 | 0 | 0
3582 | 687.86 | 4.75 | 25.3 | 0.76867 | 0 | 0 | 0.76867 | 0.76867 | 0 | 0 | 0 | 0 | 74.1246 | 687.86 | 0 | 0.05921 | 4.5045 | 0 | 0 | 0.71902 | 0 | off_peak | 687.86 | 100 | 0 | 0 | 0 | 100 | 0 | 0
3583 | 752.44 | 136.406 | 25.9 | 22.0262 | 22.0262 | 0 | 0 | 0.049645 | 0.049645 | 0 | 0 | 0 | 74.171 | 730.4635 | 0 | 0.05921 | 4.0015 | 0 | 0 | 0.71902 | 22.0262 | off_peak | 730.4138 | 0 | 100 | 2.93 | 0 | 97.07 | 88.1375 | 0
3584 | 821.02 | 338.637 | 26.5 | 54.563 | 54.563 | 0 | 0 | 0.0032064 | 0.0032064 | 0 | 0 | 0 | 74.174 | 766.4603 | 0 | 0.05921 | 3.6696 | 0 | 0 | 0.71902 | 54.563 | off_peak | 766.457 | 0 | 100 | 6.65 | 0 | 93.35 | 200.2229 | 0
3585 | 850.37 | 454.188 | 27.3 | 72.9692 | 72.9692 | 0 | 0 | 0.00020708 | 0.00020708 | 0 | 0 | 0 | 74.1742 | 777.401 | 0 | 0.05921 | 3.4606 | 0 | 0 | 0.71902 | 72.9692 | off_peak | 777.4008 | 0 | 100 | 8.58 | 0 | 91.42 | 252.5161 | 0
3586 | 883.26 | 638.909 | 27.9 | 102.4227 | 102.4227 | 0 | 0 | 1.3375e-05 | 1.3375e-05 | 0 | 0 | 0 | 74.1743 | 780.8373 | 0 | 0.05921 | 3.4011 | 0 | 0 | 0.71902 | 102.4227 | off_peak | 780.8373 | 0 | 100 | 11.6 | 0 | 88.4 | 348.3512 | 0
3587 | 871.78 | 528.168 | 28.5 | 84.4851 | 84.4851 | 0 | 8.6381e-07 | 8.6381e-07 | 0 | 0 | 0 | 0 | 74.1743 | 787.2949 | 0 | 0.05921 | 3.5626 | 0 | 0 | 0.71902 | 84.4851 | off_peak | 787.2949 | 100 | 0 | 9.69 | 0 | 90.31 | 300.9898 | 0
3588 | 944.99 | 857.002 | 29 | 136.8351 | 136.8351 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1743 | 808.1549 | 0 | 0.05921 | 3.9201 | 0 | 0 | 0.71902 | 136.8351 | off_peak | 808.1549 |  |  | 14.48 | 0 | 85.52 | 536.4085 | 0
3589 | 872.33 | 942.567 | 29.3 | 150.3321 | 150.3321 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1743 | 721.9979 | 0 | 0.088511 | 4.071 | 0 | 0 | 0.71902 | 150.3321 | on_peak | 721.9979 |  |  | 17.23 | 0 | 82.77 | 612.0048 | 0
3590 | 929.27 | 802.487 | 29.4 | 127.9436 | 127.9436 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1743 | 801.3264 | 0 | 0.088511 | 4.2211 | 0 | 0 | 0.71902 | 127.9436 | on_peak | 801.3264 |  |  | 13.77 | 0 | 86.23 | 540.0662 | 0
3591 | 923.71 | 793.047 | 29.4 | 126.4386 | 126.4386 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1743 | 797.2714 | 0 | 0.088511 | 4.4761 | 0 | 0 | 0.71902 | 126.4386 | on_peak | 797.2714 |  |  | 13.69 | 0 | 86.31 | 565.9541 | 0
3592 | 934.4 | 622.359 | 29.2 | 99.2977 | 99.2977 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1743 | 835.1023 | 0 | 0.088511 | 4.8112 | 0 | 0 | 0.71902 | 99.2977 | on_peak | 835.1023 |  |  | 10.63 | 0 | 89.37 | 477.7439 | 0
3593 | 905.25 | 392.65 | 28.8 | 62.7391 | 62.7391 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1743 | 842.5109 | 0 | 0.088511 | 5.3192 | 0 | 0 | 0.71902 | 62.7391 | on_peak | 842.5109 |  |  | 6.93 | 0 | 93.07 | 333.7237 | 0
3594 | 888.28 | 247.108 | 28.2 | 39.5703 | 39.5703 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1743 | 848.7097 | 0 | 0.088511 | 5.8098 | 0 | 0 | 0.71902 | 39.5703 | on_peak | 848.7097 |  |  | 4.45 | 0 | 95.55 | 229.8955 | 0
3595 | 854.13 | 36.6898 | 27.8 | 5.8838 | 5.8838 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1743 | 848.2462 | 0 | 0.088511 | 6.3183 | 0 | 0 | 0.71902 | 5.8838 | on_peak | 848.2462 |  |  | 0.69 | 0 | 99.31 | 37.176 | 0
3596 | 813.02 | 0 | 26.8 | 0 | 0 | 0 | 0 | 0 | 0 | 61.7727 | 61.7727 | 0 | 8.1364 | 751.2473 | 0 | 0.088511 | 6.6594 | 0 | 0 | 0.71902 | 0 | on_peak | 751.2473 |  |  | 0 | 7.6 | 92.4 | 0 | 0
3597 | 825.02 | 0 | 26.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0.67259 | 0.67259 | 0 | 7.4174 | 824.3474 | 0 | 0.088511 | 7.0662 | 0.67259 | 0 | 0 | 0.67259 | on_peak | 824.3474 |  |  | 0 | 0.08 | 99.92 | 4.7526 | 0
3598 | 795.93 | 0 | 26.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 795.93 | 0 | 0.05921 | 7.2387 | 0 | 0 | 0 | 0 | off_peak | 795.93 |  |  | 0 | 0 | 100 | 0 | 0
3599 | 826.98 | 0 | 25.9 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 18.9814 | 839.3424 | 0 | 0.05921 | 7.5352 | 0 | 0 | 0 | 0 | off_peak | 826.98 | 0 | 100 | 0 | 0 | 100 | 0 | 0
3600 | 813.89 | 0 | 25.8 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 30.5453 | 826.2524 | 0 | 0.05921 | 7.4436 | 0 | 0 | 0 | 0 | off_peak | 813.89 | 0 | 100 | 0 | 0 | 100 | 0 | 0
3601 | 781.26 | 0 | 25.7 | 0 | 0 | 0 | 0 | 8.7006 | 8.7006 | 0 | 0 | 0 | 38.684 | 789.9606 | 0 | 0.05921 | 7.3879 | 0 | 0 | 0 | 0 | off_peak | 781.26 | 0 | 100 | 0 | 0 | 100 | 0 | 0
3602 | 715.07 | 0 | 25.6 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 50.2479 | 727.4324 | 0 | 0.05921 | 7.0155 | 0 | 0 | 0 | 0 | off_peak | 715.07 | 0 | 100 | 0 | 0 | 100 | 0 | 0
3603 | 677.57 | 0 | 25.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50.2479 | 677.57 | 0 | 0.05921 | 6.3577 | 0 | 0 | 0 | 0 | off_peak | 677.57 |  |  | 0 | 0 | 100 | 0 | 0
3604 | 657.97 | 0 | 25.4 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 61.8119 | 670.3324 | 0 | 0.05921 | 5.7221 | 0 | 0 | 0 | 0 | off_peak | 657.97 | 0 | 100 | 0 | 0 | 100 | 0 | 0
3605 | 697.97 | 0 | 25.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 61.8119 | 697.97 | 0 | 0.05921 | 5.0225 | 0 | 0 | 0 | 0 | off_peak | 697.97 |  |  | 0 | 0 | 100 | 0 | 0
3606 | 764.41 | 4.75 | 25.7 | 0.76756 | 0 | 0 | 0.76756 | 12.3624 | 11.5948 | 0 | 0 | 0 | 73.3758 | 776.0048 | 0 | 0.05921 | 4.4482 | 0 | 0 | 0.71799 | 0 | off_peak | 764.41 | 6.21 | 93.79 | 0 | 0 | 100 | 0 | 0
3607 | 778.98 | 134.633 | 26.3 | 21.7085 | 21.7085 | 0 | 0 | 0.79843 | 0.79843 | 0 | 0 | 0 | 74.1227 | 758.07 | 0 | 0.05921 | 4.0687 | 0 | 0 | 0.71799 | 21.7085 | off_peak | 757.2715 | 0 | 100 | 2.79 | 0 | 97.21 | 88.3253 | 0
3608 | 825.82 | 333.93 | 26.9 | 53.7266 | 53.7266 | 0 | 0 | 0.051567 | 0.051567 | 0 | 0 | 0 | 74.1709 | 772.1449 | 0 | 0.05921 | 3.7806 | 0 | 0 | 0.71799 | 53.7266 | off_peak | 772.0934 | 0 | 100 | 6.51 | 0 | 93.49 | 203.1203 | 0
3609 | 870.9 | 468.729 | 27.5 | 75.2507 | 75.2507 | 0 | 0 | 0.0033305 | 0.0033305 | 0 | 0 | 0 | 74.174 | 795.6526 | 0 | 0.05921 | 3.5867 | 0 | 0 | 0.71799 | 75.2507 | off_peak | 795.6493 | 0 | 100 | 8.64 | 0 | 91.36 | 269.905 | 0
3610 | 828.15 | 544.225 | 28.2 | 87.1488 | 87.1488 | 0 | 0 | 0.0002151 | 0.0002151 | 0 | 0 | 0 | 74.1742 | 741.0014 | 0 | 0.05921 | 3.5604 | 0 | 0 | 0.71799 | 87.1488 | off_peak | 741.0012 | 0 | 100 | 10.52 | 0 | 89.48 | 310.2809 | 0
3611 | 838.56 | 841.647 | 28.7 | 134.5307 | 134.5307 | 0 | 0 | 1.3893e-05 | 1.3893e-05 | 0 | 0 | 0 | 74.1743 | 704.0293 | 0 | 0.05921 | 3.7316 | 0 | 0 | 0.71799 | 134.5307 | off_peak | 704.0293 | 0 | 100 | 16.04 | 0 | 83.96 | 502.0195 | 0
3612 | 886.94 | 925.34 | 29.1 | 147.6925 | 147.6925 | 0 | 0 | 8.9726e-07 | 8.9726e-07 | 0 | 0 | 0 | 74.1743 | 739.2475 | 0 | 0.05921 | 4.0617 | 0 | 0 | 0.71799 | 147.6925 | off_peak | 739.2475 | 0 | 100 | 16.65 | 0 | 83.35 | 599.8799 | 0
3613 | 868.76 | 919.99 | 29.4 | 146.6776 | 146.6776 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1743 | 722.0824 | 0 | 0.088511 | 4.2484 | 0 | 0 | 0.71799 | 146.6776 | on_peak | 722.0824 |  |  | 16.88 | 0 | 83.12 | 623.143 | 0
3614 | 959.07 | 553.726 | 29.6 | 88.2181 | 88.2181 | 0 | 0 | 0 | 0 | 15.9097 | 15.9097 | 0 | 57.1661 | 854.9422 | 0 | 0.088511 | 4.4749 | 0 | 0 | 0.71799 | 88.2181 | on_peak | 854.9422 |  |  | 9.2 | 1.66 | 89.14 | 394.771 | 0
3615 | 916.97 | 538.831 | 29.6 | 85.8451 | 85.8451 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 57.1661 | 831.1249 | 0 | 0.088511 | 4.6421 | 0 | 0 | 0.71799 | 85.8451 | on_peak | 831.1249 |  |  | 9.36 | 0 | 90.64 | 398.4997 | 0
3616 | 877.31 | 615.153 | 29.4 | 98.0763 | 98.0763 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 57.1661 | 779.2337 | 0 | 0.088511 | 4.9827 | 0 | 0 | 0.71799 | 98.0763 | on_peak | 779.2337 |  |  | 11.18 | 0 | 88.82 | 488.6874 | 0
3617 | 862.78 | 452.995 | 29 | 72.3284 | 72.3284 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 57.1661 | 790.4516 | 0 | 0.088511 | 5.3239 | 0 | 0 | 0.71799 | 72.3284 | on_peak | 790.4516 |  |  | 8.38 | 0 | 91.62 | 385.0684 | 0
3618 | 879.43 | 218.154 | 28.5 | 34.8957 | 34.8957 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 57.1661 | 844.5343 | 0 | 0.088511 | 5.8428 | 0 | 0 | 0.71799 | 34.8957 | on_peak | 844.5343 |  |  | 3.97 | 0 | 96.03 | 203.8879 | 0
3619 | 829.04 | 60.263 | 28.2 | 9.6501 | 9.6501 | 0 | 0 | 0 | 0 | 0.67162 | 0.67162 | 0 | 56.4481 | 818.7182 | 0 | 0.088511 | 6.312 | 0.67162 | 0 | 0 | 10.3218 | on_peak | 818.7182 |  |  | 1.16 | 0.08 | 98.75 | 65.1512 | 0
3620 | 830.43 | 0 | 27.2 | 0 | 0 | 0 | 0 | 0 | 0 | 45.864 | 45.864 | 0 | 7.4174 | 784.566 | 0 | 0.088511 | 6.4873 | 0 | 0 | 0 | 0 | on_peak | 784.566 |  |  | 0 | 5.52 | 94.48 | 0 | 0
3621 | 784.21 | 0 | 27.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 784.21 | 0 | 0.088511 | 6.6362 | 0 | 0 | 0 | 0 | on_peak | 784.21 |  |  | 0 | 0 | 100 | 0 | 0
3622 | 806.39 | 0 | 27.1 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 18.9814 | 818.7524 | 0 | 0.05921 | 6.7249 | 0 | 0 | 0 | 0 | off_peak | 806.39 | 0 | 100 | 0 | 0 | 100 | 0 | 0
3623 | 819.64 | 0 | 27 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 30.5453 | 832.0024 | 0 | 0.05921 | 6.6567 | 0 | 0 | 0 | 0 | off_peak | 819.64 | 0 | 100 | 0 | 0 | 100 | 0 | 0
3624 | 792.15 | 0 | 27 | 0 | 0 | 0 | 0 | 8.7006 | 8.7006 | 0 | 0 | 0 | 38.684 | 800.8506 | 0 | 0.05921 | 6.5924 | 0 | 0 | 0 | 0 | off_peak | 792.15 | 0 | 100 | 0 | 0 | 100 | 0 | 0
3625 | 765.11 | 0 | 26.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 38.684 | 765.11 | 0 | 0.05921 | 6.3338 | 0 | 0 | 0 | 0 | off_peak | 765.11 |  |  | 0 | 0 | 100 | 0 | 0
3626 | 736.6 | 0 | 26.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 38.684 | 736.6 | 0 | 0.05921 | 6.2483 | 0 | 0 | 0 | 0 | off_peak | 736.6 |  |  | 0 | 0 | 100 | 0 | 0
3627 | 664.73 | 0 | 26.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 38.684 | 664.73 | 0 | 0.05921 | 5.927 | 0 | 0 | 0 | 0 | off_peak | 664.73 |  |  | 0 | 0 | 100 | 0 | 0
3628 | 659.95 | 0 | 26.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 38.684 | 659.95 | 0 | 0.05921 | 5.3999 | 0 | 0 | 0 | 0 | off_peak | 659.95 |  |  | 0 | 0 | 100 | 0 | 0
3629 | 665.67 | 0 | 26.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 38.684 | 665.67 | 0 | 0.05921 | 4.7657 | 0 | 0 | 0 | 0 | off_peak | 665.67 |  |  | 0 | 0 | 100 | 0 | 0
3630 | 701.04 | 3.8 | 27 | 0.61117 | 0.61117 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 50.2479 | 712.7912 | 0 | 0.05921 | 4.2488 | 0 | 0 | 0 | 0.61117 | off_peak | 700.4288 | 0 | 100 | 0.09 | 0 | 99.91 | 2.5967 | 0
3631 | 795.67 | 117.29 | 27.6 | 18.8231 | 18.8231 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 61.8119 | 789.2092 | 0 | 0.05921 | 3.8224 | 0 | 0 | 0 | 18.8231 | off_peak | 776.8469 | 0 | 100 | 2.37 | 0 | 97.63 | 71.9491 | 0
3632 | 848.38 | 323.76 | 28.1 | 51.8638 | 51.8638 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 73.3758 | 808.8786 | 0 | 0.05921 | 3.5457 | 0 | 0 | 0 | 51.8638 | off_peak | 796.5162 | 0 | 100 | 6.11 | 0 | 93.89 | 183.8945 | 0
3633 | 899 | 106.619 | 28.6 | 17.0484 | 17.0484 | 0 | 0 | 0.79843 | 0.79843 | 0 | 0 | 0 | 74.1227 | 882.75 | 0 | 0.05921 | 3.4006 | 0 | 0 | 0 | 17.0484 | off_peak | 881.9516 | 0 | 100 | 1.9 | 0 | 98.1 | 57.9753 | 0
3634 | 889.85 | 501.059 | 29 | 80.0027 | 80.0027 | 0 | 0 | 0.051567 | 0.051567 | 0 | 0 | 0 | 74.1709 | 809.8989 | 0 | 0.05921 | 3.3751 | 0 | 0 | 0 | 80.0027 | off_peak | 809.8473 | 0 | 100 | 8.99 | 0 | 91.01 | 270.0177 | 0
3635 | 883.99 | 709.841 | 29.4 | 113.1727 | 113.1727 | 0 | 0 | 0.0033305 | 0.0033305 | 0 | 0 | 0 | 74.174 | 770.8206 | 0 | 0.05921 | 3.5782 | 0 | 0 | 0 | 113.1727 | off_peak | 770.8173 | 0 | 100 | 12.8 | 0 | 87.2 | 404.9559 | 0
3636 | 905.87 | 780.594 | 29.8 | 124.2711 | 124.2711 | 0 | 0 | 0.0002151 | 0.0002151 | 0 | 0 | 0 | 74.1742 | 781.5992 | 0 | 0.05921 | 3.9483 | 0 | 0 | 0 | 124.2711 | off_peak | 781.5989 | 0 | 100 | 13.72 | 0 | 86.28 | 490.6592 | 0
3637 | 900.65 | 835.072 | 29.9 | 132.8953 | 132.8953 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1742 | 767.7547 | 0 | 0.088511 | 4.3651 | 0 | 0 | 0 | 132.8953 | on_peak | 767.7547 |  |  | 14.76 | 0 | 85.24 | 580.1074 | 0
3638 | 880.37 | 891.955 | 30 | 141.8958 | 141.8958 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1742 | 738.4742 | 0 | 0.088511 | 4.6431 | 0 | 0 | 0 | 141.8958 | on_peak | 738.4742 |  |  | 16.12 | 0 | 83.88 | 658.83 | 0
3639 | 916.98 | 703.133 | 29.9 | 111.8982 | 111.8982 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1742 | 805.0818 | 0 | 0.088511 | 4.888 | 0 | 0 | 0 | 111.8982 | on_peak | 805.0818 |  |  | 12.2 | 0 | 87.8 | 546.9572 | 0
3640 | 866.67 | 592.298 | 29.7 | 94.3288 | 94.3288 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1742 | 772.3412 | 0 | 0.088511 | 5.241 | 0 | 0 | 0 | 94.3288 | on_peak | 772.3412 |  |  | 10.88 | 0 | 89.12 | 494.3813 | 0
3641 | 842.74 | 395.749 | 29.3 | 63.1189 | 63.1189 | 0 | 0 | 0 | 0 | 62.4453 | 62.4453 | 0 | 7.4174 | 717.1758 | 0 | 0.088511 | 5.5242 | 0 | 0 | 0 | 63.1189 | on_peak | 717.1758 |  |  | 7.49 | 7.41 | 85.1 | 348.68 | 0
3642 | 841.54 | 178.64 | 28.8 | 28.5438 | 28.5438 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 812.9962 | 0 | 0.088511 | 6.0304 | 0 | 0 | 0 | 28.5438 | on_peak | 812.9962 |  |  | 3.39 | 0 | 96.61 | 172.1307 | 0
3643 | 811.84 | 55.9568 | 28.5 | 8.9508 | 8.9508 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 802.8892 | 0 | 0.088511 | 6.3502 | 0 | 0 | 0 | 8.9508 | on_peak | 802.8892 |  |  | 1.1 | 0 | 98.9 | 56.8397 | 0
3644 | 817.63 | 0 | 27.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 817.63 | 0 | 0.088511 | 6.444 | 0 | 0 | 0 | 0 | on_peak | 817.63 |  |  | 0 | 0 | 100 | 0 | 0
3645 | 814.93 | 0 | 27.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 814.93 | 0 | 0.088511 | 6.4394 | 0 | 0 | 0 | 0 | on_peak | 814.93 |  |  | 0 | 0 | 100 | 0 | 0
3646 | 791.35 | 0 | 27.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 791.35 | 0 | 0.05921 | 6.5898 | 0 | 0 | 0 | 0 | off_peak | 791.35 |  |  | 0 | 0 | 100 | 0 | 0
3647 | 815.86 | 0 | 27.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 815.86 | 0 | 0.05921 | 6.6245 | 0 | 0 | 0 | 0 | off_peak | 815.86 |  |  | 0 | 0 | 100 | 0 | 0
3648 | 829.36 | 0 | 27.2 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 18.9814 | 841.7224 | 0 | 0.05921 | 6.8266 | 0 | 0 | 0 | 0 | off_peak | 829.36 | 0 | 100 | 0 | 0 | 100 | 0 | 0
3649 | 606.39 | 0 | 27.2 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 30.5453 | 618.7524 | 0 | 0.05921 | 6.7833 | 0 | 0 | 0 | 0 | off_peak | 606.39 | 0 | 100 | 0 | 0 | 100 | 0 | 0
3650 | 570.24 | 0 | 27.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30.5453 | 570.24 | 0 | 0.05921 | 6.6731 | 0 | 0 | 0 | 0 | off_peak | 570.24 |  |  | 0 | 0 | 100 | 0 | 0
3651 | 523.98 | 0 | 27.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30.5453 | 523.98 | 0 | 0.05921 | 6.2277 | 0 | 0 | 0 | 0 | off_peak | 523.98 |  |  | 0 | 0 | 100 | 0 | 0
3652 | 564.47 | 0 | 27.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30.5453 | 564.47 | 0 | 0.05921 | 5.6593 | 0 | 0 | 0 | 0 | off_peak | 564.47 |  |  | 0 | 0 | 100 | 0 | 0
3653 | 576.71 | 0 | 27.1 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 42.1093 | 589.0724 | 0 | 0.05921 | 4.8254 | 0 | 0 | 0 | 0 | off_peak | 576.71 | 0 | 100 | 0 | 0 | 100 | 0 | 0
3654 | 684.87 | 4.75 | 27.2 | 0.76341 | 0.76341 | 0 | 0 | 8.7006 | 8.7006 | 0 | 0 | 0 | 50.2479 | 692.8072 | 0 | 0.05921 | 4.3744 | 0 | 0 | 0 | 0.76341 | off_peak | 684.1066 | 0 | 100 | 0.11 | 0 | 99.89 | 3.3394 | 0
3655 | 738.92 | 132.118 | 27.5 | 21.2105 | 21.2105 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 61.8119 | 730.0719 | 0 | 0.05921 | 3.8846 | 0 | 0 | 0 | 21.2105 | off_peak | 717.7095 | 0 | 100 | 2.87 | 0 | 97.13 | 82.3934 | 0
3656 | 768.19 | 330.447 | 27.8 | 52.9928 | 52.9928 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 73.3758 | 727.5596 | 0 | 0.05921 | 3.5717 | 0 | 0 | 0 | 52.9928 | off_peak | 715.1972 | 0 | 100 | 6.9 | 0 | 93.1 | 189.2728 | 0
3657 | 763.27 | 530.938 | 28 | 85.083 | 85.083 | 0 | 0 | 0.79843 | 0.79843 | 0 | 0 | 0 | 74.1227 | 678.9854 | 0 | 0.05921 | 3.4245 | 0 | 0 | 0 | 85.083 | off_peak | 678.187 | 0 | 100 | 11.15 | 0 | 88.85 | 291.3694 | 0
3658 | 758.86 | 709.636 | 28.1 | 113.6781 | 113.6781 | 0 | 0 | 0.051567 | 0.051567 | 0 | 0 | 0 | 74.1709 | 645.2335 | 0 | 0.05921 | 3.4083 | 0 | 0 | 0 | 113.6781 | off_peak | 645.1819 | 0 | 100 | 14.98 | 0 | 85.02 | 387.4502 | 0
3659 | 771.81 | 845.418 | 28.2 | 135.38 | 135.38 | 0 | 0 | 0.0033305 | 0.0033305 | 0 | 0 | 0 | 74.174 | 636.4334 | 0 | 0.05921 | 3.5708 | 0 | 0 | 0 | 135.38 | off_peak | 636.43 | 0 | 100 | 17.54 | 0 | 82.46 | 483.4183 | 0
3660 | 790.09 | 871.174 | 28.3 | 139.4536 | 139.4533 | 0 | 0.0002151 | 0.0002151 | 0 | 0 | 0 | 0 | 74.1742 | 650.6367 | 0 | 0.05921 | 3.901 | 0 | 0 | 0.00020121 | 139.4533 | off_peak | 650.6367 | 100 | 0 | 17.65 | 0 | 82.35 | 544.0109 | 0
3661 | 759.42 | 732.304 | 28.2 | 117.2666 | 117.2666 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1742 | 642.1534 | 0 | 0.088511 | 4.1807 | 0 | 0 | 0.00020121 | 117.2666 | on_peak | 642.1534 |  |  | 15.44 | 0 | 84.56 | 490.2537 | 0
3662 | 869.76 | 604.747 | 28.2 | 96.8404 | 96.8404 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1742 | 772.9196 | 0 | 0.088511 | 4.2423 | 0 | 0 | 0.00020121 | 96.8404 | on_peak | 772.9196 |  |  | 11.13 | 0 | 88.87 | 410.8273 | 0
3663 | 894.24 | 574.069 | 28.1 | 91.9613 | 91.9613 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1742 | 802.2787 | 0 | 0.088511 | 4.4332 | 0 | 0 | 0.00020121 | 91.9613 | on_peak | 802.2787 |  |  | 10.28 | 0 | 89.72 | 407.686 | 0
3664 | 836.87 | 559.383 | 27.9 | 89.674 | 89.674 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1742 | 747.196 | 0 | 0.088511 | 4.7747 | 0 | 0 | 0.00020121 | 89.674 | on_peak | 747.196 |  |  | 10.72 | 0 | 89.28 | 428.1706 | 0
3665 | 843.25 | 196.369 | 27.7 | 31.5026 | 31.5026 | 0 | 0 | 0 | 0 | 62.4453 | 62.4453 | 0 | 7.4174 | 749.3022 | 0 | 0.088511 | 5.3247 | 0.00018821 | 0 | 0 | 31.5028 | on_peak | 749.3022 |  |  | 3.74 | 7.41 | 88.86 | 167.7428 | 0
3666 | 812.37 | 247.416 | 27.5 | 39.7207 | 39.7207 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 772.6493 | 0 | 0.088511 | 5.7235 | 0 | 0 | 0 | 39.7207 | on_peak | 772.6493 |  |  | 4.89 | 0 | 95.11 | 227.3421 | 0
3667 | 765.58 | 65.877 | 27.3 | 10.5837 | 10.5837 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 754.9963 | 0 | 0.088511 | 6.2363 | 0 | 0 | 0 | 10.5837 | on_peak | 754.9963 |  |  | 1.38 | 0 | 98.62 | 66.0032 | 0
3668 | 762.53 | 0 | 27.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 762.53 | 0 | 0.088511 | 6.3341 | 0 | 0 | 0 | 0 | on_peak | 762.53 |  |  | 0 | 0 | 100 | 0 | 0
3669 | 761.3 | 0 | 27 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 761.3 | 0 | 0.088511 | 6.2726 | 0 | 0 | 0 | 0 | on_peak | 761.3 |  |  | 0 | 0 | 100 | 0 | 0
3670 | 722.99 | 0 | 27 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 722.99 | 0 | 0.05921 | 6.3971 | 0 | 0 | 0 | 0 | off_peak | 722.99 |  |  | 0 | 0 | 100 | 0 | 0
3671 | 774.1 | 0 | 27 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 774.1 | 0 | 0.05921 | 6.5141 | 0 | 0 | 0 | 0 | off_peak | 774.1 |  |  | 0 | 0 | 100 | 0 | 0
3672 | 738.22 | 0 | 26.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 738.22 | 0 | 0.05921 | 6.5758 | 0 | 0 | 0 | 0 | off_peak | 738.22 |  |  | 0 | 0 | 100 | 0 | 0
3673 | 681.81 | 0 | 26.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 681.81 | 0 | 0.05921 | 6.6519 | 0 | 0 | 0 | 0 | off_peak | 681.81 |  |  | 0 | 0 | 100 | 0 | 0
3674 | 596.94 | 0 | 26.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 596.94 | 0 | 0.05921 | 6.5157 | 0 | 0 | 0 | 0 | off_peak | 596.94 |  |  | 0 | 0 | 100 | 0 | 0
3675 | 593.56 | 0 | 26.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 593.56 | 0 | 0.05921 | 6.0681 | 0 | 0 | 0 | 0 | off_peak | 593.56 |  |  | 0 | 0 | 100 | 0 | 0
3676 | 589.75 | 0 | 26.4 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 18.9814 | 602.1124 | 0 | 0.05921 | 5.5979 | 0 | 0 | 0 | 0 | off_peak | 589.75 | 0 | 100 | 0 | 0 | 100 | 0 | 0
3677 | 620.43 | 0 | 26.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18.9814 | 620.43 | 0 | 0.05921 | 4.9574 | 0 | 0 | 0 | 0 | off_peak | 620.43 |  |  | 0 | 0 | 100 | 0 | 0
3678 | 678.81 | 3.8 | 26.7 | 0.61183 | 0 | 0 | 0.61183 | 12.3624 | 11.7505 | 0 | 0 | 0 | 30.5453 | 690.5605 | 0 | 0.05921 | 4.452 | 0 | 0 | 0.57232 | 0 | off_peak | 678.81 | 4.95 | 95.05 | 0 | 0 | 100 | 0 | 0
3679 | 740.29 | 128.944 | 27.2 | 20.7235 | 20.7235 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30.5453 | 719.5665 | 0 | 0.05921 | 3.9882 | 0 | 0 | 0.57232 | 20.7235 | off_peak | 719.5665 |  |  | 2.8 | 0 | 97.2 | 82.6501 | 0
3680 | 741.04 | 290.259 | 27.7 | 46.5649 | 46.5649 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30.5453 | 694.4751 | 0 | 0.05921 | 3.6563 | 0 | 0 | 0.57232 | 46.5649 | off_peak | 694.4751 |  |  | 6.28 | 0 | 93.72 | 170.2569 | 0
3681 | 770.33 | 505.147 | 28.1 | 80.9205 | 80.9205 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30.5453 | 689.4095 | 0 | 0.05921 | 3.4353 | 0 | 0 | 0.57232 | 80.9205 | off_peak | 689.4095 |  |  | 10.5 | 0 | 89.5 | 277.9828 | 0
3682 | 767.22 | 662.217 | 28.6 | 105.8888 | 105.8888 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30.5453 | 661.3312 | 0 | 0.05921 | 3.3677 | 0 | 0 | 0.57232 | 105.8888 | off_peak | 661.3312 |  |  | 13.8 | 0 | 86.2 | 356.6062 | 0
3683 | 751.62 | 837.725 | 29 | 133.7572 | 133.7572 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30.5453 | 617.8628 | 0 | 0.05921 | 3.3842 | 0 | 0 | 0.57232 | 133.7572 | off_peak | 617.8628 |  |  | 17.8 | 0 | 82.2 | 452.6644 | 0
3684 | 752.94 | 932.503 | 29.3 | 148.727 | 148.727 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30.5453 | 604.213 | 0 | 0.05921 | 3.4736 | 0 | 0 | 0.57232 | 148.727 | off_peak | 604.213 |  |  | 19.75 | 0 | 80.25 | 516.6197 | 0
3685 | 758.66 | 956.239 | 29.5 | 152.4012 | 152.4012 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30.5453 | 606.2588 | 0 | 0.05921 | 3.6897 | 0 | 0 | 0.57232 | 152.4012 | off_peak | 606.2588 |  |  | 20.09 | 0 | 79.91 | 562.3217 | 0
3686 | 776.32 | 914.631 | 29.7 | 145.6632 | 145.6632 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30.5453 | 630.6568 | 0 | 0.05921 | 4.0972 | 0 | 0 | 0.57232 | 145.6632 | off_peak | 630.6568 |  |  | 18.76 | 0 | 81.24 | 596.8108 | 0
3687 | 799.02 | 750.379 | 29.7 | 119.5046 | 119.5046 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30.5453 | 679.5154 | 0 | 0.05921 | 4.567 | 0 | 0 | 0.57232 | 119.5046 | off_peak | 679.5154 |  |  | 14.96 | 0 | 85.04 | 545.7791 | 0
3688 | 787.33 | 661.989 | 29.6 | 105.4663 | 105.4663 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30.5453 | 681.8637 | 0 | 0.05921 | 4.8288 | 0 | 0 | 0.57232 | 105.4663 | off_peak | 681.8637 |  |  | 13.4 | 0 | 86.6 | 509.2777 | 0
3689 | 797.69 | 455.802 | 29.4 | 72.6703 | 72.6703 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30.5453 | 725.0197 | 0 | 0.05921 | 5.3938 | 0 | 0 | 0.57232 | 72.6703 | off_peak | 725.0197 |  |  | 9.11 | 0 | 90.89 | 391.9694 | 0
3690 | 713.34 | 214.975 | 28.9 | 34.337 | 34.337 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30.5453 | 679.003 | 0 | 0.05921 | 5.7909 | 0 | 0 | 0.57232 | 34.337 | off_peak | 679.003 |  |  | 4.81 | 0 | 95.19 | 198.8428 | 0
3691 | 654.39 | 75.7664 | 28.7 | 12.1107 | 12.1107 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30.5453 | 642.2793 | 0 | 0.05921 | 5.8458 | 0 | 0 | 0.57232 | 12.1107 | off_peak | 642.2793 |  |  | 1.85 | 0 | 98.15 | 70.7966 | 0
3692 | 635.89 | 0 | 27.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30.5453 | 635.89 | 0 | 0.05921 | 5.6601 | 0 | 0 | 0.57232 | 0 | off_peak | 635.89 |  |  | 0 | 0 | 100 | 0 | 0
3693 | 642.28 | 0 | 27.7 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 42.1093 | 654.6424 | 0 | 0.05921 | 5.7473 | 0 | 0 | 0.57232 | 0 | off_peak | 642.28 | 0 | 100 | 0 | 0 | 100 | 0 | 0
3694 | 645.03 | 0 | 27.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 42.1093 | 645.03 | 0 | 0.05921 | 6.1578 | 0 | 0 | 0.57232 | 0 | off_peak | 645.03 |  |  | 0 | 0 | 100 | 0 | 0
3695 | 619.19 | 0 | 27.4 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 53.6732 | 631.5524 | 0 | 0.05921 | 6.3452 | 0 | 0 | 0.57232 | 0 | off_peak | 619.19 | 0 | 100 | 0 | 0 | 100 | 0 | 0
3696 | 661.74 | 0 | 27.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 53.6732 | 661.74 | 0 | 0.05921 | 6.2877 | 0 | 0 | 0.57232 | 0 | off_peak | 661.74 |  |  | 0 | 0 | 100 | 0 | 0
3697 | 622.67 | 0 | 27.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 53.6732 | 622.67 | 0 | 0.05921 | 6.3394 | 0 | 0 | 0.57232 | 0 | off_peak | 622.67 |  |  | 0 | 0 | 100 | 0 | 0
3698 | 639.19 | 0 | 27 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 53.6732 | 639.19 | 0 | 0.05921 | 6.2833 | 0 | 0 | 0.57232 | 0 | off_peak | 639.19 |  |  | 0 | 0 | 100 | 0 | 0
3699 | 651.93 | 0 | 26.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 53.6732 | 651.93 | 0 | 0.05921 | 5.9628 | 0 | 0 | 0.57232 | 0 | off_peak | 651.93 |  |  | 0 | 0 | 100 | 0 | 0
3700 | 603.31 | 0 | 26.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 53.6732 | 603.31 | 0 | 0.05921 | 5.5164 | 0 | 0 | 0.57232 | 0 | off_peak | 603.31 |  |  | 0 | 0 | 100 | 0 | 0
3701 | 667.39 | 0 | 26.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 53.6732 | 667.39 | 0 | 0.05921 | 4.9285 | 0 | 0 | 0.57232 | 0 | off_peak | 667.39 |  |  | 0 | 0 | 100 | 0 | 0
3702 | 712.15 | 4.75 | 27.3 | 0.76313 | 0.76313 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 53.6732 | 711.3869 | 0 | 0.05921 | 4.3997 | 0 | 0 | 0.57232 | 0.76313 | off_peak | 711.3869 |  |  | 0.11 | 0 | 99.89 | 3.3575 | 0
3703 | 702.48 | 139.239 | 27.9 | 22.3212 | 22.3212 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 53.6732 | 680.1588 | 0 | 0.05921 | 3.9301 | 0 | 0 | 0.57232 | 22.3212 | off_peak | 680.1588 |  |  | 3.18 | 0 | 96.82 | 87.7247 | 0
3704 | 729.63 | 340.492 | 28.3 | 54.5044 | 54.5044 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 53.6732 | 675.1256 | 0 | 0.05921 | 3.5953 | 0 | 0 | 0.57232 | 54.5044 | off_peak | 675.1256 |  |  | 7.47 | 0 | 92.53 | 195.9609 | 0
3705 | 720.26 | 542.844 | 28.8 | 86.7377 | 86.7377 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 53.6732 | 633.5223 | 0 | 0.05921 | 3.3856 | 0 | 0 | 0.57232 | 86.7377 | off_peak | 633.5223 |  |  | 12.04 | 0 | 87.96 | 293.6588 | 0
3706 | 721.96 | 717.657 | 29.2 | 114.5026 | 114.5026 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 53.6732 | 607.4574 | 0 | 0.05921 | 3.2821 | 0 | 0 | 0.57232 | 114.5026 | off_peak | 607.4574 |  |  | 15.86 | 0 | 84.14 | 375.8089 | 0
3707 | 701.75 | 849.976 | 29.6 | 135.4159 | 135.4159 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 65.2371 | 578.6965 | 0 | 0.05921 | 3.249 | 0 | 0 | 0.57232 | 135.4159 | off_peak | 566.3341 | 0 | 100 | 19.3 | 0 | 80.7 | 439.9689 | 0
3708 | 740.22 | 929.918 | 30 | 147.9351 | 147.9351 | 0 | 0 | 8.9371 | 8.9371 | 0 | 0 | 0 | 73.597 | 601.222 | 0 | 0.05921 | 3.2962 | 0 | 0 | 0.57232 | 147.9351 | off_peak | 592.2849 | 0 | 100 | 19.99 | 0 | 80.01 | 487.6238 | 0
3709 | 727.52 | 946.009 | 30.2 | 150.3846 | 150.3846 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 73.597 | 577.1354 | 0 | 0.05921 | 3.521 | 0 | 0 | 0.57232 | 150.3846 | off_peak | 577.1354 |  |  | 20.67 | 0 | 79.33 | 529.4981 | 0
3710 | 706.28 | 899.145 | 30.3 | 142.8823 | 142.8823 | 0 | 0 | 0.57721 | 0.57721 | 0 | 0 | 0 | 74.137 | 563.9749 | 0 | 0.05921 | 3.7448 | 0 | 0 | 0.57232 | 142.8823 | off_peak | 563.3977 | 0 | 100 | 20.23 | 0 | 79.77 | 535.0585 | 0
3711 | 742.81 | 794.445 | 30.2 | 126.2908 | 126.2908 | 0 | 0 | 0.037279 | 0.037279 | 0 | 0 | 0 | 74.1718 | 616.5565 | 0 | 0.05921 | 4.02 | 0 | 0 | 0.57232 | 126.2908 | off_peak | 616.5192 | 0 | 100 | 17 | 0 | 83 | 507.6864 | 0
3712 | 756.3 | 634.591 | 30 | 100.9533 | 100.9533 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1718 | 655.3467 | 0 | 0.05921 | 4.5183 | 0 | 0 | 0.57232 | 100.9533 | off_peak | 655.3467 |  |  | 13.35 | 0 | 86.65 | 456.1337 | 0
3713 | 710.34 | 457.137 | 29.6 | 72.8298 | 72.8298 | 0 | 0 | 0.0024077 | 0.0024077 | 0 | 0 | 0 | 74.1741 | 637.5126 | 0 | 0.05921 | 5.0123 | 0 | 0 | 0.57232 | 72.8298 | off_peak | 637.5102 | 0 | 100 | 10.25 | 0 | 89.75 | 365.0445 | 0
3714 | 626.69 | 166.652 | 29.1 | 26.5991 | 26.5991 | 0 | 0 | 0.0001555 | 0.0001555 | 0 | 0 | 0 | 74.1742 | 600.091 | 0 | 0.05921 | 5.5805 | 0 | 0 | 0.57232 | 26.5991 | off_peak | 600.0909 | 0 | 100 | 4.24 | 0 | 95.76 | 148.4353 | 0
3715 | 610.48 | 29.5746 | 28.8 | 4.7255 | 4.7255 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1742 | 605.7545 | 0 | 0.05921 | 5.9005 | 0 | 0 | 0.57232 | 4.7255 | off_peak | 605.7545 |  |  | 0.77 | 0 | 99.23 | 27.8832 | 0
3716 | 601.09 | 0 | 28.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1742 | 601.09 | 0 | 0.05921 | 6.2652 | 0 | 0 | 0.57232 | 0 | off_peak | 601.09 |  |  | 0 | 0 | 100 | 0 | 0
3717 | 591.02 | 0 | 27.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1742 | 591.02 | 0 | 0.05921 | 6.4555 | 0 | 0 | 0.57232 | 0 | off_peak | 591.02 |  |  | 0 | 0 | 100 | 0 | 0
3718 | 601.53 | 0 | 27.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1742 | 601.53 | 0 | 0.05921 | 6.6487 | 0 | 0 | 0.57232 | 0 | off_peak | 601.53 |  |  | 0 | 0 | 100 | 0 | 0
3719 | 605.83 | 0 | 27.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1742 | 605.83 | 0 | 0.05921 | 6.9504 | 0 | 0 | 0.57232 | 0 | off_peak | 605.83 |  |  | 0 | 0 | 100 | 0 | 0
3720 | 587.22 | 0 | 27.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1742 | 587.22 | 0 | 0.05921 | 7.1137 | 0 | 0 | 0.57232 | 0 | off_peak | 587.22 |  |  | 0 | 0 | 100 | 0 | 0
3721 | 587.18 | 0 | 27.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1742 | 587.18 | 0 | 0.05921 | 7.0651 | 0 | 0 | 0.57232 | 0 | off_peak | 587.18 |  |  | 0 | 0 | 100 | 0 | 0
3722 | 554.75 | 0 | 27.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1742 | 554.75 | 0 | 0.05921 | 6.8783 | 0 | 0 | 0.57232 | 0 | off_peak | 554.75 |  |  | 0 | 0 | 100 | 0 | 0
3723 | 587.74 | 0 | 27.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1742 | 587.74 | 0 | 0.05921 | 6.5245 | 0 | 0 | 0.57232 | 0 | off_peak | 587.74 |  |  | 0 | 0 | 100 | 0 | 0
3724 | 608.22 | 0 | 27.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1742 | 608.22 | 0 | 0.05921 | 5.9377 | 0 | 0 | 0.57232 | 0 | off_peak | 608.22 |  |  | 0 | 0 | 100 | 0 | 0
3725 | 576.8 | 0 | 27.3 | 0 | 0 | 0 | 0 | 1.0737e-05 | 1.0737e-05 | 0 | 0 | 0 | 74.1743 | 576.8 | 0 | 0.05921 | 5.1982 | 0 | 0 | 0.57232 | 0 | off_peak | 576.8 | 0 | 100 | 0 | 0 | 100 | 0 | 0
3726 | 683.55 | 4.75 | 27.5 | 0.76257 | 0.76257 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1743 | 682.7874 | 0 | 0.05921 | 4.5275 | 0 | 0 | 0.57232 | 0.76257 | off_peak | 682.7874 |  |  | 0.11 | 0 | 99.89 | 3.4526 | 0
3727 | 751.5 | 135.098 | 28.1 | 21.6416 | 21.6416 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1743 | 729.8584 | 0 | 0.05921 | 3.9542 | 0 | 0 | 0.57232 | 21.6416 | off_peak | 729.8584 |  |  | 2.88 | 0 | 97.12 | 85.5758 | 0
3728 | 812.21 | 334.549 | 28.5 | 53.5141 | 53.5141 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1743 | 758.6959 | 0 | 0.05921 | 3.6528 | 0 | 0 | 0.57232 | 53.5141 | off_peak | 758.6959 |  |  | 6.59 | 0 | 93.41 | 195.4775 | 0
3729 | 822.3 | 535.83 | 28.9 | 85.5857 | 85.5857 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1743 | 736.7143 | 0 | 0.05921 | 3.4577 | 0 | 0 | 0.57232 | 85.5857 | off_peak | 736.7143 |  |  | 10.41 | 0 | 89.59 | 295.9293 | 0
3730 | 852.01 | 710.075 | 29.3 | 113.2515 | 113.2515 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1743 | 738.7585 | 0 | 0.05921 | 3.434 | 0 | 0 | 0.57232 | 113.2515 | off_peak | 738.7585 |  |  | 13.29 | 0 | 86.71 | 388.9095 | 0
3731 | 835.58 | 794.436 | 29.6 | 126.5674 | 126.5674 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1743 | 709.0126 | 0 | 0.05921 | 3.6365 | 0 | 0 | 0.57232 | 126.5674 | off_peak | 709.0126 |  |  | 15.15 | 0 | 84.85 | 460.2679 | 0
3732 | 872.57 | 893.855 | 29.8 | 142.3023 | 142.3023 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1743 | 730.2677 | 0 | 0.05921 | 3.9241 | 0 | 0 | 0.57232 | 142.3023 | off_peak | 730.2677 |  |  | 16.31 | 0 | 83.69 | 558.4026 | 0
3733 | 853.13 | 936.685 | 29.9 | 149.0662 | 149.0662 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1743 | 704.0638 | 0 | 0.088511 | 4.2573 | 0 | 0 | 0.57232 | 149.0662 | on_peak | 704.0638 |  |  | 17.47 | 0 | 82.53 | 634.6159 | 0
3734 | 858.82 | 843.677 | 29.9 | 134.2647 | 134.2647 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1743 | 724.5553 | 0 | 0.088511 | 4.4542 | 0 | 0 | 0.57232 | 134.2647 | on_peak | 724.5553 |  |  | 15.63 | 0 | 84.37 | 598.0407 | 0
3735 | 873.21 | 726.125 | 29.8 | 115.5996 | 115.5996 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1743 | 757.6104 | 0 | 0.088511 | 4.6856 | 0 | 0 | 0.57232 | 115.5996 | on_peak | 757.6104 |  |  | 13.24 | 0 | 86.76 | 541.6522 | 0
3736 | 840.26 | 594.607 | 29.6 | 94.7312 | 94.7312 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1743 | 745.5288 | 0 | 0.088511 | 4.9244 | 0 | 0 | 0.57232 | 94.7312 | on_peak | 745.5288 |  |  | 11.27 | 0 | 88.73 | 466.4932 | 0
3737 | 846.14 | 384.781 | 29.3 | 61.3696 | 61.3696 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1743 | 784.7704 | 0 | 0.088511 | 5.3049 | 0 | 0 | 0.57232 | 61.3696 | on_peak | 784.7704 |  |  | 7.25 | 0 | 92.75 | 325.5579 | 0
3738 | 859.75 | 171.222 | 28.9 | 27.3485 | 27.3485 | 0 | 0 | 0 | 0 | 62.4453 | 62.4453 | 0 | 7.4174 | 769.9562 | 0 | 0.088511 | 5.6396 | 0.53535 | 0 | 0 | 27.8839 | on_peak | 769.9562 |  |  | 3.18 | 7.26 | 89.56 | 157.2531 | 0
3739 | 834.93 | 62.8049 | 28.6 | 10.0425 | 10.0425 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 824.8875 | 0 | 0.088511 | 5.9801 | 0 | 0 | 0 | 10.0425 | on_peak | 824.8875 |  |  | 1.2 | 0 | 98.8 | 60.0553 | 0
3740 | 829.08 | 0 | 28.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 829.08 | 0 | 0.088511 | 6.1722 | 0 | 0 | 0 | 0 | on_peak | 829.08 |  |  | 0 | 0 | 100 | 0 | 0
3741 | 825.6 | 0 | 28 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 825.6 | 0 | 0.088511 | 6.3758 | 0 | 0 | 0 | 0 | on_peak | 825.6 |  |  | 0 | 0 | 100 | 0 | 0
3742 | 810.71 | 0 | 28 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 18.9814 | 823.0724 | 0 | 0.05921 | 6.6085 | 0 | 0 | 0 | 0 | off_peak | 810.71 | 0 | 100 | 0 | 0 | 100 | 0 | 0
3743 | 815.92 | 0 | 28 | 0 | 0 | 0 | 0 | 8.7006 | 8.7006 | 0 | 0 | 0 | 27.12 | 824.6206 | 0 | 0.05921 | 6.9191 | 0 | 0 | 0 | 0 | off_peak | 815.92 | 0 | 100 | 0 | 0 | 100 | 0 | 0
3744 | 804.24 | 0 | 27.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27.12 | 804.24 | 0 | 0.05921 | 7.0295 | 0 | 0 | 0 | 0 | off_peak | 804.24 |  |  | 0 | 0 | 100 | 0 | 0
3745 | 713.6 | 0 | 27.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27.12 | 713.6 | 0 | 0.05921 | 7.0754 | 0 | 0 | 0 | 0 | off_peak | 713.6 |  |  | 0 | 0 | 100 | 0 | 0
3746 | 652.2 | 0 | 27.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27.12 | 652.2 | 0 | 0.05921 | 6.9057 | 0 | 0 | 0 | 0 | off_peak | 652.2 |  |  | 0 | 0 | 100 | 0 | 0
3747 | 636.2 | 0 | 27.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27.12 | 636.2 | 0 | 0.05921 | 6.6111 | 0 | 0 | 0 | 0 | off_peak | 636.2 |  |  | 0 | 0 | 100 | 0 | 0
3748 | 662.65 | 0 | 27.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27.12 | 662.65 | 0 | 0.05921 | 6.0047 | 0 | 0 | 0 | 0 | off_peak | 662.65 |  |  | 0 | 0 | 100 | 0 | 0
3749 | 642.2 | 0 | 27.5 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 38.684 | 654.5624 | 0 | 0.05921 | 5.1865 | 0 | 0 | 0 | 0 | off_peak | 642.2 | 0 | 100 | 0 | 0 | 100 | 0 | 0
3750 | 710.77 | 3.8 | 27.7 | 0.60962 | 0.60962 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 50.2479 | 722.5228 | 0 | 0.05921 | 4.545 | 0 | 0 | 0 | 0.60962 | off_peak | 710.1604 | 0 | 100 | 0.09 | 0 | 99.91 | 2.7707 | 0
3751 | 761.44 | 90.4476 | 28.2 | 14.4837 | 14.4837 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 61.8119 | 759.3187 | 0 | 0.05921 | 4.0516 | 0 | 0 | 0 | 14.4837 | off_peak | 746.9563 | 0 | 100 | 1.9 | 0 | 98.1 | 58.6818 | 0
3752 | 803.33 | 286.978 | 28.6 | 45.8879 | 45.8879 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 73.3758 | 769.8045 | 0 | 0.05921 | 3.7128 | 0 | 0 | 0 | 45.8879 | off_peak | 757.4421 | 0 | 100 | 5.71 | 0 | 94.29 | 170.3726 | 0
3753 | 833.97 | 546.291 | 29 | 87.2248 | 87.2248 | 0 | 0 | 0.79843 | 0.79843 | 0 | 0 | 0 | 74.1227 | 747.5437 | 0 | 0.05921 | 3.4946 | 0 | 0 | 0 | 87.2248 | off_peak | 746.7452 | 0 | 100 | 10.46 | 0 | 89.54 | 304.8114 | 0
3754 | 878.75 | 724.876 | 29.4 | 115.5698 | 115.5698 | 0 | 0 | 0.051567 | 0.051567 | 0 | 0 | 0 | 74.1709 | 763.2317 | 0 | 0.05921 | 3.4448 | 0 | 0 | 0 | 115.5698 | off_peak | 763.1802 | 0 | 100 | 13.15 | 0 | 86.85 | 398.1113 | 0
3755 | 814.1 | 860.692 | 29.6 | 137.1231 | 137.1231 | 0 | 0 | 0.0033305 | 0.0033305 | 0 | 0 | 0 | 74.174 | 676.9802 | 0 | 0.05921 | 3.6445 | 0 | 0 | 0 | 137.1231 | off_peak | 676.9769 | 0 | 100 | 16.84 | 0 | 83.16 | 499.7493 | 0
3756 | 887.58 | 940.546 | 29.8 | 149.7355 | 149.7355 | 0 | 0 | 0.0002151 | 0.0002151 | 0 | 0 | 0 | 74.1742 | 737.8447 | 0 | 0.05921 | 3.9932 | 0 | 0 | 0 | 149.7355 | off_peak | 737.8445 | 0 | 100 | 16.87 | 0 | 83.13 | 597.9246 | 0
3757 | 817.31 | 943.416 | 29.9 | 150.1374 | 150.1374 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1742 | 667.1726 | 0 | 0.088511 | 4.2668 | 0 | 0 | 0 | 150.1374 | on_peak | 667.1726 |  |  | 18.37 | 0 | 81.63 | 640.6071 | 0
3758 | 851.55 | 730.406 | 29.9 | 116.2385 | 116.2385 | 0 | 0 | 0 | 0 | 62.4453 | 62.4453 | 0 | 7.4174 | 672.8662 | 0 | 0.088511 | 4.2644 | 0 | 0 | 0 | 116.2385 | on_peak | 672.8662 |  |  | 13.65 | 7.33 | 79.02 | 495.6877 | 0
3759 | 919.61 | 684.462 | 29.7 | 109.0067 | 109.0067 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 810.6033 | 0 | 0.088511 | 4.2396 | 0 | 0 | 0 | 109.0067 | on_peak | 810.6033 |  |  | 11.85 | 0 | 88.15 | 462.1402 | 0
3760 | 847.45 | 350.556 | 29.3 | 55.911 | 55.911 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 791.539 | 0 | 0.088511 | 4.3903 | 0 | 0 | 0 | 55.911 | on_peak | 791.539 |  |  | 6.6 | 0 | 93.4 | 245.4642 | 0
3761 | 864.52 | 269.85 | 29 | 43.0862 | 43.0862 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 821.4338 | 0 | 0.088511 | 4.6793 | 0 | 0 | 0 | 43.0862 | on_peak | 821.4338 |  |  | 4.98 | 0 | 95.02 | 201.6151 | 0
3762 | 857.32 | 163.792 | 28.5 | 26.2 | 26.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 831.12 | 0 | 0.088511 | 5.1031 | 0 | 0 | 0 | 26.2 | on_peak | 831.12 |  |  | 3.06 | 0 | 96.94 | 133.7016 | 0
3763 | 844.09 | 50.5548 | 28.3 | 8.0926 | 8.0926 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 835.9974 | 0 | 0.088511 | 5.5922 | 0 | 0 | 0 | 8.0926 | on_peak | 835.9974 |  |  | 0.96 | 0 | 99.04 | 45.2554 | 0
3764 | 864.88 | 0 | 27.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 864.88 | 0 | 0.088511 | 5.9675 | 0 | 0 | 0 | 0 | on_peak | 864.88 |  |  | 0 | 0 | 100 | 0 | 0
3765 | 826.43 | 0 | 27.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 826.43 | 0 | 0.088511 | 6.419 | 0 | 0 | 0 | 0 | on_peak | 826.43 |  |  | 0 | 0 | 100 | 0 | 0
3766 | 794.06 | 0 | 27.7 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 18.9814 | 806.4224 | 0 | 0.05921 | 6.6947 | 0 | 0 | 0 | 0 | off_peak | 794.06 | 0 | 100 | 0 | 0 | 100 | 0 | 0
3767 | 824.83 | 0 | 27.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18.9814 | 824.83 | 0 | 0.05921 | 6.8752 | 0 | 0 | 0 | 0 | off_peak | 824.83 |  |  | 0 | 0 | 100 | 0 | 0
3768 | 821.64 | 0 | 27.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18.9814 | 821.64 | 0 | 0.05921 | 6.9603 | 0 | 0 | 0 | 0 | off_peak | 821.64 |  |  | 0 | 0 | 100 | 0 | 0
3769 | 708.19 | 0 | 27.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18.9814 | 708.19 | 0 | 0.05921 | 6.9543 | 0 | 0 | 0 | 0 | off_peak | 708.19 |  |  | 0 | 0 | 100 | 0 | 0
3770 | 622.72 | 0 | 27.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18.9814 | 622.72 | 0 | 0.05921 | 6.8575 | 0 | 0 | 0 | 0 | off_peak | 622.72 |  |  | 0 | 0 | 100 | 0 | 0
3771 | 639.61 | 0 | 27.4 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 30.5453 | 651.9724 | 0 | 0.05921 | 6.4688 | 0 | 0 | 0 | 0 | off_peak | 639.61 | 0 | 100 | 0 | 0 | 100 | 0 | 0
3772 | 630.68 | 0 | 27.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30.5453 | 630.68 | 0 | 0.05921 | 5.8728 | 0 | 0 | 0 | 0 | off_peak | 630.68 |  |  | 0 | 0 | 100 | 0 | 0
3773 | 608.46 | 0 | 27.3 | 0 | 0 | 0 | 0 | 8.7006 | 8.7006 | 0 | 0 | 0 | 38.684 | 617.1606 | 0 | 0.05921 | 5.1957 | 0 | 0 | 0 | 0 | off_peak | 608.46 | 0 | 100 | 0 | 0 | 100 | 0 | 0
3774 | 747.01 | 3.8 | 27.5 | 0.61006 | 0.61006 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 50.2479 | 758.7623 | 0 | 0.05921 | 4.5127 | 0 | 0 | 0 | 0.61006 | off_peak | 746.3999 | 0 | 100 | 0.08 | 0 | 99.92 | 2.753 | 0
3775 | 738.83 | 119.347 | 27.9 | 19.1324 | 19.1324 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 61.8119 | 732.06 | 0 | 0.05921 | 4.075 | 0 | 0 | 0 | 19.1324 | off_peak | 719.6976 | 0 | 100 | 2.59 | 0 | 97.41 | 77.9644 | 0
3776 | 785.5 | 282.208 | 28.4 | 45.1581 | 45.1581 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 73.3758 | 752.7043 | 0 | 0.05921 | 3.7926 | 0 | 0 | 0 | 45.1581 | off_peak | 740.3419 | 0 | 100 | 5.75 | 0 | 94.25 | 171.2687 | 0
3777 | 852.47 | 305.201 | 28.8 | 48.7662 | 48.7662 | 0 | 0 | 0.79843 | 0.79843 | 0 | 0 | 0 | 74.1227 | 804.5022 | 0 | 0.05921 | 3.625 | 0 | 0 | 0 | 48.7662 | off_peak | 803.7038 | 0 | 100 | 5.72 | 0 | 94.28 | 176.7797 | 0
3778 | 844.25 | 633.765 | 29.1 | 101.1545 | 101.1545 | 0 | 0 | 0.051567 | 0.051567 | 0 | 0 | 0 | 74.1709 | 743.147 | 0 | 0.05921 | 3.5654 | 0 | 0 | 0 | 101.1545 | off_peak | 743.0955 | 0 | 100 | 11.98 | 0 | 88.02 | 360.6531 | 0
3779 | 816.99 | 686.649 | 29.4 | 109.4751 | 109.4751 | 0 | 0 | 0.0033305 | 0.0033305 | 0 | 0 | 0 | 74.174 | 707.5182 | 0 | 0.05921 | 3.6813 | 0 | 0 | 0 | 109.4751 | off_peak | 707.5149 | 0 | 100 | 13.4 | 0 | 86.6 | 403.0079 | 0
3780 | 929.01 | 848.881 | 29.6 | 135.2414 | 135.2414 | 0 | 0 | 0.0002151 | 0.0002151 | 0 | 0 | 0 | 74.1742 | 793.7688 | 0 | 0.05921 | 3.9625 | 0 | 0 | 0 | 135.2414 | off_peak | 793.7686 | 0 | 100 | 14.56 | 0 | 85.44 | 535.8975 | 0
3781 | 824.53 | 542.054 | 29.6 | 86.3586 | 86.3586 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1742 | 738.1714 | 0 | 0.088511 | 4.2904 | 0 | 0 | 0 | 86.3586 | on_peak | 738.1714 |  |  | 10.47 | 0 | 89.53 | 370.5119 | 0
3782 | 859.7 | 128.25 | 29.5 | 20.4399 | 20.4399 | 0 | 0 | 0 | 0 | 62.4453 | 62.4453 | 0 | 7.4174 | 776.8148 | 0 | 0.088511 | 4.5615 | 0 | 0 | 0 | 20.4399 | on_peak | 776.8148 |  |  | 2.38 | 7.26 | 90.36 | 93.2365 | 0
3783 | 862.46 | 264.088 | 29.3 | 42.12 | 42.12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 820.34 | 0 | 0.088511 | 4.8536 | 0 | 0 | 0 | 42.12 | on_peak | 820.34 |  |  | 4.88 | 0 | 95.12 | 204.4339 | 0
3784 | 846.61 | 84.2935 | 29 | 13.4589 | 13.4589 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 833.1511 | 0 | 0.088511 | 5.3129 | 0 | 0 | 0 | 13.4589 | on_peak | 833.1511 |  |  | 1.59 | 0 | 98.41 | 71.5057 | 0
3785 | 829.8 | 282.334 | 28.7 | 45.1289 | 45.1289 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 784.6711 | 0 | 0.088511 | 5.729 | 0 | 0 | 0 | 45.1289 | on_peak | 784.6711 |  |  | 5.44 | 0 | 94.56 | 258.5436 | 0
3786 | 831.27 | 89.2028 | 28.2 | 14.2844 | 14.2844 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 816.9856 | 0 | 0.088511 | 6.124 | 0 | 0 | 0 | 14.2844 | on_peak | 816.9856 |  |  | 1.72 | 0 | 98.28 | 87.4778 | 0
3787 | 845.7 | 48.8358 | 28 | 7.826 | 7.826 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 837.874 | 0 | 0.088511 | 6.3509 | 0 | 0 | 0 | 7.826 | on_peak | 837.874 |  |  | 0.93 | 0 | 99.07 | 49.7017 | 0
3788 | 806.82 | 0 | 27.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 806.82 | 0 | 0.088511 | 6.5835 | 0 | 0 | 0 | 0 | on_peak | 806.82 |  |  | 0 | 0 | 100 | 0 | 0
3789 | 784.59 | 0 | 27.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 784.59 | 0 | 0.088511 | 6.7807 | 0 | 0 | 0 | 0 | on_peak | 784.59 |  |  | 0 | 0 | 100 | 0 | 0
3790 | 792.89 | 0 | 27.1 | 0 | 0 | 0 | 0 | 8.7006 | 8.7006 | 0 | 0 | 0 | 15.5561 | 801.5906 | 0 | 0.05921 | 6.7303 | 0 | 0 | 0 | 0 | off_peak | 792.89 | 0 | 100 | 0 | 0 | 100 | 0 | 0
3791 | 820.5 | 0 | 27 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 27.12 | 832.8624 | 0 | 0.05921 | 6.8012 | 0 | 0 | 0 | 0 | off_peak | 820.5 | 0 | 100 | 0 | 0 | 100 | 0 | 0
3792 | 818.37 | 0 | 26.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27.12 | 818.37 | 0 | 0.05921 | 6.9306 | 0 | 0 | 0 | 0 | off_peak | 818.37 |  |  | 0 | 0 | 100 | 0 | 0
3793 | 745.63 | 0 | 26.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27.12 | 745.63 | 0 | 0.05921 | 6.9029 | 0 | 0 | 0 | 0 | off_peak | 745.63 |  |  | 0 | 0 | 100 | 0 | 0
3794 | 628.43 | 0 | 26.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27.12 | 628.43 | 0 | 0.05921 | 6.8348 | 0 | 0 | 0 | 0 | off_peak | 628.43 |  |  | 0 | 0 | 100 | 0 | 0
3795 | 573.99 | 0 | 26.7 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 38.684 | 586.3524 | 0 | 0.05921 | 6.531 | 0 | 0 | 0 | 0 | off_peak | 573.99 | 0 | 100 | 0 | 0 | 100 | 0 | 0
3796 | 578.75 | 0 | 26.7 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 50.2479 | 591.1124 | 0 | 0.05921 | 5.9126 | 0 | 0 | 0 | 0 | off_peak | 578.75 | 0 | 100 | 0 | 0 | 100 | 0 | 0
3797 | 595.86 | 0 | 26.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50.2479 | 595.86 | 0 | 0.05921 | 5.1924 | 0 | 0 | 0 | 0 | off_peak | 595.86 |  |  | 0 | 0 | 100 | 0 | 0
3798 | 642.65 | 2.85 | 26.9 | 0.45854 | 0.45854 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 61.8119 | 654.5538 | 0 | 0.05921 | 4.5948 | 0 | 0 | 0 | 0.45854 | off_peak | 642.1915 | 0 | 100 | 0.07 | 0 | 99.93 | 2.1069 | 0
3799 | 726.84 | 63.3146 | 27.4 | 10.1683 | 10.1683 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 61.8119 | 716.6717 | 0 | 0.05921 | 4.1512 | 0 | 0 | 0 | 10.1683 | off_peak | 716.6717 |  |  | 1.4 | 0 | 98.6 | 42.2106 | 0
3800 | 770.32 | 213.772 | 27.9 | 34.2695 | 34.2695 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 73.3758 | 748.4129 | 0 | 0.05921 | 3.8431 | 0 | 0 | 0 | 34.2695 | off_peak | 736.0505 | 0 | 100 | 4.45 | 0 | 95.55 | 131.7011 | 0
3801 | 835.38 | 528.923 | 28.2 | 84.6984 | 84.6984 | 0 | 0 | 0.79843 | 0.79843 | 0 | 0 | 0 | 74.1227 | 751.48 | 0 | 0.05921 | 3.6607 | 0 | 0 | 0 | 84.6984 | off_peak | 750.6816 | 0 | 100 | 10.14 | 0 | 89.86 | 310.0558 | 0
3802 | 811.78 | 664.536 | 28.6 | 106.2596 | 106.2596 | 0 | 0 | 0.051567 | 0.051567 | 0 | 0 | 0 | 74.1709 | 705.5719 | 0 | 0.05921 | 3.6014 | 0 | 0 | 0 | 106.2596 | off_peak | 705.5204 | 0 | 100 | 13.09 | 0 | 86.91 | 382.6785 | 0
3803 | 856.53 | 704.407 | 28.9 | 112.5118 | 112.5118 | 0 | 0 | 0.0033305 | 0.0033305 | 0 | 0 | 0 | 74.174 | 744.0216 | 0 | 0.05921 | 3.7495 | 0 | 0 | 0 | 112.5118 | off_peak | 744.0182 | 0 | 100 | 13.14 | 0 | 86.86 | 421.8661 | 0
3804 | 896.42 | 718.015 | 29.2 | 114.5597 | 114.5597 | 0 | 0 | 0.0002151 | 0.0002151 | 0 | 0 | 0 | 74.1742 | 781.8605 | 0 | 0.05921 | 4.0416 | 0 | 0 | 0 | 114.5597 | off_peak | 781.8603 | 0 | 100 | 12.78 | 0 | 87.22 | 463.0087 | 0
3805 | 863.51 | 489.088 | 29.3 | 78.0057 | 78.0057 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1742 | 785.5043 | 0 | 0.088511 | 4.4128 | 0 | 0 | 0 | 78.0057 | on_peak | 785.5043 |  |  | 9.03 | 0 | 90.97 | 344.2205 | 0
3806 | 930.85 | 378.536 | 29.2 | 60.3956 | 60.3956 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1742 | 870.4544 | 0 | 0.088511 | 4.6233 | 0 | 0 | 0 | 60.3956 | on_peak | 870.4544 |  |  | 6.49 | 0 | 93.51 | 279.2266 | 0
3807 | 866.71 | 63.65 | 29.1 | 10.1591 | 10.1591 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1742 | 856.5509 | 0 | 0.088511 | 5 | 0 | 0 | 0 | 10.1591 | on_peak | 856.5509 |  |  | 1.17 | 0 | 98.83 | 50.7951 | 0
3808 | 875.47 | 41.8 | 28.8 | 6.679 | 6.679 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1742 | 868.791 | 0 | 0.088511 | 5.4507 | 0 | 0 | 0 | 6.679 | on_peak | 868.791 |  |  | 0.76 | 0 | 99.24 | 36.4047 | 0
3809 | 874.19 | 269.555 | 28.5 | 43.1177 | 43.1177 | 0 | 0 | 0 | 0 | 62.4453 | 62.4453 | 0 | 7.4174 | 768.627 | 0 | 0.088511 | 6.0441 | 0 | 0 | 0 | 43.1177 | on_peak | 768.627 |  |  | 4.93 | 7.14 | 87.92 | 260.6095 | 0
3810 | 781.48 | 161.093 | 28.1 | 25.8058 | 25.8058 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 755.6742 | 0 | 0.088511 | 6.4821 | 0 | 0 | 0 | 25.8058 | on_peak | 755.6742 |  |  | 3.3 | 0 | 96.7 | 167.2768 | 0
3811 | 812.73 | 56.9589 | 27.9 | 9.131 | 9.131 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 803.599 | 0 | 0.088511 | 6.6424 | 0 | 0 | 0 | 9.131 | on_peak | 803.599 |  |  | 1.12 | 0 | 98.88 | 60.6516 | 0
3812 | 774.03 | 0 | 27.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 774.03 | 0 | 0.088511 | 6.4126 | 0 | 0 | 0 | 0 | on_peak | 774.03 |  |  | 0 | 0 | 100 | 0 | 0
3813 | 754.71 | 0 | 27.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 754.71 | 0 | 0.088511 | 6.7394 | 0 | 0 | 0 | 0 | on_peak | 754.71 |  |  | 0 | 0 | 100 | 0 | 0
3814 | 774.93 | 0 | 27 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 18.9814 | 787.2924 | 0 | 0.05921 | 6.9316 | 0 | 0 | 0 | 0 | off_peak | 774.93 | 0 | 100 | 0 | 0 | 100 | 0 | 0
3815 | 763.11 | 0 | 26.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18.9814 | 763.11 | 0 | 0.05921 | 7.0256 | 0 | 0 | 0 | 0 | off_peak | 763.11 |  |  | 0 | 0 | 100 | 0 | 0
3816 | 739.29 | 0 | 26.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18.9814 | 739.29 | 0 | 0.05921 | 7.1653 | 0 | 0 | 0 | 0 | off_peak | 739.29 |  |  | 0 | 0 | 100 | 0 | 0
3817 | 636.04 | 0 | 26.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18.9814 | 636.04 | 0 | 0.05921 | 7.2351 | 0 | 0 | 0 | 0 | off_peak | 636.04 |  |  | 0 | 0 | 100 | 0 | 0
3818 | 579.17 | 0 | 26.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18.9814 | 579.17 | 0 | 0.05921 | 7.1784 | 0 | 0 | 0 | 0 | off_peak | 579.17 |  |  | 0 | 0 | 100 | 0 | 0
3819 | 559.71 | 0 | 26.6 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 30.5453 | 572.0724 | 0 | 0.05921 | 6.9242 | 0 | 0 | 0 | 0 | off_peak | 559.71 | 0 | 100 | 0 | 0 | 100 | 0 | 0
3820 | 574.64 | 0 | 26.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30.5453 | 574.64 | 0 | 0.05921 | 6.3066 | 0 | 0 | 0 | 0 | off_peak | 574.64 |  |  | 0 | 0 | 100 | 0 | 0
3821 | 585.54 | 0 | 26.6 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 42.1093 | 597.9024 | 0 | 0.05921 | 5.4629 | 0 | 0 | 0 | 0 | off_peak | 585.54 | 0 | 100 | 0 | 0 | 100 | 0 | 0
3822 | 676.26 | 3.8 | 26.8 | 0.61161 | 0 | 0 | 0.61161 | 12.3624 | 11.7508 | 0 | 0 | 0 | 53.6732 | 688.0108 | 0 | 0.05921 | 4.6696 | 0 | 0 | 0.57211 | 0 | off_peak | 676.26 | 4.95 | 95.05 | 0 | 0 | 100 | 0 | 0
3823 | 702.16 | 106.609 | 27.2 | 17.1339 | 17.1339 | 0 | 0 | 8.7006 | 8.7006 | 0 | 0 | 0 | 61.8119 | 693.7267 | 0 | 0.05921 | 4.4726 | 0 | 0 | 0.57211 | 17.1339 | off_peak | 685.0261 | 0 | 100 | 2.44 | 0 | 97.56 | 76.6333 | 0
3824 | 815.53 | 311.692 | 27.6 | 50.0215 | 50.0215 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 73.3758 | 777.8709 | 0 | 0.05921 | 4.1751 | 0 | 0 | 0.57211 | 50.0215 | off_peak | 765.5085 | 0 | 100 | 6.13 | 0 | 93.87 | 208.8464 | 0
3825 | 821.26 | 507.072 | 27.9 | 81.2881 | 81.2881 | 0 | 0 | 0.79843 | 0.79843 | 0 | 0 | 0 | 74.1227 | 740.7704 | 0 | 0.05921 | 3.9722 | 0 | 0 | 0.57211 | 81.2881 | off_peak | 739.9719 | 0 | 100 | 9.9 | 0 | 90.1 | 322.893 | 0
3826 | 840.73 | 434.793 | 28.2 | 69.625 | 69.625 | 0 | 0 | 0.051567 | 0.051567 | 0 | 0 | 0 | 74.1709 | 771.1565 | 0 | 0.05921 | 3.8902 | 0 | 0 | 0.57211 | 69.625 | off_peak | 771.105 | 0 | 100 | 8.28 | 0 | 91.72 | 270.8556 | 0
3827 | 840.3 | 170.818 | 28.5 | 27.3238 | 27.3238 | 0 | 0 | 0.0033305 | 0.0033305 | 0 | 0 | 0 | 74.174 | 812.9795 | 0 | 0.05921 | 3.9248 | 0 | 0 | 0.57211 | 27.3238 | off_peak | 812.9762 | 0 | 100 | 3.25 | 0 | 96.75 | 107.2399 | 0
3828 | 865.52 | 497.617 | 28.6 | 79.5692 | 79.5692 | 0 | 0 | 0.0002151 | 0.0002151 | 0 | 0 | 0 | 74.1742 | 785.951 | 0 | 0.05921 | 4.1043 | 0 | 0 | 0.57211 | 79.5692 | off_peak | 785.9508 | 0 | 100 | 9.19 | 0 | 90.81 | 326.5771 | 0
3829 | 861.54 | 393.219 | 28.7 | 62.853 | 62.853 | 0 | 0 | 0 | 0 | 0.53516 | 0.53516 | 0 | 73.6021 | 798.1519 | 0 | 0.088511 | 4.5247 | 0.53516 | 0 | 0 | 63.3881 | on_peak | 798.1519 |  |  | 7.3 | 0.06 | 92.64 | 286.815 | 0
3830 | 880.67 | 89.3 | 28.6 | 14.2791 | 14.2791 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 73.6021 | 866.3909 | 0 | 0.088511 | 4.8666 | 0 | 0 | 0 | 14.2791 | on_peak | 866.3909 |  |  | 1.62 | 0 | 98.38 | 69.4903 | 0
3831 | 871.83 | 41.8 | 28.6 | 6.6838 | 6.6838 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 73.6021 | 865.1462 | 0 | 0.088511 | 5.2246 | 0 | 0 | 0 | 6.6838 | on_peak | 865.1462 |  |  | 0.77 | 0 | 99.23 | 34.9205 | 0
3832 | 829.55 | 57.95 | 28.5 | 9.2696 | 9.2696 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 73.6021 | 820.2804 | 0 | 0.088511 | 5.6193 | 0 | 0 | 0 | 9.2696 | on_peak | 820.2804 |  |  | 1.12 | 0 | 98.88 | 52.0885 | 0
3833 | 874.08 | 42.75 | 28.3 | 6.8432 | 6.8432 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 73.6021 | 867.2368 | 0 | 0.088511 | 5.8459 | 0 | 0 | 0 | 6.8432 | on_peak | 867.2368 |  |  | 0.78 | 0 | 99.22 | 40.0047 | 0
3834 | 847.56 | 120.229 | 28 | 19.2667 | 19.2667 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 73.6021 | 828.2933 | 0 | 0.088511 | 6.4275 | 0 | 0 | 0 | 19.2667 | on_peak | 828.2933 |  |  | 2.27 | 0 | 97.73 | 123.8372 | 0
3835 | 803.74 | 35.2811 | 27.9 | 5.6559 | 5.6559 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 73.6021 | 798.0841 | 0 | 0.088511 | 7.1458 | 0 | 0 | 0 | 5.6559 | on_peak | 798.0841 |  |  | 0.7 | 0 | 99.3 | 40.4155 | 0
3836 | 877.87 | 0 | 27.3 | 0 | 0 | 0 | 0 | 0 | 0 | 61.9101 | 61.9101 | 0 | 7.4174 | 815.9599 | 0 | 0.088511 | 7.2485 | 0 | 0 | 0 | 0 | on_peak | 815.9599 |  |  | 0 | 7.05 | 92.95 | 0 | 0
3837 | 823.85 | 0 | 27.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 823.85 | 0 | 0.088511 | 7.5326 | 0 | 0 | 0 | 0 | on_peak | 823.85 |  |  | 0 | 0 | 100 | 0 | 0
3838 | 833.26 | 0 | 27.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 833.26 | 0 | 0.05921 | 7.6383 | 0 | 0 | 0 | 0 | off_peak | 833.26 |  |  | 0 | 0 | 100 | 0 | 0
3839 | 817.13 | 0 | 27 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 817.13 | 0 | 0.05921 | 7.4781 | 0 | 0 | 0 | 0 | off_peak | 817.13 |  |  | 0 | 0 | 100 | 0 | 0
3840 | 822.17 | 0 | 26.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 822.17 | 0 | 0.05921 | 7.5886 | 0 | 0 | 0 | 0 | off_peak | 822.17 |  |  | 0 | 0 | 100 | 0 | 0
3841 | 707.97 | 0 | 26.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 707.97 | 0 | 0.05921 | 7.4198 | 0 | 0 | 0 | 0 | off_peak | 707.97 |  |  | 0 | 0 | 100 | 0 | 0
3842 | 646.43 | 0 | 26.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 646.43 | 0 | 0.05921 | 7.1682 | 0 | 0 | 0 | 0 | off_peak | 646.43 |  |  | 0 | 0 | 100 | 0 | 0
3843 | 654.56 | 0 | 26.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 654.56 | 0 | 0.05921 | 6.7557 | 0 | 0 | 0 | 0 | off_peak | 654.56 |  |  | 0 | 0 | 100 | 0 | 0
3844 | 655.12 | 0 | 26.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 655.12 | 0 | 0.05921 | 6.1772 | 0 | 0 | 0 | 0 | off_peak | 655.12 |  |  | 0 | 0 | 100 | 0 | 0
3845 | 641.7 | 0 | 26.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 641.7 | 0 | 0.05921 | 5.4655 | 0 | 0 | 0 | 0 | off_peak | 641.7 |  |  | 0 | 0 | 100 | 0 | 0
3846 | 701.25 | 2.85 | 26.9 | 0.45854 | 0.45854 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 700.7915 | 0 | 0.05921 | 4.8093 | 0 | 0 | 0 | 0.45854 | off_peak | 700.7915 |  |  | 0.07 | 0 | 99.93 | 2.2053 | 0
3847 | 760.77 | 92.192 | 27.1 | 14.8222 | 14.8222 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 745.9478 | 0 | 0.05921 | 4.3334 | 0 | 0 | 0 | 14.8222 | off_peak | 745.9478 |  |  | 1.95 | 0 | 98.05 | 64.2309 | 0
3848 | 783.01 | 236.63 | 27.3 | 38.0167 | 38.0167 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 744.9933 | 0 | 0.05921 | 3.9874 | 0 | 0 | 0 | 38.0167 | off_peak | 744.9933 |  |  | 4.86 | 0 | 95.14 | 151.5879 | 0
3849 | 758.58 | 413.084 | 27.5 | 66.3173 | 66.3173 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 692.2627 | 0 | 0.05921 | 3.7203 | 0 | 0 | 0 | 66.3173 | off_peak | 692.2627 |  |  | 8.74 | 0 | 91.26 | 246.718 | 0
3850 | 813.71 | 497.903 | 27.8 | 79.8472 | 79.8472 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 733.8628 | 0 | 0.05921 | 3.5685 | 0 | 0 | 0 | 79.8472 | off_peak | 733.8628 |  |  | 9.81 | 0 | 90.19 | 284.9378 | 0
3851 | 802.01 | 496.423 | 28.2 | 79.4941 | 79.4941 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 722.5159 | 0 | 0.05921 | 3.5233 | 0 | 0 | 0 | 79.4941 | off_peak | 722.5159 |  |  | 9.91 | 0 | 90.09 | 280.0839 | 0
3852 | 899 | 421.918 | 28.5 | 67.4895 | 67.4895 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 831.5105 | 0 | 0.05921 | 3.5622 | 0 | 0 | 0 | 67.4895 | off_peak | 831.5105 |  |  | 7.51 | 0 | 92.49 | 240.4097 | 0
3853 | 813.35 | 523.198 | 28.6 | 83.6596 | 83.6596 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 729.6904 | 0 | 0.05921 | 3.8939 | 0 | 0 | 0 | 83.6596 | off_peak | 729.6904 |  |  | 10.29 | 0 | 89.71 | 325.7659 | 0
3854 | 753.74 | 328.907 | 28.8 | 52.554 | 52.554 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 701.186 | 0 | 0.05921 | 4.2868 | 0 | 0 | 0 | 52.554 | off_peak | 701.186 |  |  | 6.97 | 0 | 93.03 | 225.2874 | 0
3855 | 783.36 | 445.171 | 28.9 | 71.1052 | 71.1052 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 712.2548 | 0 | 0.05921 | 4.6592 | 0 | 0 | 0 | 71.1052 | off_peak | 712.2548 |  |  | 9.08 | 0 | 90.92 | 331.2936 | 0
3856 | 749.3 | 74.1 | 28.8 | 11.84 | 11.84 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 18.9814 | 749.8224 | 0 | 0.05921 | 5.1223 | 0 | 0 | 0 | 11.84 | off_peak | 737.46 | 0 | 100 | 1.58 | 0 | 98.42 | 60.6476 | 0
3857 | 726.23 | 333.608 | 28.5 | 53.3635 | 53.3635 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 30.5453 | 685.2288 | 0 | 0.05921 | 5.6788 | 0 | 0 | 0 | 53.3635 | off_peak | 672.8665 | 0 | 100 | 7.35 | 0 | 92.65 | 303.0421 | 0
3858 | 660.74 | 156.273 | 28.1 | 25.0337 | 25.0337 | 0 | 0 | 8.7006 | 8.7006 | 0 | 0 | 0 | 38.684 | 644.4069 | 0 | 0.05921 | 6.3191 | 0 | 0 | 0 | 25.0337 | off_peak | 635.7063 | 0 | 100 | 3.79 | 0 | 96.21 | 158.1905 | 0
3859 | 629.81 | 57.2162 | 27.9 | 9.1723 | 9.1723 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 50.2479 | 633.0001 | 0 | 0.05921 | 6.9396 | 0 | 0 | 0 | 9.1723 | off_peak | 620.6377 | 0 | 100 | 1.46 | 0 | 98.54 | 63.6517 | 0
3860 | 608 | 0 | 27.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50.2479 | 608 | 0 | 0.05921 | 7.3633 | 0 | 0 | 0 | 0 | off_peak | 608 |  |  | 0 | 0 | 100 | 0 | 0
3861 | 601.16 | 0 | 27.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50.2479 | 601.16 | 0 | 0.05921 | 7.6508 | 0 | 0 | 0 | 0 | off_peak | 601.16 |  |  | 0 | 0 | 100 | 0 | 0
3862 | 583.55 | 0 | 27.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50.2479 | 583.55 | 0 | 0.05921 | 7.947 | 0 | 0 | 0 | 0 | off_peak | 583.55 |  |  | 0 | 0 | 100 | 0 | 0
3863 | 611.7 | 0 | 27.1 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 61.8119 | 624.0624 | 0 | 0.05921 | 8.1744 | 0 | 0 | 0 | 0 | off_peak | 611.7 | 0 | 100 | 0 | 0 | 100 | 0 | 0
3864 | 590.22 | 0 | 27 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 61.8119 | 590.22 | 0 | 0.05921 | 7.8471 | 0 | 0 | 0 | 0 | off_peak | 590.22 |  |  | 0 | 0 | 100 | 0 | 0
3865 | 578.87 | 0 | 26.9 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 73.3758 | 591.2324 | 0 | 0.05921 | 7.4734 | 0 | 0 | 0 | 0 | off_peak | 578.87 | 0 | 100 | 0 | 0 | 100 | 0 | 0
3866 | 617.33 | 0 | 26.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 73.3758 | 617.33 | 0 | 0.05921 | 7.13 | 0 | 0 | 0 | 0 | off_peak | 617.33 |  |  | 0 | 0 | 100 | 0 | 0
3867 | 598.9 | 0 | 26.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 73.3758 | 598.9 | 0 | 0.05921 | 6.787 | 0 | 0 | 0 | 0 | off_peak | 598.9 |  |  | 0 | 0 | 100 | 0 | 0
3868 | 604.24 | 0 | 26.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 73.3758 | 604.24 | 0 | 0.05921 | 6.2831 | 0 | 0 | 0 | 0 | off_peak | 604.24 |  |  | 0 | 0 | 100 | 0 | 0
3869 | 602.72 | 0 | 26.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 73.3758 | 602.72 | 0 | 0.05921 | 5.6151 | 0 | 0 | 0 | 0 | off_peak | 602.72 |  |  | 0 | 0 | 100 | 0 | 0
3870 | 694.65 | 2.85 | 26.8 | 0.45871 | 0.45871 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 73.3758 | 694.1913 | 0 | 0.05921 | 4.9896 | 0 | 0 | 0 | 0.45871 | off_peak | 694.1913 |  |  | 0.07 | 0 | 99.93 | 2.2888 | 0
3871 | 724.67 | 114.982 | 27.1 | 18.4863 | 18.4863 | 0 | 0 | 0.79843 | 0.79843 | 0 | 0 | 0 | 74.1227 | 706.9822 | 0 | 0.05921 | 4.5503 | 0 | 0 | 0 | 18.4863 | off_peak | 706.1837 | 0 | 100 | 2.55 | 0 | 97.45 | 84.1183 | 0
3872 | 741.58 | 304.754 | 27.6 | 48.908 | 48.908 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1227 | 692.672 | 0 | 0.05921 | 4.1775 | 0 | 0 | 0 | 48.908 | off_peak | 692.672 |  |  | 6.6 | 0 | 93.4 | 204.3127 | 0
3873 | 742.43 | 445.975 | 28.2 | 71.4157 | 71.4157 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1227 | 671.0143 | 0 | 0.05921 | 3.9085 | 0 | 0 | 0 | 71.4157 | off_peak | 671.0143 |  |  | 9.62 | 0 | 90.38 | 279.1305 | 0
3874 | 708.53 | 512.895 | 28.6 | 82.0122 | 82.0122 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1227 | 626.5178 | 0 | 0.05921 | 3.7391 | 0 | 0 | 0 | 82.0122 | off_peak | 626.5178 |  |  | 11.57 | 0 | 88.43 | 306.6504 | 0
3875 | 759.5 | 395.567 | 29 | 63.1591 | 63.1591 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1227 | 696.3409 | 0 | 0.05921 | 3.6537 | 0 | 0 | 0 | 63.1591 | off_peak | 696.3409 |  |  | 8.32 | 0 | 91.68 | 230.7617 | 0
3876 | 748.07 | 346.301 | 29.2 | 55.2525 | 55.2525 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1227 | 692.8175 | 0 | 0.05921 | 3.6788 | 0 | 0 | 0 | 55.2525 | off_peak | 692.8175 |  |  | 7.39 | 0 | 92.61 | 203.2642 | 0
3877 | 742.66 | 296.391 | 29.3 | 47.2721 | 47.2721 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1227 | 695.3879 | 0 | 0.05921 | 3.9308 | 0 | 0 | 0 | 47.2721 | off_peak | 695.3879 |  |  | 6.37 | 0 | 93.63 | 185.8186 | 0
3878 | 753.39 | 237.354 | 29.3 | 37.8561 | 37.8561 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1227 | 715.5339 | 0 | 0.05921 | 4.3652 | 0 | 0 | 0 | 37.8561 | off_peak | 715.5339 |  |  | 5.02 | 0 | 94.98 | 165.2512 | 0
3879 | 734.21 | 383.163 | 29.2 | 61.1339 | 61.1339 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1227 | 673.0761 | 0 | 0.05921 | 4.8631 | 0 | 0 | 0 | 61.1339 | off_peak | 673.0761 |  |  | 8.33 | 0 | 91.67 | 297.2993 | 0
3880 | 736.84 | 633.072 | 29 | 101.0808 | 101.0808 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1227 | 635.7592 | 0 | 0.05921 | 5.2198 | 0 | 0 | 0 | 101.0808 | off_peak | 635.7592 |  |  | 13.72 | 0 | 86.28 | 527.6218 | 0
3881 | 650.7 | 327.37 | 28.7 | 52.3275 | 52.3275 | 0 | 0 | 0.051567 | 0.051567 | 0 | 0 | 0 | 74.1709 | 598.424 | 0 | 0.05921 | 5.6928 | 0 | 0 | 0 | 52.3275 | off_peak | 598.3725 | 0 | 100 | 8.04 | 0 | 91.96 | 297.8878 | 0
3882 | 649.26 | 191.117 | 28.3 | 30.5931 | 30.5931 | 0 | 0 | 0.0033305 | 0.0033305 | 0 | 0 | 0 | 74.174 | 618.6702 | 0 | 0.05921 | 6.245 | 0 | 0 | 0 | 30.5931 | off_peak | 618.6669 | 0 | 100 | 4.71 | 0 | 95.29 | 191.0548 | 0
3883 | 601.7 | 53.4669 | 28 | 8.5681 | 8.5681 | 0 | 0 | 0.0002151 | 0.0002151 | 0 | 0 | 0 | 74.1742 | 593.1321 | 0 | 0.05921 | 6.4454 | 0 | 0 | 0 | 8.5681 | off_peak | 593.1319 | 0 | 100 | 1.42 | 0 | 98.58 | 55.2249 | 0
3884 | 595.17 | 0 | 27.5 | 0 | 0 | 0 | 0 | 1.4852e-05 | 1.4852e-05 | 0 | 0 | 0 | 74.1743 | 595.17 | 0 | 0.05921 | 6.7071 | 0 | 0 | 0 | 0 | off_peak | 595.17 | 0 | 100 | 0 | 0 | 100 | 0 | 0
3885 | 572.08 | 0 | 27.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1743 | 572.08 | 0 | 0.05921 | 7.0967 | 0 | 0 | 0 | 0 | off_peak | 572.08 |  |  | 0 | 0 | 100 | 0 | 0
3886 | 588.28 | 0 | 27.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1743 | 588.28 | 0 | 0.05921 | 7.5149 | 0 | 0 | 0 | 0 | off_peak | 588.28 |  |  | 0 | 0 | 100 | 0 | 0
3887 | 594.26 | 0 | 27.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1743 | 594.26 | 0 | 0.05921 | 7.8978 | 0 | 0 | 0 | 0 | off_peak | 594.26 |  |  | 0 | 0 | 100 | 0 | 0
3888 | 566.78 | 0 | 27.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1743 | 566.78 | 0 | 0.05921 | 7.9637 | 0 | 0 | 0 | 0 | off_peak | 566.78 |  |  | 0 | 0 | 100 | 0 | 0
3889 | 567.31 | 0 | 27.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1743 | 567.31 | 0 | 0.05921 | 7.8724 | 0 | 0 | 0 | 0 | off_peak | 567.31 |  |  | 0 | 0 | 100 | 0 | 0
3890 | 562.89 | 0 | 27 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1743 | 562.89 | 0 | 0.05921 | 7.708 | 0 | 0 | 0 | 0 | off_peak | 562.89 |  |  | 0 | 0 | 100 | 0 | 0
3891 | 573.15 | 0 | 27 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1743 | 573.15 | 0 | 0.05921 | 7.3166 | 0 | 0 | 0 | 0 | off_peak | 573.15 |  |  | 0 | 0 | 100 | 0 | 0
3892 | 568.92 | 0 | 26.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1743 | 568.92 | 0 | 0.05921 | 6.6999 | 0 | 0 | 0 | 0 | off_peak | 568.92 |  |  | 0 | 0 | 100 | 0 | 0
3893 | 605.6 | 0 | 27 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1743 | 605.6 | 0 | 0.05921 | 5.8508 | 0 | 0 | 0 | 0 | off_peak | 605.6 |  |  | 0 | 0 | 100 | 0 | 0
3894 | 696 | 2.85 | 27.2 | 0.45804 | 0.45804 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1743 | 695.542 | 0 | 0.05921 | 5.19 | 0 | 0 | 0 | 0.45804 | off_peak | 695.542 |  |  | 0.07 | 0 | 99.93 | 2.3772 | 0
3895 | 729.01 | 86.3502 | 27.7 | 13.8528 | 13.8528 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1743 | 715.1572 | 0 | 0.05921 | 4.7302 | 0 | 0 | 0 | 13.8528 | off_peak | 715.1572 |  |  | 1.9 | 0 | 98.1 | 65.5269 | 0
3896 | 781.44 | 245.097 | 28.1 | 39.2626 | 39.2626 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1743 | 742.1774 | 0 | 0.05921 | 4.3795 | 0 | 0 | 0 | 39.2626 | off_peak | 742.1774 |  |  | 5.02 | 0 | 94.98 | 171.9505 | 0
3897 | 825.67 | 296.075 | 28.4 | 47.3771 | 47.3771 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1743 | 778.2929 | 0 | 0.05921 | 4.1575 | 0 | 0 | 0 | 47.3771 | off_peak | 778.2929 |  |  | 5.74 | 0 | 94.26 | 196.9689 | 0
3898 | 857.47 | 640.906 | 28.6 | 102.4812 | 102.4812 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1743 | 754.9888 | 0 | 0.05921 | 4.0811 | 0 | 0 | 0 | 102.4812 | off_peak | 754.9888 |  |  | 11.95 | 0 | 88.05 | 418.2367 | 0
3899 | 843.35 | 830.891 | 28.7 | 132.8114 | 132.8114 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1743 | 710.5386 | 0 | 0.05921 | 4.2345 | 0 | 0 | 0 | 132.8114 | off_peak | 710.5386 |  |  | 15.75 | 0 | 84.25 | 562.3928 | 0
3900 | 895.93 | 613.911 | 28.8 | 98.0931 | 98.0931 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1743 | 797.8369 | 0 | 0.05921 | 4.47 | 0 | 0 | 0 | 98.0931 | off_peak | 797.8369 |  |  | 10.95 | 0 | 89.05 | 438.4804 | 0
3901 | 870.34 | 197.597 | 28.7 | 31.5843 | 31.5843 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1743 | 838.7557 | 0 | 0.088511 | 4.8038 | 0 | 0 | 0 | 31.5843 | on_peak | 838.7557 |  |  | 3.63 | 0 | 96.37 | 151.726 | 0
3902 | 891.24 | 71.25 | 28.6 | 11.3929 | 11.3929 | 0 | 0 | 0 | 0 | 3.184 | 3.184 | 0 | 70.7704 | 876.663 | 0 | 0.088511 | 5.1763 | 0 | 0 | 0 | 11.3929 | on_peak | 876.663 |  |  | 1.28 | 0.36 | 98.36 | 58.9734 | 0
3903 | 918.89 | 89.3 | 28.4 | 14.2895 | 14.2895 | 0 | 0 | 0 | 0 | 27.9374 | 27.9374 | 0 | 40.904 | 876.663 | 0 | 0.088511 | 5.6636 | 0 | 0 | 0 | 14.2895 | on_peak | 876.663 |  |  | 1.56 | 3.04 | 95.4 | 80.9296 | 0
3904 | 890.2 | 520.256 | 28.2 | 83.3105 | 83.3105 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40.904 | 806.8895 | 0 | 0.088511 | 6.1095 | 0 | 0 | 0 | 83.3105 | on_peak | 806.8895 |  |  | 9.36 | 0 | 90.64 | 508.9828 | 0
3905 | 834.27 | 432.443 | 27.9 | 69.3244 | 69.3244 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40.904 | 764.9456 | 0 | 0.088511 | 6.4985 | 0 | 0 | 0 | 69.3244 | on_peak | 764.9456 |  |  | 8.31 | 0 | 91.69 | 450.5072 | 0
3906 | 902.18 | 219.163 | 27.6 | 35.1721 | 35.1721 | 0 | 0 | 0 | 0 | 31.3238 | 31.3238 | 0 | 7.4174 | 835.6841 | 0 | 0.088511 | 6.6478 | 0 | 0 | 0 | 35.1721 | on_peak | 835.6841 |  |  | 3.9 | 3.47 | 92.63 | 233.8152 | 0
3907 | 827.92 | 60.2373 | 27.4 | 9.6741 | 9.6741 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 818.2459 | 0 | 0.088511 | 6.8297 | 0 | 0 | 0 | 9.6741 | on_peak | 818.2459 |  |  | 1.17 | 0 | 98.83 | 66.0715 | 0
3908 | 851.17 | 0 | 27 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 851.17 | 0 | 0.088511 | 7.1757 | 0 | 0 | 0 | 0 | on_peak | 851.17 |  |  | 0 | 0 | 100 | 0 | 0
3909 | 833.23 | 0 | 27 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 833.23 | 0 | 0.088511 | 7.6279 | 0 | 0 | 0 | 0 | on_peak | 833.23 |  |  | 0 | 0 | 100 | 0 | 0
3910 | 774.08 | 0 | 26.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 774.08 | 0 | 0.05921 | 7.5546 | 0 | 0 | 0 | 0 | off_peak | 774.08 |  |  | 0 | 0 | 100 | 0 | 0
3911 | 803.08 | 0 | 26.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 803.08 | 0 | 0.05921 | 7.6505 | 0 | 0 | 0 | 0 | off_peak | 803.08 |  |  | 0 | 0 | 100 | 0 | 0
3912 | 779.09 | 0 | 26.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 779.09 | 0 | 0.05921 | 7.9571 | 0 | 0 | 0 | 0 | off_peak | 779.09 |  |  | 0 | 0 | 100 | 0 | 0
3913 | 708.01 | 0 | 26.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 708.01 | 0 | 0.05921 | 7.9952 | 0 | 0 | 0 | 0 | off_peak | 708.01 |  |  | 0 | 0 | 100 | 0 | 0
3914 | 645.36 | 0 | 26.8 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 18.9814 | 657.7224 | 0 | 0.05921 | 7.8783 | 0 | 0 | 0 | 0 | off_peak | 645.36 | 0 | 100 | 0 | 0 | 100 | 0 | 0
3915 | 598.45 | 0 | 26.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18.9814 | 598.45 | 0 | 0.05921 | 7.3882 | 0 | 0 | 0 | 0 | off_peak | 598.45 |  |  | 0 | 0 | 100 | 0 | 0
3916 | 634.73 | 0 | 26.7 | 0 | 0 | 0 | 0 | 8.7006 | 8.7006 | 0 | 0 | 0 | 27.12 | 643.4306 | 0 | 0.05921 | 6.6922 | 0 | 0 | 0 | 0 | off_peak | 634.73 | 0 | 100 | 0 | 0 | 100 | 0 | 0
3917 | 660.8 | 0 | 26.7 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 38.684 | 673.1624 | 0 | 0.05921 | 5.8487 | 0 | 0 | 0 | 0 | off_peak | 660.8 | 0 | 100 | 0 | 0 | 100 | 0 | 0
3918 | 721.26 | 2.85 | 26.8 | 0.45871 | 0.45871 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 50.2479 | 733.1637 | 0 | 0.05921 | 5.2647 | 0 | 0 | 0 | 0.45871 | off_peak | 720.8013 | 0 | 100 | 0.06 | 0 | 99.94 | 2.4149 | 0
3919 | 736.35 | 77.8596 | 27.2 | 12.5134 | 12.5134 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 61.8119 | 736.199 | 0 | 0.05921 | 4.7445 | 0 | 0 | 0 | 12.5134 | off_peak | 723.8366 | 0 | 100 | 1.7 | 0 | 98.3 | 59.3696 | 0
3920 | 820.2 | 58.3459 | 27.5 | 9.367 | 9.367 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 73.3758 | 823.1954 | 0 | 0.05921 | 4.3929 | 0 | 0 | 0 | 9.367 | off_peak | 810.833 | 0 | 100 | 1.14 | 0 | 98.86 | 41.1478 | 0
3921 | 827.06 | 196.248 | 27.7 | 31.4832 | 31.4832 | 0 | 0 | 0.79843 | 0.79843 | 0 | 0 | 0 | 74.1227 | 796.3753 | 0 | 0.05921 | 4.1774 | 0 | 0 | 0 | 31.4832 | off_peak | 795.5768 | 0 | 100 | 3.81 | 0 | 96.19 | 131.5173 | 0
3922 | 834.99 | 367.078 | 28 | 58.8244 | 58.8244 | 0 | 0 | 0.051567 | 0.051567 | 0 | 0 | 0 | 74.1709 | 776.2172 | 0 | 0.05921 | 4.1127 | 0 | 0 | 0 | 58.8244 | off_peak | 776.1656 | 0 | 100 | 7.04 | 0 | 92.96 | 241.9299 | 0
3923 | 853.86 | 578.621 | 28.3 | 92.623 | 92.623 | 0 | 0 | 0.0033305 | 0.0033305 | 0 | 0 | 0 | 74.174 | 761.2403 | 0 | 0.05921 | 4.2111 | 0 | 0 | 0 | 92.623 | off_peak | 761.237 | 0 | 100 | 10.85 | 0 | 89.15 | 390.0464 | 0
3924 | 888.28 | 703.52 | 28.6 | 112.4932 | 112.4932 | 0 | 0 | 0.0002151 | 0.0002151 | 0 | 0 | 0 | 74.1742 | 775.787 | 0 | 0.05921 | 4.4437 | 0 | 0 | 0 | 112.4932 | off_peak | 775.7868 | 0 | 100 | 12.66 | 0 | 87.34 | 499.8852 | 0
3925 | 851.09 | 632.256 | 28.7 | 101.0612 | 101.0612 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1742 | 750.0288 | 0 | 0.088511 | 4.6999 | 0 | 0 | 0 | 101.0612 | on_peak | 750.0288 |  |  | 11.87 | 0 | 88.13 | 474.9732 | 0
3926 | 904.81 | 529.362 | 28.8 | 84.5835 | 84.5835 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1742 | 820.2265 | 0 | 0.088511 | 5.0682 | 0 | 0 | 0 | 84.5835 | on_peak | 820.2265 |  |  | 9.35 | 0 | 90.65 | 428.6891 | 0
3927 | 887.11 | 306.056 | 28.7 | 48.9207 | 48.9207 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1742 | 838.1893 | 0 | 0.088511 | 5.5106 | 0 | 0 | 0 | 48.9207 | on_peak | 838.1893 |  |  | 5.51 | 0 | 94.49 | 269.5843 | 0
3928 | 908.91 | 464.379 | 28.6 | 74.2544 | 74.2544 | 0 | 0 | 0 | 0 | 62.4453 | 62.4453 | 0 | 7.4174 | 772.2103 | 0 | 0.088511 | 5.9862 | 0 | 0 | 0 | 74.2544 | on_peak | 772.2103 |  |  | 8.17 | 6.87 | 84.96 | 444.5034 | 0
3929 | 877.63 | 417.657 | 28.4 | 66.8323 | 66.8323 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 810.7977 | 0 | 0.088511 | 6.598 | 0 | 0 | 0 | 66.8323 | on_peak | 810.7977 |  |  | 7.62 | 0 | 92.38 | 440.9615 | 0
3930 | 907.37 | 209.738 | 28.1 | 33.5984 | 33.5984 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 873.7716 | 0 | 0.088511 | 7.1252 | 0 | 0 | 0 | 33.5984 | on_peak | 873.7716 |  |  | 3.7 | 0 | 96.3 | 239.3939 | 0
3931 | 864.63 | 57.2702 | 27.9 | 9.1809 | 9.1809 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 855.4491 | 0 | 0.088511 | 7.5565 | 0 | 0 | 0 | 9.1809 | on_peak | 855.4491 |  |  | 1.06 | 0 | 98.94 | 69.3753 | 0
3932 | 861.5 | 0 | 27.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 861.5 | 0 | 0.088511 | 7.8746 | 0 | 0 | 0 | 0 | on_peak | 861.5 |  |  | 0 | 0 | 100 | 0 | 0
3933 | 835.83 | 0 | 27.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 835.83 | 0 | 0.088511 | 7.9782 | 0 | 0 | 0 | 0 | on_peak | 835.83 |  |  | 0 | 0 | 100 | 0 | 0
3934 | 789.6 | 0 | 27.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 789.6 | 0 | 0.05921 | 8.1413 | 0 | 0 | 0 | 0 | off_peak | 789.6 |  |  | 0 | 0 | 100 | 0 | 0
3935 | 842.21 | 0 | 27 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 18.9814 | 854.5724 | 0 | 0.05921 | 8.2944 | 0 | 0 | 0 | 0 | off_peak | 842.21 | 0 | 100 | 0 | 0 | 100 | 0 | 0
3936 | 790.49 | 0 | 26.9 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 30.5453 | 802.8524 | 0 | 0.05921 | 8.1781 | 0 | 0 | 0 | 0 | off_peak | 790.49 | 0 | 100 | 0 | 0 | 100 | 0 | 0
3937 | 732.61 | 0 | 26.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30.5453 | 732.61 | 0 | 0.05921 | 7.8889 | 0 | 0 | 0 | 0 | off_peak | 732.61 |  |  | 0 | 0 | 100 | 0 | 0
3938 | 667.72 | 0 | 26.7 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 42.1093 | 680.0824 | 0 | 0.05921 | 7.5531 | 0 | 0 | 0 | 0 | off_peak | 667.72 | 0 | 100 | 0 | 0 | 100 | 0 | 0
3939 | 656.67 | 0 | 26.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 42.1093 | 656.67 | 0 | 0.05921 | 7.2036 | 0 | 0 | 0 | 0 | off_peak | 656.67 |  |  | 0 | 0 | 100 | 0 | 0
3940 | 665.66 | 0 | 26.6 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 53.6732 | 678.0224 | 0 | 0.05921 | 6.5875 | 0 | 0 | 0 | 0 | off_peak | 665.66 | 0 | 100 | 0 | 0 | 100 | 0 | 0
3941 | 668.89 | 0 | 26.6 | 0 | 0 | 0 | 0 | 8.7006 | 8.7006 | 0 | 0 | 0 | 61.8119 | 677.5906 | 0 | 0.05921 | 5.8012 | 0 | 0 | 0 | 0 | off_peak | 668.89 | 0 | 100 | 0 | 0 | 100 | 0 | 0
3942 | 742.28 | 2.85 | 26.9 | 0.45854 | 0.45854 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 73.3758 | 754.1838 | 0 | 0.05921 | 5.1602 | 0 | 0 | 0 | 0.45854 | off_peak | 741.8215 | 0 | 100 | 0.06 | 0 | 99.94 | 2.3662 | 0
3943 | 763.37 | 93.668 | 27.4 | 15.0431 | 15.0431 | 0 | 0 | 0.79843 | 0.79843 | 0 | 0 | 0 | 74.1227 | 749.1253 | 0 | 0.05921 | 4.6764 | 0 | 0 | 0 | 15.0431 | off_peak | 748.3269 | 0 | 100 | 1.97 | 0 | 98.03 | 70.3475 | 0
3944 | 791.77 | 269.289 | 27.8 | 43.1851 | 43.1851 | 0 | 0 | 0.051567 | 0.051567 | 0 | 0 | 0 | 74.1709 | 748.6365 | 0 | 0.05921 | 4.3599 | 0 | 0 | 0 | 43.1851 | off_peak | 748.5849 | 0 | 100 | 5.45 | 0 | 94.55 | 188.2844 | 0
3945 | 825.64 | 410.356 | 28.2 | 65.7118 | 65.7118 | 0 | 0 | 0.0033305 | 0.0033305 | 0 | 0 | 0 | 74.174 | 759.9315 | 0 | 0.05921 | 4.1738 | 0 | 0 | 0 | 65.7118 | off_peak | 759.9282 | 0 | 100 | 7.96 | 0 | 92.04 | 274.2662 | 0
3946 | 851.6 | 567.008 | 28.5 | 90.6979 | 90.6979 | 0 | 0 | 0.0002151 | 0.0002151 | 0 | 0 | 0 | 74.1742 | 760.9023 | 0 | 0.05921 | 4.1124 | 0 | 0 | 0 | 90.6979 | off_peak | 760.9021 | 0 | 100 | 10.65 | 0 | 89.35 | 372.9881 | 0
3947 | 861.28 | 629.349 | 28.7 | 100.5965 | 100.5965 | 0 | 0 | 1.3893e-05 | 1.3893e-05 | 0 | 0 | 0 | 74.1743 | 760.6835 | 0 | 0.05921 | 4.2363 | 0 | 0 | 0 | 100.5965 | off_peak | 760.6835 | 0 | 100 | 11.68 | 0 | 88.32 | 426.1616 | 0
3948 | 928.85 | 395.567 | 28.9 | 63.1821 | 63.1821 | 0 | 0 | 8.9726e-07 | 8.9726e-07 | 0 | 0 | 0 | 74.1743 | 865.6679 | 0 | 0.05921 | 4.4545 | 0 | 0 | 0 | 63.1821 | off_peak | 865.6679 | 0 | 100 | 6.8 | 0 | 93.2 | 281.4449 | 0
3949 | 878.09 | 55.1 | 28.9 | 8.8009 | 8.8009 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1743 | 869.2891 | 0 | 0.088511 | 4.8749 | 0 | 0 | 0 | 8.8009 | on_peak | 869.2891 |  |  | 1 | 0 | 99 | 42.903 | 0
3950 | 866.09 | 153.864 | 28.9 | 24.576 | 24.576 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1743 | 841.514 | 0 | 0.088511 | 5.2915 | 0 | 0 | 0 | 24.576 | on_peak | 841.514 |  |  | 2.84 | 0 | 97.16 | 130.0431 | 0
3951 | 884.21 | 94.05 | 28.8 | 15.0277 | 15.0277 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1743 | 869.1823 | 0 | 0.088511 | 5.8415 | 0 | 0 | 0 | 15.0277 | on_peak | 869.1823 |  |  | 1.7 | 0 | 98.3 | 87.7836 | 0
3952 | 831.04 | 114 | 28.6 | 18.2287 | 18.2287 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1743 | 812.8113 | 0 | 0.088511 | 6.358 | 0 | 0 | 0 | 18.2287 | on_peak | 812.8113 |  |  | 2.19 | 0 | 97.81 | 115.8973 | 0
3953 | 862.38 | 78.4315 | 28.3 | 12.555 | 12.555 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1743 | 849.825 | 0 | 0.088511 | 6.761 | 0 | 0 | 0 | 12.555 | on_peak | 849.825 |  |  | 1.46 | 0 | 98.54 | 84.8838 | 0
3954 | 862.53 | 109.054 | 27.9 | 17.4823 | 17.4823 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1743 | 845.0477 | 0 | 0.088511 | 7.1846 | 0 | 0 | 0 | 17.4823 | on_peak | 845.0477 |  |  | 2.03 | 0 | 97.97 | 125.6031 | 0
3955 | 862 | 54.4234 | 27.8 | 8.7277 | 8.7277 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1743 | 853.2723 | 0 | 0.088511 | 7.6773 | 0 | 0 | 0 | 8.7277 | on_peak | 853.2723 |  |  | 1.01 | 0 | 98.99 | 67.0051 | 0
3956 | 838.2 | 0 | 27.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1743 | 838.2 | 0 | 0.088511 | 8.0404 | 0 | 0 | 0 | 0 | on_peak | 838.2 |  |  | 0 | 0 | 100 | 0 | 0
3957 | 827.03 | 0 | 27 | 0 | 0 | 0 | 0 | 0 | 0 | 62.4453 | 62.4453 | 0 | 7.4174 | 764.5847 | 0 | 0.088511 | 8.4328 | 0 | 0 | 0 | 0 | on_peak | 764.5847 |  |  | 0 | 7.55 | 92.45 | 0 | 0
3958 | 797.3 | 0 | 26.9 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 18.9814 | 809.6624 | 0 | 0.05921 | 8.6588 | 0 | 0 | 0 | 0 | off_peak | 797.3 | 0 | 100 | 0 | 0 | 100 | 0 | 0
3959 | 829.82 | 0 | 26.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18.9814 | 829.82 | 0 | 0.05921 | 8.7343 | 0 | 0 | 0 | 0 | off_peak | 829.82 |  |  | 0 | 0 | 100 | 0 | 0
3960 | 772.1 | 0 | 26.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18.9814 | 772.1 | 0 | 0.05921 | 8.6216 | 0 | 0 | 0 | 0 | off_peak | 772.1 |  |  | 0 | 0 | 100 | 0 | 0
3961 | 716.96 | 0 | 26.5 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 30.5453 | 729.3224 | 0 | 0.05921 | 8.58 | 0 | 0 | 0 | 0 | off_peak | 716.96 | 0 | 100 | 0 | 0 | 100 | 0 | 0
3962 | 622.6 | 0 | 26.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30.5453 | 622.6 | 0 | 0.05921 | 8.3438 | 0 | 0 | 0 | 0 | off_peak | 622.6 |  |  | 0 | 0 | 100 | 0 | 0
3963 | 584.87 | 0 | 26.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30.5453 | 584.87 | 0 | 0.05921 | 7.9313 | 0 | 0 | 0 | 0 | off_peak | 584.87 |  |  | 0 | 0 | 100 | 0 | 0
3964 | 600.47 | 0 | 26.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30.5453 | 600.47 | 0 | 0.05921 | 7.1611 | 0 | 0 | 0 | 0 | off_peak | 600.47 |  |  | 0 | 0 | 100 | 0 | 0
3965 | 596.8 | 0 | 26.3 | 0 | 0 | 0 | 0 | 8.7006 | 8.7006 | 0 | 0 | 0 | 38.684 | 605.5006 | 0 | 0.05921 | 6.3741 | 0 | 0 | 0 | 0 | off_peak | 596.8 | 0 | 100 | 0 | 0 | 100 | 0 | 0
3966 | 691.21 | 2.85 | 26.6 | 0.45904 | 0.45904 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 50.2479 | 703.1133 | 0 | 0.05921 | 5.7299 | 0 | 0 | 0 | 0.45904 | off_peak | 690.751 | 0 | 100 | 0.07 | 0 | 99.93 | 2.6302 | 0
3967 | 755.4 | 111.578 | 27 | 17.9455 | 17.9455 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 61.8119 | 749.8169 | 0 | 0.05921 | 5.2199 | 0 | 0 | 0 | 17.9455 | off_peak | 737.4545 | 0 | 100 | 2.38 | 0 | 97.62 | 93.6744 | 0
3968 | 820.67 | 322.498 | 27.5 | 51.7745 | 51.7745 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 73.3758 | 781.2579 | 0 | 0.05921 | 4.8794 | 0 | 0 | 0 | 51.7745 | off_peak | 768.8955 | 0 | 100 | 6.31 | 0 | 93.69 | 252.6305 | 0
3969 | 872.49 | 487.646 | 27.9 | 78.1739 | 78.1739 | 0 | 0 | 0.79843 | 0.79843 | 0 | 0 | 0 | 74.1227 | 795.1145 | 0 | 0.05921 | 4.6265 | 0 | 0 | 0 | 78.1739 | off_peak | 794.3161 | 0 | 100 | 8.96 | 0 | 91.04 | 361.6738 | 0
3970 | 823.71 | 585.214 | 28.3 | 93.6784 | 93.6784 | 0 | 0 | 0.051567 | 0.051567 | 0 | 0 | 0 | 74.1709 | 730.0832 | 0 | 0.05921 | 4.5303 | 0 | 0 | 0 | 93.6784 | off_peak | 730.0316 | 0 | 100 | 11.37 | 0 | 88.63 | 424.3955 | 0
3971 | 855.71 | 619.72 | 28.8 | 99.0212 | 99.0212 | 0 | 0 | 0.0033305 | 0.0033305 | 0 | 0 | 0 | 74.174 | 756.6921 | 0 | 0.05921 | 4.5473 | 0 | 0 | 0 | 99.0212 | off_peak | 756.6888 | 0 | 100 | 11.57 | 0 | 88.43 | 450.2764 | 0
3972 | 902.59 | 455.941 | 29.2 | 72.7456 | 72.7454 | 0 | 0.0002151 | 0.0002151 | 0 | 0 | 0 | 0 | 74.1742 | 829.8446 | 0 | 0.05921 | 4.7219 | 0 | 0 | 0.00020121 | 72.7454 | off_peak | 829.8446 | 100 | 0 | 8.06 | 0 | 91.94 | 343.4974 | 0
3973 | 821.69 | 610.631 | 29.5 | 97.3197 | 97.3197 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1742 | 724.3703 | 0 | 0.088511 | 4.9242 | 0 | 0 | 0.00020121 | 97.3197 | on_peak | 724.3703 |  |  | 11.84 | 0 | 88.16 | 479.2201 | 0
3974 | 872.32 | 810.772 | 29.7 | 129.1227 | 129.1227 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1742 | 743.1973 | 0 | 0.088511 | 5.2516 | 0 | 0 | 0.00020121 | 129.1227 | on_peak | 743.1973 |  |  | 14.8 | 0 | 85.2 | 678.1001 | 0
3975 | 877.34 | 516.618 | 29.8 | 82.2459 | 82.2459 | 0 | 0 | 0 | 0 | 62.4451 | 62.4451 | 0 | 7.4176 | 732.649 | 0 | 0.088511 | 5.6745 | 0 | 0 | 0.00020121 | 82.2459 | on_peak | 732.649 |  |  | 9.37 | 7.12 | 83.51 | 466.7016 | 0
3976 | 844.25 | 242.537 | 29.7 | 38.6262 | 38.6262 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4176 | 805.6238 | 0 | 0.088511 | 6.1547 | 0 | 0 | 0.00020121 | 38.6262 | on_peak | 805.6238 |  |  | 4.58 | 0 | 95.42 | 237.7311 | 0
3977 | 866.36 | 126.808 | 29.4 | 20.2175 | 20.2175 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4176 | 846.1425 | 0 | 0.088511 | 6.7237 | 0 | 0 | 0.00020121 | 20.2175 | on_peak | 846.1425 |  |  | 2.33 | 0 | 97.67 | 135.9371 | 0
3978 | 860.32 | 15.2 | 28.9 | 2.4278 | 2.4278 | 0 | 0 | 0 | 0 | 0.00018821 | 0.00018821 | 0 | 7.4174 | 857.892 | 0 | 0.088511 | 7.1871 | 0.00018821 | 0 | 0 | 2.428 | on_peak | 857.892 |  |  | 0.28 | 0 | 99.72 | 17.4504 | 0
3979 | 811.44 | 30.4 | 28.7 | 4.8592 | 4.8592 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 806.5808 | 0 | 0.088511 | 7.7672 | 0 | 0 | 0 | 4.8592 | on_peak | 806.5808 |  |  | 0.6 | 0 | 99.4 | 37.7426 | 0
3980 | 831.69 | 0 | 27.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 831.69 | 0 | 0.088511 | 8.196 | 0 | 0 | 0 | 0 | on_peak | 831.69 |  |  | 0 | 0 | 100 | 0 | 0
3981 | 832.65 | 0 | 27.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 832.65 | 0 | 0.088511 | 8.5597 | 0 | 0 | 0 | 0 | on_peak | 832.65 |  |  | 0 | 0 | 100 | 0 | 0
3982 | 814.72 | 0 | 27.4 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 18.9814 | 827.0824 | 0 | 0.05921 | 8.7794 | 0 | 0 | 0 | 0 | off_peak | 814.72 | 0 | 100 | 0 | 0 | 100 | 0 | 0
3983 | 837.09 | 0 | 27.2 | 0 | 0 | 0 | 0 | 8.7006 | 8.7006 | 0 | 0 | 0 | 27.12 | 845.7906 | 0 | 0.05921 | 8.8646 | 0 | 0 | 0 | 0 | off_peak | 837.09 | 0 | 100 | 0 | 0 | 100 | 0 | 0
3984 | 825.56 | 0 | 27.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27.12 | 825.56 | 0 | 0.05921 | 8.9026 | 0 | 0 | 0 | 0 | off_peak | 825.56 |  |  | 0 | 0 | 100 | 0 | 0
3985 | 748.13 | 0 | 27 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27.12 | 748.13 | 0 | 0.05921 | 8.6417 | 0 | 0 | 0 | 0 | off_peak | 748.13 |  |  | 0 | 0 | 100 | 0 | 0
3986 | 667.74 | 0 | 26.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27.12 | 667.74 | 0 | 0.05921 | 8.283 | 0 | 0 | 0 | 0 | off_peak | 667.74 |  |  | 0 | 0 | 100 | 0 | 0
3987 | 634.21 | 0 | 26.9 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 38.684 | 646.5724 | 0 | 0.05921 | 7.8721 | 0 | 0 | 0 | 0 | off_peak | 634.21 | 0 | 100 | 0 | 0 | 100 | 0 | 0
3988 | 603.23 | 0 | 26.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 38.684 | 603.23 | 0 | 0.05921 | 7.262 | 0 | 0 | 0 | 0 | off_peak | 603.23 |  |  | 0 | 0 | 100 | 0 | 0
3989 | 625.93 | 0 | 26.9 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 50.2479 | 638.2924 | 0 | 0.05921 | 6.4391 | 0 | 0 | 0 | 0 | off_peak | 625.93 | 0 | 100 | 0 | 0 | 100 | 0 | 0
3990 | 707.02 | 3.8 | 27.3 | 0.6105 | 0.6105 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 61.8119 | 718.7719 | 0 | 0.05921 | 5.7452 | 0 | 0 | 0 | 0.6105 | off_peak | 706.4095 | 0 | 100 | 0.09 | 0 | 99.91 | 3.5074 | 0
3991 | 754.26 | 109.338 | 27.9 | 17.5278 | 17.5278 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 61.8119 | 736.7322 | 0 | 0.05921 | 5.1735 | 0 | 0 | 0 | 17.5278 | off_peak | 736.7322 |  |  | 2.32 | 0 | 97.68 | 90.6801 | 0
3992 | 807.63 | 321.496 | 28.4 | 51.4449 | 51.4449 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 73.3758 | 768.5475 | 0 | 0.05921 | 4.7958 | 0 | 0 | 0 | 51.4449 | off_peak | 756.1851 | 0 | 100 | 6.37 | 0 | 93.63 | 246.7194 | 0
3993 | 838.26 | 503.836 | 28.8 | 80.5049 | 80.5049 | 0 | 0 | 0.79843 | 0.79843 | 0 | 0 | 0 | 74.1227 | 758.5536 | 0 | 0.05921 | 4.5129 | 0 | 0 | 0 | 80.5049 | off_peak | 757.7551 | 0 | 100 | 9.6 | 0 | 90.4 | 363.3068 | 0
3994 | 871.19 | 691.949 | 29 | 110.4816 | 110.4816 | 0 | 0 | 0.051567 | 0.051567 | 0 | 0 | 0 | 74.1709 | 760.76 | 0 | 0.05921 | 4.3944 | 0 | 0 | 0 | 110.4816 | off_peak | 760.7084 | 0 | 100 | 12.68 | 0 | 87.32 | 485.4948 | 0
3995 | 858.37 | 645.57 | 29.2 | 103.0011 | 103.0011 | 0 | 0 | 0.0033305 | 0.0033305 | 0 | 0 | 0 | 74.174 | 755.3723 | 0 | 0.05921 | 4.4641 | 0 | 0 | 0 | 103.0011 | off_peak | 755.3689 | 0 | 100 | 12 | 0 | 88 | 459.8073 | 0
3996 | 930.74 | 569.647 | 29.3 | 90.8543 | 90.8543 | 0 | 0 | 0.0002151 | 0.0002151 | 0 | 0 | 0 | 74.1742 | 839.8859 | 0 | 0.05921 | 4.6512 | 0 | 0 | 0 | 90.8543 | off_peak | 839.8857 | 0 | 100 | 9.76 | 0 | 90.24 | 422.5799 | 0
3997 | 838.14 | 169.1 | 29.3 | 26.9701 | 26.9701 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1742 | 811.1699 | 0 | 0.088511 | 4.9636 | 0 | 0 | 0 | 26.9701 | on_peak | 811.1699 |  |  | 3.22 | 0 | 96.78 | 133.8681 | 0
3998 | 853.63 | 560.922 | 29.2 | 89.4954 | 89.4954 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1742 | 764.1346 | 0 | 0.088511 | 5.3875 | 0 | 0 | 0 | 89.4954 | on_peak | 764.1346 |  |  | 10.48 | 0 | 89.52 | 482.16 | 0
3999 | 878.68 | 784.548 | 29.2 | 125.1751 | 125.1751 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1742 | 753.5049 | 0 | 0.088511 | 5.7801 | 0 | 0 | 0 | 125.1751 | on_peak | 753.5049 |  |  | 14.25 | 0 | 85.75 | 723.5248 | 0
4000 | 871.51 | 638.79 | 29 | 101.9938 | 101.9938 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1742 | 769.5162 | 0 | 0.088511 | 6.3657 | 0 | 0 | 0 | 101.9938 | on_peak | 769.5162 |  |  | 11.7 | 0 | 88.3 | 649.265 | 0
4001 | 846.98 | 408.809 | 28.8 | 65.3211 | 65.3211 | 0 | 0 | 0 | 0 | 47.4083 | 47.4083 | 0 | 23.4926 | 734.2506 | 0 | 0.088511 | 6.9056 | 0 | 0 | 0 | 65.3211 | on_peak | 734.2506 |  |  | 7.71 | 5.6 | 86.69 | 451.0782 | 0
4002 | 882.93 | 256.16 | 28.5 | 40.975 | 40.975 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 23.4926 | 841.955 | 0 | 0.088511 | 7.238 | 0 | 0 | 0 | 40.975 | on_peak | 841.955 |  |  | 4.64 | 0 | 95.36 | 296.5754 | 0
4003 | 833.31 | 65.8683 | 28.3 | 10.5439 | 10.5439 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 23.4926 | 822.7661 | 0 | 0.088511 | 7.4991 | 0 | 0 | 0 | 10.5439 | on_peak | 822.7661 |  |  | 1.27 | 0 | 98.73 | 79.0693 | 0
4004 | 891.7 | 0 | 27.7 | 0 | 0 | 0 | 0 | 0 | 0 | 15.037 | 15.037 | 0 | 7.4174 | 876.663 | 0 | 0.088511 | 7.7614 | 0 | 0 | 0 | 0 | on_peak | 876.663 |  |  | 0 | 1.69 | 98.31 | 0 | 0
4005 | 858.59 | 0 | 27.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 858.59 | 0 | 0.088511 | 7.8077 | 0 | 0 | 0 | 0 | on_peak | 858.59 |  |  | 0 | 0 | 100 | 0 | 0
4006 | 865.19 | 0 | 27.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 865.19 | 0 | 0.05921 | 7.8095 | 0 | 0 | 0 | 0 | off_peak | 865.19 |  |  | 0 | 0 | 100 | 0 | 0
4007 | 871.31 | 0 | 27.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 871.31 | 0 | 0.05921 | 8.148 | 0 | 0 | 0 | 0 | off_peak | 871.31 |  |  | 0 | 0 | 100 | 0 | 0
4008 | 856.1 | 0 | 27.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 856.1 | 0 | 0.05921 | 8.207 | 0 | 0 | 0 | 0 | off_peak | 856.1 |  |  | 0 | 0 | 100 | 0 | 0
4009 | 804.36 | 0 | 27.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 804.36 | 0 | 0.05921 | 8.0591 | 0 | 0 | 0 | 0 | off_peak | 804.36 |  |  | 0 | 0 | 100 | 0 | 0
4010 | 701.03 | 0 | 27.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 701.03 | 0 | 0.05921 | 7.7395 | 0 | 0 | 0 | 0 | off_peak | 701.03 |  |  | 0 | 0 | 100 | 0 | 0
4011 | 677.68 | 0 | 27.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 677.68 | 0 | 0.05921 | 7.2794 | 0 | 0 | 0 | 0 | off_peak | 677.68 |  |  | 0 | 0 | 100 | 0 | 0
4012 | 677.49 | 0 | 27.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 677.49 | 0 | 0.05921 | 6.7524 | 0 | 0 | 0 | 0 | off_peak | 677.49 |  |  | 0 | 0 | 100 | 0 | 0
4013 | 684.8 | 0 | 27.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 684.8 | 0 | 0.05921 | 6.1154 | 0 | 0 | 0 | 0 | off_peak | 684.8 |  |  | 0 | 0 | 100 | 0 | 0
4014 | 784.13 | 2.85 | 27.3 | 0.45788 | 0.45788 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 783.6721 | 0 | 0.05921 | 5.5239 | 0 | 0 | 0 | 0.45788 | off_peak | 783.6721 |  |  | 0.06 | 0 | 99.94 | 2.5293 | 0
4015 | 759.69 | 94.8954 | 27.4 | 15.2402 | 15.2402 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 744.4498 | 0 | 0.05921 | 5.1151 | 0 | 0 | 0 | 15.2402 | off_peak | 744.4498 |  |  | 2.01 | 0 | 97.99 | 77.9553 | 0
4016 | 846.16 | 241.434 | 27.5 | 38.7603 | 38.7603 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 807.3997 | 0 | 0.05921 | 4.7925 | 0 | 0 | 0 | 38.7603 | off_peak | 807.3997 |  |  | 4.58 | 0 | 95.42 | 185.7598 | 0
4017 | 801.8 | 373.654 | 27.5 | 59.9872 | 59.9872 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 741.8128 | 0 | 0.05921 | 4.5398 | 0 | 0 | 0 | 59.9872 | off_peak | 741.8128 |  |  | 7.48 | 0 | 92.52 | 272.3309 | 0
4018 | 807.17 | 594.211 | 27.6 | 95.3612 | 95.3612 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 711.8088 | 0 | 0.05921 | 4.3984 | 0 | 0 | 0 | 95.3612 | off_peak | 711.8088 |  |  | 11.81 | 0 | 88.19 | 419.4389 | 0
4019 | 800.05 | 467.294 | 27.8 | 74.9386 | 74.9386 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 725.1114 | 0 | 0.05921 | 4.3651 | 0 | 0 | 0 | 74.9386 | off_peak | 725.1114 |  |  | 9.37 | 0 | 90.63 | 327.1178 | 0
4020 | 832.11 | 483.802 | 28.3 | 77.4448 | 77.4448 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 754.6652 | 0 | 0.05921 | 4.4786 | 0 | 0 | 0 | 77.4448 | off_peak | 754.6652 |  |  | 9.31 | 0 | 90.69 | 346.8423 | 0
4021 | 770.34 | 689.279 | 28.8 | 110.1356 | 110.1356 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 660.2044 | 0 | 0.05921 | 4.7096 | 0 | 0 | 0 | 110.1356 | off_peak | 660.2044 |  |  | 14.3 | 0 | 85.7 | 518.6953 | 0
4022 | 798.18 | 748.962 | 29.2 | 119.4973 | 119.4973 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 18.9814 | 691.0451 | 0 | 0.05921 | 5.1402 | 0 | 0 | 0 | 119.4973 | off_peak | 678.6827 | 0 | 100 | 14.97 | 0 | 85.03 | 614.2424 | 0
4023 | 788.04 | 682.233 | 29.3 | 108.8109 | 108.8109 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18.9814 | 679.2291 | 0 | 0.05921 | 5.6522 | 0 | 0 | 0 | 108.8109 | off_peak | 679.2291 |  |  | 13.81 | 0 | 86.19 | 615.0159 | 0
4024 | 730.91 | 473.693 | 29.2 | 75.578 | 75.578 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18.9814 | 655.332 | 0 | 0.05921 | 6.2255 | 0 | 0 | 0 | 75.578 | off_peak | 655.332 |  |  | 10.34 | 0 | 89.66 | 470.5136 | 0
4025 | 730.27 | 43.7 | 28.9 | 6.98 | 6.98 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 30.5453 | 735.6524 | 0 | 0.05921 | 6.6606 | 0 | 0 | 0 | 6.98 | off_peak | 723.29 | 0 | 100 | 0.96 | 0 | 99.04 | 46.4911 | 0
4026 | 677.69 | 40.3968 | 28.5 | 6.4618 | 6.4618 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 42.1093 | 683.5906 | 0 | 0.05921 | 7.01 | 0 | 0 | 0 | 6.4618 | off_peak | 671.2282 | 0 | 100 | 0.95 | 0 | 99.05 | 45.2972 | 0
4027 | 608.56 | 43.9791 | 28.2 | 7.0425 | 7.0425 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 42.1093 | 601.5175 | 0 | 0.05921 | 6.7122 | 0 | 0 | 0 | 7.0425 | off_peak | 601.5175 |  |  | 1.16 | 0 | 98.84 | 47.2709 | 0
4028 | 597.68 | 0 | 27.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 42.1093 | 597.68 | 0 | 0.05921 | 6.4889 | 0 | 0 | 0 | 0 | off_peak | 597.68 |  |  | 0 | 0 | 100 | 0 | 0
4029 | 582.84 | 0 | 27.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 42.1093 | 582.84 | 0 | 0.05921 | 6.7026 | 0 | 0 | 0 | 0 | off_peak | 582.84 |  |  | 0 | 0 | 100 | 0 | 0
4030 | 607.49 | 0 | 27.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 42.1093 | 607.49 | 0 | 0.05921 | 7.1401 | 0 | 0 | 0 | 0 | off_peak | 607.49 |  |  | 0 | 0 | 100 | 0 | 0
4031 | 569.34 | 0 | 27.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 42.1093 | 569.34 | 0 | 0.05921 | 7.2938 | 0 | 0 | 0 | 0 | off_peak | 569.34 |  |  | 0 | 0 | 100 | 0 | 0
4032 | 568.25 | 0 | 27.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 42.1093 | 568.25 | 0 | 0.05921 | 7.2902 | 0 | 0 | 0 | 0 | off_peak | 568.25 |  |  | 0 | 0 | 100 | 0 | 0
4033 | 600.68 | 0 | 27.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 42.1093 | 600.68 | 0 | 0.05921 | 7.1994 | 0 | 0 | 0 | 0 | off_peak | 600.68 |  |  | 0 | 0 | 100 | 0 | 0
4034 | 597.35 | 0 | 27.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 42.1093 | 597.35 | 0 | 0.05921 | 6.828 | 0 | 0 | 0 | 0 | off_peak | 597.35 |  |  | 0 | 0 | 100 | 0 | 0
4035 | 572.73 | 0 | 27.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 42.1093 | 572.73 | 0 | 0.05921 | 6.5085 | 0 | 0 | 0 | 0 | off_peak | 572.73 |  |  | 0 | 0 | 100 | 0 | 0
4036 | 606.88 | 0 | 27.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 42.1093 | 606.88 | 0 | 0.05921 | 6.1064 | 0 | 0 | 0 | 0 | off_peak | 606.88 |  |  | 0 | 0 | 100 | 0 | 0
4037 | 585.05 | 0 | 27.2 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 53.6732 | 597.4124 | 0 | 0.05921 | 5.4545 | 0 | 0 | 0 | 0 | off_peak | 585.05 | 0 | 100 | 0 | 0 | 100 | 0 | 0
4038 | 664.23 | 2.85 | 27.3 | 0.45788 | 0.45788 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 53.6732 | 663.7721 | 0 | 0.05921 | 4.9312 | 0 | 0 | 0 | 0.45788 | off_peak | 663.7721 |  |  | 0.07 | 0 | 99.93 | 2.2579 | 0
4039 | 677.61 | 122.176 | 27.5 | 19.6144 | 19.6144 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 53.6732 | 657.9956 | 0 | 0.05921 | 4.5218 | 0 | 0 | 0 | 19.6144 | off_peak | 657.9956 |  |  | 2.89 | 0 | 97.11 | 88.6923 | 0
4040 | 713.02 | 237.653 | 27.6 | 38.1394 | 38.1394 | 0 | 0 | 8.7006 | 8.7006 | 0 | 0 | 0 | 61.8119 | 683.5812 | 0 | 0.05921 | 4.2023 | 0 | 0 | 0 | 38.1394 | off_peak | 674.8806 | 0 | 100 | 5.35 | 0 | 94.65 | 160.275 | 0
4041 | 728.59 | 504.626 | 27.7 | 80.9548 | 80.9548 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 61.8119 | 647.6352 | 0 | 0.05921 | 3.9646 | 0 | 0 | 0 | 80.9548 | off_peak | 647.6352 |  |  | 11.11 | 0 | 88.89 | 320.9536 | 0
4042 | 692.99 | 529.09 | 27.7 | 84.8795 | 84.8795 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 61.8119 | 608.1105 | 0 | 0.05921 | 3.7992 | 0 | 0 | 0 | 84.8795 | off_peak | 608.1105 |  |  | 12.25 | 0 | 87.75 | 322.47 | 0
4043 | 696.48 | 676.462 | 27.6 | 108.5611 | 108.5611 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 61.8119 | 587.9189 | 0 | 0.05921 | 3.7539 | 0 | 0 | 0 | 108.5611 | off_peak | 587.9189 |  |  | 15.59 | 0 | 84.41 | 407.5289 | 0
4044 | 733.7 | 732.358 | 27.5 | 117.5742 | 117.5742 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 61.8119 | 616.1258 | 0 | 0.05921 | 3.7451 | 0 | 0 | 0 | 117.5742 | off_peak | 616.1258 |  |  | 16.02 | 0 | 83.98 | 440.3293 | 0
4045 | 728.76 | 581.119 | 27.4 | 93.3279 | 93.3279 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 61.8119 | 635.4321 | 0 | 0.05921 | 3.7925 | 0 | 0 | 0 | 93.3279 | off_peak | 635.4321 |  |  | 12.81 | 0 | 87.19 | 353.945 | 0
4046 | 700.43 | 733.239 | 27.3 | 117.8012 | 117.8012 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 61.8119 | 582.6288 | 0 | 0.05921 | 3.8991 | 0 | 0 | 0 | 117.8012 | off_peak | 582.6288 |  |  | 16.82 | 0 | 83.18 | 459.3184 | 0
4047 | 664.38 | 683.054 | 27.2 | 109.7784 | 109.7784 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 73.3758 | 566.964 | 0 | 0.05921 | 4.2392 | 0 | 0 | 0 | 109.7784 | off_peak | 554.6016 | 0 | 100 | 16.52 | 0 | 83.48 | 465.3695 | 0
4048 | 645.55 | 650.113 | 27 | 104.56 | 104.56 | 0 | 0 | 0.03626 | 0.03626 | 0 | 0 | 0 | 73.4097 | 541.0262 | 0 | 0.05921 | 4.6509 | 0 | 0 | 0 | 104.56 | off_peak | 540.99 | 0 | 100 | 16.2 | 0 | 83.8 | 486.2933 | 0
4049 | 668.71 | 467.832 | 26.7 | 75.325 | 75.325 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 73.4097 | 593.385 | 0 | 0.05921 | 5.1875 | 0 | 0 | 0 | 75.325 | off_peak | 593.385 |  |  | 11.26 | 0 | 88.74 | 390.7452 | 0
4050 | 562.36 | 267.619 | 26.4 | 43.1358 | 43.1358 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 73.4097 | 519.2242 | 0 | 0.05921 | 5.7726 | 0 | 0 | 0 | 43.1358 | off_peak | 519.2242 |  |  | 7.67 | 0 | 92.33 | 249.0069 | 0
4051 | 575.38 | 83.421 | 26.3 | 13.451 | 13.451 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 73.4097 | 561.929 | 0 | 0.05921 | 6.2417 | 0 | 0 | 0 | 13.451 | off_peak | 561.929 |  |  | 2.34 | 0 | 97.66 | 83.9571 | 0
4052 | 542.61 | 0 | 25.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 73.4097 | 542.61 | 0 | 0.05921 | 6.4989 | 0 | 0 | 0 | 0 | off_peak | 542.61 |  |  | 0 | 0 | 100 | 0 | 0
4053 | 542.62 | 0 | 25.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 73.4097 | 542.62 | 0 | 0.05921 | 6.2014 | 0 | 0 | 0 | 0 | off_peak | 542.62 |  |  | 0 | 0 | 100 | 0 | 0
4054 | 548.43 | 0 | 25.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 73.4097 | 548.43 | 0 | 0.05921 | 6.3387 | 0 | 0 | 0 | 0 | off_peak | 548.43 |  |  | 0 | 0 | 100 | 0 | 0
4055 | 549.91 | 0 | 25.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 73.4097 | 549.91 | 0 | 0.05921 | 6.7736 | 0 | 0 | 0 | 0 | off_peak | 549.91 |  |  | 0 | 0 | 100 | 0 | 0
4056 | 540.47 | 0 | 26.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 73.4097 | 540.47 | 0 | 0.05921 | 6.9076 | 0 | 0 | 0 | 0 | off_peak | 540.47 |  |  | 0 | 0 | 100 | 0 | 0
4057 | 557.1 | 0 | 26.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 73.4097 | 557.1 | 0 | 0.05921 | 6.8284 | 0 | 0 | 0 | 0 | off_peak | 557.1 |  |  | 0 | 0 | 100 | 0 | 0
4058 | 560.95 | 0 | 26.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 73.4097 | 560.95 | 0 | 0.05921 | 6.8301 | 0 | 0 | 0 | 0 | off_peak | 560.95 |  |  | 0 | 0 | 100 | 0 | 0
4059 | 527.26 | 0 | 26.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 73.4097 | 527.26 | 0 | 0.05921 | 6.5201 | 0 | 0 | 0 | 0 | off_peak | 527.26 |  |  | 0 | 0 | 100 | 0 | 0
4060 | 535.66 | 0 | 26.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 73.4097 | 535.66 | 0 | 0.05921 | 6.1687 | 0 | 0 | 0 | 0 | off_peak | 535.66 |  |  | 0 | 0 | 100 | 0 | 0
4061 | 572.34 | 0 | 26.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 73.4097 | 572.34 | 0 | 0.05921 | 5.4392 | 0 | 0 | 0 | 0 | off_peak | 572.34 |  |  | 0 | 0 | 100 | 0 | 0
4062 | 645.99 | 4.75 | 26.8 | 0.76451 | 0 | 0 | 0.76451 | 0.76451 | 0 | 0 | 0 | 0 | 74.1249 | 645.99 | 0 | 0.05921 | 4.9184 | 0 | 0 | 0.71514 | 0 | off_peak | 645.99 | 100 | 0 | 0 | 0 | 100 | 0 | 0
4063 | 740.92 | 130.071 | 27 | 20.9198 | 20.9198 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1249 | 720.0002 | 0 | 0.05921 | 4.4649 | 0 | 0 | 0.71514 | 20.9198 | off_peak | 720.0002 |  |  | 2.82 | 0 | 97.18 | 93.4053 | 0
4064 | 776.91 | 327.924 | 27.2 | 52.7029 | 52.7029 | 0 | 0 | 0.049377 | 0.049377 | 0 | 0 | 0 | 74.1711 | 724.2564 | 0 | 0.05921 | 4.1771 | 0 | 0 | 0.71514 | 52.7029 | off_peak | 724.2071 | 0 | 100 | 6.78 | 0 | 93.22 | 220.1452 | 0
4065 | 869.38 | 496.745 | 27.3 | 79.8064 | 79.8064 | 0 | 0 | 0.003189 | 0.003189 | 0 | 0 | 0 | 74.174 | 789.5768 | 0 | 0.05921 | 4.0289 | 0 | 0 | 0.71514 | 79.8064 | off_peak | 789.5736 | 0 | 100 | 9.18 | 0 | 90.82 | 321.533 | 0
4066 | 885.03 | 531.809 | 27.5 | 85.3777 | 85.3775 | 0 | 0.00020596 | 0.00020596 | 0 | 0 | 0 | 0 | 74.1742 | 799.6525 | 0 | 0.05921 | 4.011 | 0 | 0 | 0.71533 | 85.3775 | off_peak | 799.6525 | 100 | 0 | 9.65 | 0 | 90.35 | 342.4503 | 0
4067 | 841.33 | 684.076 | 27.6 | 109.783 | 109.783 | 0 | 0 | 1.3302e-05 | 1.3302e-05 | 0 | 0 | 0 | 74.1743 | 731.547 | 0 | 0.05921 | 4.1413 | 0 | 0 | 0.71533 | 109.783 | off_peak | 731.547 | 0 | 100 | 13.05 | 0 | 86.95 | 454.6498 | 0
4068 | 853.86 | 663.087 | 27.9 | 106.2986 | 106.2986 | 0 | 8.5914e-07 | 8.5914e-07 | 0 | 0 | 0 | 0 | 74.1743 | 747.5614 | 0 | 0.05921 | 4.3193 | 0 | 0 | 0.71533 | 106.2986 | off_peak | 747.5614 | 100 | 0 | 12.45 | 0 | 87.55 | 459.1402 | 0
4069 | 925.89 | 502.443 | 28.1 | 80.4874 | 80.4874 | 0 | 0 | 0 | 0 | 61.7762 | 61.7762 | 0 | 8.1328 | 783.6264 | 0 | 0.088511 | 4.6102 | 0 | 0 | 0.71533 | 80.4874 | on_peak | 783.6264 |  |  | 8.69 | 6.67 | 84.63 | 371.0657 | 0
4070 | 915.74 | 835.978 | 28.3 | 133.8195 | 133.8195 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.1328 | 781.9205 | 0 | 0.088511 | 5.0466 | 0 | 0 | 0.71533 | 133.8195 | on_peak | 781.9205 |  |  | 14.61 | 0 | 85.39 | 675.335 | 0
4071 | 922.91 | 688.598 | 28.4 | 110.1875 | 110.1875 | 0 | 0 | 0 | 0 | 0.66913 | 0.66913 | 0 | 7.4174 | 812.0534 | 0 | 0.088511 | 5.5376 | 0.66913 | 0 | 0 | 110.8566 | on_peak | 812.0534 |  |  | 11.94 | 0.07 | 87.99 | 613.8845 | 0
4072 | 889.22 | 663.967 | 28.4 | 106.2461 | 106.2461 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 782.9739 | 0 | 0.088511 | 6.1158 | 0 | 0 | 0 | 106.2461 | on_peak | 782.9739 |  |  | 11.95 | 0 | 88.05 | 649.7833 | 0
4073 | 848.34 | 445.047 | 28.4 | 71.2151 | 71.2151 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 777.1249 | 0 | 0.088511 | 6.6109 | 0 | 0 | 0 | 71.2151 | on_peak | 777.1249 |  |  | 8.39 | 0 | 91.61 | 470.7947 | 0
4074 | 855.94 | 278.893 | 28.3 | 44.6439 | 44.6439 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 811.2961 | 0 | 0.088511 | 7.1543 | 0 | 0 | 0 | 44.6439 | on_peak | 811.2961 |  |  | 5.22 | 0 | 94.78 | 319.3949 | 0
4075 | 836.07 | 89.1898 | 28.2 | 14.2823 | 14.2823 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 821.7877 | 0 | 0.088511 | 7.611 | 0 | 0 | 0 | 14.2823 | on_peak | 821.7877 |  |  | 1.71 | 0 | 98.29 | 108.7032 | 0
4076 | 792.01 | 0 | 27.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 792.01 | 0 | 0.088511 | 7.7179 | 0 | 0 | 0 | 0 | on_peak | 792.01 |  |  | 0 | 0 | 100 | 0 | 0
4077 | 838.83 | 0 | 27.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 838.83 | 0 | 0.088511 | 7.5283 | 0 | 0 | 0 | 0 | on_peak | 838.83 |  |  | 0 | 0 | 100 | 0 | 0
4078 | 764.62 | 0 | 27.6 | 0 | 0 | 0 | 0 | 8.7006 | 8.7006 | 0 | 0 | 0 | 15.5561 | 773.3206 | 0 | 0.05921 | 7.4473 | 0 | 0 | 0 | 0 | off_peak | 764.62 | 0 | 100 | 0 | 0 | 100 | 0 | 0
4079 | 846 | 0 | 27.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15.5561 | 846 | 0 | 0.05921 | 7.3512 | 0 | 0 | 0 | 0 | off_peak | 846 |  |  | 0 | 0 | 100 | 0 | 0
4080 | 809.66 | 0 | 27 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15.5561 | 809.66 | 0 | 0.05921 | 7.4048 | 0 | 0 | 0 | 0 | off_peak | 809.66 |  |  | 0 | 0 | 100 | 0 | 0
4081 | 813.29 | 0 | 26.7 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 27.12 | 825.6524 | 0 | 0.05921 | 7.2494 | 0 | 0 | 0 | 0 | off_peak | 813.29 | 0 | 100 | 0 | 0 | 100 | 0 | 0
4082 | 675.8 | 0 | 26.4 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 38.684 | 688.1624 | 0 | 0.05921 | 6.9722 | 0 | 0 | 0 | 0 | off_peak | 675.8 | 0 | 100 | 0 | 0 | 100 | 0 | 0
4083 | 665.35 | 0 | 26.2 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 50.2479 | 677.7124 | 0 | 0.05921 | 6.5072 | 0 | 0 | 0 | 0 | off_peak | 665.35 | 0 | 100 | 0 | 0 | 100 | 0 | 0
4084 | 625.1 | 0 | 26 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 61.8119 | 637.4624 | 0 | 0.05921 | 5.8936 | 0 | 0 | 0 | 0 | off_peak | 625.1 | 0 | 100 | 0 | 0 | 100 | 0 | 0
4085 | 696.51 | 0 | 26 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 61.8119 | 696.51 | 0 | 0.05921 | 5.2115 | 0 | 0 | 0 | 0 | off_peak | 696.51 |  |  | 0 | 0 | 100 | 0 | 0
4086 | 737.95 | 0 | 26.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 61.8119 | 737.95 | 0 | 0.05921 | 4.6231 | 0 | 0 | 0 | 0 | off_peak | 737.95 |  |  | 0 | 0 | 100 | 0 | 0
4087 | 788.31 | 96.3583 | 26.9 | 15.5033 | 15.5033 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 73.3758 | 785.1691 | 0 | 0.05921 | 4.1964 | 0 | 0 | 0 | 15.5033 | off_peak | 772.8067 | 0 | 100 | 1.97 | 0 | 98.03 | 65.0585 | 0
4088 | 890.88 | 287.078 | 27.4 | 46.1048 | 46.1048 | 0 | 0 | 0.79843 | 0.79843 | 0 | 0 | 0 | 74.1227 | 845.5736 | 0 | 0.05921 | 3.8617 | 0 | 0 | 0 | 46.1048 | off_peak | 844.7752 | 0 | 100 | 5.18 | 0 | 94.82 | 178.0423 | 0
4089 | 924.07 | 531.182 | 27.9 | 85.1531 | 85.1531 | 0 | 0 | 0.051567 | 0.051567 | 0 | 0 | 0 | 74.1709 | 838.9685 | 0 | 0.05921 | 3.6459 | 0 | 0 | 0 | 85.1531 | off_peak | 838.9169 | 0 | 100 | 9.22 | 0 | 90.78 | 310.456 | 0
4090 | 963.12 | 673.658 | 28.3 | 107.8361 | 107.8361 | 0 | 0 | 0.0033305 | 0.0033305 | 0 | 0 | 0 | 74.174 | 855.2872 | 0 | 0.05921 | 3.6087 | 0 | 0 | 0 | 107.8361 | off_peak | 855.2839 | 0 | 100 | 11.2 | 0 | 88.8 | 389.1445 | 0
4091 | 884.19 | 831.719 | 28.7 | 132.9438 | 132.9438 | 0 | 0 | 0.0002151 | 0.0002151 | 0 | 0 | 0 | 74.1742 | 751.2465 | 0 | 0.05921 | 3.7241 | 0 | 0 | 0 | 132.9438 | off_peak | 751.2462 | 0 | 100 | 15.04 | 0 | 84.96 | 495.1006 | 0
4092 | 943.28 | 796.296 | 29 | 127.1424 | 127.1424 | 0 | 0 | 1.3893e-05 | 1.3893e-05 | 0 | 0 | 0 | 74.1743 | 816.1377 | 0 | 0.05921 | 4.0118 | 0 | 0 | 0 | 127.1424 | off_peak | 816.1376 | 0 | 100 | 13.48 | 0 | 86.52 | 510.0758 | 0
4093 | 936.38 | 807.778 | 29.2 | 128.8814 | 128.8814 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1743 | 807.4986 | 0 | 0.088511 | 4.3549 | 0 | 0 | 0 | 128.8814 | on_peak | 807.4986 |  |  | 13.76 | 0 | 86.24 | 561.2681 | 0
4094 | 973.87 | 834.637 | 29.2 | 133.1668 | 133.1668 | 0 | 0 | 0 | 0 | 62.4453 | 62.4453 | 0 | 7.4174 | 778.2579 | 0 | 0.088511 | 4.6076 | 0 | 0 | 0 | 133.1668 | on_peak | 778.2579 |  |  | 13.67 | 6.41 | 79.91 | 613.5805 | 0
4095 | 948.93 | 759.168 | 29.2 | 121.1257 | 121.1257 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 827.8043 | 0 | 0.088511 | 5.0335 | 0 | 0 | 0 | 121.1257 | on_peak | 827.8043 |  |  | 12.76 | 0 | 87.24 | 609.6807 | 0
4096 | 888.12 | 622.706 | 29.1 | 99.3894 | 99.3894 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 788.7306 | 0 | 0.088511 | 5.3687 | 0 | 0 | 0 | 99.3894 | on_peak | 788.7306 |  |  | 11.19 | 0 | 88.81 | 533.5918 | 0
4097 | 875.13 | 370.913 | 28.9 | 59.2443 | 59.2443 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 815.8857 | 0 | 0.088511 | 5.8385 | 0 | 0 | 0 | 59.2443 | on_peak | 815.8857 |  |  | 6.77 | 0 | 93.23 | 345.8978 | 0
4098 | 834.4 | 267.307 | 28.5 | 42.7581 | 42.7581 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 791.6419 | 0 | 0.088511 | 6.2724 | 0 | 0 | 0 | 42.7581 | on_peak | 791.6419 |  |  | 5.12 | 0 | 94.88 | 268.1949 | 0
4099 | 839.03 | 86.4738 | 28.3 | 13.8423 | 13.8423 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 825.1877 | 0 | 0.088511 | 6.5888 | 0 | 0 | 0 | 13.8423 | on_peak | 825.1877 |  |  | 1.65 | 0 | 98.35 | 91.2039 | 0
4100 | 858.12 | 0 | 27.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 858.12 | 0 | 0.088511 | 7.0618 | 0 | 0 | 0 | 0 | on_peak | 858.12 |  |  | 0 | 0 | 100 | 0 | 0
4101 | 793.81 | 0 | 27.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 793.81 | 0 | 0.088511 | 7.4157 | 0 | 0 | 0 | 0 | on_peak | 793.81 |  |  | 0 | 0 | 100 | 0 | 0
4102 | 795.51 | 0 | 27.6 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 18.9814 | 807.8724 | 0 | 0.05921 | 7.3984 | 0 | 0 | 0 | 0 | off_peak | 795.51 | 0 | 100 | 0 | 0 | 100 | 0 | 0
4103 | 735.41 | 0 | 27.5 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 30.5453 | 747.7724 | 0 | 0.05921 | 7.0532 | 0 | 0 | 0 | 0 | off_peak | 735.41 | 0 | 100 | 0 | 0 | 100 | 0 | 0
4104 | 685.27 | 0 | 27.3 | 0 | 0 | 0 | 0 | 8.7006 | 8.7006 | 0 | 0 | 0 | 38.684 | 693.9706 | 0 | 0.05921 | 7.022 | 0 | 0 | 0 | 0 | off_peak | 685.27 | 0 | 100 | 0 | 0 | 100 | 0 | 0
4105 | 638.79 | 0 | 27.2 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 50.2479 | 651.1524 | 0 | 0.05921 | 6.9096 | 0 | 0 | 0 | 0 | off_peak | 638.79 | 0 | 100 | 0 | 0 | 100 | 0 | 0
4106 | 505.29 | 0 | 27.1 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 61.8119 | 517.6524 | 0 | 0.05921 | 6.6956 | 0 | 0 | 0 | 0 | off_peak | 505.29 | 0 | 100 | 0 | 0 | 100 | 0 | 0
4107 | 504.51 | 0 | 27 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 73.3758 | 516.8724 | 0 | 0.05921 | 6.2018 | 0 | 0 | 0 | 0 | off_peak | 504.51 | 0 | 100 | 0 | 0 | 100 | 0 | 0
4108 | 473.1 | 0 | 26.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 73.3758 | 473.1 | 0 | 0.05921 | 5.5798 | 0 | 0 | 0 | 0 | off_peak | 473.1 |  |  | 0 | 0 | 100 | 0 | 0
4109 | 506.64 | 0 | 26.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 73.3758 | 506.64 | 0 | 0.05921 | 4.8538 | 0 | 0 | 0 | 0 | off_peak | 506.64 |  |  | 0 | 0 | 100 | 0 | 0
4110 | 628.86 | 0 | 27.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 73.3758 | 628.86 | 0 | 0.05921 | 4.2946 | 0 | 0 | 0 | 0 | off_peak | 628.86 |  |  | 0 | 0 | 100 | 0 | 0
4111 | 752.98 | 122.514 | 27.5 | 19.6686 | 19.6686 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 73.3758 | 733.3114 | 0 | 0.05921 | 3.8792 | 0 | 0 | 0 | 19.6686 | off_peak | 733.3114 |  |  | 2.61 | 0 | 97.39 | 76.2984 | 0
4112 | 760.23 | 313.494 | 27.8 | 50.2741 | 49.4757 | 0 | 0.79843 | 0.79843 | 0 | 0 | 0 | 0 | 74.1227 | 710.7543 | 0 | 0.05921 | 3.5518 | 0 | 0 | 0.74686 | 49.4757 | off_peak | 710.7543 | 100 | 0 | 6.51 | 0 | 93.49 | 175.7254 | 0
4113 | 800.66 | 510.201 | 28.1 | 81.7302 | 81.7302 | 0 | 0 | 0.051567 | 0.051567 | 0 | 0 | 0 | 74.1709 | 718.9814 | 0 | 0.05921 | 3.362 | 0 | 0 | 0.74686 | 81.7302 | off_peak | 718.9298 | 0 | 100 | 10.21 | 0 | 89.79 | 274.777 | 0
4114 | 838.36 | 685.176 | 28.3 | 109.6798 | 109.6765 | 0 | 0.0033305 | 0.0033305 | 0 | 0 | 0 | 0 | 74.174 | 728.6835 | 0 | 0.05921 | 3.323 | 0 | 0 | 0.74998 | 109.6765 | off_peak | 728.6835 | 100 | 0 | 13.08 | 0 | 86.92 | 364.4556 | 0
4115 | 760.71 | 815.151 | 28.5 | 130.3906 | 130.3906 | 0 | 0 | 0.0002151 | 0.0002151 | 0 | 0 | 0 | 74.1742 | 630.3196 | 0 | 0.05921 | 3.492 | 0 | 0 | 0.74998 | 130.3906 | off_peak | 630.3194 | 0 | 100 | 17.14 | 0 | 82.86 | 455.3187 | 0
4116 | 847.92 | 881.527 | 28.7 | 140.9052 | 140.9052 | 0 | 1.3893e-05 | 1.3893e-05 | 0 | 0 | 0 | 0 | 74.1743 | 707.0148 | 0 | 0.05921 | 3.7036 | 0 | 0 | 0.74999 | 140.9052 | off_peak | 707.0148 | 100 | 0 | 16.62 | 0 | 83.38 | 521.8512 | 0
4117 | 773.19 | 881.696 | 29 | 140.7779 | 140.7779 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1743 | 632.4121 | 0 | 0.088511 | 3.9704 | 0 | 0 | 0.74999 | 140.7779 | on_peak | 632.4121 |  |  | 18.21 | 0 | 81.79 | 558.9443 | 0
4118 | 820.51 | 717.134 | 29.1 | 114.461 | 114.461 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1743 | 706.049 | 0 | 0.088511 | 4.2413 | 0 | 0 | 0.74999 | 114.461 | on_peak | 706.049 |  |  | 13.95 | 0 | 86.05 | 485.4682 | 0
4119 | 849.8 | 700.421 | 29.2 | 111.7526 | 111.7526 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1743 | 738.0474 | 0 | 0.088511 | 4.612 | 0 | 0 | 0.74999 | 111.7526 | on_peak | 738.0474 |  |  | 13.15 | 0 | 86.85 | 515.4075 | 0
4120 | 737.58 | 543.09 | 29.2 | 86.6503 | 86.6503 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1743 | 650.9297 | 0 | 0.088511 | 4.9625 | 0 | 0 | 0.74999 | 86.6503 | on_peak | 650.9297 |  |  | 11.75 | 0 | 88.25 | 429.9996 | 0
4121 | 771.67 | 411.527 | 29 | 65.7074 | 65.7074 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1743 | 705.9626 | 0 | 0.088511 | 5.3271 | 0 | 0 | 0.74999 | 65.7074 | on_peak | 705.9626 |  |  | 8.51 | 0 | 91.49 | 350.0268 | 0
4122 | 869.4 | 182.32 | 28.7 | 29.1424 | 29.1424 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1743 | 840.2576 | 0 | 0.088511 | 5.8592 | 0 | 0 | 0.74999 | 29.1424 | on_peak | 840.2576 |  |  | 3.35 | 0 | 96.65 | 170.7507 | 0
4123 | 843.95 | 44.985 | 28.6 | 7.1931 | 7.1931 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1743 | 836.7569 | 0 | 0.088511 | 6.552 | 0 | 0 | 0.74999 | 7.1931 | on_peak | 836.7569 |  |  | 0.85 | 0 | 99.15 | 47.1295 | 0
4124 | 891.27 | 0 | 28.2 | 0 | 0 | 0 | 0 | 0 | 0 | 62.4453 | 62.4453 | 0 | 7.4174 | 828.8247 | 0 | 0.088511 | 6.9532 | 0.70155 | 0 | 0 | 0.70155 | on_peak | 828.8247 |  |  | 0 | 7.01 | 92.99 | 4.8781 | 0
4125 | 831.55 | 0 | 28 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 831.55 | 0 | 0.088511 | 7.1403 | 0 | 0 | 0 | 0 | on_peak | 831.55 |  |  | 0 | 0 | 100 | 0 | 0
4126 | 790.79 | 0 | 27.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 790.79 | 0 | 0.05921 | 7.1853 | 0 | 0 | 0 | 0 | off_peak | 790.79 |  |  | 0 | 0 | 100 | 0 | 0
4127 | 855.91 | 0 | 27.6 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 18.9814 | 868.2724 | 0 | 0.05921 | 7.3646 | 0 | 0 | 0 | 0 | off_peak | 855.91 | 0 | 100 | 0 | 0 | 100 | 0 | 0
4128 | 794.11 | 0 | 27.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18.9814 | 794.11 | 0 | 0.05921 | 7.3881 | 0 | 0 | 0 | 0 | off_peak | 794.11 |  |  | 0 | 0 | 100 | 0 | 0
4129 | 702.75 | 0 | 27.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18.9814 | 702.75 | 0 | 0.05921 | 7.0622 | 0 | 0 | 0 | 0 | off_peak | 702.75 |  |  | 0 | 0 | 100 | 0 | 0
4130 | 636 | 0 | 27.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18.9814 | 636 | 0 | 0.05921 | 6.7789 | 0 | 0 | 0 | 0 | off_peak | 636 |  |  | 0 | 0 | 100 | 0 | 0
4131 | 625.99 | 0 | 27 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 30.5453 | 638.3524 | 0 | 0.05921 | 6.3594 | 0 | 0 | 0 | 0 | off_peak | 625.99 | 0 | 100 | 0 | 0 | 100 | 0 | 0
4132 | 619.77 | 0 | 27 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 42.1093 | 632.1324 | 0 | 0.05921 | 5.8153 | 0 | 0 | 0 | 0 | off_peak | 619.77 | 0 | 100 | 0 | 0 | 100 | 0 | 0
4133 | 635.1 | 0 | 27 | 0 | 0 | 0 | 0 | 8.7006 | 8.7006 | 0 | 0 | 0 | 50.2479 | 643.8006 | 0 | 0.05921 | 5.1954 | 0 | 0 | 0 | 0 | off_peak | 635.1 | 0 | 100 | 0 | 0 | 100 | 0 | 0
4134 | 718.42 | 0 | 27.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50.2479 | 718.42 | 0 | 0.05921 | 4.5712 | 0 | 0 | 0 | 0 | off_peak | 718.42 |  |  | 0 | 0 | 100 | 0 | 0
4135 | 776.86 | 122.668 | 27.9 | 19.6648 | 19.6648 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 61.8119 | 769.5576 | 0 | 0.05921 | 4.1016 | 0 | 0 | 0 | 19.6648 | off_peak | 757.1952 | 0 | 100 | 2.53 | 0 | 97.47 | 80.6561 | 0
4136 | 833.95 | 311.888 | 28.3 | 49.9256 | 49.9256 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 73.3758 | 796.3868 | 0 | 0.05921 | 3.7859 | 0 | 0 | 0 | 49.9256 | off_peak | 784.0244 | 0 | 100 | 5.99 | 0 | 94.01 | 189.0155 | 0
4137 | 877.6 | 352.853 | 28.6 | 56.4214 | 56.4214 | 0 | 0 | 0.79843 | 0.79843 | 0 | 0 | 0 | 74.1227 | 821.9771 | 0 | 0.05921 | 3.607 | 0 | 0 | 0 | 56.4214 | off_peak | 821.1786 | 0 | 100 | 6.43 | 0 | 93.57 | 203.5103 | 0
4138 | 851.02 | 628.528 | 28.8 | 100.4286 | 100.4286 | 0 | 0 | 0.051567 | 0.051567 | 0 | 0 | 0 | 74.1709 | 750.6429 | 0 | 0.05921 | 3.5521 | 0 | 0 | 0 | 100.4286 | off_peak | 750.5914 | 0 | 100 | 11.8 | 0 | 88.2 | 356.7363 | 0
4139 | 820.7 | 768.751 | 28.9 | 122.7892 | 122.7892 | 0 | 0 | 0.0033305 | 0.0033305 | 0 | 0 | 0 | 74.174 | 697.9142 | 0 | 0.05921 | 3.6919 | 0 | 0 | 0 | 122.7892 | off_peak | 697.9108 | 0 | 100 | 14.96 | 0 | 85.04 | 453.3193 | 0
4140 | 907.4 | 770.935 | 29.1 | 123.0481 | 123.0481 | 0 | 0 | 0.0002151 | 0.0002151 | 0 | 0 | 0 | 74.1742 | 784.3521 | 0 | 0.05921 | 3.9714 | 0 | 0 | 0 | 123.0481 | off_peak | 784.3519 | 0 | 100 | 13.56 | 0 | 86.44 | 488.6775 | 0
4141 | 842.7 | 934.765 | 29.2 | 149.1423 | 149.1423 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1742 | 693.5577 | 0 | 0.088511 | 4.315 | 0 | 0 | 0 | 149.1423 | on_peak | 693.5577 |  |  | 17.7 | 0 | 82.3 | 643.5544 | 0
4142 | 876.5 | 889.959 | 29.2 | 141.9935 | 141.9935 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1742 | 734.5065 | 0 | 0.088511 | 4.5968 | 0 | 0 | 0 | 141.9935 | on_peak | 734.5065 |  |  | 16.2 | 0 | 83.8 | 652.7139 | 0
4143 | 915.12 | 764.044 | 29.3 | 121.8591 | 121.8591 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1742 | 793.2609 | 0 | 0.088511 | 5.0404 | 0 | 0 | 0 | 121.8591 | on_peak | 793.2609 |  |  | 13.32 | 0 | 86.68 | 614.2187 | 0
4144 | 844.78 | 540.806 | 29.1 | 86.3174 | 86.3174 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1742 | 758.4626 | 0 | 0.088511 | 5.5311 | 0 | 0 | 0 | 86.3174 | on_peak | 758.4626 |  |  | 10.22 | 0 | 89.78 | 477.4271 | 0
4145 | 821.13 | 342.031 | 28.8 | 54.651 | 54.651 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1742 | 766.479 | 0 | 0.088511 | 6.0193 | 0 | 0 | 0 | 54.651 | on_peak | 766.479 |  |  | 6.66 | 0 | 93.34 | 328.963 | 0
4146 | 851.5 | 40.6809 | 28.3 | 6.512 | 6.512 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1742 | 844.988 | 0 | 0.088511 | 6.3901 | 0 | 0 | 0 | 6.512 | on_peak | 844.988 |  |  | 0.76 | 0 | 99.24 | 41.6125 | 0
4147 | 857.51 | 20.9 | 28.1 | 3.348 | 3.348 | 0 | 0 | 0 | 0 | 62.4453 | 62.4453 | 0 | 7.4174 | 791.7167 | 0 | 0.088511 | 6.8761 | 0 | 0 | 0 | 3.348 | on_peak | 791.7167 |  |  | 0.39 | 7.28 | 92.33 | 23.0213 | 0
4148 | 862.44 | 0 | 27.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 862.44 | 0 | 0.088511 | 7.1666 | 0 | 0 | 0 | 0 | on_peak | 862.44 |  |  | 0 | 0 | 100 | 0 | 0
4149 | 851.67 | 0 | 26.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 851.67 | 0 | 0.088511 | 7.4251 | 0 | 0 | 0 | 0 | on_peak | 851.67 |  |  | 0 | 0 | 100 | 0 | 0
4150 | 773.88 | 0 | 26.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 773.88 | 0 | 0.05921 | 7.6188 | 0 | 0 | 0 | 0 | off_peak | 773.88 |  |  | 0 | 0 | 100 | 0 | 0
4151 | 860.78 | 0 | 26.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 860.78 | 0 | 0.05921 | 7.4994 | 0 | 0 | 0 | 0 | off_peak | 860.78 |  |  | 0 | 0 | 100 | 0 | 0
4152 | 835.83 | 0 | 26.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 835.83 | 0 | 0.05921 | 7.472 | 0 | 0 | 0 | 0 | off_peak | 835.83 |  |  | 0 | 0 | 100 | 0 | 0
4153 | 765.45 | 0 | 26.8 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 18.9814 | 777.8124 | 0 | 0.05921 | 7.4045 | 0 | 0 | 0 | 0 | off_peak | 765.45 | 0 | 100 | 0 | 0 | 100 | 0 | 0
4154 | 638.99 | 0 | 26.8 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 30.5453 | 651.3524 | 0 | 0.05921 | 7.3886 | 0 | 0 | 0 | 0 | off_peak | 638.99 | 0 | 100 | 0 | 0 | 100 | 0 | 0
4155 | 620.05 | 0 | 26.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30.5453 | 620.05 | 0 | 0.05921 | 7.0565 | 0 | 0 | 0 | 0 | off_peak | 620.05 |  |  | 0 | 0 | 100 | 0 | 0
4156 | 612 | 0 | 27 | 0 | 0 | 0 | 0 | 8.7006 | 8.7006 | 0 | 0 | 0 | 38.684 | 620.7006 | 0 | 0.05921 | 6.5659 | 0 | 0 | 0 | 0 | off_peak | 612 | 0 | 100 | 0 | 0 | 100 | 0 | 0
4157 | 640.94 | 0 | 27.1 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 50.2479 | 653.3024 | 0 | 0.05921 | 5.8337 | 0 | 0 | 0 | 0 | off_peak | 640.94 | 0 | 100 | 0 | 0 | 100 | 0 | 0
4158 | 690.76 | 0 | 27.3 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 61.8119 | 703.1224 | 0 | 0.05921 | 5.2312 | 0 | 0 | 0 | 0 | off_peak | 690.76 | 0 | 100 | 0 | 0 | 100 | 0 | 0
4159 | 739.27 | 119.408 | 27.8 | 19.1491 | 19.1491 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 73.3758 | 732.4833 | 0 | 0.05921 | 4.7492 | 0 | 0 | 0 | 19.1491 | off_peak | 720.1209 | 0 | 100 | 2.59 | 0 | 97.41 | 90.943 | 0
4160 | 795.73 | 310.986 | 28.2 | 49.7994 | 49.7994 | 0 | 0 | 0.79843 | 0.79843 | 0 | 0 | 0 | 74.1227 | 746.7291 | 0 | 0.05921 | 4.441 | 0 | 0 | 0 | 49.7994 | off_peak | 745.9306 | 0 | 100 | 6.26 | 0 | 93.74 | 221.1596 | 0
4161 | 817.24 | 499.348 | 28.5 | 79.8751 | 79.8751 | 0 | 0 | 0.051567 | 0.051567 | 0 | 0 | 0 | 74.1709 | 737.4165 | 0 | 0.05921 | 4.2799 | 0 | 0 | 0 | 79.8751 | off_peak | 737.3649 | 0 | 100 | 9.77 | 0 | 90.23 | 341.856 | 0
4162 | 868.81 | 452.823 | 28.7 | 72.3802 | 72.3802 | 0 | 0 | 0.0033305 | 0.0033305 | 0 | 0 | 0 | 74.174 | 796.4331 | 0 | 0.05921 | 4.2701 | 0 | 0 | 0 | 72.3802 | off_peak | 796.4298 | 0 | 100 | 8.33 | 0 | 91.67 | 309.0706 | 0
4163 | 852.39 | 290.795 | 29 | 46.4304 | 46.4304 | 0 | 0 | 0.0002151 | 0.0002151 | 0 | 0 | 0 | 74.1742 | 805.9598 | 0 | 0.05921 | 4.4164 | 0 | 0 | 0 | 46.4304 | off_peak | 805.9596 | 0 | 100 | 5.45 | 0 | 94.55 | 205.0539 | 0
4164 | 904.83 | 395.994 | 29.2 | 63.1811 | 63.1811 | 0 | 0 | 1.3893e-05 | 1.3893e-05 | 0 | 0 | 0 | 74.1743 | 841.6489 | 0 | 0.05921 | 4.5957 | 0 | 0 | 0 | 63.1811 | off_peak | 841.6489 | 0 | 100 | 6.98 | 0 | 93.02 | 290.3598 | 0
4165 | 870.69 | 580.254 | 29.3 | 92.546 | 92.546 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1743 | 778.144 | 0 | 0.088511 | 4.7964 | 0 | 0 | 0 | 92.546 | on_peak | 778.144 |  |  | 10.63 | 0 | 89.37 | 443.8842 | 0
4166 | 825.95 | 843.709 | 29.4 | 134.5158 | 134.5158 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1743 | 691.4342 | 0 | 0.088511 | 5.102 | 0 | 0 | 0 | 134.5158 | on_peak | 691.4342 |  |  | 16.29 | 0 | 83.71 | 686.3025 | 0
4167 | 847.66 | 750.171 | 29.5 | 119.559 | 119.559 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1743 | 728.101 | 0 | 0.088511 | 5.5828 | 0 | 0 | 0 | 119.559 | on_peak | 728.101 |  |  | 14.1 | 0 | 85.9 | 667.4702 | 0
4168 | 785.6 | 396.838 | 29.4 | 63.2694 | 63.2694 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1743 | 722.3306 | 0 | 0.088511 | 6.0128 | 0 | 0 | 0 | 63.2694 | on_peak | 722.3306 |  |  | 8.05 | 0 | 91.95 | 380.4259 | 0
4169 | 830.9 | 76.915 | 29.1 | 12.2763 | 12.2763 | 0 | 0 | 0 | 0 | 62.4453 | 62.4453 | 0 | 7.4174 | 756.1784 | 0 | 0.088511 | 6.33 | 0 | 0 | 0 | 12.2763 | on_peak | 756.1784 |  |  | 1.48 | 7.52 | 91.01 | 77.7089 | 0
4170 | 824.82 | 222.347 | 28.7 | 35.5404 | 35.5404 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 789.2796 | 0 | 0.088511 | 6.7499 | 0 | 0 | 0 | 35.5404 | on_peak | 789.2796 |  |  | 4.31 | 0 | 95.69 | 239.8939 | 0
4171 | 765.44 | 60.8908 | 28.5 | 9.74 | 9.74 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 755.7 | 0 | 0.088511 | 7.0011 | 0 | 0 | 0 | 9.74 | on_peak | 755.7 |  |  | 1.27 | 0 | 98.73 | 68.1913 | 0
4172 | 803.38 | 0 | 27.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 803.38 | 0 | 0.088511 | 7.3356 | 0 | 0 | 0 | 0 | on_peak | 803.38 |  |  | 0 | 0 | 100 | 0 | 0
4173 | 803.45 | 0 | 27.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 803.45 | 0 | 0.088511 | 7.4092 | 0 | 0 | 0 | 0 | on_peak | 803.45 |  |  | 0 | 0 | 100 | 0 | 0
4174 | 778.71 | 0 | 27.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 778.71 | 0 | 0.05921 | 7.6176 | 0 | 0 | 0 | 0 | off_peak | 778.71 |  |  | 0 | 0 | 100 | 0 | 0
4175 | 761.35 | 0 | 27.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 761.35 | 0 | 0.05921 | 7.9207 | 0 | 0 | 0 | 0 | off_peak | 761.35 |  |  | 0 | 0 | 100 | 0 | 0
4176 | 798.84 | 0 | 27.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 798.84 | 0 | 0.05921 | 7.9746 | 0 | 0 | 0 | 0 | off_peak | 798.84 |  |  | 0 | 0 | 100 | 0 | 0
4177 | 689.12 | 0 | 27.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 689.12 | 0 | 0.05921 | 7.7717 | 0 | 0 | 0 | 0 | off_peak | 689.12 |  |  | 0 | 0 | 100 | 0 | 0
4178 | 604.72 | 0 | 27.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 604.72 | 0 | 0.05921 | 7.5479 | 0 | 0 | 0 | 0 | off_peak | 604.72 |  |  | 0 | 0 | 100 | 0 | 0
4179 | 625.21 | 0 | 27.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 625.21 | 0 | 0.05921 | 7.1332 | 0 | 0 | 0 | 0 | off_peak | 625.21 |  |  | 0 | 0 | 100 | 0 | 0
4180 | 582.66 | 0 | 27.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 582.66 | 0 | 0.05921 | 6.5265 | 0 | 0 | 0 | 0 | off_peak | 582.66 |  |  | 0 | 0 | 100 | 0 | 0
4181 | 608.7 | 0 | 27.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 608.7 | 0 | 0.05921 | 6.0092 | 0 | 0 | 0 | 0 | off_peak | 608.7 |  |  | 0 | 0 | 100 | 0 | 0
4182 | 667.6 | 0 | 27.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 667.6 | 0 | 0.05921 | 5.382 | 0 | 0 | 0 | 0 | off_peak | 667.6 |  |  | 0 | 0 | 100 | 0 | 0
4183 | 711.75 | 126.166 | 28.2 | 20.2034 | 20.2034 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 691.5466 | 0 | 0.05921 | 4.9281 | 0 | 0 | 0 | 20.2034 | off_peak | 691.5466 |  |  | 2.84 | 0 | 97.16 | 99.565 | 0
4184 | 745.1 | 321.185 | 28.5 | 51.3764 | 51.3764 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 693.7236 | 0 | 0.05921 | 4.5546 | 0 | 0 | 0 | 51.3764 | off_peak | 693.7236 |  |  | 6.9 | 0 | 93.1 | 234.0002 | 0
4185 | 819.68 | 518.602 | 28.7 | 82.8945 | 82.8945 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 736.7855 | 0 | 0.05921 | 4.2774 | 0 | 0 | 0 | 82.8945 | off_peak | 736.7855 |  |  | 10.11 | 0 | 89.89 | 354.5729 | 0
4186 | 757.76 | 290.348 | 28.9 | 46.376 | 46.376 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 711.384 | 0 | 0.05921 | 4.1258 | 0 | 0 | 0 | 46.376 | off_peak | 711.384 |  |  | 6.12 | 0 | 93.88 | 191.3403 | 0
4187 | 795.26 | 218.103 | 29.1 | 34.8112 | 34.8112 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 760.4488 | 0 | 0.05921 | 4.0814 | 0 | 0 | 0 | 34.8112 | off_peak | 760.4488 |  |  | 4.38 | 0 | 95.62 | 142.0794 | 0
4188 | 806.63 | 473.096 | 29.2 | 75.4827 | 75.4827 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 731.1473 | 0 | 0.05921 | 4.1565 | 0 | 0 | 0 | 75.4827 | off_peak | 731.1473 |  |  | 9.36 | 0 | 90.64 | 313.7416 | 0
4189 | 779.63 | 931.94 | 29.2 | 148.6915 | 148.6915 | 0 | 0 | 8.7006 | 8.7006 | 0 | 0 | 0 | 15.5561 | 639.6391 | 0 | 0.05921 | 4.3053 | 0 | 0 | 0 | 148.6915 | off_peak | 630.9385 | 0 | 100 | 19.07 | 0 | 80.93 | 640.1686 | 0
4190 | 738.63 | 892.582 | 29.2 | 142.412 | 142.412 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15.5561 | 596.218 | 0 | 0.05921 | 4.5314 | 0 | 0 | 0 | 142.412 | off_peak | 596.218 |  |  | 19.28 | 0 | 80.72 | 645.3232 | 0
4191 | 751.45 | 799.321 | 29.1 | 127.5787 | 127.5787 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 27.12 | 636.2336 | 0 | 0.05921 | 4.9499 | 0 | 0 | 0 | 127.5787 | off_peak | 623.8713 | 0 | 100 | 16.98 | 0 | 83.02 | 631.4973 | 0
4192 | 717.75 | 584.978 | 29 | 93.4018 | 93.4018 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27.12 | 624.3482 | 0 | 0.05921 | 5.5818 | 0 | 0 | 0 | 93.4018 | off_peak | 624.3482 |  |  | 13.01 | 0 | 86.99 | 521.3512 | 0
4193 | 736.82 | 395.964 | 28.8 | 63.2686 | 63.2686 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27.12 | 673.5514 | 0 | 0.05921 | 6.2608 | 0 | 0 | 0 | 63.2686 | off_peak | 673.5514 |  |  | 8.59 | 0 | 91.41 | 396.1106 | 0
4194 | 680.16 | 114.077 | 28.4 | 18.2543 | 18.2543 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27.12 | 661.9057 | 0 | 0.05921 | 6.9174 | 0 | 0 | 0 | 18.2543 | off_peak | 661.9057 |  |  | 2.68 | 0 | 97.32 | 126.2721 | 0
4195 | 580.51 | 86.0882 | 28.2 | 13.7856 | 13.7856 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 38.684 | 579.0867 | 0 | 0.05921 | 7.2173 | 0 | 0 | 0 | 13.7856 | off_peak | 566.7244 | 0 | 100 | 2.37 | 0 | 97.63 | 99.4947 | 0
4196 | 587.93 | 0 | 27.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 38.684 | 587.93 | 0 | 0.05921 | 7.4023 | 0 | 0 | 0 | 0 | off_peak | 587.93 |  |  | 0 | 0 | 100 | 0 | 0
4197 | 584.59 | 0 | 27.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 38.684 | 584.59 | 0 | 0.05921 | 7.4342 | 0 | 0 | 0 | 0 | off_peak | 584.59 |  |  | 0 | 0 | 100 | 0 | 0
4198 | 558.97 | 0 | 27.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 38.684 | 558.97 | 0 | 0.05921 | 7.2221 | 0 | 0 | 0 | 0 | off_peak | 558.97 |  |  | 0 | 0 | 100 | 0 | 0
4199 | 589.97 | 0 | 27.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 38.684 | 589.97 | 0 | 0.05921 | 7.1448 | 0 | 0 | 0 | 0 | off_peak | 589.97 |  |  | 0 | 0 | 100 | 0 | 0
4200 | 569.59 | 0 | 27.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 38.684 | 569.59 | 0 | 0.05921 | 6.9037 | 0 | 0 | 0 | 0 | off_peak | 569.59 |  |  | 0 | 0 | 100 | 0 | 0
4201 | 572.03 | 0 | 27.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 38.684 | 572.03 | 0 | 0.05921 | 6.5406 | 0 | 0 | 0 | 0 | off_peak | 572.03 |  |  | 0 | 0 | 100 | 0 | 0
4202 | 571.86 | 0 | 27.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 38.684 | 571.86 | 0 | 0.05921 | 6.3846 | 0 | 0 | 0 | 0 | off_peak | 571.86 |  |  | 0 | 0 | 100 | 0 | 0
4203 | 580.32 | 0 | 27.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 38.684 | 580.32 | 0 | 0.05921 | 6.0567 | 0 | 0 | 0 | 0 | off_peak | 580.32 |  |  | 0 | 0 | 100 | 0 | 0
4204 | 571.12 | 0 | 27.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 38.684 | 571.12 | 0 | 0.05921 | 5.6165 | 0 | 0 | 0 | 0 | off_peak | 571.12 |  |  | 0 | 0 | 100 | 0 | 0
4205 | 597.54 | 0 | 27.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 38.684 | 597.54 | 0 | 0.05921 | 5.1123 | 0 | 0 | 0 | 0 | off_peak | 597.54 |  |  | 0 | 0 | 100 | 0 | 0
4206 | 669.05 | 0 | 27.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 38.684 | 669.05 | 0 | 0.05921 | 4.5984 | 0 | 0 | 0 | 0 | off_peak | 669.05 |  |  | 0 | 0 | 100 | 0 | 0
4207 | 663.13 | 98.4254 | 28.2 | 15.7612 | 15.7612 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 50.2479 | 659.7311 | 0 | 0.05921 | 4.2159 | 0 | 0 | 0 | 15.7612 | off_peak | 647.3688 | 0 | 100 | 2.38 | 0 | 97.62 | 66.4481 | 0
4208 | 714.43 | 291.274 | 28.5 | 46.5918 | 46.5918 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50.2479 | 667.8382 | 0 | 0.05921 | 3.8856 | 0 | 0 | 0 | 46.5918 | off_peak | 667.8382 |  |  | 6.52 | 0 | 93.48 | 181.0393 | 0
4209 | 704.33 | 483.023 | 28.7 | 77.2074 | 77.2074 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 61.8119 | 639.4849 | 0 | 0.05921 | 3.6608 | 0 | 0 | 0 | 77.2074 | off_peak | 627.1226 | 0 | 100 | 10.96 | 0 | 89.04 | 282.6383 | 0
4210 | 736.73 | 411.463 | 28.9 | 65.7211 | 65.7211 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 61.8119 | 671.0089 | 0 | 0.05921 | 3.5752 | 0 | 0 | 0 | 65.7211 | off_peak | 671.0089 |  |  | 8.92 | 0 | 91.08 | 234.9643 | 0
4211 | 691.26 | 737.214 | 29.1 | 117.6659 | 117.6659 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 61.8119 | 573.5941 | 0 | 0.05921 | 3.5035 | 0 | 0 | 0 | 117.6659 | off_peak | 573.5941 |  |  | 17.02 | 0 | 82.98 | 412.2373 | 0
4212 | 739.96 | 892.716 | 29.3 | 142.3813 | 142.3813 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 61.8119 | 597.5787 | 0 | 0.05921 | 3.5639 | 0 | 0 | 0 | 142.3813 | off_peak | 597.5787 |  |  | 19.24 | 0 | 80.76 | 507.4365 | 0
4213 | 731.56 | 779.453 | 29.3 | 124.3167 | 124.3167 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 61.8119 | 607.2433 | 0 | 0.05921 | 3.6616 | 0 | 0 | 0 | 124.3167 | off_peak | 607.2433 |  |  | 16.99 | 0 | 83.01 | 455.192 | 0
4214 | 718.81 | 767.439 | 29.3 | 122.4006 | 122.4006 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 61.8119 | 596.4094 | 0 | 0.05921 | 4.0003 | 0 | 0 | 0 | 122.4006 | off_peak | 596.4094 |  |  | 17.03 | 0 | 82.97 | 489.6385 | 0
4215 | 707.69 | 574.127 | 29.2 | 91.6023 | 91.6023 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 61.8119 | 616.0877 | 0 | 0.05921 | 4.5193 | 0 | 0 | 0 | 91.6023 | off_peak | 616.0877 |  |  | 12.94 | 0 | 87.06 | 413.9816 | 0
4216 | 698.32 | 522.521 | 29.1 | 83.399 | 83.399 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 61.8119 | 614.921 | 0 | 0.05921 | 5.1399 | 0 | 0 | 0 | 83.399 | off_peak | 614.921 |  |  | 11.94 | 0 | 88.06 | 428.6665 | 0
4217 | 667.71 | 474.613 | 28.8 | 75.8355 | 75.8355 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 61.8119 | 591.8745 | 0 | 0.05921 | 5.7018 | 0 | 0 | 0 | 75.8355 | off_peak | 591.8745 |  |  | 11.36 | 0 | 88.64 | 432.4004 | 0
4218 | 625.51 | 276.011 | 28.4 | 44.1665 | 44.1665 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 61.8119 | 581.3435 | 0 | 0.05921 | 6.2341 | 0 | 0 | 0 | 44.1665 | off_peak | 581.3435 |  |  | 7.06 | 0 | 92.94 | 275.3366 | 0
4219 | 585.42 | 89.1887 | 28.2 | 14.2821 | 14.2821 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 61.8119 | 571.1379 | 0 | 0.05921 | 6.4134 | 0 | 0 | 0 | 14.2821 | off_peak | 571.1379 |  |  | 2.44 | 0 | 97.56 | 91.597 | 0
4220 | 579.92 | 0 | 27.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 61.8119 | 579.92 | 0 | 0.05921 | 6.5634 | 0 | 0 | 0 | 0 | off_peak | 579.92 |  |  | 0 | 0 | 100 | 0 | 0
4221 | 558.85 | 0 | 27.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 61.8119 | 558.85 | 0 | 0.05921 | 6.7186 | 0 | 0 | 0 | 0 | off_peak | 558.85 |  |  | 0 | 0 | 100 | 0 | 0
4222 | 578.95 | 0 | 27.8 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 73.3758 | 591.3124 | 0 | 0.05921 | 6.994 | 0 | 0 | 0 | 0 | off_peak | 578.95 | 0 | 100 | 0 | 0 | 100 | 0 | 0
4223 | 563.93 | 0 | 27.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 73.3758 | 563.93 | 0 | 0.05921 | 6.9607 | 0 | 0 | 0 | 0 | off_peak | 563.93 |  |  | 0 | 0 | 100 | 0 | 0
4224 | 555.68 | 0 | 27.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 73.3758 | 555.68 | 0 | 0.05921 | 6.8106 | 0 | 0 | 0 | 0 | off_peak | 555.68 |  |  | 0 | 0 | 100 | 0 | 0
4225 | 585.74 | 0 | 27.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 73.3758 | 585.74 | 0 | 0.05921 | 6.7305 | 0 | 0 | 0 | 0 | off_peak | 585.74 |  |  | 0 | 0 | 100 | 0 | 0
4226 | 562.5 | 0 | 27.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 73.3758 | 562.5 | 0 | 0.05921 | 6.7316 | 0 | 0 | 0 | 0 | off_peak | 562.5 |  |  | 0 | 0 | 100 | 0 | 0
4227 | 575.63 | 0 | 27.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 73.3758 | 575.63 | 0 | 0.05921 | 6.5057 | 0 | 0 | 0 | 0 | off_peak | 575.63 |  |  | 0 | 0 | 100 | 0 | 0
4228 | 562.86 | 0 | 27.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 73.3758 | 562.86 | 0 | 0.05921 | 5.8979 | 0 | 0 | 0 | 0 | off_peak | 562.86 |  |  | 0 | 0 | 100 | 0 | 0
4229 | 576.93 | 0 | 27.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 73.3758 | 576.93 | 0 | 0.05921 | 5.2547 | 0 | 0 | 0 | 0 | off_peak | 576.93 |  |  | 0 | 0 | 100 | 0 | 0
4230 | 694.74 | 0 | 27.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 73.3758 | 694.74 | 0 | 0.05921 | 4.5986 | 0 | 0 | 0 | 0 | off_peak | 694.74 |  |  | 0 | 0 | 100 | 0 | 0
4231 | 727.39 | 126.852 | 27.9 | 20.3355 | 20.3355 | 0 | 0 | 0.79843 | 0.79843 | 0 | 0 | 0 | 74.1227 | 707.853 | 0 | 0.05921 | 4.1642 | 0 | 0 | 0 | 20.3355 | off_peak | 707.0545 | 0 | 100 | 2.8 | 0 | 97.2 | 84.6803 | 0
4232 | 790.99 | 302.31 | 28.3 | 48.3924 | 48.3408 | 0 | 0.051567 | 0.051567 | 0 | 0 | 0 | 0 | 74.1709 | 742.6492 | 0 | 0.05921 | 3.8983 | 0 | 0 | 0.048237 | 48.3408 | off_peak | 742.6492 | 100 | 0 | 6.11 | 0 | 93.89 | 188.4477 | 0
4233 | 828.34 | 439.83 | 28.6 | 70.329 | 70.329 | 0 | 0 | 0.0033305 | 0.0033305 | 0 | 0 | 0 | 74.174 | 758.0143 | 0 | 0.05921 | 3.7214 | 0 | 0 | 0.048237 | 70.329 | off_peak | 758.011 | 0 | 100 | 8.49 | 0 | 91.51 | 261.7232 | 0
4234 | 852.22 | 695.979 | 28.8 | 111.2062 | 111.2062 | 0 | 0 | 0.0002151 | 0.0002151 | 0 | 0 | 0 | 74.1742 | 741.014 | 0 | 0.05921 | 3.6902 | 0 | 0 | 0.048237 | 111.2062 | off_peak | 741.0138 | 0 | 100 | 13.05 | 0 | 86.95 | 410.3776 | 0
4235 | 842.74 | 834.541 | 28.9 | 133.2975 | 133.2975 | 0 | 0 | 1.3893e-05 | 1.3893e-05 | 0 | 0 | 0 | 74.1743 | 709.4425 | 0 | 0.05921 | 3.8135 | 0 | 0 | 0.048237 | 133.2975 | off_peak | 709.4425 | 0 | 100 | 15.82 | 0 | 84.18 | 508.3333 | 0
4236 | 940.74 | 919.068 | 29 | 146.745 | 146.745 | 0 | 0 | 8.9726e-07 | 8.9726e-07 | 0 | 0 | 0 | 74.1743 | 793.995 | 0 | 0.05921 | 4.0806 | 0 | 0 | 0.048237 | 146.745 | off_peak | 793.995 | 0 | 100 | 15.6 | 0 | 84.4 | 598.806 | 0
4237 | 834.16 | 943.286 | 29.1 | 150.5568 | 150.5568 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1743 | 683.6032 | 0 | 0.088511 | 4.4303 | 0 | 0 | 0.048237 | 150.5568 | on_peak | 683.6032 |  |  | 18.05 | 0 | 81.95 | 667.0146 | 0
4238 | 857.04 | 907.229 | 29 | 144.8547 | 144.8547 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1743 | 712.1853 | 0 | 0.088511 | 4.8475 | 0 | 0 | 0.048237 | 144.8547 | on_peak | 712.1853 |  |  | 16.9 | 0 | 83.1 | 702.1869 | 0
4239 | 922.37 | 811.122 | 29 | 129.5096 | 129.5096 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1743 | 792.8604 | 0 | 0.088511 | 5.1645 | 0 | 0 | 0.048237 | 129.5096 | on_peak | 792.8604 |  |  | 14.04 | 0 | 85.96 | 668.8558 | 0
4240 | 848.17 | 664.778 | 28.8 | 106.2208 | 106.2208 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1743 | 741.9492 | 0 | 0.088511 | 5.5767 | 0 | 0 | 0.048237 | 106.2208 | on_peak | 741.9492 |  |  | 12.52 | 0 | 87.48 | 592.3578 | 0
4241 | 880.13 | 473.401 | 28.6 | 75.697 | 75.697 | 0 | 0 | 0 | 0 | 61.6983 | 61.6983 | 0 | 8.216 | 742.7346 | 0 | 0.088511 | 6.1067 | 0 | 0 | 0.048237 | 75.697 | on_peak | 742.7346 |  |  | 8.6 | 7.01 | 84.39 | 462.2555 | 0
4242 | 882.32 | 235.579 | 28.2 | 37.7242 | 37.7242 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.216 | 844.5958 | 0 | 0.088511 | 6.6131 | 0 | 0 | 0.048237 | 37.7242 | on_peak | 844.5958 |  |  | 4.28 | 0 | 95.72 | 249.4726 | 0
4243 | 865.33 | 78.689 | 28 | 12.6099 | 12.6099 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.216 | 852.7201 | 0 | 0.088511 | 6.752 | 0 | 0 | 0.048237 | 12.6099 | on_peak | 852.7201 |  |  | 1.46 | 0 | 98.54 | 85.1421 | 0
4244 | 877.41 | 0 | 27.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0.74696 | 0.74696 | 0 | 7.4174 | 876.663 | 0 | 0.088511 | 6.8206 | 0.045121 | 0 | 0 | 0.045121 | on_peak | 876.663 |  |  | 0 | 0.09 | 99.91 | 0.30775 | 0
4245 | 866.29 | 0 | 27.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 866.29 | 0 | 0.088511 | 7.1035 | 0 | 0 | 0 | 0 | on_peak | 866.29 |  |  | 0 | 0 | 100 | 0 | 0
4246 | 824.46 | 0 | 27.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 824.46 | 0 | 0.05921 | 7.5255 | 0 | 0 | 0 | 0 | off_peak | 824.46 |  |  | 0 | 0 | 100 | 0 | 0
4247 | 841.8 | 0 | 27.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 841.8 | 0 | 0.05921 | 7.8651 | 0 | 0 | 0 | 0 | off_peak | 841.8 |  |  | 0 | 0 | 100 | 0 | 0
4248 | 871.8 | 0 | 27.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 871.8 | 0 | 0.05921 | 8.1219 | 0 | 0 | 0 | 0 | off_peak | 871.8 |  |  | 0 | 0 | 100 | 0 | 0
4249 | 750.21 | 0 | 27.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 750.21 | 0 | 0.05921 | 8.224 | 0 | 0 | 0 | 0 | off_peak | 750.21 |  |  | 0 | 0 | 100 | 0 | 0
4250 | 685.95 | 0 | 27.3 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 18.9814 | 698.3124 | 0 | 0.05921 | 8.2069 | 0 | 0 | 0 | 0 | off_peak | 685.95 | 0 | 100 | 0 | 0 | 100 | 0 | 0
4251 | 639.64 | 0 | 27.3 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 30.5453 | 652.0024 | 0 | 0.05921 | 7.7058 | 0 | 0 | 0 | 0 | off_peak | 639.64 | 0 | 100 | 0 | 0 | 100 | 0 | 0
4252 | 624.34 | 0 | 27.3 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 42.1093 | 636.7024 | 0 | 0.05921 | 6.9073 | 0 | 0 | 0 | 0 | off_peak | 624.34 | 0 | 100 | 0 | 0 | 100 | 0 | 0
4253 | 654.17 | 0 | 27.3 | 0 | 0 | 0 | 0 | 8.7006 | 8.7006 | 0 | 0 | 0 | 50.2479 | 662.8706 | 0 | 0.05921 | 6.0533 | 0 | 0 | 0 | 0 | off_peak | 654.17 | 0 | 100 | 0 | 0 | 100 | 0 | 0
4254 | 740.45 | 0 | 27.4 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 61.8119 | 752.8124 | 0 | 0.05921 | 5.3668 | 0 | 0 | 0 | 0 | off_peak | 740.45 | 0 | 100 | 0 | 0 | 100 | 0 | 0
4255 | 754.72 | 125.615 | 27.9 | 20.1372 | 20.1372 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 61.8119 | 734.5828 | 0 | 0.05921 | 4.8463 | 0 | 0 | 0 | 20.1372 | off_peak | 734.5828 |  |  | 2.67 | 0 | 97.33 | 97.5918 | 0
4256 | 835.75 | 321.307 | 28.2 | 51.4521 | 51.4521 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 73.3758 | 796.6603 | 0 | 0.05921 | 4.5117 | 0 | 0 | 0 | 51.4521 | off_peak | 784.2979 | 0 | 100 | 6.16 | 0 | 93.84 | 232.1361 | 0
4257 | 862.03 | 519.377 | 28.4 | 83.1092 | 83.1092 | 0 | 0 | 0.79843 | 0.79843 | 0 | 0 | 0 | 74.1227 | 779.7192 | 0 | 0.05921 | 4.2804 | 0 | 0 | 0 | 83.1092 | off_peak | 778.9208 | 0 | 100 | 9.64 | 0 | 90.36 | 355.7427 | 0
4258 | 870.22 | 692.259 | 28.7 | 110.6522 | 110.6522 | 0 | 0 | 0.051567 | 0.051567 | 0 | 0 | 0 | 74.1709 | 759.6194 | 0 | 0.05921 | 4.18 | 0 | 0 | 0 | 110.6522 | off_peak | 759.5678 | 0 | 100 | 12.72 | 0 | 87.28 | 462.5307 | 0
4259 | 840.54 | 531.137 | 28.9 | 84.8361 | 84.8361 | 0 | 0 | 0.0033305 | 0.0033305 | 0 | 0 | 0 | 74.174 | 755.7072 | 0 | 0.05921 | 4.2617 | 0 | 0 | 0 | 84.8361 | off_peak | 755.7039 | 0 | 100 | 10.09 | 0 | 89.91 | 361.55 | 0
4260 | 905.35 | 456.63 | 29.1 | 72.8822 | 72.8822 | 0 | 0 | 0.0002151 | 0.0002151 | 0 | 0 | 0 | 74.1742 | 832.468 | 0 | 0.05921 | 4.4669 | 0 | 0 | 0 | 72.8822 | off_peak | 832.4678 | 0 | 100 | 8.05 | 0 | 91.95 | 325.5595 | 0
4261 | 826.47 | 236.544 | 29.2 | 37.7407 | 37.7407 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1742 | 788.7293 | 0 | 0.088511 | 4.7085 | 0 | 0 | 0 | 37.7407 | on_peak | 788.7293 |  |  | 4.57 | 0 | 95.43 | 177.7022 | 0
4262 | 899.58 | 609.965 | 29.2 | 97.3203 | 97.3203 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1742 | 802.2597 | 0 | 0.088511 | 5.1046 | 0 | 0 | 0 | 97.3203 | on_peak | 802.2597 |  |  | 10.82 | 0 | 89.18 | 496.7779 | 0
4263 | 897.27 | 782.772 | 29.3 | 124.8461 | 124.8461 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1742 | 772.4239 | 0 | 0.088511 | 5.3727 | 0 | 0 | 0 | 124.8461 | on_peak | 772.4239 |  |  | 13.91 | 0 | 86.09 | 670.7636 | 0
4264 | 860.64 | 644.908 | 29.2 | 102.8954 | 102.8954 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1742 | 757.7446 | 0 | 0.088511 | 5.8571 | 0 | 0 | 0 | 102.8954 | on_peak | 757.7446 |  |  | 11.96 | 0 | 88.04 | 602.6658 | 0
4265 | 840.57 | 463.876 | 29 | 74.0658 | 74.0658 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1742 | 766.5042 | 0 | 0.088511 | 6.3333 | 0 | 0 | 0 | 74.0658 | on_peak | 766.5042 |  |  | 8.81 | 0 | 91.19 | 469.0795 | 0
4266 | 899.78 | 233.406 | 28.7 | 37.3081 | 37.3081 | 0 | 0 | 0 | 0 | 59.9983 | 59.9983 | 0 | 10.0333 | 802.4736 | 0 | 0.088511 | 6.8394 | 0 | 0 | 0 | 37.3081 | on_peak | 802.4736 |  |  | 4.15 | 6.67 | 89.19 | 255.1658 | 0
4267 | 836.88 | 63.0649 | 28.5 | 10.0878 | 10.0878 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10.0333 | 826.7922 | 0 | 0.088511 | 7.3565 | 0 | 0 | 0 | 10.0878 | on_peak | 826.7922 |  |  | 1.21 | 0 | 98.79 | 74.211 | 0
4268 | 868.25 | 0 | 28 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10.0333 | 868.25 | 0 | 0.088511 | 7.7964 | 0 | 0 | 0 | 0 | on_peak | 868.25 |  |  | 0 | 0 | 100 | 0 | 0
4269 | 879.11 | 0 | 27.9 | 0 | 0 | 0 | 0 | 0 | 0 | 2.447 | 2.447 | 0 | 7.4174 | 876.663 | 0 | 0.088511 | 8.1366 | 0 | 0 | 0 | 0 | on_peak | 876.663 |  |  | 0 | 0.28 | 99.72 | 0 | 0
4270 | 808.12 | 0 | 27.8 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 18.9814 | 820.4824 | 0 | 0.05921 | 8.4793 | 0 | 0 | 0 | 0 | off_peak | 808.12 | 0 | 100 | 0 | 0 | 100 | 0 | 0
4271 | 818.71 | 0 | 27.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18.9814 | 818.71 | 0 | 0.05921 | 8.842 | 0 | 0 | 0 | 0 | off_peak | 818.71 |  |  | 0 | 0 | 100 | 0 | 0
4272 | 819.1 | 0 | 27.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18.9814 | 819.1 | 0 | 0.05921 | 9.0607 | 0 | 0 | 0 | 0 | off_peak | 819.1 |  |  | 0 | 0 | 100 | 0 | 0
4273 | 745.01 | 0 | 27.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18.9814 | 745.01 | 0 | 0.05921 | 8.9763 | 0 | 0 | 0 | 0 | off_peak | 745.01 |  |  | 0 | 0 | 100 | 0 | 0
4274 | 682.96 | 0 | 27.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18.9814 | 682.96 | 0 | 0.05921 | 8.677 | 0 | 0 | 0 | 0 | off_peak | 682.96 |  |  | 0 | 0 | 100 | 0 | 0
4275 | 665.99 | 0 | 27.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18.9814 | 665.99 | 0 | 0.05921 | 8.2253 | 0 | 0 | 0 | 0 | off_peak | 665.99 |  |  | 0 | 0 | 100 | 0 | 0
4276 | 607.24 | 0 | 27.3 | 0 | 0 | 0 | 0 | 8.7006 | 8.7006 | 0 | 0 | 0 | 27.12 | 615.9406 | 0 | 0.05921 | 7.5106 | 0 | 0 | 0 | 0 | off_peak | 607.24 | 0 | 100 | 0 | 0 | 100 | 0 | 0
4277 | 623.48 | 0 | 27.2 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 38.684 | 635.8424 | 0 | 0.05921 | 6.6497 | 0 | 0 | 0 | 0 | off_peak | 623.48 | 0 | 100 | 0 | 0 | 100 | 0 | 0
4278 | 731.21 | 0 | 27.4 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 50.2479 | 743.5724 | 0 | 0.05921 | 6.0049 | 0 | 0 | 0 | 0 | off_peak | 731.21 | 0 | 100 | 0 | 0 | 100 | 0 | 0
4279 | 755.5 | 111.917 | 27.9 | 17.9413 | 17.9413 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 61.8119 | 749.9211 | 0 | 0.05921 | 5.4977 | 0 | 0 | 0 | 17.9413 | off_peak | 737.5587 | 0 | 100 | 2.37 | 0 | 97.63 | 98.6356 | 0
4280 | 773.8 | 309.886 | 28.4 | 49.5871 | 49.5871 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 73.3758 | 736.5753 | 0 | 0.05921 | 5.1484 | 0 | 0 | 0 | 49.5871 | off_peak | 724.2129 | 0 | 100 | 6.41 | 0 | 93.59 | 255.2952 | 0
4281 | 816.28 | 503.024 | 28.7 | 80.4044 | 80.4044 | 0 | 0 | 0.79843 | 0.79843 | 0 | 0 | 0 | 74.1227 | 736.674 | 0 | 0.05921 | 4.8439 | 0 | 0 | 0 | 80.4044 | off_peak | 735.8756 | 0 | 100 | 9.85 | 0 | 90.15 | 389.474 | 0
4282 | 861.72 | 669.398 | 29 | 106.8809 | 106.8293 | 0 | 0.051567 | 0.051567 | 0 | 0 | 0 | 0 | 74.1709 | 754.8907 | 0 | 0.05921 | 4.7314 | 0 | 0 | 0.048237 | 106.8293 | off_peak | 754.8907 | 100 | 0 | 12.4 | 0 | 87.6 | 505.4521 | 0
4283 | 862.9 | 695.118 | 29.2 | 110.9065 | 110.9065 | 0 | 0 | 0.0033305 | 0.0033305 | 0 | 0 | 0 | 74.174 | 751.9969 | 0 | 0.05921 | 4.8242 | 0 | 0 | 0.048237 | 110.9065 | off_peak | 751.9935 | 0 | 100 | 12.85 | 0 | 87.15 | 535.0301 | 0
4284 | 920.18 | 854.174 | 29.4 | 136.1843 | 136.1843 | 0 | 0 | 0.0002151 | 0.0002151 | 0 | 0 | 0 | 74.1742 | 783.9959 | 0 | 0.05921 | 4.879 | 0 | 0 | 0.048237 | 136.1843 | off_peak | 783.9957 | 0 | 100 | 14.8 | 0 | 85.2 | 664.4465 | 0
4285 | 827.34 | 926.236 | 29.5 | 147.6194 | 147.6194 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1742 | 679.7206 | 0 | 0.088511 | 5.1197 | 0 | 0 | 0.048237 | 147.6194 | on_peak | 679.7206 |  |  | 17.84 | 0 | 82.16 | 755.7633 | 0
4286 | 879.55 | 432.183 | 29.5 | 68.8794 | 68.8794 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1742 | 810.6706 | 0 | 0.088511 | 5.4172 | 0 | 0 | 0.048237 | 68.8794 | on_peak | 810.6706 |  |  | 7.83 | 0 | 92.17 | 373.1349 | 0
4287 | 873.19 | 542.817 | 29.4 | 86.5434 | 86.5434 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1742 | 786.6466 | 0 | 0.088511 | 5.7972 | 0 | 0 | 0.048237 | 86.5434 | on_peak | 786.6466 |  |  | 9.91 | 0 | 90.09 | 501.7097 | 0
4288 | 881.13 | 489.539 | 29.3 | 78.0777 | 78.0777 | 0 | 0 | 0 | 0 | 62.4002 | 62.4002 | 0 | 7.4657 | 740.6522 | 0 | 0.088511 | 6.3011 | 0 | 0 | 0.048237 | 78.0777 | on_peak | 740.6522 |  |  | 8.86 | 7.08 | 84.06 | 491.9761 | 0
4289 | 830.14 | 280.801 | 29 | 44.8347 | 44.8347 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4657 | 785.3053 | 0 | 0.088511 | 6.8219 | 0 | 0 | 0.048237 | 44.8347 | on_peak | 785.3053 |  |  | 5.4 | 0 | 94.6 | 305.8577 | 0
4290 | 876.47 | 126.794 | 28.7 | 20.267 | 20.267 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4657 | 856.203 | 0 | 0.088511 | 7.3894 | 0 | 0 | 0.048237 | 20.267 | on_peak | 856.203 |  |  | 2.31 | 0 | 97.69 | 149.7619 | 0
4291 | 802.61 | 29.45 | 28.5 | 4.7108 | 4.7108 | 0 | 0 | 0 | 0 | 0.045121 | 0.045121 | 0 | 7.4174 | 797.8541 | 0 | 0.088511 | 7.8531 | 0.045121 | 0 | 0 | 4.7559 | on_peak | 797.8541 |  |  | 0.59 | 0.01 | 99.41 | 37.3485 | 0
4292 | 845.9 | 0 | 28 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 845.9 | 0 | 0.088511 | 8.1578 | 0 | 0 | 0 | 0 | on_peak | 845.9 |  |  | 0 | 0 | 100 | 0 | 0
4293 | 872.98 | 0 | 27.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 872.98 | 0 | 0.088511 | 8.4323 | 0 | 0 | 0 | 0 | on_peak | 872.98 |  |  | 0 | 0 | 100 | 0 | 0
4294 | 838.2 | 0 | 27.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 838.2 | 0 | 0.05921 | 8.6023 | 0 | 0 | 0 | 0 | off_peak | 838.2 |  |  | 0 | 0 | 100 | 0 | 0
4295 | 889.93 | 0 | 27.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 889.93 | 0 | 0.05921 | 8.7147 | 0 | 0 | 0 | 0 | off_peak | 889.93 |  |  | 0 | 0 | 100 | 0 | 0
4296 | 819.44 | 0 | 27.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 819.44 | 0 | 0.05921 | 8.8101 | 0 | 0 | 0 | 0 | off_peak | 819.44 |  |  | 0 | 0 | 100 | 0 | 0
4297 | 769.51 | 0 | 27.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 769.51 | 0 | 0.05921 | 8.7498 | 0 | 0 | 0 | 0 | off_peak | 769.51 |  |  | 0 | 0 | 100 | 0 | 0
4298 | 694.35 | 0 | 27.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 694.35 | 0 | 0.05921 | 8.5514 | 0 | 0 | 0 | 0 | off_peak | 694.35 |  |  | 0 | 0 | 100 | 0 | 0
4299 | 633.26 | 0 | 27.5 | 0 | 0 | 0 | 0 | 8.7006 | 8.7006 | 0 | 0 | 0 | 15.5561 | 641.9606 | 0 | 0.05921 | 8.0414 | 0 | 0 | 0 | 0 | off_peak | 633.26 | 0 | 100 | 0 | 0 | 100 | 0 | 0
4300 | 642.23 | 0 | 27.5 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 27.12 | 654.5924 | 0 | 0.05921 | 7.1941 | 0 | 0 | 0 | 0 | off_peak | 642.23 | 0 | 100 | 0 | 0 | 100 | 0 | 0
4301 | 660.47 | 0 | 27.5 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 38.684 | 672.8324 | 0 | 0.05921 | 6.388 | 0 | 0 | 0 | 0 | off_peak | 660.47 | 0 | 100 | 0 | 0 | 100 | 0 | 0
4302 | 706.37 | 0 | 27.7 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 50.2479 | 718.7324 | 0 | 0.05921 | 5.6523 | 0 | 0 | 0 | 0 | off_peak | 706.37 | 0 | 100 | 0 | 0 | 100 | 0 | 0
4303 | 740.64 | 117.994 | 28.1 | 18.9017 | 18.9017 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 61.8119 | 734.1007 | 0 | 0.05921 | 5.1415 | 0 | 0 | 0 | 18.9017 | off_peak | 721.7383 | 0 | 100 | 2.55 | 0 | 97.45 | 97.1833 | 0
4304 | 760.3 | 309.228 | 28.4 | 49.4818 | 49.4818 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 73.3758 | 723.1806 | 0 | 0.05921 | 4.7923 | 0 | 0 | 0 | 49.4818 | off_peak | 710.8182 | 0 | 100 | 6.51 | 0 | 93.49 | 237.1316 | 0
4305 | 809.3 | 507.514 | 28.7 | 81.1221 | 81.1221 | 0 | 0 | 0.79843 | 0.79843 | 0 | 0 | 0 | 74.1227 | 728.9763 | 0 | 0.05921 | 4.5418 | 0 | 0 | 0 | 81.1221 | off_peak | 728.1779 | 0 | 100 | 10.02 | 0 | 89.98 | 368.4387 | 0
4306 | 845.77 | 681.142 | 28.9 | 108.7958 | 108.7958 | 0 | 0 | 0.051567 | 0.051567 | 0 | 0 | 0 | 74.1709 | 737.0258 | 0 | 0.05921 | 4.4301 | 0 | 0 | 0 | 108.7958 | off_peak | 736.9742 | 0 | 100 | 12.86 | 0 | 87.14 | 481.9789 | 0
4307 | 858.12 | 669.974 | 29.2 | 106.8947 | 106.8947 | 0 | 0 | 0.0033305 | 0.0033305 | 0 | 0 | 0 | 74.174 | 751.2286 | 0 | 0.05921 | 4.5107 | 0 | 0 | 0 | 106.8947 | off_peak | 751.2253 | 0 | 100 | 12.46 | 0 | 87.54 | 482.1667 | 0
4308 | 945.59 | 747.689 | 29.3 | 119.2506 | 119.2506 | 0 | 0 | 0.0002151 | 0.0002151 | 0 | 0 | 0 | 74.1742 | 826.3396 | 0 | 0.05921 | 4.6769 | 0 | 0 | 0 | 119.2506 | off_peak | 826.3394 | 0 | 100 | 12.61 | 0 | 87.39 | 557.7274 | 0
4309 | 850.71 | 736.669 | 29.5 | 117.4071 | 117.4071 | 0 | 0 | 1.3893e-05 | 1.3893e-05 | 0 | 0 | 0 | 74.1743 | 733.303 | 0 | 0.088511 | 4.7509 | 0 | 0 | 0 | 117.4071 | on_peak | 733.3029 | 0 | 100 | 13.8 | 0 | 86.2 | 557.793 | 0
4310 | 905.14 | 555.807 | 29.5 | 88.5821 | 88.5821 | 0 | 0 | 8.9726e-07 | 8.9726e-07 | 0 | 0 | 0 | 74.1743 | 816.5579 | 0 | 0.088511 | 5.0787 | 0 | 0 | 0 | 88.5821 | on_peak | 816.5579 | 0 | 100 | 9.79 | 0 | 90.21 | 449.8848 | 0
4311 | 948.32 | 349.814 | 29.6 | 55.7314 | 55.7314 | 0 | 0 | 0 | 0 | 15.9255 | 15.9255 | 0 | 57.1491 | 876.663 | 0 | 0.088511 | 5.4294 | 0 | 0 | 0 | 55.7314 | on_peak | 876.663 |  |  | 5.88 | 1.68 | 92.44 | 302.5862 | 0
4312 | 918.76 | 520.165 | 29.5 | 82.9016 | 82.9016 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 68.7131 | 848.2208 | 0 | 0.088511 | 5.9872 | 0 | 0 | 0 | 82.9016 | on_peak | 835.8584 | 0 | 100 | 9.02 | 0 | 90.98 | 496.3519 | 0
4313 | 908.45 | 440.751 | 29.3 | 70.2964 | 70.2964 | 0 | 0 | 5.4612 | 5.4612 | 0 | 0 | 0 | 73.8215 | 843.6148 | 0 | 0.088511 | 6.5599 | 0 | 0 | 0 | 70.2964 | on_peak | 838.1536 | 0 | 100 | 7.74 | 0 | 92.26 | 461.1393 | 0
4314 | 912.3 | 273.181 | 29 | 43.618 | 43.618 | 0 | 0 | 0.35271 | 0.35271 | 0 | 0 | 0 | 74.1515 | 869.0347 | 0 | 0.088511 | 6.947 | 0 | 0 | 0 | 43.618 | on_peak | 868.682 | 0 | 100 | 4.78 | 0 | 95.22 | 303.0165 | 0
4315 | 883.31 | 72.8508 | 28.8 | 11.6404 | 11.6176 | 0 | 0.02278 | 0.02278 | 0 | 0 | 0 | 0 | 74.1728 | 871.6924 | 0 | 0.088511 | 7.6054 | 0 | 0 | 0.021309 | 11.6176 | on_peak | 871.6924 | 100 | 0 | 1.32 | 0 | 98.68 | 88.3569 | 0
4316 | 903.02 | 0 | 28.2 | 0 | 0 | 0 | 0 | 0 | 0 | 26.357 | 26.357 | 0 | 45.996 | 876.663 | 0 | 0.088511 | 7.7649 | 0.019933 | 0 | 0 | 0.019933 | on_peak | 876.663 |  |  | 0 | 2.92 | 97.08 | 0.15478 | 0
4317 | 912.75 | 0 | 28 | 0 | 0 | 0 | 0 | 0 | 0 | 36.087 | 36.087 | 0 | 7.4174 | 876.663 | 0 | 0.088511 | 7.5488 | 0 | 0 | 0 | 0 | on_peak | 876.663 |  |  | 0 | 3.95 | 96.05 | 0 | 0
4318 | 898.63 | 0 | 27.9 | 0 | 0 | 0 | 0 | 1.28 | 1.28 | 0 | 0 | 0 | 8.6148 | 899.91 | 0 | 0.05921 | 7.5593 | 0 | 0 | 0 | 0 | off_peak | 898.63 | 0 | 100 | 0 | 0 | 100 | 0 | 0
4319 | 901.03 | 0 | 27.7 | 0 | 0 | 0 | 0 | 0 | 0 | 1.12 | 1.12 | 0 | 7.4174 | 899.91 | 0 | 0.05921 | 7.7988 | 0 | 0 | 0 | 0 | off_peak | 899.91 |  |  | 0 | 0.12 | 99.88 | 0 | 0
4320 | 855.91 | 0 | 27.6 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 18.9814 | 868.2724 | 0 | 0.05921 | 8.0187 | 0 | 0 | 0 | 0 | off_peak | 855.91 | 0 | 100 | 0 | 0 | 100 | 0 | 0
4321 | 808.07 | 0 | 27.6 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 30.5453 | 820.4324 | 0 | 0.05921 | 8.0122 | 0 | 0 | 0 | 0 | off_peak | 808.07 | 0 | 100 | 0 | 0 | 100 | 0 | 0
4322 | 700.18 | 0 | 27.5 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 42.1093 | 712.5424 | 0 | 0.05921 | 7.7607 | 0 | 0 | 0 | 0 | off_peak | 700.18 | 0 | 100 | 0 | 0 | 100 | 0 | 0
4323 | 689.71 | 0 | 27.5 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 53.6732 | 702.0724 | 0 | 0.05921 | 7.344 | 0 | 0 | 0 | 0 | off_peak | 689.71 | 0 | 100 | 0 | 0 | 100 | 0 | 0
4324 | 691.77 | 0 | 27.5 | 0 | 0 | 0 | 0 | 8.7006 | 8.7006 | 0 | 0 | 0 | 61.8119 | 700.4706 | 0 | 0.05921 | 6.848 | 0 | 0 | 0 | 0 | off_peak | 691.77 | 0 | 100 | 0 | 0 | 100 | 0 | 0
4325 | 652.42 | 0 | 27.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 61.8119 | 652.42 | 0 | 0.05921 | 6.1972 | 0 | 0 | 0 | 0 | off_peak | 652.42 |  |  | 0 | 0 | 100 | 0 | 0
4326 | 796.84 | 0 | 27.7 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 73.3758 | 809.2024 | 0 | 0.05921 | 5.5312 | 0 | 0 | 0 | 0 | off_peak | 796.84 | 0 | 100 | 0 | 0 | 100 | 0 | 0
4327 | 841.46 | 105.825 | 28 | 16.9585 | 16.9585 | 0 | 0 | 0.79843 | 0.79843 | 0 | 0 | 0 | 74.1227 | 825.2999 | 0 | 0.05921 | 4.9401 | 0 | 0 | 0 | 16.9585 | off_peak | 824.5015 | 0 | 100 | 2.02 | 0 | 97.98 | 83.776 | 0
4328 | 861.1 | 27.9337 | 28.4 | 4.4699 | 4.4699 | 0 | 0 | 0.051567 | 0.051567 | 0 | 0 | 0 | 74.1709 | 856.6817 | 0 | 0.05921 | 4.5396 | 0 | 0 | 0 | 4.4699 | off_peak | 856.6301 | 0 | 100 | 0.52 | 0 | 99.48 | 20.2913 | 0
4329 | 910.25 | 18.05 | 28.6 | 2.8862 | 2.8862 | 0 | 0 | 0 | 0 | 7.4538 | 7.4538 | 0 | 66.2025 | 899.91 | 0 | 0.05921 | 4.298 | 0 | 0 | 0 | 2.8862 | off_peak | 899.91 |  |  | 0.32 | 0.82 | 98.86 | 12.405 | 0
4330 | 941.69 | 537.796 | 28.8 | 85.9311 | 85.9311 | 0 | 0 | 7.9718 | 7.9718 | 0 | 0 | 0 | 73.6594 | 863.7307 | 0 | 0.05921 | 4.1918 | 0 | 0 | 0 | 85.9311 | off_peak | 855.7589 | 0 | 100 | 9.13 | 0 | 90.87 | 360.2084 | 0
4331 | 905.85 | 447.146 | 29.1 | 71.3685 | 71.3685 | 0 | 0 | 0.51486 | 0.51486 | 0 | 0 | 0 | 74.141 | 834.9964 | 0 | 0.05921 | 4.2528 | 0 | 0 | 0 | 71.3685 | off_peak | 834.4815 | 0 | 100 | 7.88 | 0 | 92.12 | 303.5135 | 0
4332 | 974.85 | 251.585 | 29.3 | 40.1259 | 40.1259 | 0 | 0 | 0 | 0 | 34.8141 | 34.8141 | 0 | 36.9231 | 899.91 | 0 | 0.05921 | 4.4395 | 0 | 0 | 0 | 40.1259 | off_peak | 899.91 |  |  | 4.12 | 3.57 | 92.31 | 178.1397 | 0
4333 | 914.45 | 542.299 | 29.4 | 86.4609 | 86.4609 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 36.9231 | 827.9891 | 0 | 0.088511 | 4.6461 | 0 | 0 | 0 | 86.4609 | on_peak | 827.9891 |  |  | 9.45 | 0 | 90.55 | 401.702 | 0
4334 | 929.73 | 562.378 | 29.4 | 89.6621 | 89.6621 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 36.9231 | 840.0679 | 0 | 0.088511 | 5.019 | 0 | 0 | 0 | 89.6621 | on_peak | 840.0679 |  |  | 9.64 | 0 | 90.36 | 450.0141 | 0
4335 | 947.18 | 514.986 | 29.4 | 82.1062 | 82.1062 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 36.9231 | 865.0738 | 0 | 0.088511 | 5.4925 | 0 | 0 | 0 | 82.1062 | on_peak | 865.0738 |  |  | 8.67 | 0 | 91.33 | 450.972 | 0
4336 | 893.49 | 448.287 | 29.3 | 71.4983 | 71.4983 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 36.9231 | 821.9917 | 0 | 0.088511 | 5.9493 | 0 | 0 | 0 | 71.4983 | on_peak | 821.9917 |  |  | 8 | 0 | 92 | 425.3676 | 0
4337 | 903.1 | 478.94 | 29.2 | 76.4151 | 76.4151 | 0 | 0 | 0 | 0 | 16.5331 | 16.5331 | 0 | 19.2485 | 810.1518 | 0 | 0.088511 | 6.3663 | 0 | 0 | 0 | 76.4151 | on_peak | 810.1518 |  |  | 8.46 | 1.83 | 89.71 | 486.4825 | 0
4338 | 887.66 | 283.102 | 28.9 | 45.2186 | 45.2186 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19.2485 | 842.4414 | 0 | 0.088511 | 6.6553 | 0 | 0 | 0 | 45.2186 | on_peak | 842.4414 |  |  | 5.09 | 0 | 94.91 | 300.9435 | 0
4339 | 886.01 | 70.0284 | 28.7 | 11.1935 | 11.1935 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19.2485 | 874.8165 | 0 | 0.088511 | 6.8055 | 0 | 0 | 0 | 11.1935 | on_peak | 874.8165 |  |  | 1.26 | 0 | 98.74 | 76.1778 | 0
4340 | 887.73 | 0 | 27.6 | 0 | 0 | 0 | 0 | 0 | 0 | 11.067 | 11.067 | 0 | 7.4174 | 876.663 | 0 | 0.088511 | 6.8945 | 0 | 0 | 0 | 0 | on_peak | 876.663 |  |  | 0 | 1.25 | 98.75 | 0 | 0
4341 | 857.14 | 0 | 27.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 857.14 | 0 | 0.088511 | 7.1954 | 0 | 0 | 0 | 0 | on_peak | 857.14 |  |  | 0 | 0 | 100 | 0 | 0
4342 | 835.6 | 0 | 27.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 835.6 | 0 | 0.05921 | 7.5435 | 0 | 0 | 0 | 0 | off_peak | 835.6 |  |  | 0 | 0 | 100 | 0 | 0
4343 | 852.37 | 0 | 27.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 852.37 | 0 | 0.05921 | 7.7541 | 0 | 0 | 0 | 0 | off_peak | 852.37 |  |  | 0 | 0 | 100 | 0 | 0
4344 | 851.91 | 0 | 27.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 851.91 | 0 | 0.05921 | 7.894 | 0 | 0 | 0 | 0 | off_peak | 851.91 |  |  | 0 | 0 | 100 | 0 | 0
4345 | 743.62 | 0 | 27.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 743.62 | 0 | 0.05921 | 7.9798 | 0 | 0 | 0 | 0 | off_peak | 743.62 |  |  | 0 | 0 | 100 | 0 | 0
4346 | 708.41 | 0 | 27.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 708.41 | 0 | 0.05921 | 7.7705 | 0 | 0 | 0 | 0 | off_peak | 708.41 |  |  | 0 | 0 | 100 | 0 | 0
4347 | 651.52 | 0 | 27 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 651.52 | 0 | 0.05921 | 7.3122 | 0 | 0 | 0 | 0 | off_peak | 651.52 |  |  | 0 | 0 | 100 | 0 | 0
4348 | 683.67 | 0 | 27 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 683.67 | 0 | 0.05921 | 6.7962 | 0 | 0 | 0 | 0 | off_peak | 683.67 |  |  | 0 | 0 | 100 | 0 | 0
4349 | 691.87 | 0 | 27 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 691.87 | 0 | 0.05921 | 6.171 | 0 | 0 | 0 | 0 | off_peak | 691.87 |  |  | 0 | 0 | 100 | 0 | 0
4350 | 746.31 | 0 | 27.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 746.31 | 0 | 0.05921 | 5.6381 | 0 | 0 | 0 | 0 | off_peak | 746.31 |  |  | 0 | 0 | 100 | 0 | 0
4351 | 800.65 | 86.7005 | 27.6 | 13.914 | 13.914 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 786.736 | 0 | 0.05921 | 5.1201 | 0 | 0 | 0 | 13.914 | off_peak | 786.736 |  |  | 1.74 | 0 | 98.26 | 71.2408 | 0
4352 | 822.7 | 244.12 | 28 | 39.1203 | 39.1203 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 783.5797 | 0 | 0.05921 | 4.7271 | 0 | 0 | 0 | 39.1203 | off_peak | 783.5797 |  |  | 4.76 | 0 | 95.24 | 184.9259 | 0
4353 | 858.84 | 514.472 | 28.3 | 82.3543 | 82.3543 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 776.4857 | 0 | 0.05921 | 4.437 | 0 | 0 | 0 | 82.3543 | off_peak | 776.4857 |  |  | 9.59 | 0 | 90.41 | 365.4067 | 0
4354 | 826.64 | 692.662 | 28.5 | 110.7974 | 110.7974 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 715.8426 | 0 | 0.05921 | 4.2707 | 0 | 0 | 0 | 110.7974 | off_peak | 715.8426 |  |  | 13.4 | 0 | 86.6 | 473.1851 | 0
4355 | 816.58 | 786.418 | 28.8 | 125.6569 | 125.6569 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 690.9231 | 0 | 0.05921 | 4.2362 | 0 | 0 | 0 | 125.6569 | off_peak | 690.9231 |  |  | 15.39 | 0 | 84.61 | 532.3106 | 0
4356 | 858.86 | 873.086 | 29 | 139.4032 | 130.7026 | 0 | 8.7006 | 8.7006 | 0 | 0 | 0 | 0 | 15.5561 | 728.1574 | 0 | 0.05921 | 4.2407 | 0 | 0 | 8.1387 | 130.7026 | off_peak | 728.1574 | 100 | 0 | 15.22 | 0 | 84.78 | 554.2644 | 0
4357 | 803.29 | 945.072 | 29.2 | 150.7868 | 150.7868 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15.5561 | 652.5032 | 0 | 0.05921 | 4.3977 | 0 | 0 | 8.1387 | 150.7868 | off_peak | 652.5032 |  |  | 18.77 | 0 | 81.23 | 663.1175 | 0
4358 | 797.82 | 910.765 | 29.3 | 145.2599 | 145.2599 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15.5561 | 652.5601 | 0 | 0.05921 | 4.8615 | 0 | 0 | 8.1387 | 145.2599 | off_peak | 652.5601 |  |  | 18.21 | 0 | 81.79 | 706.1749 | 0
4359 | 779.69 | 815.628 | 29.3 | 130.0863 | 130.0863 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15.5561 | 649.6037 | 0 | 0.05921 | 5.3287 | 0 | 0 | 8.1387 | 130.0863 | off_peak | 649.6037 |  |  | 16.68 | 0 | 83.32 | 693.1906 | 0
4360 | 820.62 | 671.374 | 29.2 | 107.1181 | 107.1181 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15.5561 | 713.5019 | 0 | 0.05921 | 5.8104 | 0 | 0 | 8.1387 | 107.1181 | off_peak | 713.5019 |  |  | 13.05 | 0 | 86.95 | 622.4016 | 0
4361 | 802.32 | 487.968 | 29 | 77.9125 | 77.9125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15.5561 | 724.4075 | 0 | 0.05921 | 6.3024 | 0 | 0 | 8.1387 | 77.9125 | off_peak | 724.4075 |  |  | 9.71 | 0 | 90.29 | 491.0378 | 0
4362 | 786.89 | 285.764 | 28.6 | 45.6938 | 45.6938 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15.5561 | 741.1962 | 0 | 0.05921 | 6.7152 | 0 | 0 | 8.1387 | 45.6938 | off_peak | 741.1962 |  |  | 5.81 | 0 | 94.19 | 306.8416 | 0
4363 | 679.62 | 93.4044 | 28.4 | 14.9463 | 2.5839 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 0 | 27.12 | 677.0361 | 0 | 0.05921 | 6.972 | 0 | 0 | 19.7026 | 2.5839 | off_peak | 677.0361 | 100 | 0 | 0.38 | 0 | 99.62 | 18.015 | 0
4364 | 696.89 | 0 | 27.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27.12 | 696.89 | 0 | 0.05921 | 7.173 | 0 | 0 | 19.7026 | 0 | off_peak | 696.89 |  |  | 0 | 0 | 100 | 0 | 0
4365 | 689.52 | 0 | 27.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27.12 | 689.52 | 0 | 0.05921 | 7.4858 | 0 | 0 | 19.7026 | 0 | off_peak | 689.52 |  |  | 0 | 0 | 100 | 0 | 0
4366 | 693.36 | 0 | 27.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27.12 | 693.36 | 0 | 0.05921 | 7.756 | 0 | 0 | 19.7026 | 0 | off_peak | 693.36 |  |  | 0 | 0 | 100 | 0 | 0
4367 | 682.92 | 0 | 27.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27.12 | 682.92 | 0 | 0.05921 | 7.9149 | 0 | 0 | 19.7026 | 0 | off_peak | 682.92 |  |  | 0 | 0 | 100 | 0 | 0
4368 | 656 | 0 | 27.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27.12 | 656 | 0 | 0.05921 | 7.9831 | 0 | 0 | 19.7026 | 0 | off_peak | 656 |  |  | 0 | 0 | 100 | 0 | 0
4369 | 706.09 | 0 | 27.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27.12 | 706.09 | 0 | 0.05921 | 8.007 | 0 | 0 | 19.7026 | 0 | off_peak | 706.09 |  |  | 0 | 0 | 100 | 0 | 0
4370 | 664.52 | 0 | 27.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27.12 | 664.52 | 0 | 0.05921 | 7.8044 | 0 | 0 | 19.7026 | 0 | off_peak | 664.52 |  |  | 0 | 0 | 100 | 0 | 0
4371 | 672.79 | 0 | 27 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27.12 | 672.79 | 0 | 0.05921 | 7.2976 | 0 | 0 | 19.7026 | 0 | off_peak | 672.79 |  |  | 0 | 0 | 100 | 0 | 0
4372 | 702.91 | 0 | 27 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27.12 | 702.91 | 0 | 0.05921 | 6.7205 | 0 | 0 | 19.7026 | 0 | off_peak | 702.91 |  |  | 0 | 0 | 100 | 0 | 0
4373 | 708.77 | 0 | 27 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27.12 | 708.77 | 0 | 0.05921 | 6.1674 | 0 | 0 | 19.7026 | 0 | off_peak | 708.77 |  |  | 0 | 0 | 100 | 0 | 0
4374 | 741.57 | 0 | 27.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27.12 | 741.57 | 0 | 0.05921 | 5.5509 | 0 | 0 | 19.7026 | 0 | off_peak | 741.57 |  |  | 0 | 0 | 100 | 0 | 0
4375 | 756.16 | 93.0262 | 27.6 | 14.9292 | 14.9292 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27.12 | 741.2308 | 0 | 0.05921 | 5.0615 | 0 | 0 | 19.7026 | 14.9292 | off_peak | 741.2308 |  |  | 1.97 | 0 | 98.03 | 75.564 | 0
4376 | 798.95 | 143.675 | 27.9 | 23.0324 | 23.0324 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27.12 | 775.9176 | 0 | 0.05921 | 4.6975 | 0 | 0 | 19.7026 | 23.0324 | off_peak | 775.9176 |  |  | 2.88 | 0 | 97.12 | 108.195 | 0
4377 | 802.2 | 513.126 | 28 | 82.2286 | 82.2286 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 38.684 | 732.3337 | 0 | 0.05921 | 4.435 | 0 | 0 | 19.7026 | 82.2286 | off_peak | 719.9714 | 0 | 100 | 10.25 | 0 | 89.75 | 364.6817 | 0
4378 | 819.79 | 648.081 | 28.2 | 103.7796 | 103.7796 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 50.2479 | 728.3727 | 0 | 0.05921 | 4.2468 | 0 | 0 | 19.7026 | 103.7796 | off_peak | 716.0104 | 0 | 100 | 12.66 | 0 | 87.34 | 440.7298 | 0
4379 | 836.92 | 422.996 | 28.4 | 67.6866 | 67.6866 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 61.8119 | 781.5958 | 0 | 0.05921 | 4.1604 | 0 | 0 | 19.7026 | 67.6866 | off_peak | 769.2334 | 0 | 100 | 8.09 | 0 | 91.91 | 281.6042 | 0
4380 | 814.26 | 839.142 | 28.6 | 134.1792 | 134.1792 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 73.3758 | 692.4432 | 0 | 0.05921 | 4.1449 | 0 | 0 | 19.7026 | 134.1792 | off_peak | 680.0808 | 0 | 100 | 16.48 | 0 | 83.52 | 556.1532 | 0
4381 | 834.32 | 943.139 | 28.7 | 150.7534 | 150.7534 | 0 | 0 | 0.79843 | 0.79843 | 0 | 0 | 0 | 74.1227 | 684.3651 | 0 | 0.05921 | 4.2393 | 0 | 0 | 19.7026 | 150.7534 | off_peak | 683.5666 | 0 | 100 | 18.07 | 0 | 81.93 | 639.085 | 0
4382 | 799.08 | 823.107 | 28.7 | 131.5672 | 131.5672 | 0 | 0 | 0.051567 | 0.051567 | 0 | 0 | 0 | 74.1709 | 667.5644 | 0 | 0.05921 | 4.6399 | 0 | 0 | 19.7026 | 131.5672 | off_peak | 667.5128 | 0 | 100 | 16.46 | 0 | 83.54 | 610.4531 | 0
4383 | 798.31 | 812.051 | 28.7 | 129.8 | 129.8 | 0 | 0 | 0.0033305 | 0.0033305 | 0 | 0 | 0 | 74.174 | 668.5133 | 0 | 0.05921 | 5.1784 | 0 | 0 | 19.7026 | 129.8 | off_peak | 668.51 | 0 | 100 | 16.26 | 0 | 83.74 | 672.16 | 0
4384 | 786.82 | 667.187 | 28.7 | 106.6446 | 106.6446 | 0 | 0 | 0.0002151 | 0.0002151 | 0 | 0 | 0 | 74.1742 | 680.1756 | 0 | 0.05921 | 5.7346 | 0 | 0 | 19.7026 | 106.6446 | off_peak | 680.1754 | 0 | 100 | 13.55 | 0 | 86.45 | 611.5614 | 0
4385 | 757.03 | 476.033 | 28.5 | 76.1457 | 76.1457 | 0 | 1.4852e-05 | 1.4852e-05 | 0 | 0 | 0 | 0 | 74.1743 | 680.8843 | 0 | 0.05921 | 6.3444 | 0 | 0 | 19.7026 | 76.1457 | off_peak | 680.8843 | 100 | 0 | 10.06 | 0 | 89.94 | 483.1015 | 0
4386 | 747.46 | 265.568 | 28.2 | 42.5264 | 42.5264 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1743 | 704.9336 | 0 | 0.05921 | 6.9806 | 0 | 0 | 19.7026 | 42.5264 | off_peak | 704.9336 |  |  | 5.69 | 0 | 94.31 | 296.8608 | 0
4387 | 680.55 | 89.5663 | 28 | 14.353 | 14.353 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1743 | 666.197 | 0 | 0.05921 | 7.4921 | 0 | 0 | 19.7026 | 14.353 | off_peak | 666.197 |  |  | 2.11 | 0 | 97.89 | 107.5342 | 0
4388 | 664.54 | 0 | 27.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1743 | 664.54 | 0 | 0.05921 | 7.8088 | 0 | 0 | 19.7026 | 0 | off_peak | 664.54 |  |  | 0 | 0 | 100 | 0 | 0
4389 | 662.87 | 0 | 27.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1743 | 662.87 | 0 | 0.05921 | 7.925 | 0 | 0 | 19.7026 | 0 | off_peak | 662.87 |  |  | 0 | 0 | 100 | 0 | 0
4390 | 652.76 | 0 | 27.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1743 | 652.76 | 0 | 0.05921 | 8.2159 | 0 | 0 | 19.7026 | 0 | off_peak | 652.76 |  |  | 0 | 0 | 100 | 0 | 0
4391 | 664.28 | 0 | 27.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1743 | 664.28 | 0 | 0.05921 | 8.2881 | 0 | 0 | 19.7026 | 0 | off_peak | 664.28 |  |  | 0 | 0 | 100 | 0 | 0
4392 | 672.53 | 0 | 27 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1743 | 672.53 | 0 | 0.05921 | 8.2934 | 0 | 0 | 19.7026 | 0 | off_peak | 672.53 |  |  | 0 | 0 | 100 | 0 | 0
4393 | 638.74 | 0 | 26.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1743 | 638.74 | 0 | 0.05921 | 8.1646 | 0 | 0 | 19.7026 | 0 | off_peak | 638.74 |  |  | 0 | 0 | 100 | 0 | 0
4394 | 655.29 | 0 | 26.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1743 | 655.29 | 0 | 0.05921 | 7.7503 | 0 | 0 | 19.7026 | 0 | off_peak | 655.29 |  |  | 0 | 0 | 100 | 0 | 0
4395 | 666 | 0 | 26.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1743 | 666 | 0 | 0.05921 | 7.3272 | 0 | 0 | 19.7026 | 0 | off_peak | 666 |  |  | 0 | 0 | 100 | 0 | 0
4396 | 649.29 | 0 | 26.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1743 | 649.29 | 0 | 0.05921 | 6.7722 | 0 | 0 | 19.7026 | 0 | off_peak | 649.29 |  |  | 0 | 0 | 100 | 0 | 0
4397 | 668.43 | 0 | 26.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1743 | 668.43 | 0 | 0.05921 | 6.1403 | 0 | 0 | 19.7026 | 0 | off_peak | 668.43 |  |  | 0 | 0 | 100 | 0 | 0
4398 | 797.81 | 0 | 27 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1743 | 797.81 | 0 | 0.05921 | 5.5721 | 0 | 0 | 19.7026 | 0 | off_peak | 797.81 |  |  | 0 | 0 | 100 | 0 | 0
4399 | 775.9 | 118.305 | 27.5 | 18.9929 | 18.9929 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1743 | 756.9071 | 0 | 0.05921 | 5.0449 | 0 | 0 | 19.7026 | 18.9929 | off_peak | 756.9071 |  |  | 2.45 | 0 | 97.55 | 95.8181 | 0
4400 | 837.95 | 316.085 | 27.9 | 50.6712 | 50.6712 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1743 | 787.2788 | 0 | 0.05921 | 4.7205 | 0 | 0 | 19.7026 | 50.6712 | off_peak | 787.2788 |  |  | 6.05 | 0 | 93.95 | 239.193 | 0
4401 | 900.6 | 458.135 | 28.3 | 73.3362 | 73.3362 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1743 | 827.2638 | 0 | 0.05921 | 4.5163 | 0 | 0 | 19.7026 | 73.3362 | off_peak | 827.2638 |  |  | 8.14 | 0 | 91.86 | 331.2084 | 0
4402 | 900.67 | 698.718 | 28.7 | 111.6846 | 111.6846 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1743 | 788.9854 | 0 | 0.05921 | 4.4207 | 0 | 0 | 19.7026 | 111.6846 | off_peak | 788.9854 |  |  | 12.4 | 0 | 87.6 | 493.7222 | 0
4403 | 799.69 | 838.458 | 29.1 | 133.8253 | 133.8253 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1743 | 665.8647 | 0 | 0.05921 | 4.5195 | 0 | 0 | 19.7026 | 133.8253 | off_peak | 665.8647 |  |  | 16.73 | 0 | 83.27 | 604.8185 | 0
4404 | 868.75 | 924.241 | 29.3 | 147.4093 | 147.4093 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1743 | 721.3407 | 0 | 0.05921 | 4.6764 | 0 | 0 | 19.7026 | 147.4093 | off_peak | 721.3407 |  |  | 16.97 | 0 | 83.03 | 689.3418 | 0
4405 | 844.78 | 948.774 | 29.5 | 151.2114 | 151.2114 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1743 | 693.5686 | 0 | 0.088511 | 4.8678 | 0 | 0 | 19.7026 | 151.2114 | on_peak | 693.5686 |  |  | 17.9 | 0 | 82.1 | 736.0713 | 0
4406 | 856.31 | 893.517 | 29.6 | 142.3527 | 142.3527 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1743 | 713.9573 | 0 | 0.088511 | 5.3286 | 0 | 0 | 19.7026 | 142.3527 | on_peak | 713.9573 |  |  | 16.62 | 0 | 83.38 | 758.542 | 0
4407 | 898.97 | 797.416 | 29.5 | 127.0887 | 127.0887 | 0 | 0 | 0 | 0 | 62.4453 | 62.4453 | 0 | 7.4174 | 709.4361 | 0 | 0.088511 | 5.781 | 18.4301 | 0 | 0 | 145.5188 | on_peak | 709.4361 |  |  | 14.14 | 6.95 | 78.92 | 841.2439 | 0
4408 | 872.61 | 652.805 | 29.3 | 104.1173 | 104.1173 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 768.4927 | 0 | 0.088511 | 6.373 | 0 | 0 | 0 | 104.1173 | on_peak | 768.4927 |  |  | 11.93 | 0 | 88.07 | 663.5418 | 0
4409 | 840.78 | 471.055 | 29 | 75.212 | 75.212 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 765.568 | 0 | 0.088511 | 7.012 | 0 | 0 | 0 | 75.212 | on_peak | 765.568 |  |  | 8.95 | 0 | 91.05 | 527.3875 | 0
4410 | 782.81 | 272.047 | 28.6 | 43.5004 | 43.5004 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 739.3096 | 0 | 0.088511 | 7.6409 | 0 | 0 | 0 | 43.5004 | on_peak | 739.3096 |  |  | 5.56 | 0 | 94.44 | 332.3831 | 0
4411 | 788.76 | 86.2231 | 28.4 | 13.7972 | 13.7972 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 774.9628 | 0 | 0.088511 | 8.0509 | 0 | 0 | 0 | 13.7972 | on_peak | 774.9628 |  |  | 1.75 | 0 | 98.25 | 111.0803 | 0
4412 | 777.62 | 0 | 27.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 777.62 | 0 | 0.088511 | 8.3378 | 0 | 0 | 0 | 0 | on_peak | 777.62 |  |  | 0 | 0 | 100 | 0 | 0
4413 | 789.41 | 0 | 27.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 789.41 | 0 | 0.088511 | 8.4545 | 0 | 0 | 0 | 0 | on_peak | 789.41 |  |  | 0 | 0 | 100 | 0 | 0
4414 | 782.71 | 0 | 27.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 782.71 | 0 | 0.05921 | 8.6239 | 0 | 0 | 0 | 0 | off_peak | 782.71 |  |  | 0 | 0 | 100 | 0 | 0
4415 | 709.22 | 0 | 27.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 709.22 | 0 | 0.05921 | 8.5957 | 0 | 0 | 0 | 0 | off_peak | 709.22 |  |  | 0 | 0 | 100 | 0 | 0
4416 | 731.86 | 0 | 27.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 731.86 | 0 | 0.05921 | 8.6494 | 0 | 0 | 0 | 0 | off_peak | 731.86 |  |  | 0 | 0 | 100 | 0 | 0
4417 | 693.89 | 0 | 27.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 693.89 | 0 | 0.05921 | 8.423 | 0 | 0 | 0 | 0 | off_peak | 693.89 |  |  | 0 | 0 | 100 | 0 | 0
4418 | 597.81 | 0 | 27.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 597.81 | 0 | 0.05921 | 8.205 | 0 | 0 | 0 | 0 | off_peak | 597.81 |  |  | 0 | 0 | 100 | 0 | 0
4419 | 608.58 | 0 | 27.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 608.58 | 0 | 0.05921 | 7.7275 | 0 | 0 | 0 | 0 | off_peak | 608.58 |  |  | 0 | 0 | 100 | 0 | 0
4420 | 610.75 | 0 | 27.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 610.75 | 0 | 0.05921 | 7.2014 | 0 | 0 | 0 | 0 | off_peak | 610.75 |  |  | 0 | 0 | 100 | 0 | 0
4421 | 594.65 | 0 | 27.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 594.65 | 0 | 0.05921 | 6.6062 | 0 | 0 | 0 | 0 | off_peak | 594.65 |  |  | 0 | 0 | 100 | 0 | 0
4422 | 586.81 | 0 | 27.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 586.81 | 0 | 0.05921 | 5.9552 | 0 | 0 | 0 | 0 | off_peak | 586.81 |  |  | 0 | 0 | 100 | 0 | 0
4423 | 580.9 | 78.4762 | 27.5 | 12.5987 | 12.5987 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 18.9814 | 580.6636 | 0 | 0.05921 | 5.4309 | 0 | 0 | 0 | 12.5987 | off_peak | 568.3013 | 0 | 100 | 2.17 | 0 | 97.83 | 68.4226 | 0
4424 | 603.54 | 310.015 | 27.8 | 49.7162 | 49.7162 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 30.5453 | 566.1862 | 0 | 0.05921 | 5.0295 | 0 | 0 | 0 | 49.7162 | off_peak | 553.8238 | 0 | 100 | 8.24 | 0 | 91.76 | 250.0484 | 0
4425 | 578.41 | 424.225 | 27.9 | 68.007 | 68.007 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 42.1093 | 522.7654 | 0 | 0.05921 | 4.7458 | 0 | 0 | 0 | 68.007 | off_peak | 510.403 | 0 | 100 | 11.76 | 0 | 88.24 | 322.7476 | 0
4426 | 562.95 | 573.872 | 28.1 | 91.9297 | 91.9297 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 53.6732 | 483.3826 | 0 | 0.05921 | 4.5582 | 0 | 0 | 0 | 91.9297 | off_peak | 471.0203 | 0 | 100 | 16.33 | 0 | 83.67 | 419.0325 | 0
4427 | 610.3 | 741.581 | 28.3 | 118.7089 | 118.7089 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 53.6732 | 491.5911 | 0 | 0.05921 | 4.4234 | 0 | 0 | 0 | 118.7089 | off_peak | 491.5911 |  |  | 19.45 | 0 | 80.55 | 525.1026 | 0
4428 | 612.87 | 597.253 | 28.6 | 95.501 | 95.501 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 53.6732 | 517.369 | 0 | 0.05921 | 4.4249 | 0 | 0 | 0 | 95.501 | off_peak | 517.369 |  |  | 15.58 | 0 | 84.42 | 422.5809 | 0
4429 | 572.12 | 181.449 | 28.7 | 29.0032 | 29.0032 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 53.6732 | 543.1168 | 0 | 0.05921 | 4.488 | 0 | 0 | 0 | 29.0032 | on_peak | 543.1168 |  |  | 5.07 | 0 | 94.93 | 130.1668 | 0
4430 | 609.57 | 633.833 | 28.8 | 101.2763 | 101.2763 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 53.6732 | 508.2937 | 0 | 0.05921 | 4.9248 | 0 | 0 | 0 | 101.2763 | on_peak | 508.2937 |  |  | 16.61 | 0 | 83.39 | 498.7654 | 0
4431 | 592.65 | 565.109 | 28.8 | 90.2953 | 90.2953 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 53.6732 | 502.3547 | 0 | 0.05921 | 5.6053 | 0 | 0 | 0 | 90.2953 | on_peak | 502.3547 |  |  | 15.24 | 0 | 84.76 | 506.1294 | 0
4432 | 602.96 | 662.632 | 28.8 | 105.8779 | 105.8779 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 53.6732 | 497.0821 | 0 | 0.05921 | 6.2702 | 0 | 0 | 0 | 105.8779 | on_peak | 497.0821 |  |  | 17.56 | 0 | 82.44 | 663.8791 | 0
4433 | 593.69 | 482.922 | 28.8 | 77.1631 | 77.1631 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 53.6732 | 516.5269 | 0 | 0.05921 | 6.9096 | 0 | 0 | 0 | 77.1631 | on_peak | 516.5269 |  |  | 13 | 0 | 87 | 533.1627 | 0
4434 | 596.71 | 282.289 | 28.6 | 45.1381 | 45.1381 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 53.6732 | 551.5719 | 0 | 0.05921 | 7.553 | 0 | 0 | 0 | 45.1381 | on_peak | 551.5719 |  |  | 7.56 | 0 | 92.44 | 340.9295 | 0
4435 | 601.46 | 92.2655 | 28.5 | 14.7587 | 14.7587 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 53.6732 | 586.7013 | 0 | 0.05921 | 8.0736 | 0 | 0 | 0 | 14.7587 | on_peak | 586.7013 |  |  | 2.45 | 0 | 97.55 | 119.155 | 0
4436 | 605.08 | 0 | 28 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 65.2371 | 617.4424 | 0 | 0.05921 | 8.3152 | 0 | 0 | 0 | 0 | on_peak | 605.08 | 0 | 100 | 0 | 0 | 100 | 0 | 0
4437 | 575.67 | 0 | 27.9 | 0 | 0 | 0 | 0 | 8.9371 | 8.9371 | 0 | 0 | 0 | 73.597 | 584.6071 | 0 | 0.05921 | 8.4668 | 0 | 0 | 0 | 0 | on_peak | 575.67 | 0 | 100 | 0 | 0 | 100 | 0 | 0
4438 | 591.06 | 0 | 27.9 | 0 | 0 | 0 | 0 | 0.57721 | 0.57721 | 0 | 0 | 0 | 74.137 | 591.6372 | 0 | 0.05921 | 8.6516 | 0 | 0 | 0 | 0 | off_peak | 591.06 | 0 | 100 | 0 | 0 | 100 | 0 | 0
4439 | 587.51 | 0 | 27.8 | 0 | 0 | 0 | 0 | 0.037279 | 0.037279 | 0 | 0 | 0 | 74.1718 | 587.5473 | 0 | 0.05921 | 8.5426 | 0 | 0 | 0 | 0 | off_peak | 587.51 | 0 | 100 | 0 | 0 | 100 | 0 | 0
4440 | 575.96 | 0 | 27.7 | 0 | 0 | 0 | 0 | 0.0024077 | 0.0024077 | 0 | 0 | 0 | 74.1741 | 575.9624 | 0 | 0.05921 | 8.4097 | 0 | 0 | 0 | 0 | off_peak | 575.96 | 0 | 100 | 0 | 0 | 100 | 0 | 0
4441 | 580.02 | 0 | 27.6 | 0 | 0 | 0 | 0 | 0.0001555 | 0.0001555 | 0 | 0 | 0 | 74.1742 | 580.0202 | 0 | 0.05921 | 8.1826 | 0 | 0 | 0 | 0 | off_peak | 580.02 | 0 | 100 | 0 | 0 | 100 | 0 | 0
4442 | 601.28 | 0 | 27.5 | 0 | 0 | 0 | 0 | 1.0737e-05 | 1.0737e-05 | 0 | 0 | 0 | 74.1743 | 601.28 | 0 | 0.05921 | 7.9403 | 0 | 0 | 0 | 0 | off_peak | 601.28 | 0 | 100 | 0 | 0 | 100 | 0 | 0
4443 | 584.12 | 0 | 27.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1743 | 584.12 | 0 | 0.05921 | 7.5173 | 0 | 0 | 0 | 0 | off_peak | 584.12 |  |  | 0 | 0 | 100 | 0 | 0
4444 | 583.34 | 0 | 27.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1743 | 583.34 | 0 | 0.05921 | 7.3197 | 0 | 0 | 0 | 0 | off_peak | 583.34 |  |  | 0 | 0 | 100 | 0 | 0
4445 | 604.29 | 0 | 27.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1743 | 604.29 | 0 | 0.05921 | 6.8643 | 0 | 0 | 0 | 0 | off_peak | 604.29 |  |  | 0 | 0 | 100 | 0 | 0
4446 | 690.7 | 0 | 27.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1743 | 690.7 | 0 | 0.05921 | 6.1795 | 0 | 0 | 0 | 0 | off_peak | 690.7 |  |  | 0 | 0 | 100 | 0 | 0
4447 | 759.17 | 114.301 | 27.9 | 18.3234 | 18.3234 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1743 | 740.8466 | 0 | 0.05921 | 5.561 | 0 | 0 | 0 | 18.3234 | off_peak | 740.8466 |  |  | 2.41 | 0 | 97.59 | 101.8968 | 0
4448 | 807.74 | 309.728 | 28.2 | 49.5979 | 49.5979 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1743 | 758.1421 | 0 | 0.05921 | 5.1596 | 0 | 0 | 0 | 49.5979 | off_peak | 758.1421 |  |  | 6.14 | 0 | 93.86 | 255.9071 | 0
4449 | 814.24 | 512.276 | 28.3 | 82.0028 | 82.0028 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1743 | 732.2372 | 0 | 0.05921 | 4.8902 | 0 | 0 | 0 | 82.0028 | off_peak | 732.2372 |  |  | 10.07 | 0 | 89.93 | 401.0084 | 0
4450 | 822.4 | 586.67 | 28.4 | 93.8772 | 93.8772 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1743 | 728.5228 | 0 | 0.05921 | 4.7861 | 0 | 0 | 0 | 93.8772 | off_peak | 728.5228 |  |  | 11.42 | 0 | 88.58 | 449.3059 | 0
4451 | 843.32 | 834.469 | 28.5 | 133.4807 | 133.4807 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1743 | 709.8393 | 0 | 0.05921 | 4.8579 | 0 | 0 | 0 | 133.4807 | off_peak | 709.8393 |  |  | 15.83 | 0 | 84.17 | 648.4387 | 0
4452 | 957.93 | 865.632 | 28.6 | 138.415 | 138.415 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1743 | 819.515 | 0 | 0.05921 | 5.0442 | 0 | 0 | 0 | 138.415 | off_peak | 819.515 |  |  | 14.45 | 0 | 85.55 | 698.1903 | 0
4453 | 902.98 | 952.454 | 28.7 | 152.2423 | 152.2423 | 0 | 0 | 0 | 0 | 62.4453 | 62.4453 | 0 | 7.4174 | 688.2924 | 0 | 0.088511 | 5.1883 | 0 | 0 | 0 | 152.2423 | on_peak | 688.2924 |  |  | 16.86 | 6.92 | 76.22 | 789.8812 | 0
4454 | 893.05 | 891.792 | 28.8 | 142.494 | 142.494 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 750.556 | 0 | 0.088511 | 5.5874 | 0 | 0 | 0 | 142.494 | on_peak | 750.556 |  |  | 15.96 | 0 | 84.04 | 796.1677 | 0
4455 | 879.43 | 795.215 | 28.8 | 127.0625 | 127.0625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 752.3675 | 0 | 0.088511 | 6.1254 | 0 | 0 | 0 | 127.0625 | on_peak | 752.3675 |  |  | 14.45 | 0 | 85.55 | 778.3148 | 0
4456 | 859.06 | 651.355 | 28.8 | 104.076 | 104.076 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 754.984 | 0 | 0.088511 | 6.7429 | 0 | 0 | 0 | 104.076 | on_peak | 754.984 |  |  | 12.12 | 0 | 87.88 | 701.7721 | 0
4457 | 853.63 | 470.055 | 28.7 | 75.1346 | 75.1346 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 778.4954 | 0 | 0.088511 | 7.2954 | 0 | 0 | 0 | 75.1346 | on_peak | 778.4954 |  |  | 8.8 | 0 | 91.2 | 548.1361 | 0
4458 | 896.37 | 271.244 | 28.5 | 43.3879 | 43.3879 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 852.9821 | 0 | 0.088511 | 7.8959 | 0 | 0 | 0 | 43.3879 | on_peak | 852.9821 |  |  | 4.84 | 0 | 95.16 | 342.5884 | 0
4459 | 847.67 | 85.5188 | 28.3 | 13.6895 | 13.6895 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 833.9805 | 0 | 0.088511 | 8.4152 | 0 | 0 | 0 | 13.6895 | on_peak | 833.9805 |  |  | 1.61 | 0 | 98.39 | 115.1994 | 0
4460 | 880.86 | 0 | 28 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 880.86 | 0 | 0.088511 | 8.505 | 0 | 0 | 0 | 0 | on_peak | 880.86 |  |  | 0 | 0 | 100 | 0 | 0
4461 | 869.4 | 0 | 28 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 869.4 | 0 | 0.088511 | 8.6427 | 0 | 0 | 0 | 0 | on_peak | 869.4 |  |  | 0 | 0 | 100 | 0 | 0
4462 | 807.51 | 0 | 28 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 18.9814 | 819.8724 | 0 | 0.05921 | 8.7651 | 0 | 0 | 0 | 0 | off_peak | 807.51 | 0 | 100 | 0 | 0 | 100 | 0 | 0
4463 | 849.64 | 0 | 27.9 | 0 | 0 | 0 | 0 | 8.7006 | 8.7006 | 0 | 0 | 0 | 27.12 | 858.3406 | 0 | 0.05921 | 8.7917 | 0 | 0 | 0 | 0 | off_peak | 849.64 | 0 | 100 | 0 | 0 | 100 | 0 | 0
4464 | 816.81 | 0 | 27.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27.12 | 816.81 | 0 | 0.05921 | 8.5836 | 0 | 0 | 0 | 0 | off_peak | 816.81 |  |  | 0 | 0 | 100 | 0 | 0
4465 | 741.34 | 0 | 27.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27.12 | 741.34 | 0 | 0.05921 | 8.2442 | 0 | 0 | 0 | 0 | off_peak | 741.34 |  |  | 0 | 0 | 100 | 0 | 0
4466 | 651.91 | 0 | 27.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27.12 | 651.91 | 0 | 0.05921 | 8.0297 | 0 | 0 | 0 | 0 | off_peak | 651.91 |  |  | 0 | 0 | 100 | 0 | 0
4467 | 641.96 | 0 | 27.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27.12 | 641.96 | 0 | 0.05921 | 7.8185 | 0 | 0 | 0 | 0 | off_peak | 641.96 |  |  | 0 | 0 | 100 | 0 | 0
4468 | 634.71 | 0 | 27.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27.12 | 634.71 | 0 | 0.05921 | 7.2825 | 0 | 0 | 0 | 0 | off_peak | 634.71 |  |  | 0 | 0 | 100 | 0 | 0
4469 | 662.05 | 0 | 27.6 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 38.684 | 674.4124 | 0 | 0.05921 | 6.7006 | 0 | 0 | 0 | 0 | off_peak | 662.05 | 0 | 100 | 0 | 0 | 100 | 0 | 0
4470 | 690.94 | 0 | 27.7 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 50.2479 | 703.3024 | 0 | 0.05921 | 6.0173 | 0 | 0 | 0 | 0 | off_peak | 690.94 | 0 | 100 | 0 | 0 | 100 | 0 | 0
4471 | 728.06 | 116.195 | 28.1 | 18.6135 | 18.6135 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 61.8119 | 721.8089 | 0 | 0.05921 | 5.4794 | 0 | 0 | 0 | 18.6135 | off_peak | 709.4465 | 0 | 100 | 2.56 | 0 | 97.44 | 101.9902 | 0
4472 | 797.97 | 313.584 | 28.5 | 50.1605 | 50.1605 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 73.3758 | 760.1719 | 0 | 0.05921 | 5.1587 | 0 | 0 | 0 | 50.1605 | off_peak | 747.8095 | 0 | 100 | 6.29 | 0 | 93.71 | 258.7632 | 0
4473 | 882.13 | 516.312 | 28.8 | 82.4983 | 82.4983 | 0 | 0 | 0.79843 | 0.79843 | 0 | 0 | 0 | 74.1227 | 800.4301 | 0 | 0.05921 | 4.9217 | 0 | 0 | 0 | 82.4983 | off_peak | 799.6317 | 0 | 100 | 9.35 | 0 | 90.65 | 406.0326 | 0
4474 | 832.29 | 511.034 | 29.2 | 81.5358 | 81.5358 | 0 | 0 | 0.051567 | 0.051567 | 0 | 0 | 0 | 74.1709 | 750.8058 | 0 | 0.05921 | 4.8264 | 0 | 0 | 0 | 81.5358 | off_peak | 750.7542 | 0 | 100 | 9.8 | 0 | 90.2 | 393.5248 | 0
4475 | 854.78 | 760.265 | 29.4 | 121.212 | 121.212 | 0 | 0 | 0.0033305 | 0.0033305 | 0 | 0 | 0 | 74.174 | 733.5713 | 0 | 0.05921 | 4.9093 | 0 | 0 | 0 | 121.212 | off_peak | 733.568 | 0 | 100 | 14.18 | 0 | 85.82 | 595.0682 | 0
4476 | 945.43 | 917.459 | 29.6 | 146.1671 | 146.1671 | 0 | 0 | 0.0002151 | 0.0002151 | 0 | 0 | 0 | 74.1742 | 799.2631 | 0 | 0.05921 | 5.084 | 0 | 0 | 0 | 146.1671 | off_peak | 799.2629 | 0 | 100 | 15.46 | 0 | 84.54 | 743.1064 | 0
4477 | 888.57 | 405.639 | 29.7 | 64.6016 | 64.6016 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1742 | 823.9684 | 0 | 0.088511 | 5.2801 | 0 | 0 | 0 | 64.6016 | on_peak | 823.9684 |  |  | 7.27 | 0 | 92.73 | 341.1053 | 0
4478 | 897.61 | 909.68 | 29.7 | 144.8747 | 144.8747 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1742 | 752.7353 | 0 | 0.088511 | 5.6417 | 0 | 0 | 0 | 144.8747 | on_peak | 752.7353 |  |  | 16.14 | 0 | 83.86 | 817.3448 | 0
4479 | 1003.94 | 816.227 | 29.7 | 129.9915 | 129.9915 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1742 | 873.9485 | 0 | 0.088511 | 6.101 | 0 | 0 | 0 | 129.9915 | on_peak | 873.9485 |  |  | 12.95 | 0 | 87.05 | 793.0752 | 0
4480 | 864.55 | 670.849 | 29.5 | 106.917 | 106.917 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1742 | 757.633 | 0 | 0.088511 | 6.6345 | 0 | 0 | 0 | 106.917 | on_peak | 757.633 |  |  | 12.37 | 0 | 87.63 | 709.3406 | 0
4481 | 850.88 | 487.016 | 29.3 | 77.6753 | 77.6753 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1742 | 773.2047 | 0 | 0.088511 | 7.2035 | 0 | 0 | 0 | 77.6753 | on_peak | 773.2047 |  |  | 9.13 | 0 | 90.87 | 559.533 | 0
4482 | 897.87 | 283.623 | 28.9 | 45.3018 | 45.3018 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1742 | 852.5682 | 0 | 0.088511 | 7.6843 | 0 | 0 | 0 | 45.3018 | on_peak | 852.5682 |  |  | 5.05 | 0 | 94.95 | 348.1131 | 0
4483 | 885.95 | 91.5283 | 28.7 | 14.6301 | 14.6301 | 0 | 0 | 0 | 0 | 62.4453 | 62.4453 | 0 | 7.4174 | 808.8746 | 0 | 0.088511 | 8.2054 | 0 | 0 | 0 | 14.6301 | on_peak | 808.8746 |  |  | 1.65 | 7.05 | 91.3 | 120.0452 | 0
4484 | 914.35 | 0 | 28.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 914.35 | 0 | 0.088511 | 8.5337 | 0 | 0 | 0 | 0 | on_peak | 914.35 |  |  | 0 | 0 | 100 | 0 | 0
4485 | 902.85 | 0 | 28.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 902.85 | 0 | 0.088511 | 8.6584 | 0 | 0 | 0 | 0 | on_peak | 902.85 |  |  | 0 | 0 | 100 | 0 | 0
4486 | 856.69 | 0 | 28 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 856.69 | 0 | 0.05921 | 8.6109 | 0 | 0 | 0 | 0 | off_peak | 856.69 |  |  | 0 | 0 | 100 | 0 | 0
4487 | 860.03 | 0 | 27.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 860.03 | 0 | 0.05921 | 8.5615 | 0 | 0 | 0 | 0 | off_peak | 860.03 |  |  | 0 | 0 | 100 | 0 | 0
4488 | 862.64 | 0 | 27.8 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 18.9814 | 875.0024 | 0 | 0.05921 | 8.488 | 0 | 0 | 0 | 0 | off_peak | 862.64 | 0 | 100 | 0 | 0 | 100 | 0 | 0
4489 | 738.81 | 0 | 27.7 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 30.5453 | 751.1724 | 0 | 0.05921 | 8.1299 | 0 | 0 | 0 | 0 | off_peak | 738.81 | 0 | 100 | 0 | 0 | 100 | 0 | 0
4490 | 655.82 | 0 | 27.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30.5453 | 655.82 | 0 | 0.05921 | 7.9416 | 0 | 0 | 0 | 0 | off_peak | 655.82 |  |  | 0 | 0 | 100 | 0 | 0
4491 | 636.04 | 0 | 27.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30.5453 | 636.04 | 0 | 0.05921 | 7.6337 | 0 | 0 | 0 | 0 | off_peak | 636.04 |  |  | 0 | 0 | 100 | 0 | 0
4492 | 658.67 | 0 | 27.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30.5453 | 658.67 | 0 | 0.05921 | 7.0337 | 0 | 0 | 0 | 0 | off_peak | 658.67 |  |  | 0 | 0 | 100 | 0 | 0
4493 | 657.67 | 0 | 27.4 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 42.1093 | 670.0324 | 0 | 0.05921 | 6.3229 | 0 | 0 | 0 | 0 | off_peak | 657.67 | 0 | 100 | 0 | 0 | 100 | 0 | 0
4494 | 731.61 | 0 | 27.6 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 53.6732 | 743.9724 | 0 | 0.05921 | 5.768 | 0 | 0 | 0 | 0 | off_peak | 731.61 | 0 | 100 | 0 | 0 | 100 | 0 | 0
4495 | 732.99 | 81.3588 | 28.1 | 13.033 | 13.033 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 65.2371 | 732.3193 | 0 | 0.05921 | 5.3309 | 0 | 0 | 0 | 13.033 | off_peak | 719.957 | 0 | 100 | 1.78 | 0 | 98.22 | 69.4783 | 0
4496 | 847.69 | 310.879 | 28.4 | 49.746 | 49.746 | 0 | 0 | 8.9371 | 8.9371 | 0 | 0 | 0 | 73.597 | 806.8811 | 0 | 0.05921 | 4.9892 | 0 | 0 | 0 | 49.746 | off_peak | 797.944 | 0 | 100 | 5.87 | 0 | 94.13 | 248.1905 | 0
4497 | 911.62 | 488.674 | 28.8 | 78.0822 | 78.0822 | 0 | 0 | 0.57721 | 0.57721 | 0 | 0 | 0 | 74.137 | 834.115 | 0 | 0.05921 | 4.7698 | 0 | 0 | 0 | 78.0822 | off_peak | 833.5378 | 0 | 100 | 8.57 | 0 | 91.43 | 372.4374 | 0
4498 | 872.98 | 638.293 | 29.1 | 101.8772 | 101.8772 | 0 | 0 | 0.037279 | 0.037279 | 0 | 0 | 0 | 74.1718 | 771.14 | 0 | 0.05921 | 4.6795 | 0 | 0 | 0 | 101.8772 | off_peak | 771.1028 | 0 | 100 | 11.67 | 0 | 88.33 | 476.7312 | 0
4499 | 824.9 | 660.444 | 29.4 | 105.2972 | 105.2972 | 0 | 0 | 0.0024077 | 0.0024077 | 0 | 0 | 0 | 74.1741 | 719.6052 | 0 | 0.05921 | 4.7761 | 0 | 0 | 0 | 105.2972 | off_peak | 719.6028 | 0 | 100 | 12.76 | 0 | 87.24 | 502.9136 | 0
4500 | 909.53 | 819.498 | 29.6 | 130.5602 | 130.5602 | 0 | 0 | 0.0001555 | 0.0001555 | 0 | 0 | 0 | 74.1742 | 778.97 | 0 | 0.05921 | 4.9317 | 0 | 0 | 0 | 130.5602 | off_peak | 778.9698 | 0 | 100 | 14.35 | 0 | 85.65 | 643.8834 | 0
4501 | 850.38 | 884.121 | 29.7 | 140.8042 | 140.8042 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1742 | 709.5758 | 0 | 0.088511 | 5.1425 | 0 | 0 | 0 | 140.8042 | on_peak | 709.5758 |  |  | 16.56 | 0 | 83.44 | 724.088 | 0
4502 | 867.56 | 848.928 | 29.7 | 135.1994 | 135.1994 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1742 | 732.3606 | 0 | 0.088511 | 5.5499 | 0 | 0 | 0 | 135.1994 | on_peak | 732.3606 |  |  | 15.58 | 0 | 84.42 | 750.346 | 0
4503 | 949.46 | 614.887 | 29.6 | 97.9621 | 97.9621 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1742 | 851.4979 | 0 | 0.088511 | 6.0706 | 0 | 0 | 0 | 97.9621 | on_peak | 851.4979 |  |  | 10.32 | 0 | 89.68 | 594.6866 | 0
4504 | 899.44 | 523.476 | 29.5 | 83.4293 | 83.4293 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1742 | 816.0107 | 0 | 0.088511 | 6.5642 | 0 | 0 | 0 | 83.4293 | on_peak | 816.0107 |  |  | 9.28 | 0 | 90.72 | 547.6488 | 0
4505 | 937.62 | 477.025 | 29.3 | 76.0818 | 76.0818 | 0 | 0 | 0 | 0 | 62.4453 | 62.4453 | 0 | 7.4174 | 799.0929 | 0 | 0.088511 | 7.1496 | 0 | 0 | 0 | 76.0818 | on_peak | 799.0929 |  |  | 8.11 | 6.66 | 85.23 | 543.9561 | 0
4506 | 940.05 | 277.548 | 28.9 | 44.3315 | 44.3315 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 895.7185 | 0 | 0.088511 | 7.6689 | 0 | 0 | 0 | 44.3315 | on_peak | 895.7185 |  |  | 4.72 | 0 | 95.28 | 339.9728 | 0
4507 | 867.96 | 88.1406 | 28.8 | 14.0834 | 14.0834 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 853.8766 | 0 | 0.088511 | 8.0883 | 0 | 0 | 0 | 14.0834 | on_peak | 853.8766 |  |  | 1.62 | 0 | 98.38 | 113.9105 | 0
4508 | 933.95 | 0 | 28.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 933.95 | 0 | 0.088511 | 8.1893 | 0 | 0 | 0 | 0 | on_peak | 933.95 |  |  | 0 | 0 | 100 | 0 | 0
4509 | 847.65 | 0 | 28.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 847.65 | 0 | 0.088511 | 8.1169 | 0 | 0 | 0 | 0 | on_peak | 847.65 |  |  | 0 | 0 | 100 | 0 | 0
4510 | 798.73 | 0 | 28.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 798.73 | 0 | 0.05921 | 8.0822 | 0 | 0 | 0 | 0 | off_peak | 798.73 |  |  | 0 | 0 | 100 | 0 | 0
4511 | 864.51 | 0 | 28.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 864.51 | 0 | 0.05921 | 8.0449 | 0 | 0 | 0 | 0 | off_peak | 864.51 |  |  | 0 | 0 | 100 | 0 | 0
4512 | 797.93 | 0 | 28 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 797.93 | 0 | 0.05921 | 7.7529 | 0 | 0 | 0 | 0 | off_peak | 797.93 |  |  | 0 | 0 | 100 | 0 | 0
4513 | 744.28 | 0 | 27.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 744.28 | 0 | 0.05921 | 7.6032 | 0 | 0 | 0 | 0 | off_peak | 744.28 |  |  | 0 | 0 | 100 | 0 | 0
4514 | 695.78 | 0 | 27.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 695.78 | 0 | 0.05921 | 7.3515 | 0 | 0 | 0 | 0 | off_peak | 695.78 |  |  | 0 | 0 | 100 | 0 | 0
4515 | 678.36 | 0 | 27.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 678.36 | 0 | 0.05921 | 7.0028 | 0 | 0 | 0 | 0 | off_peak | 678.36 |  |  | 0 | 0 | 100 | 0 | 0
4516 | 708.71 | 0 | 27.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 708.71 | 0 | 0.05921 | 6.5087 | 0 | 0 | 0 | 0 | off_peak | 708.71 |  |  | 0 | 0 | 100 | 0 | 0
4517 | 701.46 | 0 | 27.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 701.46 | 0 | 0.05921 | 5.9753 | 0 | 0 | 0 | 0 | off_peak | 701.46 |  |  | 0 | 0 | 100 | 0 | 0
4518 | 698.64 | 0 | 27.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 698.64 | 0 | 0.05921 | 5.3413 | 0 | 0 | 0 | 0 | off_peak | 698.64 |  |  | 0 | 0 | 100 | 0 | 0
4519 | 681.42 | 113.614 | 28.3 | 18.1868 | 18.1868 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 663.2332 | 0 | 0.05921 | 4.895 | 0 | 0 | 0 | 18.1868 | off_peak | 663.2332 |  |  | 2.67 | 0 | 97.33 | 89.0253 | 0
4520 | 785.39 | 310.151 | 28.7 | 49.5752 | 49.5752 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 735.8148 | 0 | 0.05921 | 4.6099 | 0 | 0 | 0 | 49.5752 | off_peak | 735.8148 |  |  | 6.31 | 0 | 93.69 | 228.5387 | 0
4521 | 808.09 | 472.753 | 28.9 | 75.5107 | 75.5107 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 18.9814 | 744.9417 | 0 | 0.05921 | 4.3772 | 0 | 0 | 0 | 75.5107 | off_peak | 732.5793 | 0 | 100 | 9.34 | 0 | 90.66 | 330.5279 | 0
4522 | 811.68 | 380.704 | 29.2 | 60.7415 | 60.7415 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18.9814 | 750.9385 | 0 | 0.05921 | 4.2442 | 0 | 0 | 0 | 60.7415 | off_peak | 750.9385 |  |  | 7.48 | 0 | 92.52 | 257.802 | 0
4523 | 774.19 | 98.8 | 29.5 | 15.7463 | 15.7463 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18.9814 | 758.4437 | 0 | 0.05921 | 4.2353 | 0 | 0 | 0 | 15.7463 | off_peak | 758.4437 |  |  | 2.03 | 0 | 97.97 | 66.6898 | 0
4524 | 780.7 | 776.934 | 29.7 | 123.7337 | 123.7337 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18.9814 | 656.9663 | 0 | 0.05921 | 4.2881 | 0 | 0 | 0 | 123.7337 | off_peak | 656.9663 |  |  | 15.85 | 0 | 84.15 | 530.5775 | 0
4525 | 747.57 | 938.955 | 29.8 | 149.4822 | 149.4822 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18.9814 | 598.0878 | 0 | 0.05921 | 4.4389 | 0 | 0 | 0 | 149.4822 | off_peak | 598.0878 |  |  | 20 | 0 | 80 | 663.5307 | 0
4526 | 762.85 | 857.84 | 29.9 | 136.5186 | 136.5186 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18.9814 | 626.3314 | 0 | 0.05921 | 4.8825 | 0 | 0 | 0 | 136.5186 | off_peak | 626.3314 |  |  | 17.9 | 0 | 82.1 | 666.5482 | 0
4527 | 788.78 | 808.064 | 29.8 | 128.6443 | 128.6443 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18.9814 | 660.1357 | 0 | 0.05921 | 5.5026 | 0 | 0 | 0 | 128.6443 | off_peak | 660.1357 |  |  | 16.31 | 0 | 83.69 | 707.8829 | 0
4528 | 771.08 | 512.561 | 29.7 | 81.6299 | 81.6299 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 30.5453 | 701.8124 | 0 | 0.05921 | 6.0226 | 0 | 0 | 0 | 81.6299 | off_peak | 689.4501 | 0 | 100 | 10.59 | 0 | 89.41 | 491.628 | 0
4529 | 788.41 | 481.494 | 29.5 | 76.7384 | 76.7384 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 42.1093 | 724.034 | 0 | 0.05921 | 6.5774 | 0 | 0 | 0 | 76.7384 | off_peak | 711.6716 | 0 | 100 | 9.73 | 0 | 90.27 | 504.7412 | 0
4530 | 678.74 | 279.156 | 29.1 | 44.5558 | 44.5558 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 53.6732 | 646.5466 | 0 | 0.05921 | 7.1543 | 0 | 0 | 0 | 44.5558 | off_peak | 634.1842 | 0 | 100 | 6.56 | 0 | 93.44 | 318.7644 | 0
4531 | 671.77 | 54.2967 | 28.9 | 8.6726 | 8.6726 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 65.2371 | 675.4598 | 0 | 0.05921 | 7.4812 | 0 | 0 | 0 | 8.6726 | off_peak | 663.0974 | 0 | 100 | 1.29 | 0 | 98.71 | 64.8816 | 0
4532 | 619.92 | 0 | 28.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 65.2371 | 619.92 | 0 | 0.05921 | 7.5286 | 0 | 0 | 0 | 0 | off_peak | 619.92 |  |  | 0 | 0 | 100 | 0 | 0
4533 | 653.43 | 0 | 28.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 65.2371 | 653.43 | 0 | 0.05921 | 7.5266 | 0 | 0 | 0 | 0 | off_peak | 653.43 |  |  | 0 | 0 | 100 | 0 | 0
4534 | 621.4 | 0 | 27.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 65.2371 | 621.4 | 0 | 0.05921 | 7.5652 | 0 | 0 | 0 | 0 | off_peak | 621.4 |  |  | 0 | 0 | 100 | 0 | 0
4535 | 588.54 | 0 | 27.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 65.2371 | 588.54 | 0 | 0.05921 | 7.6859 | 0 | 0 | 0 | 0 | off_peak | 588.54 |  |  | 0 | 0 | 100 | 0 | 0
4536 | 651.57 | 0 | 27.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 65.2371 | 651.57 | 0 | 0.05921 | 7.448 | 0 | 0 | 0 | 0 | off_peak | 651.57 |  |  | 0 | 0 | 100 | 0 | 0
4537 | 618.85 | 0 | 27.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 65.2371 | 618.85 | 0 | 0.05921 | 7.2676 | 0 | 0 | 0 | 0 | off_peak | 618.85 |  |  | 0 | 0 | 100 | 0 | 0
4538 | 611.94 | 0 | 27.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 65.2371 | 611.94 | 0 | 0.05921 | 7.0669 | 0 | 0 | 0 | 0 | off_peak | 611.94 |  |  | 0 | 0 | 100 | 0 | 0
4539 | 634.08 | 0 | 27.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 65.2371 | 634.08 | 0 | 0.05921 | 6.7447 | 0 | 0 | 0 | 0 | off_peak | 634.08 |  |  | 0 | 0 | 100 | 0 | 0
4540 | 635.25 | 0 | 27.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 65.2371 | 635.25 | 0 | 0.05921 | 6.2823 | 0 | 0 | 0 | 0 | off_peak | 635.25 |  |  | 0 | 0 | 100 | 0 | 0
4541 | 637.34 | 0 | 27 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 65.2371 | 637.34 | 0 | 0.05921 | 5.7368 | 0 | 0 | 0 | 0 | off_peak | 637.34 |  |  | 0 | 0 | 100 | 0 | 0
4542 | 710.81 | 0 | 27.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 65.2371 | 710.81 | 0 | 0.05921 | 5.3217 | 0 | 0 | 0 | 0 | off_peak | 710.81 |  |  | 0 | 0 | 100 | 0 | 0
4543 | 730.98 | 113.809 | 27.9 | 18.2446 | 18.2446 | 0 | 0 | 8.9371 | 8.9371 | 0 | 0 | 0 | 73.597 | 721.6725 | 0 | 0.05921 | 4.9211 | 0 | 0 | 0 | 18.2446 | off_peak | 712.7354 | 0 | 100 | 2.5 | 0 | 97.5 | 89.7842 | 0
4544 | 791.92 | 311.34 | 28.3 | 49.8379 | 49.8379 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 73.597 | 742.0821 | 0 | 0.05921 | 4.6478 | 0 | 0 | 0 | 49.8379 | off_peak | 742.0821 |  |  | 6.29 | 0 | 93.71 | 231.6341 | 0
4545 | 757.23 | 512.825 | 28.7 | 81.9711 | 81.9711 | 0 | 0 | 0.57721 | 0.57721 | 0 | 0 | 0 | 74.137 | 675.8362 | 0 | 0.05921 | 4.4333 | 0 | 0 | 0 | 81.9711 | off_peak | 675.2589 | 0 | 100 | 10.83 | 0 | 89.17 | 363.4032 | 0
4546 | 791.68 | 644.168 | 29 | 102.8525 | 102.8525 | 0 | 0 | 0.037279 | 0.037279 | 0 | 0 | 0 | 74.1718 | 688.8648 | 0 | 0.05921 | 4.3063 | 0 | 0 | 0 | 102.8525 | off_peak | 688.8275 | 0 | 100 | 12.99 | 0 | 87.01 | 442.9093 | 0
4547 | 766.01 | 833.35 | 29.3 | 132.9129 | 132.9129 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1718 | 633.0971 | 0 | 0.05921 | 4.2682 | 0 | 0 | 0 | 132.9129 | off_peak | 633.0971 |  |  | 17.35 | 0 | 82.65 | 567.303 | 0
4548 | 804.71 | 922.856 | 29.5 | 147.0807 | 147.0807 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1718 | 657.6293 | 0 | 0.05921 | 4.2901 | 0 | 0 | 0 | 147.0807 | off_peak | 657.6293 |  |  | 18.28 | 0 | 81.72 | 630.9911 | 0
4549 | 791.25 | 845.092 | 29.6 | 134.6378 | 134.6378 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1718 | 656.6122 | 0 | 0.05921 | 4.3062 | 0 | 0 | 0 | 134.6378 | off_peak | 656.6122 |  |  | 17.02 | 0 | 82.98 | 579.771 | 0
4550 | 796.37 | 857.042 | 29.7 | 136.4916 | 136.4916 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1718 | 659.8784 | 0 | 0.05921 | 4.6289 | 0 | 0 | 0 | 136.4916 | off_peak | 659.8784 |  |  | 17.14 | 0 | 82.86 | 631.804 | 0
4551 | 767.8 | 818.241 | 29.7 | 130.3122 | 130.3122 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1718 | 637.4878 | 0 | 0.05921 | 5.0779 | 0 | 0 | 0 | 130.3122 | off_peak | 637.4878 |  |  | 16.97 | 0 | 83.03 | 661.7183 | 0
4552 | 756.38 | 673.748 | 29.5 | 107.379 | 107.379 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1718 | 649.001 | 0 | 0.05921 | 5.7694 | 0 | 0 | 0 | 107.379 | off_peak | 649.001 |  |  | 14.2 | 0 | 85.8 | 619.5127 | 0
4553 | 758.18 | 489.991 | 29.3 | 78.1498 | 78.1498 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1718 | 680.0302 | 0 | 0.05921 | 6.4411 | 0 | 0 | 0 | 78.1498 | off_peak | 680.0302 |  |  | 10.31 | 0 | 89.69 | 503.3703 | 0
4554 | 700.67 | 286.247 | 28.9 | 45.721 | 45.721 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1718 | 654.949 | 0 | 0.05921 | 6.9858 | 0 | 0 | 0 | 45.721 | off_peak | 654.949 |  |  | 6.53 | 0 | 93.47 | 319.3958 | 0
4555 | 660.26 | 93.1116 | 28.6 | 14.8886 | 14.8886 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1718 | 645.3714 | 0 | 0.05921 | 7.5227 | 0 | 0 | 0 | 14.8886 | off_peak | 645.3714 |  |  | 2.25 | 0 | 97.75 | 112.0026 | 0
4556 | 627.02 | 0 | 28.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1718 | 627.02 | 0 | 0.05921 | 7.7676 | 0 | 0 | 0 | 0 | off_peak | 627.02 |  |  | 0 | 0 | 100 | 0 | 0
4557 | 643.21 | 0 | 28.1 | 0 | 0 | 0 | 0 | 0.0024077 | 0.0024077 | 0 | 0 | 0 | 74.1741 | 643.2124 | 0 | 0.05921 | 8.1632 | 0 | 0 | 0 | 0 | off_peak | 643.21 | 0 | 100 | 0 | 0 | 100 | 0 | 0
4558 | 653.05 | 0 | 28.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1741 | 653.05 | 0 | 0.05921 | 8.4502 | 0 | 0 | 0 | 0 | off_peak | 653.05 |  |  | 0 | 0 | 100 | 0 | 0
4559 | 656.94 | 0 | 28 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1741 | 656.94 | 0 | 0.05921 | 8.7033 | 0 | 0 | 0 | 0 | off_peak | 656.94 |  |  | 0 | 0 | 100 | 0 | 0
4560 | 648.06 | 0 | 27.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1741 | 648.06 | 0 | 0.05921 | 8.817 | 0 | 0 | 0 | 0 | off_peak | 648.06 |  |  | 0 | 0 | 100 | 0 | 0
4561 | 656.92 | 0 | 27.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1741 | 656.92 | 0 | 0.05921 | 8.3178 | 0 | 0 | 0 | 0 | off_peak | 656.92 |  |  | 0 | 0 | 100 | 0 | 0
4562 | 641.95 | 0 | 27.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1741 | 641.95 | 0 | 0.05921 | 8.1229 | 0 | 0 | 0 | 0 | off_peak | 641.95 |  |  | 0 | 0 | 100 | 0 | 0
4563 | 617.19 | 0 | 27.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1741 | 617.19 | 0 | 0.05921 | 7.7424 | 0 | 0 | 0 | 0 | off_peak | 617.19 |  |  | 0 | 0 | 100 | 0 | 0
4564 | 637.86 | 0 | 27.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1741 | 637.86 | 0 | 0.05921 | 7.1175 | 0 | 0 | 0 | 0 | off_peak | 637.86 |  |  | 0 | 0 | 100 | 0 | 0
4565 | 671.05 | 0 | 27.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1741 | 671.05 | 0 | 0.05921 | 6.4398 | 0 | 0 | 0 | 0 | off_peak | 671.05 |  |  | 0 | 0 | 100 | 0 | 0
4566 | 716.83 | 0 | 27.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1741 | 716.83 | 0 | 0.05921 | 0 | 0 | 0 | 0 | 0 | off_peak | 716.83 |  |  | 0 | 0 | 100 | 0 | 0
4567 | 782.79 | 41.9693 | 28.4 | 6.7158 | 6.7158 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1741 | 776.0742 | 0 | 0.05921 | 0 | 0 | 0 | 0 | 6.7158 | off_peak | 776.0742 |  |  | 0.86 | 0 | 99.14 | 0 | 0
4568 | 853.48 | 144.668 | 28.8 | 23.1156 | 23.1156 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1741 | 830.3644 | 0 | 0.05921 | 0 | 0 | 0 | 0 | 23.1156 | off_peak | 830.3644 |  |  | 2.71 | 0 | 97.29 | 0 | 0
4569 | 894.04 | 237.099 | 29.1 | 37.8431 | 37.8431 | 0 | 0 | 0.0001555 | 0.0001555 | 0 | 0 | 0 | 74.1742 | 856.197 | 0 | 0.05921 | 0 | 0 | 0 | 0 | 37.8431 | off_peak | 856.1969 | 0 | 100 | 4.23 | 0 | 95.77 | 0 | 0
4570 | 901.31 | 224.746 | 29.3 | 35.8452 | 35.8452 | 0 | 0 | 1.0737e-05 | 1.0737e-05 | 0 | 0 | 0 | 74.1743 | 865.4648 | 0 | 0.05921 | 0 | 0 | 0 | 0 | 35.8452 | off_peak | 865.4648 | 0 | 100 | 3.98 | 0 | 96.02 | 0 | 0
4571 | 903.57 | 505.139 | 29.5 | 80.5068 | 80.5068 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1743 | 823.0632 | 0 | 0.05921 | 0 | 0 | 0 | 0 | 80.5068 | off_peak | 823.0632 |  |  | 8.91 | 0 | 91.09 | 0 | 0
4572 | 932.91 | 716.086 | 29.6 | 114.0849 | 114.0849 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1743 | 818.8251 | 0 | 0.05921 | 0 | 0 | 0 | 0 | 114.0849 | off_peak | 818.8251 |  |  | 12.23 | 0 | 87.77 | 0 | 0
4573 | 850.71 | 739.159 | 29.7 | 117.7177 | 117.7177 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1743 | 732.9923 | 0 | 0.088511 | 0 | 0 | 0 | 0 | 117.7177 | on_peak | 732.9923 |  |  | 13.84 | 0 | 86.16 | 0 | 0
4574 | 833.24 | 554.083 | 29.8 | 88.2104 | 88.2104 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1743 | 745.0296 | 0 | 0.088511 | 0 | 0 | 0 | 0 | 88.2104 | on_peak | 745.0296 |  |  | 10.59 | 0 | 89.41 | 0 | 0
4575 | 938.74 | 520.203 | 29.8 | 82.8167 | 82.8167 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1743 | 855.9233 | 0 | 0.088511 | 0 | 0 | 0 | 0 | 82.8167 | on_peak | 855.9233 |  |  | 8.82 | 0 | 91.18 | 0 | 0
4576 | 929.28 | 490.048 | 29.8 | 78.016 | 78.016 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1743 | 851.264 | 0 | 0.088511 | 0 | 0 | 0 | 0 | 78.016 | on_peak | 851.264 |  |  | 8.4 | 0 | 91.6 | 0 | 0
4577 | 921.04 | 369.012 | 29.5 | 58.8115 | 58.8115 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1743 | 862.2285 | 0 | 0.088511 | 0 | 0 | 0 | 0 | 58.8115 | on_peak | 862.2285 |  |  | 6.39 | 0 | 93.61 | 0 | 0
4578 | 946.87 | 264.994 | 29.2 | 42.2799 | 42.2799 | 0 | 0 | 0 | 0 | 62.4453 | 62.4453 | 0 | 7.4174 | 842.1448 | 0 | 0.088511 | 0 | 0 | 0 | 0 | 42.2799 | on_peak | 842.1448 |  |  | 4.47 | 6.59 | 88.94 | 0 | 0
4579 | 928.29 | 59.41 | 29 | 9.4858 | 9.4858 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 918.8042 | 0 | 0.088511 | 0 | 0 | 0 | 0 | 9.4858 | on_peak | 918.8042 |  |  | 1.02 | 0 | 98.98 | 0 | 0
4580 | 912.41 | 0 | 28.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 912.41 | 0 | 0.088511 | 0 | 0 | 0 | 0 | 0 | on_peak | 912.41 |  |  | 0 | 0 | 100 | 0 | 0
4581 | 912.53 | 0 | 28.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 912.53 | 0 | 0.088511 | 0 | 0 | 0 | 0 | 0 | on_peak | 912.53 |  |  | 0 | 0 | 100 | 0 | 0
4582 | 901.67 | 0 | 28.4 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 18.9814 | 914.0324 | 0 | 0.05921 | 0 | 0 | 0 | 0 | 0 | off_peak | 901.67 | 0 | 100 | 0 | 0 | 100 | 0 | 0
4583 | 930.5 | 0 | 28.3 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 30.5453 | 942.8624 | 0 | 0.05921 | 0 | 0 | 0 | 0 | 0 | off_peak | 930.5 | 0 | 100 | 0 | 0 | 100 | 0 | 0
4584 | 881.38 | 0 | 28.2 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 42.1093 | 893.7424 | 0 | 0.05921 | 0 | 0 | 0 | 0 | 0 | off_peak | 881.38 | 0 | 100 | 0 | 0 | 100 | 0 | 0
4585 | 763.26 | 0 | 28.1 | 0 | 0 | 0 | 0 | 8.7006 | 8.7006 | 0 | 0 | 0 | 50.2479 | 771.9606 | 0 | 0.05921 | 0 | 0 | 0 | 0 | 0 | off_peak | 763.26 | 0 | 100 | 0 | 0 | 100 | 0 | 0
4586 | 663.94 | 0 | 28.1 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 61.8119 | 676.3024 | 0 | 0.05921 | 0 | 0 | 0 | 0 | 0 | off_peak | 663.94 | 0 | 100 | 0 | 0 | 100 | 0 | 0
4587 | 694.82 | 0 | 28 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 73.3758 | 707.1824 | 0 | 0.05921 | 0 | 0 | 0 | 0 | 0 | off_peak | 694.82 | 0 | 100 | 0 | 0 | 100 | 0 | 0
4588 | 653.74 | 0 | 28 | 0 | 0 | 0 | 0 | 0.79843 | 0.79843 | 0 | 0 | 0 | 74.1227 | 654.5384 | 0 | 0.05921 | 0 | 0 | 0 | 0 | 0 | off_peak | 653.74 | 0 | 100 | 0 | 0 | 100 | 0 | 0
4589 | 679.7 | 0 | 27.9 | 0 | 0 | 0 | 0 | 0.051567 | 0.051567 | 0 | 0 | 0 | 74.1709 | 679.7516 | 0 | 0.05921 | 0 | 0 | 0 | 0 | 0 | off_peak | 679.7 | 0 | 100 | 0 | 0 | 100 | 0 | 0
4590 | 718.65 | 0 | 28.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1709 | 718.65 | 0 | 0.05921 | 5.8977 | 0 | 0 | 0 | 0 | off_peak | 718.65 |  |  | 0 | 0 | 100 | 0 | 0
4591 | 757.78 | 73.6604 | 28.5 | 11.7826 | 11.7826 | 0 | 0 | 0.0033305 | 0.0033305 | 0 | 0 | 0 | 74.174 | 746.0007 | 0 | 0.05921 | 5.3971 | 0 | 0 | 0 | 11.7826 | off_peak | 745.9974 | 0 | 100 | 1.55 | 0 | 98.45 | 63.5917 | 0
4592 | 872.08 | 297.821 | 28.9 | 47.5696 | 47.5696 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.174 | 824.5104 | 0 | 0.05921 | 5.0614 | 0 | 0 | 0 | 47.5696 | off_peak | 824.5104 |  |  | 5.45 | 0 | 94.55 | 240.7695 | 0
4593 | 874.27 | 508.04 | 29.1 | 81.0877 | 81.0877 | 0 | 0 | 0.0002151 | 0.0002151 | 0 | 0 | 0 | 74.1742 | 793.1825 | 0 | 0.05921 | 4.8264 | 0 | 0 | 0 | 81.0877 | off_peak | 793.1823 | 0 | 100 | 9.27 | 0 | 90.73 | 391.359 | 0
4594 | 891.39 | 686.422 | 29.3 | 109.479 | 109.479 | 0 | 0 | 1.4852e-05 | 1.4852e-05 | 0 | 0 | 0 | 74.1743 | 781.911 | 0 | 0.05921 | 4.7288 | 0 | 0 | 0 | 109.479 | off_peak | 781.911 | 0 | 100 | 12.28 | 0 | 87.72 | 517.709 | 0
4595 | 869.2 | 710.626 | 29.5 | 113.2564 | 113.2564 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1743 | 755.9436 | 0 | 0.05921 | 4.8026 | 0 | 0 | 0 | 113.2564 | off_peak | 755.9436 |  |  | 13.03 | 0 | 86.97 | 543.9276 | 0
4596 | 936.43 | 736.903 | 29.7 | 117.3584 | 117.3584 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1743 | 819.0716 | 0 | 0.05921 | 4.9971 | 0 | 0 | 0 | 117.3584 | off_peak | 819.0716 |  |  | 12.53 | 0 | 87.47 | 586.448 | 0
4597 | 956.47 | 560.258 | 29.8 | 89.1934 | 89.1934 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1743 | 867.2766 | 0 | 0.088511 | 4.9912 | 0 | 0 | 0 | 89.1934 | on_peak | 867.2766 |  |  | 9.33 | 0 | 90.67 | 445.1814 | 0
4598 | 917.38 | 720.648 | 29.8 | 114.7276 | 114.7276 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1743 | 802.6524 | 0 | 0.088511 | 5.2995 | 0 | 0 | 0 | 114.7276 | on_peak | 802.6524 |  |  | 12.51 | 0 | 87.49 | 608.0011 | 0
4599 | 962.94 | 813.741 | 29.7 | 129.5955 | 129.5955 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1743 | 833.3445 | 0 | 0.088511 | 5.7233 | 0 | 0 | 0 | 129.5955 | on_peak | 833.3445 |  |  | 13.46 | 0 | 86.54 | 741.7148 | 0
4600 | 906.44 | 628.957 | 29.6 | 100.2037 | 100.2037 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1743 | 806.2363 | 0 | 0.088511 | 6.2554 | 0 | 0 | 0 | 100.2037 | on_peak | 806.2363 |  |  | 11.05 | 0 | 88.95 | 626.8139 | 0
4601 | 908.57 | 432.31 | 29.4 | 68.9249 | 68.9249 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1743 | 839.6451 | 0 | 0.088511 | 6.8532 | 0 | 0 | 0 | 68.9249 | on_peak | 839.6451 |  |  | 7.59 | 0 | 92.41 | 472.3588 | 0
4602 | 938.82 | 282.683 | 29.2 | 45.1022 | 45.1022 | 0 | 0 | 0 | 0 | 26.1636 | 26.1636 | 0 | 46.2042 | 867.5542 | 0 | 0.088511 | 7.3242 | 0 | 0 | 0 | 45.1022 | on_peak | 867.5542 |  |  | 4.8 | 2.79 | 92.41 | 330.3357 | 0
4603 | 950 | 90.3481 | 29 | 14.4256 | 14.4256 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 46.2042 | 935.5744 | 0 | 0.088511 | 7.7847 | 0 | 0 | 0 | 14.4256 | on_peak | 935.5744 |  |  | 1.52 | 0 | 98.48 | 112.299 | 0
4604 | 942.36 | 0 | 28.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 46.2042 | 942.36 | 0 | 0.088511 | 8.0759 | 0 | 0 | 0 | 0 | on_peak | 942.36 |  |  | 0 | 0 | 100 | 0 | 0
4605 | 982.04 | 0 | 28.4 | 0 | 0 | 0 | 0 | 0 | 0 | 36.2817 | 36.2817 | 0 | 7.4174 | 945.7583 | 0 | 0.088511 | 8.3582 | 0 | 0 | 0 | 0 | on_peak | 945.7583 |  |  | 0 | 3.69 | 96.31 | 0 | 0
4606 | 900.59 | 0 | 28.3 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 18.9814 | 912.9524 | 0 | 0.05921 | 8.6808 | 0 | 0 | 0 | 0 | off_peak | 900.59 | 0 | 100 | 0 | 0 | 100 | 0 | 0
4607 | 950.76 | 0 | 28.2 | 0 | 0 | 0 | 0 | 0 | 0 | 5.0017 | 5.0017 | 0 | 13.6343 | 945.7583 | 0 | 0.05921 | 8.9501 | 0 | 0 | 0 | 0 | off_peak | 945.7583 |  |  | 0 | 0.53 | 99.47 | 0 | 0
4608 | 887.21 | 0 | 28 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 25.1982 | 899.5724 | 0 | 0.05921 | 8.8951 | 0 | 0 | 0 | 0 | off_peak | 887.21 | 0 | 100 | 0 | 0 | 100 | 0 | 0
4609 | 848.29 | 0 | 27.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25.1982 | 848.29 | 0 | 0.05921 | 8.8099 | 0 | 0 | 0 | 0 | off_peak | 848.29 |  |  | 0 | 0 | 100 | 0 | 0
4610 | 760.76 | 0 | 27.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25.1982 | 760.76 | 0 | 0.05921 | 8.6842 | 0 | 0 | 0 | 0 | off_peak | 760.76 |  |  | 0 | 0 | 100 | 0 | 0
4611 | 733.75 | 0 | 27.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25.1982 | 733.75 | 0 | 0.05921 | 8.1933 | 0 | 0 | 0 | 0 | off_peak | 733.75 |  |  | 0 | 0 | 100 | 0 | 0
4612 | 738.4 | 0 | 27.7 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 36.7622 | 750.7624 | 0 | 0.05921 | 7.5512 | 0 | 0 | 0 | 0 | off_peak | 738.4 | 0 | 100 | 0 | 0 | 100 | 0 | 0
4613 | 736.22 | 0 | 27.7 | 0 | 0 | 0 | 0 | 2.0545 | 2.0545 | 0 | 0 | 0 | 38.684 | 738.2745 | 0 | 0.05921 | 6.9863 | 0 | 0 | 0 | 0 | off_peak | 736.22 | 0 | 100 | 0 | 0 | 100 | 0 | 0
4614 | 789.96 | 0 | 27.9 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 50.2479 | 802.3224 | 0 | 0.05921 | 6.3574 | 0 | 0 | 0 | 0 | off_peak | 789.96 | 0 | 100 | 0 | 0 | 100 | 0 | 0
4615 | 805.65 | 107.186 | 28.3 | 17.1578 | 17.1578 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 61.8119 | 800.8545 | 0 | 0.05921 | 5.8199 | 0 | 0 | 0 | 17.1578 | off_peak | 788.4922 | 0 | 100 | 2.13 | 0 | 97.87 | 99.8567 | 0
4616 | 846.67 | 301.265 | 28.7 | 48.1548 | 48.1548 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 73.3758 | 810.8775 | 0 | 0.05921 | 5.4814 | 0 | 0 | 0 | 48.1548 | off_peak | 798.5152 | 0 | 100 | 5.69 | 0 | 94.31 | 263.955 | 0
4617 | 904.93 | 245.52 | 28.9 | 39.2158 | 39.2158 | 0 | 0 | 0.79843 | 0.79843 | 0 | 0 | 0 | 74.1227 | 866.5126 | 0 | 0.05921 | 5.2093 | 0 | 0 | 0 | 39.2158 | off_peak | 865.7142 | 0 | 100 | 4.33 | 0 | 95.67 | 204.288 | 0
4618 | 925.73 | 365.829 | 29.1 | 58.3896 | 58.3896 | 0 | 0 | 0.051567 | 0.051567 | 0 | 0 | 0 | 74.1709 | 867.392 | 0 | 0.05921 | 5.0882 | 0 | 0 | 0 | 58.3896 | off_peak | 867.3404 | 0 | 100 | 6.31 | 0 | 93.69 | 297.0966 | 0
4619 | 892.23 | 818.358 | 29.3 | 130.5218 | 130.5218 | 0 | 0 | 0.0033305 | 0.0033305 | 0 | 0 | 0 | 74.174 | 761.7116 | 0 | 0.05921 | 5.1434 | 0 | 0 | 0 | 130.5218 | off_peak | 761.7082 | 0 | 100 | 14.63 | 0 | 85.37 | 671.3244 | 0
4620 | 977.64 | 901.766 | 29.5 | 143.7195 | 143.7195 | 0 | 0 | 0.0002151 | 0.0002151 | 0 | 0 | 0 | 74.1742 | 833.9207 | 0 | 0.05921 | 5.2804 | 0 | 0 | 0 | 143.7195 | off_peak | 833.9205 | 0 | 100 | 14.7 | 0 | 85.3 | 758.8952 | 0
4621 | 922.3 | 927.181 | 29.7 | 147.6619 | 147.6619 | 0 | 0 | 1.3893e-05 | 1.3893e-05 | 0 | 0 | 0 | 74.1743 | 774.6381 | 0 | 0.088511 | 5.2868 | 0 | 0 | 0 | 147.6619 | on_peak | 774.6381 | 0 | 100 | 16.01 | 0 | 83.99 | 780.6527 | 0
4622 | 964.86 | 715.901 | 29.8 | 113.9719 | 113.9719 | 0 | 0 | 8.9726e-07 | 8.9726e-07 | 0 | 0 | 0 | 74.1743 | 850.8881 | 0 | 0.088511 | 5.6349 | 0 | 0 | 0 | 113.9719 | on_peak | 850.8881 | 0 | 100 | 11.81 | 0 | 88.19 | 642.2162 | 0
4623 | 1005.13 | 182.286 | 29.8 | 29.02 | 29.02 | 0 | 0 | 0 | 0 | 30.3517 | 30.3517 | 0 | 41.7269 | 945.7583 | 0 | 0.088511 | 5.9633 | 0 | 0 | 0 | 29.02 | on_peak | 945.7583 |  |  | 2.89 | 3.02 | 94.09 | 173.0545 | 0
4624 | 939.12 | 212.539 | 29.7 | 33.8487 | 33.8487 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 53.2909 | 917.6336 | 0 | 0.088511 | 6.5118 | 0 | 0 | 0 | 33.8487 | on_peak | 905.2713 | 0 | 100 | 3.6 | 0 | 96.4 | 220.4161 | 0
4625 | 966.81 | 75.05 | 29.5 | 11.9611 | 11.9611 | 0 | 0 | 0 | 0 | 9.0906 | 9.0906 | 0 | 43.5726 | 945.7583 | 0 | 0.088511 | 7.1505 | 0 | 0 | 0 | 11.9611 | on_peak | 945.7583 |  |  | 1.24 | 0.94 | 97.82 | 85.5279 | 0
4626 | 977.58 | 52.25 | 29.2 | 8.3365 | 8.3365 | 0 | 0 | 0 | 0 | 23.4852 | 23.4852 | 0 | 18.4659 | 945.7583 | 0 | 0.088511 | 7.709 | 0 | 0 | 0 | 8.3365 | on_peak | 945.7583 |  |  | 0.85 | 2.4 | 96.74 | 64.2665 | 0
4627 | 944.53 | 4.75 | 29 | 0.75842 | 0.75842 | 0 | 0 | 1.9867 | 1.9867 | 0 | 0 | 0 | 20.3243 | 945.7583 | 0 | 0.088511 | 8.1329 | 0 | 0 | 0 | 0.75842 | on_peak | 943.7716 | 0 | 100 | 0.08 | 0 | 99.92 | 6.1681 | 0
4628 | 933.52 | 0 | 28.4 | 0 | 0 | 0 | 0 | 12.2383 | 12.2383 | 0 | 0 | 0 | 31.7721 | 945.7583 | 0 | 0.088511 | 8.3115 | 0 | 0 | 0 | 0 | on_peak | 933.52 | 0 | 100 | 0 | 0 | 100 | 0 | 0
4629 | 968.54 | 0 | 28.3 | 0 | 0 | 0 | 0 | 0 | 0 | 22.7817 | 22.7817 | 0 | 7.4174 | 945.7583 | 0 | 0.088511 | 8.5176 | 0 | 0 | 0 | 0 | on_peak | 945.7583 |  |  | 0 | 2.35 | 97.65 | 0 | 0
4630 | 934.12 | 0 | 28.2 | 0 | 0 | 0 | 0 | 11.6383 | 11.6383 | 0 | 0 | 0 | 18.304 | 945.7583 | 0 | 0.05921 | 8.7488 | 0 | 0 | 0 | 0 | off_peak | 934.12 | 0 | 100 | 0 | 0 | 100 | 0 | 0
4631 | 947.33 | 0 | 28.1 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5717 | 1.5717 | 0 | 16.6238 | 945.7583 | 0 | 0.05921 | 8.9212 | 0 | 0 | 0 | 0 | off_peak | 945.7583 |  |  | 0 | 0.17 | 99.83 | 0 | 0
4632 | 907.13 | 0 | 28 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16.6238 | 907.13 | 0 | 0.05921 | 8.9742 | 0 | 0 | 0 | 0 | off_peak | 907.13 |  |  | 0 | 0 | 100 | 0 | 0
4633 | 844.18 | 0 | 27.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16.6238 | 844.18 | 0 | 0.05921 | 8.7432 | 0 | 0 | 0 | 0 | off_peak | 844.18 |  |  | 0 | 0 | 100 | 0 | 0
4634 | 765.86 | 0 | 27.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16.6238 | 765.86 | 0 | 0.05921 | 8.553 | 0 | 0 | 0 | 0 | off_peak | 765.86 |  |  | 0 | 0 | 100 | 0 | 0
4635 | 701.79 | 0 | 27.6 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 28.1877 | 714.1524 | 0 | 0.05921 | 8.1131 | 0 | 0 | 0 | 0 | off_peak | 701.79 | 0 | 100 | 0 | 0 | 100 | 0 | 0
4636 | 751.28 | 0 | 27.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 28.1877 | 751.28 | 0 | 0.05921 | 7.517 | 0 | 0 | 0 | 0 | off_peak | 751.28 |  |  | 0 | 0 | 100 | 0 | 0
4637 | 746.02 | 0 | 27.5 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 39.7517 | 758.3824 | 0 | 0.05921 | 6.992 | 0 | 0 | 0 | 0 | off_peak | 746.02 | 0 | 100 | 0 | 0 | 100 | 0 | 0
4638 | 785.82 | 0 | 27.7 | 0 | 0 | 0 | 0 | 11.221 | 11.221 | 0 | 0 | 0 | 50.2479 | 797.041 | 0 | 0.05921 | 6.3622 | 0 | 0 | 0 | 0 | off_peak | 785.82 | 0 | 100 | 0 | 0 | 100 | 0 | 0
4639 | 798.03 | 49.7306 | 28.1 | 7.9664 | 7.9664 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 61.8119 | 802.4259 | 0 | 0.05921 | 5.8575 | 0 | 0 | 0 | 7.9664 | off_peak | 790.0636 | 0 | 100 | 1 | 0 | 99 | 46.6634 | 0
4640 | 849.14 | 130.996 | 28.4 | 20.9616 | 20.9616 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 73.3758 | 840.5408 | 0 | 0.05921 | 5.4588 | 0 | 0 | 0 | 20.9616 | off_peak | 828.1784 | 0 | 100 | 2.47 | 0 | 97.53 | 114.4243 | 0
4641 | 844.44 | 443.482 | 28.7 | 70.8871 | 70.8871 | 0 | 0 | 0.79843 | 0.79843 | 0 | 0 | 0 | 74.1227 | 774.3513 | 0 | 0.05921 | 5.2088 | 0 | 0 | 0 | 70.8871 | off_peak | 773.5529 | 0 | 100 | 8.39 | 0 | 91.61 | 369.2363 | 0
4642 | 899.59 | 637.76 | 28.9 | 101.8665 | 101.8665 | 0 | 0 | 0.051567 | 0.051567 | 0 | 0 | 0 | 74.1709 | 797.775 | 0 | 0.05921 | 5.1073 | 0 | 0 | 0 | 101.8665 | off_peak | 797.7235 | 0 | 100 | 11.32 | 0 | 88.68 | 520.258 | 0
4643 | 865.42 | 504.478 | 29.2 | 80.4897 | 80.4897 | 0 | 0 | 0.0033305 | 0.0033305 | 0 | 0 | 0 | 74.174 | 784.9336 | 0 | 0.05921 | 5.1817 | 0 | 0 | 0 | 80.4897 | off_peak | 784.9303 | 0 | 100 | 9.3 | 0 | 90.7 | 417.0718 | 0
4644 | 979.42 | 791.287 | 29.3 | 126.2041 | 126.2041 | 0 | 0 | 0.0002151 | 0.0002151 | 0 | 0 | 0 | 74.1742 | 853.2161 | 0 | 0.05921 | 5.3746 | 0 | 0 | 0 | 126.2041 | off_peak | 853.2159 | 0 | 100 | 12.89 | 0 | 87.11 | 678.2932 | 0
4645 | 919.36 | 804.355 | 29.4 | 128.2415 | 128.2415 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1742 | 791.1185 | 0 | 0.088511 | 5.3778 | 0 | 0 | 0 | 128.2415 | on_peak | 791.1185 |  |  | 13.95 | 0 | 86.05 | 689.6617 | 0
4646 | 982.3 | 680.329 | 29.4 | 108.4675 | 108.4675 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1742 | 873.8325 | 0 | 0.088511 | 5.8058 | 0 | 0 | 0 | 108.4675 | on_peak | 873.8325 |  |  | 11.04 | 0 | 88.96 | 629.7444 | 0
4647 | 951.21 | 518.505 | 29.4 | 82.6673 | 82.6673 | 0 | 0 | 0 | 0 | 62.4453 | 62.4453 | 0 | 7.4174 | 806.0974 | 0 | 0.088511 | 6.1789 | 0 | 0 | 0 | 82.6673 | on_peak | 806.0974 |  |  | 8.69 | 6.56 | 84.74 | 510.7964 | 0
4648 | 885.07 | 604.458 | 29.2 | 96.4416 | 96.4416 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 788.6284 | 0 | 0.088511 | 6.611 | 0 | 0 | 0 | 96.4416 | on_peak | 788.6284 |  |  | 10.9 | 0 | 89.1 | 637.5777 | 0
4649 | 853.22 | 397.11 | 29 | 63.4054 | 63.4054 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 789.8146 | 0 | 0.088511 | 7.1751 | 0 | 0 | 0 | 63.4054 | on_peak | 789.8146 |  |  | 7.43 | 0 | 92.57 | 454.9377 | 0
4650 | 873.09 | 175.17 | 28.7 | 27.9996 | 27.9996 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 845.0904 | 0 | 0.088511 | 7.6784 | 0 | 0 | 0 | 27.9996 | on_peak | 845.0904 |  |  | 3.21 | 0 | 96.79 | 214.9913 | 0
4651 | 881.46 | 85.0047 | 28.6 | 13.5923 | 13.5923 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 867.8677 | 0 | 0.088511 | 7.9657 | 0 | 0 | 0 | 13.5923 | on_peak | 867.8677 |  |  | 1.54 | 0 | 98.46 | 108.2727 | 0
4652 | 876.92 | 0 | 28.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 876.92 | 0 | 0.088511 | 8.2494 | 0 | 0 | 0 | 0 | on_peak | 876.92 |  |  | 0 | 0 | 100 | 0 | 0
4653 | 883.48 | 0 | 28.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 883.48 | 0 | 0.088511 | 8.4108 | 0 | 0 | 0 | 0 | on_peak | 883.48 |  |  | 0 | 0 | 100 | 0 | 0
4654 | 801.29 | 0 | 28.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 801.29 | 0 | 0.05921 | 8.5511 | 0 | 0 | 0 | 0 | off_peak | 801.29 |  |  | 0 | 0 | 100 | 0 | 0
4655 | 850.35 | 0 | 28 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 850.35 | 0 | 0.05921 | 8.6314 | 0 | 0 | 0 | 0 | off_peak | 850.35 |  |  | 0 | 0 | 100 | 0 | 0
4656 | 845.53 | 0 | 28 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 845.53 | 0 | 0.05921 | 8.7403 | 0 | 0 | 0 | 0 | off_peak | 845.53 |  |  | 0 | 0 | 100 | 0 | 0
4657 | 756.94 | 0 | 27.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 756.94 | 0 | 0.05921 | 8.4192 | 0 | 0 | 0 | 0 | off_peak | 756.94 |  |  | 0 | 0 | 100 | 0 | 0
4658 | 619.58 | 0 | 27.8 | 0 | 0 | 0 | 0 | 8.7006 | 8.7006 | 0 | 0 | 0 | 15.5561 | 628.2806 | 0 | 0.05921 | 8.0333 | 0 | 0 | 0 | 0 | off_peak | 619.58 | 0 | 100 | 0 | 0 | 100 | 0 | 0
4659 | 642.39 | 0 | 27.7 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 27.12 | 654.7524 | 0 | 0.05921 | 7.4982 | 0 | 0 | 0 | 0 | off_peak | 642.39 | 0 | 100 | 0 | 0 | 100 | 0 | 0
4660 | 600.01 | 0 | 27.6 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 38.684 | 612.3724 | 0 | 0.05921 | 6.8715 | 0 | 0 | 0 | 0 | off_peak | 600.01 | 0 | 100 | 0 | 0 | 100 | 0 | 0
4661 | 653.95 | 0 | 27.5 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 50.2479 | 666.3124 | 0 | 0.05921 | 6.3943 | 0 | 0 | 0 | 0 | off_peak | 653.95 | 0 | 100 | 0 | 0 | 100 | 0 | 0
4662 | 742.37 | 0 | 27.7 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 61.8119 | 754.7324 | 0 | 0.05921 | 5.7454 | 0 | 0 | 0 | 0 | off_peak | 742.37 | 0 | 100 | 0 | 0 | 100 | 0 | 0
4663 | 792.56 | 51.7918 | 28.1 | 8.2966 | 8.2966 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 61.8119 | 784.2634 | 0 | 0.05921 | 5.2516 | 0 | 0 | 0 | 8.2966 | off_peak | 784.2634 |  |  | 1.05 | 0 | 98.95 | 43.5705 | 0
4664 | 843.84 | 158.4 | 28.5 | 25.3375 | 25.3375 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 73.3758 | 830.8649 | 0 | 0.05921 | 4.902 | 0 | 0 | 0 | 25.3375 | off_peak | 818.5025 | 0 | 100 | 3 | 0 | 97 | 124.2031 | 0
4665 | 883.84 | 340.49 | 28.8 | 54.4048 | 54.4048 | 0 | 0 | 0.79843 | 0.79843 | 0 | 0 | 0 | 74.1227 | 830.2336 | 0 | 0.05921 | 4.7065 | 0 | 0 | 0 | 54.4048 | off_peak | 829.4352 | 0 | 100 | 6.16 | 0 | 93.84 | 256.0544 | 0
4666 | 907.4 | 682.839 | 29 | 109.027 | 109.027 | 0 | 0 | 0.051567 | 0.051567 | 0 | 0 | 0 | 74.1709 | 798.4246 | 0 | 0.05921 | 4.6192 | 0 | 0 | 0 | 109.027 | off_peak | 798.373 | 0 | 100 | 12.02 | 0 | 87.98 | 503.6222 | 0
4667 | 907.21 | 752.823 | 29.3 | 120.0694 | 120.0694 | 0 | 0 | 0.0033305 | 0.0033305 | 0 | 0 | 0 | 74.174 | 787.1439 | 0 | 0.05921 | 4.7025 | 0 | 0 | 0 | 120.0694 | off_peak | 787.1406 | 0 | 100 | 13.24 | 0 | 86.76 | 564.6317 | 0
4668 | 945.71 | 820.947 | 29.5 | 130.8389 | 130.8389 | 0 | 0 | 0.0002151 | 0.0002151 | 0 | 0 | 0 | 74.1742 | 814.8713 | 0 | 0.05921 | 4.889 | 0 | 0 | 0 | 130.8389 | off_peak | 814.8711 | 0 | 100 | 13.83 | 0 | 86.17 | 639.6659 | 0
4669 | 909.2 | 700.489 | 29.7 | 111.5591 | 111.5591 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1742 | 797.6409 | 0 | 0.088511 | 4.9411 | 0 | 0 | 0 | 111.5591 | on_peak | 797.6409 |  |  | 12.27 | 0 | 87.73 | 551.2226 | 0
4670 | 942.64 | 909.975 | 29.7 | 144.9217 | 144.9217 | 0 | 0 | 0 | 0 | 62.4453 | 62.4453 | 0 | 7.4174 | 735.273 | 0 | 0.088511 | 5.4309 | 0 | 0 | 0 | 144.9217 | on_peak | 735.273 |  |  | 15.37 | 6.62 | 78 | 787.0551 | 0
4671 | 933.79 | 816.687 | 29.7 | 130.0647 | 130.0647 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 803.7253 | 0 | 0.088511 | 5.9245 | 0 | 0 | 0 | 130.0647 | on_peak | 803.7253 |  |  | 13.93 | 0 | 86.07 | 770.5629 | 0
4672 | 891.2 | 672.197 | 29.6 | 107.0926 | 107.0926 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 784.1074 | 0 | 0.088511 | 6.3282 | 0 | 0 | 0 | 107.0926 | on_peak | 784.1074 |  |  | 12.02 | 0 | 87.98 | 677.7022 | 0
4673 | 893.44 | 488.197 | 29.4 | 77.8352 | 77.8352 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 815.6048 | 0 | 0.088511 | 6.7617 | 0 | 0 | 0 | 77.8352 | on_peak | 815.6048 |  |  | 8.71 | 0 | 91.29 | 526.2957 | 0
4674 | 898.61 | 284.501 | 29.1 | 45.4089 | 45.4089 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 853.2011 | 0 | 0.088511 | 7.2005 | 0 | 0 | 0 | 45.4089 | on_peak | 853.2011 |  |  | 5.05 | 0 | 94.95 | 326.9644 | 0
4675 | 875.6 | 90.5214 | 29 | 14.4533 | 14.4533 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 861.1467 | 0 | 0.088511 | 7.5433 | 0 | 0 | 0 | 14.4533 | on_peak | 861.1467 |  |  | 1.65 | 0 | 98.35 | 109.0255 | 0
4676 | 862.46 | 0 | 28.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 862.46 | 0 | 0.088511 | 7.7016 | 0 | 0 | 0 | 0 | on_peak | 862.46 |  |  | 0 | 0 | 100 | 0 | 0
4677 | 849.24 | 0 | 28.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 849.24 | 0 | 0.088511 | 7.7868 | 0 | 0 | 0 | 0 | on_peak | 849.24 |  |  | 0 | 0 | 100 | 0 | 0
4678 | 862.7 | 0 | 28.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 862.7 | 0 | 0.05921 | 7.9893 | 0 | 0 | 0 | 0 | off_peak | 862.7 |  |  | 0 | 0 | 100 | 0 | 0
4679 | 893.83 | 0 | 28 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 893.83 | 0 | 0.05921 | 8.0147 | 0 | 0 | 0 | 0 | off_peak | 893.83 |  |  | 0 | 0 | 100 | 0 | 0
4680 | 857.8 | 0 | 27.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 857.8 | 0 | 0.05921 | 7.7939 | 0 | 0 | 0 | 0 | off_peak | 857.8 |  |  | 0 | 0 | 100 | 0 | 0
4681 | 765.27 | 0 | 27.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 765.27 | 0 | 0.05921 | 7.4202 | 0 | 0 | 0 | 0 | off_peak | 765.27 |  |  | 0 | 0 | 100 | 0 | 0
4682 | 656.34 | 0 | 27.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 656.34 | 0 | 0.05921 | 7.2216 | 0 | 0 | 0 | 0 | off_peak | 656.34 |  |  | 0 | 0 | 100 | 0 | 0
4683 | 649.63 | 0 | 27.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 649.63 | 0 | 0.05921 | 6.9363 | 0 | 0 | 0 | 0 | off_peak | 649.63 |  |  | 0 | 0 | 100 | 0 | 0
4684 | 670.57 | 0 | 27.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 670.57 | 0 | 0.05921 | 6.4266 | 0 | 0 | 0 | 0 | off_peak | 670.57 |  |  | 0 | 0 | 100 | 0 | 0
4685 | 686.19 | 0 | 27.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 686.19 | 0 | 0.05921 | 5.9712 | 0 | 0 | 0 | 0 | off_peak | 686.19 |  |  | 0 | 0 | 100 | 0 | 0
4686 | 698.02 | 0 | 27.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 698.02 | 0 | 0.05921 | 5.3995 | 0 | 0 | 0 | 0 | off_peak | 698.02 |  |  | 0 | 0 | 100 | 0 | 0
4687 | 743.39 | 106.505 | 28.4 | 17.0426 | 17.0426 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 726.3474 | 0 | 0.05921 | 4.9696 | 0 | 0 | 0 | 17.0426 | off_peak | 726.3474 |  |  | 2.29 | 0 | 97.71 | 84.6954 | 0
4688 | 735.94 | 87.4 | 28.7 | 13.9702 | 13.9702 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 721.9698 | 0 | 0.05921 | 4.6181 | 0 | 0 | 0 | 13.9702 | off_peak | 721.9698 |  |  | 1.9 | 0 | 98.1 | 64.5163 | 0
4689 | 762.15 | 247.542 | 29 | 39.5243 | 39.5243 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 722.6257 | 0 | 0.05921 | 4.4001 | 0 | 0 | 0 | 39.5243 | off_peak | 722.6257 |  |  | 5.19 | 0 | 94.81 | 173.9095 | 0
4690 | 725.14 | 690.86 | 29.3 | 110.1868 | 110.1868 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 614.9532 | 0 | 0.05921 | 4.265 | 0 | 0 | 0 | 110.1868 | off_peak | 614.9532 |  |  | 15.2 | 0 | 84.8 | 469.9413 | 0
4691 | 757.33 | 833.502 | 29.6 | 132.7913 | 132.7913 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 624.5387 | 0 | 0.05921 | 4.2482 | 0 | 0 | 0 | 132.7913 | off_peak | 624.5387 |  |  | 17.53 | 0 | 82.47 | 564.1276 | 0
4692 | 734.43 | 922.256 | 29.8 | 146.8237 | 146.8237 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 18.9814 | 599.9686 | 0 | 0.05921 | 4.2908 | 0 | 0 | 0 | 146.8237 | off_peak | 587.6063 | 0 | 100 | 19.99 | 0 | 80.01 | 629.989 | 0
4693 | 759.63 | 949.359 | 30 | 151.0278 | 151.0278 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18.9814 | 608.6022 | 0 | 0.05921 | 4.3757 | 0 | 0 | 0 | 151.0278 | off_peak | 608.6022 |  |  | 19.88 | 0 | 80.12 | 660.8599 | 0
4694 | 685.41 | 913.525 | 30.1 | 145.2739 | 145.2739 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18.9814 | 540.1361 | 0 | 0.05921 | 4.9513 | 0 | 0 | 0 | 145.2739 | off_peak | 540.1361 |  |  | 21.2 | 0 | 78.8 | 719.2994 | 0
4695 | 762.63 | 818.464 | 30 | 130.2045 | 130.2045 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18.9814 | 632.4255 | 0 | 0.05921 | 5.5305 | 0 | 0 | 0 | 130.2045 | off_peak | 632.4255 |  |  | 17.07 | 0 | 82.93 | 720.0928 | 0
4696 | 701.1 | 671.821 | 29.9 | 106.9152 | 106.9152 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18.9814 | 594.1848 | 0 | 0.05921 | 5.9735 | 0 | 0 | 0 | 106.9152 | off_peak | 594.1848 |  |  | 15.25 | 0 | 84.75 | 638.6552 | 0
4697 | 689.38 | 486.609 | 29.6 | 77.5252 | 77.5252 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 30.5453 | 624.2172 | 0 | 0.05921 | 6.3159 | 0 | 0 | 0 | 77.5252 | off_peak | 611.8548 | 0 | 100 | 11.25 | 0 | 88.75 | 489.6424 | 0
4698 | 581.24 | 282.565 | 29.2 | 45.0834 | 45.0834 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30.5453 | 536.1566 | 0 | 0.05921 | 6.5547 | 0 | 0 | 0 | 45.0834 | off_peak | 536.1566 |  |  | 7.76 | 0 | 92.24 | 295.5078 | 0
4699 | 547.65 | 87.8289 | 29 | 14.0234 | 14.0234 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30.5453 | 533.6266 | 0 | 0.05921 | 6.8163 | 0 | 0 | 0 | 14.0234 | off_peak | 533.6266 |  |  | 2.56 | 0 | 97.44 | 95.5878 | 0
4700 | 542.96 | 0 | 28.4 | 0 | 0 | 0 | 0 | 8.7006 | 8.7006 | 0 | 0 | 0 | 38.684 | 551.6606 | 0 | 0.05921 | 7.0979 | 0 | 0 | 0 | 0 | off_peak | 542.96 | 0 | 100 | 0 | 0 | 100 | 0 | 0
4701 | 526.67 | 0 | 28.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 38.684 | 526.67 | 0 | 0.05921 | 7.5121 | 0 | 0 | 0 | 0 | off_peak | 526.67 |  |  | 0 | 0 | 100 | 0 | 0
4702 | 537.01 | 0 | 28.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 38.684 | 537.01 | 0 | 0.05921 | 7.9276 | 0 | 0 | 0 | 0 | off_peak | 537.01 |  |  | 0 | 0 | 100 | 0 | 0
4703 | 537.1 | 0 | 27.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 38.684 | 537.1 | 0 | 0.05921 | 8.1845 | 0 | 0 | 0 | 0 | off_peak | 537.1 |  |  | 0 | 0 | 100 | 0 | 0
4704 | 530.87 | 0 | 27.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 38.684 | 530.87 | 0 | 0.05921 | 8.2909 | 0 | 0 | 0 | 0 | off_peak | 530.87 |  |  | 0 | 0 | 100 | 0 | 0
4705 | 528.4 | 0 | 27.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 38.684 | 528.4 | 0 | 0.05921 | 7.9568 | 0 | 0 | 0 | 0 | off_peak | 528.4 |  |  | 0 | 0 | 100 | 0 | 0
4706 | 522.85 | 0 | 27.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 38.684 | 522.85 | 0 | 0.05921 | 7.7111 | 0 | 0 | 0 | 0 | off_peak | 522.85 |  |  | 0 | 0 | 100 | 0 | 0
4707 | 544.57 | 0 | 27.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 38.684 | 544.57 | 0 | 0.05921 | 7.3224 | 0 | 0 | 0 | 0 | off_peak | 544.57 |  |  | 0 | 0 | 100 | 0 | 0
4708 | 543.37 | 0 | 27.4 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 50.2479 | 555.7324 | 0 | 0.05921 | 6.7582 | 0 | 0 | 0 | 0 | off_peak | 543.37 | 0 | 100 | 0 | 0 | 100 | 0 | 0
4709 | 557.74 | 0 | 27.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50.2479 | 557.74 | 0 | 0.05921 | 6.2491 | 0 | 0 | 0 | 0 | off_peak | 557.74 |  |  | 0 | 0 | 100 | 0 | 0
4710 | 617.54 | 0 | 27.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50.2479 | 617.54 | 0 | 0.05921 | 5.8162 | 0 | 0 | 0 | 0 | off_peak | 617.54 |  |  | 0 | 0 | 100 | 0 | 0
4711 | 721.68 | 101.433 | 28 | 16.2547 | 16.2547 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50.2479 | 705.4253 | 0 | 0.05921 | 5.3583 | 0 | 0 | 0 | 16.2547 | off_peak | 705.4253 |  |  | 2.25 | 0 | 97.75 | 87.0976 | 0
4712 | 701.97 | 296.953 | 28.3 | 47.5349 | 47.5349 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50.2479 | 654.4351 | 0 | 0.05921 | 4.9855 | 0 | 0 | 0 | 47.5349 | off_peak | 654.4351 |  |  | 6.77 | 0 | 93.23 | 236.9829 | 0
4713 | 714.73 | 499.453 | 28.6 | 79.8628 | 79.8628 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50.2479 | 634.8672 | 0 | 0.05921 | 4.7276 | 0 | 0 | 0 | 79.8628 | off_peak | 634.8672 |  |  | 11.17 | 0 | 88.83 | 377.5609 | 0
4714 | 716.93 | 479.931 | 28.8 | 76.6852 | 76.6852 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50.2479 | 640.2448 | 0 | 0.05921 | 4.5806 | 0 | 0 | 0 | 76.6852 | off_peak | 640.2448 |  |  | 10.7 | 0 | 89.3 | 351.2655 | 0
4715 | 718.05 | 676.308 | 29.2 | 107.9053 | 107.9053 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50.2479 | 610.1447 | 0 | 0.05921 | 4.5294 | 0 | 0 | 0 | 107.9053 | off_peak | 610.1447 |  |  | 15.03 | 0 | 84.97 | 488.7473 | 0
4716 | 689.26 | 703.179 | 29.5 | 112.0696 | 112.0696 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50.2479 | 577.1904 | 0 | 0.05921 | 4.5411 | 0 | 0 | 0 | 112.0696 | off_peak | 577.1904 |  |  | 16.26 | 0 | 83.74 | 508.917 | 0
4717 | 722.96 | 869.921 | 29.7 | 138.5427 | 138.5427 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50.2479 | 584.4173 | 0 | 0.05921 | 4.5393 | 0 | 0 | 0 | 138.5427 | off_peak | 584.4173 |  |  | 19.16 | 0 | 80.84 | 628.8897 | 0
4718 | 720.76 | 810.211 | 29.8 | 128.9861 | 128.9861 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50.2479 | 591.7739 | 0 | 0.05921 | 5.1215 | 0 | 0 | 0 | 128.9861 | off_peak | 591.7739 |  |  | 17.9 | 0 | 82.1 | 660.6001 | 0
4719 | 726.39 | 708.232 | 29.8 | 112.751 | 112.751 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50.2479 | 613.639 | 0 | 0.05921 | 5.7452 | 0 | 0 | 0 | 112.751 | off_peak | 613.639 |  |  | 15.52 | 0 | 84.48 | 647.7746 | 0
4720 | 737 | 667.107 | 29.7 | 106.2428 | 106.2428 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50.2479 | 630.7572 | 0 | 0.05921 | 6.2647 | 0 | 0 | 0 | 106.2428 | off_peak | 630.7572 |  |  | 14.42 | 0 | 85.58 | 665.5804 | 0
4721 | 711.64 | 482.537 | 29.5 | 76.9046 | 76.9046 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50.2479 | 634.7354 | 0 | 0.05921 | 6.6845 | 0 | 0 | 0 | 76.9046 | off_peak | 634.7354 |  |  | 10.81 | 0 | 89.19 | 514.0707 | 0
4722 | 709.84 | 216.266 | 29.1 | 34.518 | 34.518 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50.2479 | 675.322 | 0 | 0.05921 | 7.1979 | 0 | 0 | 0 | 34.518 | off_peak | 675.322 |  |  | 4.86 | 0 | 95.14 | 248.4561 | 0
4723 | 598.28 | 57.3295 | 28.9 | 9.157 | 9.157 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50.2479 | 589.123 | 0 | 0.05921 | 7.7407 | 0 | 0 | 0 | 9.157 | off_peak | 589.123 |  |  | 1.53 | 0 | 98.47 | 70.8816 | 0
4724 | 587.76 | 0 | 28.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50.2479 | 587.76 | 0 | 0.05921 | 8.2353 | 0 | 0 | 0 | 0 | off_peak | 587.76 |  |  | 0 | 0 | 100 | 0 | 0
4725 | 593.74 | 0 | 28.1 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 61.8119 | 606.1024 | 0 | 0.05921 | 8.4395 | 0 | 0 | 0 | 0 | off_peak | 593.74 | 0 | 100 | 0 | 0 | 100 | 0 | 0
4726 | 596.68 | 0 | 28 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 61.8119 | 596.68 | 0 | 0.05921 | 8.6767 | 0 | 0 | 0 | 0 | off_peak | 596.68 |  |  | 0 | 0 | 100 | 0 | 0
4727 | 591.66 | 0 | 27.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 61.8119 | 591.66 | 0 | 0.05921 | 8.2017 | 0 | 0 | 0 | 0 | off_peak | 591.66 |  |  | 0 | 0 | 100 | 0 | 0
4728 | 609.22 | 0 | 27.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 61.8119 | 609.22 | 0 | 0.05921 | 7.5129 | 0 | 0 | 0 | 0 | off_peak | 609.22 |  |  | 0 | 0 | 100 | 0 | 0
4729 | 558.99 | 0 | 27.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 61.8119 | 558.99 | 0 | 0.05921 | 7.1349 | 0 | 0 | 0 | 0 | off_peak | 558.99 |  |  | 0 | 0 | 100 | 0 | 0
4730 | 576.54 | 0 | 27.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 61.8119 | 576.54 | 0 | 0.05921 | 6.9685 | 0 | 0 | 0 | 0 | off_peak | 576.54 |  |  | 0 | 0 | 100 | 0 | 0
4731 | 548.41 | 0 | 27.4 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 73.3758 | 560.7724 | 0 | 0.05921 | 6.6362 | 0 | 0 | 0 | 0 | off_peak | 548.41 | 0 | 100 | 0 | 0 | 100 | 0 | 0
4732 | 604.7 | 0 | 27.3 | 0 | 0 | 0 | 0 | 0.79843 | 0.79843 | 0 | 0 | 0 | 74.1227 | 605.4984 | 0 | 0.05921 | 6.1448 | 0 | 0 | 0 | 0 | off_peak | 604.7 | 0 | 100 | 0 | 0 | 100 | 0 | 0
4733 | 589.47 | 0 | 27.3 | 0 | 0 | 0 | 0 | 0.051567 | 0.051567 | 0 | 0 | 0 | 74.1709 | 589.5216 | 0 | 0.05921 | 5.74 | 0 | 0 | 0 | 0 | off_peak | 589.47 | 0 | 100 | 0 | 0 | 100 | 0 | 0
4734 | 667 | 0 | 27.5 | 0 | 0 | 0 | 0 | 0.0033305 | 0.0033305 | 0 | 0 | 0 | 74.174 | 667.0033 | 0 | 0.05921 | 5.2445 | 0 | 0 | 0 | 0 | off_peak | 667 | 0 | 100 | 0 | 0 | 100 | 0 | 0
4735 | 748.04 | 104.068 | 27.9 | 16.683 | 16.683 | 0 | 0 | 0.0002151 | 0.0002151 | 0 | 0 | 0 | 74.1742 | 731.3572 | 0 | 0.05921 | 4.8636 | 0 | 0 | 0 | 16.683 | off_peak | 731.357 | 0 | 100 | 2.23 | 0 | 97.77 | 81.1397 | 0
4736 | 844.14 | 300.93 | 28.2 | 48.1891 | 48.1891 | 0 | 0 | 1.4852e-05 | 1.4852e-05 | 0 | 0 | 0 | 74.1743 | 795.951 | 0 | 0.05921 | 4.6173 | 0 | 0 | 0 | 48.1891 | off_peak | 795.9509 | 0 | 100 | 5.71 | 0 | 94.29 | 222.5051 | 0
4737 | 852.32 | 504.402 | 28.4 | 80.713 | 80.713 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1743 | 771.607 | 0 | 0.05921 | 4.4624 | 0 | 0 | 0 | 80.713 | off_peak | 771.607 |  |  | 9.47 | 0 | 90.53 | 360.1751 | 0
4738 | 871.34 | 684.959 | 28.6 | 109.5253 | 109.5253 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1743 | 761.8147 | 0 | 0.05921 | 4.4453 | 0 | 0 | 0 | 109.5253 | off_peak | 761.8147 |  |  | 12.57 | 0 | 87.43 | 486.8754 | 0
4739 | 854.21 | 825.705 | 28.8 | 131.9343 | 131.9343 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1743 | 722.2757 | 0 | 0.05921 | 4.6165 | 0 | 0 | 0 | 131.9343 | off_peak | 722.2757 |  |  | 15.45 | 0 | 84.55 | 609.0741 | 0
4740 | 913.28 | 758.548 | 28.9 | 121.1595 | 121.1595 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1743 | 792.1205 | 0 | 0.05921 | 4.8686 | 0 | 0 | 0 | 121.1595 | off_peak | 792.1205 |  |  | 13.27 | 0 | 86.73 | 589.8731 | 0
4741 | 877.93 | 551.591 | 29 | 88.071 | 88.071 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1743 | 789.859 | 0 | 0.088511 | 4.9331 | 0 | 0 | 0 | 88.071 | on_peak | 789.859 |  |  | 10.03 | 0 | 89.97 | 434.4644 | 0
4742 | 905.59 | 834.259 | 29.1 | 133.1551 | 133.1551 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1743 | 772.4349 | 0 | 0.088511 | 5.1852 | 0 | 0 | 0 | 133.1551 | on_peak | 772.4349 |  |  | 14.7 | 0 | 85.3 | 690.4367 | 0
4743 | 899.8 | 735.574 | 29.1 | 117.4041 | 117.4041 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1743 | 782.3959 | 0 | 0.088511 | 5.7433 | 0 | 0 | 0 | 117.4041 | on_peak | 782.3959 |  |  | 13.05 | 0 | 86.95 | 674.288 | 0
4744 | 743.88 | 155.313 | 29 | 24.7984 | 24.7984 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1743 | 719.0816 | 0 | 0.088511 | 6.4578 | 0 | 0 | 0 | 24.7984 | on_peak | 719.0816 |  |  | 3.33 | 0 | 96.67 | 160.144 | 0
4745 | 792.64 | 217.327 | 28.8 | 34.7253 | 34.7253 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1743 | 757.9147 | 0 | 0.088511 | 7.0313 | 0 | 0 | 0 | 34.7253 | on_peak | 757.9147 |  |  | 4.38 | 0 | 95.62 | 244.1636 | 0
4746 | 818.51 | 120.924 | 28.6 | 19.3358 | 19.3358 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1743 | 799.1742 | 0 | 0.088511 | 7.4068 | 0 | 0 | 0 | 19.3358 | on_peak | 799.1742 |  |  | 2.36 | 0 | 97.64 | 143.2163 | 0
4747 | 790.63 | 52.0064 | 28.5 | 8.3189 | 8.3189 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1743 | 782.3111 | 0 | 0.088511 | 7.3326 | 0 | 0 | 0 | 8.3189 | on_peak | 782.3111 |  |  | 1.05 | 0 | 98.95 | 60.9992 | 0
4748 | 838.51 | 0 | 28.1 | 0 | 0 | 0 | 0 | 0 | 0 | 62.4453 | 62.4453 | 0 | 7.4174 | 776.0647 | 0 | 0.088511 | 7.2037 | 0 | 0 | 0 | 0 | on_peak | 776.0647 |  |  | 0 | 7.45 | 92.55 | 0 | 0
4749 | 818.44 | 0 | 28.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 818.44 | 0 | 0.088511 | 7.0398 | 0 | 0 | 0 | 0 | on_peak | 818.44 |  |  | 0 | 0 | 100 | 0 | 0
4750 | 757.91 | 0 | 28 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 18.9814 | 770.2724 | 0 | 0.05921 | 7.1558 | 0 | 0 | 0 | 0 | off_peak | 757.91 | 0 | 100 | 0 | 0 | 100 | 0 | 0
4751 | 786.51 | 0 | 27.9 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 30.5453 | 798.8724 | 0 | 0.05921 | 7.0266 | 0 | 0 | 0 | 0 | off_peak | 786.51 | 0 | 100 | 0 | 0 | 100 | 0 | 0
4752 | 775.53 | 0 | 27.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30.5453 | 775.53 | 0 | 0.05921 | 6.8082 | 0 | 0 | 0 | 0 | off_peak | 775.53 |  |  | 0 | 0 | 100 | 0 | 0
4753 | 647.91 | 0 | 27.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30.5453 | 647.91 | 0 | 0.05921 | 6.6538 | 0 | 0 | 0 | 0 | off_peak | 647.91 |  |  | 0 | 0 | 100 | 0 | 0
4754 | 599.55 | 0 | 27.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30.5453 | 599.55 | 0 | 0.05921 | 6.6226 | 0 | 0 | 0 | 0 | off_peak | 599.55 |  |  | 0 | 0 | 100 | 0 | 0
4755 | 555.53 | 0 | 27.7 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 42.1093 | 567.8924 | 0 | 0.05921 | 6.384 | 0 | 0 | 0 | 0 | off_peak | 555.53 | 0 | 100 | 0 | 0 | 100 | 0 | 0
4756 | 570.7 | 0 | 27.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 42.1093 | 570.7 | 0 | 0.05921 | 5.9395 | 0 | 0 | 0 | 0 | off_peak | 570.7 |  |  | 0 | 0 | 100 | 0 | 0
4757 | 561.42 | 0 | 27.6 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 53.6732 | 573.7824 | 0 | 0.05921 | 5.4692 | 0 | 0 | 0 | 0 | off_peak | 561.42 | 0 | 100 | 0 | 0 | 100 | 0 | 0
4758 | 668.52 | 0 | 27.8 | 0 | 0 | 0 | 0 | 8.7006 | 8.7006 | 0 | 0 | 0 | 61.8119 | 677.2206 | 0 | 0.05921 | 5.0391 | 0 | 0 | 0 | 0 | off_peak | 668.52 | 0 | 100 | 0 | 0 | 100 | 0 | 0
4759 | 671.02 | 100.688 | 28.2 | 16.1235 | 16.1235 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 73.3758 | 667.2588 | 0 | 0.05921 | 4.6417 | 0 | 0 | 0 | 16.1235 | off_peak | 654.8965 | 0 | 100 | 2.4 | 0 | 97.6 | 74.8401 | 0
4760 | 772.98 | 295.429 | 28.5 | 47.2565 | 47.2565 | 0 | 0 | 0.79843 | 0.79843 | 0 | 0 | 0 | 74.1227 | 726.522 | 0 | 0.05921 | 4.3958 | 0 | 0 | 0 | 47.2565 | off_peak | 725.7235 | 0 | 100 | 6.11 | 0 | 93.89 | 207.7321 | 0
4761 | 818.67 | 497.114 | 28.7 | 79.4598 | 79.4598 | 0 | 0 | 0.051567 | 0.051567 | 0 | 0 | 0 | 74.1709 | 739.2618 | 0 | 0.05921 | 4.2466 | 0 | 0 | 0 | 79.4598 | off_peak | 739.2102 | 0 | 100 | 9.71 | 0 | 90.29 | 337.4327 | 0
4762 | 847.3 | 677.824 | 28.9 | 108.2658 | 108.2658 | 0 | 0 | 0.0033305 | 0.0033305 | 0 | 0 | 0 | 74.174 | 739.0375 | 0 | 0.05921 | 4.232 | 0 | 0 | 0 | 108.2658 | off_peak | 739.0342 | 0 | 100 | 12.78 | 0 | 87.22 | 458.1767 | 0
4763 | 818.21 | 417.03 | 29.2 | 66.5374 | 66.5374 | 0 | 0 | 0.0002151 | 0.0002151 | 0 | 0 | 0 | 74.1742 | 751.6728 | 0 | 0.05921 | 4.3976 | 0 | 0 | 0 | 66.5374 | off_peak | 751.6726 | 0 | 100 | 8.13 | 0 | 91.87 | 292.6041 | 0
4764 | 919.78 | 758.556 | 29.5 | 120.8953 | 120.8953 | 0 | 0 | 1.3893e-05 | 1.3893e-05 | 0 | 0 | 0 | 74.1743 | 798.8847 | 0 | 0.05921 | 4.6362 | 0 | 0 | 0 | 120.8953 | off_peak | 798.8847 | 0 | 100 | 13.14 | 0 | 86.86 | 560.4974 | 0
4765 | 846.37 | 793.688 | 29.7 | 126.4019 | 126.4019 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1743 | 719.9681 | 0 | 0.088511 | 4.8621 | 0 | 0 | 0 | 126.4019 | on_peak | 719.9681 |  |  | 14.93 | 0 | 85.07 | 614.5825 | 0
4766 | 867.22 | 114.95 | 29.8 | 18.3001 | 18.3001 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1743 | 848.9199 | 0 | 0.088511 | 5.2665 | 0 | 0 | 0 | 18.3001 | on_peak | 848.9199 |  |  | 2.11 | 0 | 97.89 | 96.3767 | 0
4767 | 895.03 | 88.35 | 29.8 | 14.0654 | 14.0654 | 0 | 0 | 0 | 0 | 62.4453 | 62.4453 | 0 | 7.4174 | 818.5193 | 0 | 0.088511 | 5.6197 | 0 | 0 | 0 | 14.0654 | on_peak | 818.5193 |  |  | 1.57 | 6.98 | 91.45 | 79.0429 | 0
4768 | 799.47 | 116.606 | 29.7 | 18.5706 | 18.5706 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 780.8994 | 0 | 0.088511 | 6.0715 | 0 | 0 | 0 | 18.5706 | on_peak | 780.8994 |  |  | 2.32 | 0 | 97.68 | 112.7516 | 0
4769 | 833.01 | 70.3 | 29.5 | 11.2041 | 11.2041 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 821.8059 | 0 | 0.088511 | 6.4989 | 0 | 0 | 0 | 11.2041 | on_peak | 821.8059 |  |  | 1.35 | 0 | 98.65 | 72.8141 | 0
4770 | 873.59 | 61.1464 | 29.2 | 9.7559 | 9.7559 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 863.8341 | 0 | 0.088511 | 6.7836 | 0 | 0 | 0 | 9.7559 | on_peak | 863.8341 |  |  | 1.12 | 0 | 98.88 | 66.1806 | 0
4771 | 864.82 | 27.55 | 29 | 4.3988 | 4.3988 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 860.4212 | 0 | 0.088511 | 7.0174 | 0 | 0 | 0 | 4.3988 | on_peak | 860.4212 |  |  | 0.51 | 0 | 99.49 | 30.8685 | 0
4772 | 898.66 | 0 | 28.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 898.66 | 0 | 0.088511 | 7.3215 | 0 | 0 | 0 | 0 | on_peak | 898.66 |  |  | 0 | 0 | 100 | 0 | 0
4773 | 870.29 | 0 | 28.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 870.29 | 0 | 0.088511 | 7.7333 | 0 | 0 | 0 | 0 | on_peak | 870.29 |  |  | 0 | 0 | 100 | 0 | 0
4774 | 798.37 | 0 | 28.2 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 18.9814 | 810.7324 | 0 | 0.05921 | 7.9023 | 0 | 0 | 0 | 0 | off_peak | 798.37 | 0 | 100 | 0 | 0 | 100 | 0 | 0
4775 | 875.33 | 0 | 28.1 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 30.5453 | 887.6924 | 0 | 0.05921 | 8.0493 | 0 | 0 | 0 | 0 | off_peak | 875.33 | 0 | 100 | 0 | 0 | 100 | 0 | 0
4776 | 798.52 | 0 | 28 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 42.1093 | 810.8824 | 0 | 0.05921 | 7.8873 | 0 | 0 | 0 | 0 | off_peak | 798.52 | 0 | 100 | 0 | 0 | 100 | 0 | 0
4777 | 767.56 | 0 | 27.9 | 0 | 0 | 0 | 0 | 8.7006 | 8.7006 | 0 | 0 | 0 | 50.2479 | 776.2606 | 0 | 0.05921 | 7.7994 | 0 | 0 | 0 | 0 | off_peak | 767.56 | 0 | 100 | 0 | 0 | 100 | 0 | 0
4778 | 665.35 | 0 | 27.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50.2479 | 665.35 | 0 | 0.05921 | 7.666 | 0 | 0 | 0 | 0 | off_peak | 665.35 |  |  | 0 | 0 | 100 | 0 | 0
4779 | 703.85 | 0 | 27.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50.2479 | 703.85 | 0 | 0.05921 | 7.3269 | 0 | 0 | 0 | 0 | off_peak | 703.85 |  |  | 0 | 0 | 100 | 0 | 0
4780 | 662.21 | 0 | 27.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50.2479 | 662.21 | 0 | 0.05921 | 6.7606 | 0 | 0 | 0 | 0 | off_peak | 662.21 |  |  | 0 | 0 | 100 | 0 | 0
4781 | 639.73 | 0 | 27.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50.2479 | 639.73 | 0 | 0.05921 | 6.1529 | 0 | 0 | 0 | 0 | off_peak | 639.73 |  |  | 0 | 0 | 100 | 0 | 0
4782 | 717.67 | 0 | 28 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50.2479 | 717.67 | 0 | 0.05921 | 5.5586 | 0 | 0 | 0 | 0 | off_peak | 717.67 |  |  | 0 | 0 | 100 | 0 | 0
4783 | 748.35 | 98.949 | 28.5 | 15.8278 | 15.8278 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 61.8119 | 744.8846 | 0 | 0.05921 | 5.0828 | 0 | 0 | 0 | 15.8278 | off_peak | 732.5222 | 0 | 100 | 2.12 | 0 | 97.88 | 80.4497 | 0
4784 | 817.94 | 294.005 | 28.8 | 46.9772 | 46.9772 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 73.3758 | 783.3251 | 0 | 0.05921 | 4.7291 | 0 | 0 | 0 | 46.9772 | off_peak | 770.9628 | 0 | 100 | 5.74 | 0 | 94.26 | 222.1616 | 0
4785 | 859.54 | 496.844 | 29 | 79.3297 | 79.3297 | 0 | 0 | 0.79843 | 0.79843 | 0 | 0 | 0 | 74.1227 | 781.0087 | 0 | 0.05921 | 4.532 | 0 | 0 | 0 | 79.3297 | off_peak | 780.2103 | 0 | 100 | 9.23 | 0 | 90.77 | 359.5233 | 0
4786 | 814.96 | 677.253 | 29.2 | 108.0561 | 108.0561 | 0 | 0 | 0.051567 | 0.051567 | 0 | 0 | 0 | 74.1709 | 706.9555 | 0 | 0.05921 | 4.4689 | 0 | 0 | 0 | 108.0561 | off_peak | 706.9039 | 0 | 100 | 13.26 | 0 | 86.74 | 482.8932 | 0
4787 | 829.66 | 817.821 | 29.4 | 130.3884 | 130.3884 | 0 | 0 | 0.0033305 | 0.0033305 | 0 | 0 | 0 | 74.174 | 699.2749 | 0 | 0.05921 | 4.5898 | 0 | 0 | 0 | 130.3884 | off_peak | 699.2716 | 0 | 100 | 15.72 | 0 | 84.28 | 598.458 | 0
4788 | 864.25 | 277.256 | 29.6 | 44.1717 | 44.1717 | 0 | 0 | 0.0002151 | 0.0002151 | 0 | 0 | 0 | 74.1742 | 820.0785 | 0 | 0.05921 | 4.8842 | 0 | 0 | 0 | 44.1717 | off_peak | 820.0783 | 0 | 100 | 5.11 | 0 | 94.89 | 215.7418 | 0
4789 | 871.33 | 723.01 | 29.7 | 115.1458 | 115.1458 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1742 | 756.1842 | 0 | 0.088511 | 5.1136 | 0 | 0 | 0 | 115.1458 | on_peak | 756.1842 |  |  | 13.21 | 0 | 86.79 | 588.8082 | 0
4790 | 868.04 | 494.868 | 29.7 | 78.8122 | 78.8122 | 0 | 0 | 0 | 0 | 62.4453 | 62.4453 | 0 | 7.4174 | 726.7826 | 0 | 0.088511 | 5.3816 | 0 | 0 | 0 | 78.8122 | on_peak | 726.7826 |  |  | 9.08 | 7.19 | 83.73 | 424.1369 | 0
4791 | 878.12 | 439.873 | 29.7 | 70.0537 | 70.0537 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 808.0663 | 0 | 0.088511 | 5.6388 | 0 | 0 | 0 | 70.0537 | on_peak | 808.0663 |  |  | 7.98 | 0 | 92.02 | 395.0221 | 0
4792 | 801.18 | 656.379 | 29.6 | 104.5725 | 104.5725 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 696.6075 | 0 | 0.088511 | 6.1057 | 0 | 0 | 0 | 104.5725 | on_peak | 696.6075 |  |  | 13.05 | 0 | 86.95 | 638.4862 | 0
4793 | 851.95 | 440.305 | 29.4 | 70.1996 | 70.1996 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 781.7504 | 0 | 0.088511 | 6.7511 | 0 | 0 | 0 | 70.1996 | on_peak | 781.7504 |  |  | 8.24 | 0 | 91.76 | 473.9277 | 0
4794 | 882.73 | 208.788 | 29.1 | 33.3244 | 33.3244 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 849.4056 | 0 | 0.088511 | 7.2777 | 0 | 0 | 0 | 33.3244 | on_peak | 849.4056 |  |  | 3.78 | 0 | 96.22 | 242.525 | 0
4795 | 862.54 | 25.65 | 28.9 | 4.097 | 4.097 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 858.443 | 0 | 0.088511 | 7.9314 | 0 | 0 | 0 | 4.097 | on_peak | 858.443 |  |  | 0.47 | 0 | 99.53 | 32.4945 | 0
4796 | 896.82 | 0 | 28.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 896.82 | 0 | 0.088511 | 8.4003 | 0 | 0 | 0 | 0 | on_peak | 896.82 |  |  | 0 | 0 | 100 | 0 | 0
4797 | 848.09 | 0 | 28.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 848.09 | 0 | 0.088511 | 8.7714 | 0 | 0 | 0 | 0 | on_peak | 848.09 |  |  | 0 | 0 | 100 | 0 | 0
4798 | 817.89 | 0 | 28.3 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 18.9814 | 830.2524 | 0 | 0.05921 | 8.9792 | 0 | 0 | 0 | 0 | off_peak | 817.89 | 0 | 100 | 0 | 0 | 100 | 0 | 0
4799 | 882.87 | 0 | 28.2 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 30.5453 | 895.2324 | 0 | 0.05921 | 8.6865 | 0 | 0 | 0 | 0 | off_peak | 882.87 | 0 | 100 | 0 | 0 | 100 | 0 | 0
4800 | 829.62 | 0 | 28.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30.5453 | 829.62 | 0 | 0.05921 | 8.4259 | 0 | 0 | 0 | 0 | off_peak | 829.62 |  |  | 0 | 0 | 100 | 0 | 0
4801 | 731.22 | 0 | 28.1 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 42.1093 | 743.5824 | 0 | 0.05921 | 8.1272 | 0 | 0 | 0 | 0 | off_peak | 731.22 | 0 | 100 | 0 | 0 | 100 | 0 | 0
4802 | 723.92 | 0 | 28 | 0 | 0 | 0 | 0 | 8.7006 | 8.7006 | 0 | 0 | 0 | 50.2479 | 732.6206 | 0 | 0.05921 | 8.066 | 0 | 0 | 0 | 0 | off_peak | 723.92 | 0 | 100 | 0 | 0 | 100 | 0 | 0
4803 | 653.04 | 0 | 28 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 61.8119 | 665.4024 | 0 | 0.05921 | 7.7509 | 0 | 0 | 0 | 0 | off_peak | 653.04 | 0 | 100 | 0 | 0 | 100 | 0 | 0
4804 | 643.22 | 0 | 27.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 61.8119 | 643.22 | 0 | 0.05921 | 7.2214 | 0 | 0 | 0 | 0 | off_peak | 643.22 |  |  | 0 | 0 | 100 | 0 | 0
4805 | 691.28 | 0 | 27.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 61.8119 | 691.28 | 0 | 0.05921 | 6.5464 | 0 | 0 | 0 | 0 | off_peak | 691.28 |  |  | 0 | 0 | 100 | 0 | 0
4806 | 733.92 | 0 | 28 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 61.8119 | 733.92 | 0 | 0.05921 | 5.9776 | 0 | 0 | 0 | 0 | off_peak | 733.92 |  |  | 0 | 0 | 100 | 0 | 0
4807 | 720.35 | 96.488 | 28.3 | 15.4454 | 15.4454 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 61.8119 | 704.9046 | 0 | 0.05921 | 5.5174 | 0 | 0 | 0 | 15.4454 | off_peak | 704.9046 |  |  | 2.14 | 0 | 97.86 | 85.218 | 0
4808 | 844.28 | 290.375 | 28.7 | 46.4142 | 46.4142 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 73.3758 | 810.2282 | 0 | 0.05921 | 5.1972 | 0 | 0 | 0 | 46.4142 | off_peak | 797.8658 | 0 | 100 | 5.5 | 0 | 94.5 | 241.2216 | 0
4809 | 834.83 | 494.204 | 28.9 | 78.937 | 78.937 | 0 | 0 | 0.79843 | 0.79843 | 0 | 0 | 0 | 74.1227 | 756.6914 | 0 | 0.05921 | 5.0068 | 0 | 0 | 0 | 78.937 | off_peak | 755.893 | 0 | 100 | 9.46 | 0 | 90.54 | 395.2196 | 0
4810 | 883.49 | 555.149 | 29.3 | 88.542 | 88.542 | 0 | 0 | 0.051567 | 0.051567 | 0 | 0 | 0 | 74.1709 | 794.9996 | 0 | 0.05921 | 4.902 | 0 | 0 | 0 | 88.542 | off_peak | 794.948 | 0 | 100 | 10.02 | 0 | 89.98 | 434.0339 | 0
4811 | 872.73 | 609.28 | 29.7 | 97.0333 | 97.0333 | 0 | 0 | 0.0033305 | 0.0033305 | 0 | 0 | 0 | 74.174 | 775.7 | 0 | 0.05921 | 5.0122 | 0 | 0 | 0 | 97.0333 | off_peak | 775.6967 | 0 | 100 | 11.12 | 0 | 88.88 | 486.3551 | 0
4812 | 896.79 | 899.747 | 30 | 143.1354 | 143.1351 | 0 | 0.0002151 | 0.0002151 | 0 | 0 | 0 | 0 | 74.1742 | 753.6549 | 0 | 0.05921 | 5.2233 | 0 | 0 | 0.00020121 | 143.1351 | off_peak | 753.6549 | 100 | 0 | 15.96 | 0 | 84.04 | 747.6373 | 0
4813 | 888.02 | 459.613 | 30.3 | 73.0367 | 73.0367 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1742 | 814.9833 | 0 | 0.088511 | 5.3356 | 0 | 0 | 0.00020121 | 73.0367 | on_peak | 814.9833 |  |  | 8.22 | 0 | 91.78 | 389.694 | 0
4814 | 905.31 | 515.677 | 30.4 | 81.9157 | 81.9157 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1742 | 823.3943 | 0 | 0.088511 | 5.5951 | 0 | 0 | 0.00020121 | 81.9157 | on_peak | 823.3943 |  |  | 9.05 | 0 | 90.95 | 458.3244 | 0
4815 | 917.08 | 670.067 | 30.5 | 106.4015 | 106.4015 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1742 | 810.6785 | 0 | 0.088511 | 5.8591 | 0 | 0 | 0.00020121 | 106.4015 | on_peak | 810.6785 |  |  | 11.6 | 0 | 88.4 | 623.4157 | 0
4816 | 894.09 | 542.451 | 30.5 | 86.1371 | 86.1371 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1742 | 807.9529 | 0 | 0.088511 | 6.2467 | 0 | 0 | 0.00020121 | 86.1371 | on_peak | 807.9529 |  |  | 9.63 | 0 | 90.37 | 538.0762 | 0
4817 | 862.35 | 363.438 | 30.3 | 57.7536 | 57.7536 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1742 | 804.5964 | 0 | 0.088511 | 6.7119 | 0 | 0 | 0.00020121 | 57.7536 | on_peak | 804.5964 |  |  | 6.7 | 0 | 93.3 | 387.6387 | 0
4818 | 907.33 | 196.867 | 29.9 | 31.3299 | 31.3299 | 0 | 0 | 0 | 0 | 62.4453 | 62.4453 | 0 | 7.4174 | 813.5548 | 0 | 0.088511 | 7.3241 | 0.00018821 | 0 | 0 | 31.3301 | on_peak | 813.5548 |  |  | 3.45 | 6.88 | 89.66 | 229.4649 | 0
4819 | 900.4 | 49.8147 | 29.7 | 7.9334 | 7.9334 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 892.4666 | 0 | 0.088511 | 7.8601 | 0 | 0 | 0 | 7.9334 | on_peak | 892.4666 |  |  | 0.88 | 0 | 99.12 | 62.3579 | 0
4820 | 937.3 | 0 | 29 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 937.3 | 0 | 0.088511 | 8.2779 | 0 | 0 | 0 | 0 | on_peak | 937.3 |  |  | 0 | 0 | 100 | 0 | 0
4821 | 888.48 | 0 | 28.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 888.48 | 0 | 0.088511 | 8.3936 | 0 | 0 | 0 | 0 | on_peak | 888.48 |  |  | 0 | 0 | 100 | 0 | 0
4822 | 863.85 | 0 | 28.5 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 18.9814 | 876.2124 | 0 | 0.05921 | 8.7558 | 0 | 0 | 0 | 0 | off_peak | 863.85 | 0 | 100 | 0 | 0 | 100 | 0 | 0
4823 | 896.09 | 0 | 28.4 | 0 | 0 | 0 | 0 | 8.7006 | 8.7006 | 0 | 0 | 0 | 27.12 | 904.7906 | 0 | 0.05921 | 8.8835 | 0 | 0 | 0 | 0 | off_peak | 896.09 | 0 | 100 | 0 | 0 | 100 | 0 | 0
4824 | 846.99 | 0 | 28.3 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 38.684 | 859.3524 | 0 | 0.05921 | 8.8037 | 0 | 0 | 0 | 0 | off_peak | 846.99 | 0 | 100 | 0 | 0 | 100 | 0 | 0
4825 | 818.5 | 0 | 28.3 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 50.2479 | 830.8624 | 0 | 0.05921 | 8.6977 | 0 | 0 | 0 | 0 | off_peak | 818.5 | 0 | 100 | 0 | 0 | 100 | 0 | 0
4826 | 742.96 | 0 | 28.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50.2479 | 742.96 | 0 | 0.05921 | 8.4887 | 0 | 0 | 0 | 0 | off_peak | 742.96 |  |  | 0 | 0 | 100 | 0 | 0
4827 | 732.72 | 0 | 28.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50.2479 | 732.72 | 0 | 0.05921 | 8.316 | 0 | 0 | 0 | 0 | off_peak | 732.72 |  |  | 0 | 0 | 100 | 0 | 0
4828 | 683.12 | 0 | 28.1 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 61.8119 | 695.4824 | 0 | 0.05921 | 7.7511 | 0 | 0 | 0 | 0 | off_peak | 683.12 | 0 | 100 | 0 | 0 | 100 | 0 | 0
4829 | 750.55 | 0 | 28.1 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 73.3758 | 762.9124 | 0 | 0.05921 | 7.0267 | 0 | 0 | 0 | 0 | off_peak | 750.55 | 0 | 100 | 0 | 0 | 100 | 0 | 0
4830 | 765.96 | 0 | 28.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 73.3758 | 765.96 | 0 | 0.05921 | 6.4302 | 0 | 0 | 0 | 0 | off_peak | 765.96 |  |  | 0 | 0 | 100 | 0 | 0
4831 | 809.31 | 93.9694 | 28.4 | 15.0367 | 15.0367 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 73.3758 | 794.2733 | 0 | 0.05921 | 5.9416 | 0 | 0 | 0 | 15.0367 | off_peak | 794.2733 |  |  | 1.86 | 0 | 98.14 | 89.3428 | 0
4832 | 835.66 | 286.849 | 28.8 | 45.8338 | 45.8338 | 0 | 0 | 0.79843 | 0.79843 | 0 | 0 | 0 | 74.1227 | 790.6246 | 0 | 0.05921 | 5.5604 | 0 | 0 | 0 | 45.8338 | off_peak | 789.8262 | 0 | 100 | 5.48 | 0 | 94.52 | 254.8525 | 0
4833 | 905.2 | 489.479 | 29 | 78.1537 | 78.1537 | 0 | 0 | 0.051567 | 0.051567 | 0 | 0 | 0 | 74.1709 | 827.0978 | 0 | 0.05921 | 5.2924 | 0 | 0 | 0 | 78.1537 | off_peak | 827.0463 | 0 | 100 | 8.63 | 0 | 91.37 | 413.6183 | 0
4834 | 887.52 | 523.606 | 29.2 | 83.5416 | 83.5416 | 0 | 0 | 0.0033305 | 0.0033305 | 0 | 0 | 0 | 74.174 | 803.9817 | 0 | 0.05921 | 5.1453 | 0 | 0 | 0 | 83.5416 | off_peak | 803.9784 | 0 | 100 | 9.41 | 0 | 90.59 | 429.8432 | 0
4835 | 897.09 | 579.973 | 29.5 | 92.4335 | 92.4335 | 0 | 0 | 0.0002151 | 0.0002151 | 0 | 0 | 0 | 74.1742 | 804.6567 | 0 | 0.05921 | 5.1967 | 0 | 0 | 0 | 92.4335 | off_peak | 804.6565 | 0 | 100 | 10.3 | 0 | 89.7 | 480.3498 | 0
4836 | 937.62 | 41.8 | 29.7 | 6.657 | 6.657 | 0 | 0 | 1.3893e-05 | 1.3893e-05 | 0 | 0 | 0 | 74.1743 | 930.963 | 0 | 0.05921 | 5.3392 | 0 | 0 | 0 | 6.657 | off_peak | 930.963 | 0 | 100 | 0.71 | 0 | 99.29 | 35.5429 | 0
4837 | 927.72 | 90.25 | 29.9 | 14.3626 | 14.3626 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1743 | 913.3574 | 0 | 0.088511 | 5.5013 | 0 | 0 | 0 | 14.3626 | on_peak | 913.3574 |  |  | 1.55 | 0 | 98.45 | 79.0131 | 0
4838 | 936 | 89.3 | 30 | 14.2062 | 14.2062 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1743 | 921.7938 | 0 | 0.088511 | 5.8061 | 0 | 0 | 0 | 14.2062 | on_peak | 921.7938 |  |  | 1.52 | 0 | 98.48 | 82.4831 | 0
4839 | 968.64 | 159.484 | 30 | 25.3714 | 25.3714 | 0 | 0 | 0 | 0 | 62.4453 | 62.4453 | 0 | 7.4174 | 880.8234 | 0 | 0.088511 | 6.2568 | 0 | 0 | 0 | 25.3714 | on_peak | 880.8234 |  |  | 2.62 | 6.45 | 90.93 | 158.743 | 0
4840 | 918.11 | 239.34 | 29.9 | 38.0891 | 38.0891 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 880.0209 | 0 | 0.088511 | 6.8003 | 0 | 0 | 0 | 38.0891 | on_peak | 880.0209 |  |  | 4.15 | 0 | 95.85 | 259.0163 | 0
4841 | 906.07 | 194.679 | 29.7 | 31.0044 | 31.0044 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 875.0656 | 0 | 0.088511 | 7.3084 | 0 | 0 | 0 | 31.0044 | on_peak | 875.0656 |  |  | 3.42 | 0 | 96.58 | 226.5935 | 0
4842 | 908.79 | 142.827 | 29.4 | 22.7715 | 22.7715 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 886.0185 | 0 | 0.088511 | 7.8324 | 0 | 0 | 0 | 22.7715 | on_peak | 886.0185 |  |  | 2.51 | 0 | 97.49 | 178.3552 | 0
4843 | 911.78 | 58.9094 | 29.2 | 9.399 | 9.399 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 902.381 | 0 | 0.088511 | 8.2351 | 0 | 0 | 0 | 9.399 | on_peak | 902.381 |  |  | 1.03 | 0 | 98.97 | 77.4015 | 0
4844 | 881.71 | 0 | 28.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 881.71 | 0 | 0.088511 | 8.3874 | 0 | 0 | 0 | 0 | on_peak | 881.71 |  |  | 0 | 0 | 100 | 0 | 0
4845 | 886.53 | 0 | 28.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 886.53 | 0 | 0.088511 | 8.0503 | 0 | 0 | 0 | 0 | on_peak | 886.53 |  |  | 0 | 0 | 100 | 0 | 0
4846 | 869.16 | 0 | 28.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 869.16 | 0 | 0.05921 | 8.0409 | 0 | 0 | 0 | 0 | off_peak | 869.16 |  |  | 0 | 0 | 100 | 0 | 0
4847 | 871.93 | 0 | 28.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 871.93 | 0 | 0.05921 | 8.0863 | 0 | 0 | 0 | 0 | off_peak | 871.93 |  |  | 0 | 0 | 100 | 0 | 0
4848 | 824.14 | 0 | 28.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 824.14 | 0 | 0.05921 | 8.0937 | 0 | 0 | 0 | 0 | off_peak | 824.14 |  |  | 0 | 0 | 100 | 0 | 0
4849 | 764.38 | 0 | 28.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 764.38 | 0 | 0.05921 | 8.0687 | 0 | 0 | 0 | 0 | off_peak | 764.38 |  |  | 0 | 0 | 100 | 0 | 0
4850 | 712.29 | 0 | 28.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 712.29 | 0 | 0.05921 | 7.9794 | 0 | 0 | 0 | 0 | off_peak | 712.29 |  |  | 0 | 0 | 100 | 0 | 0
4851 | 743.68 | 0 | 28.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 743.68 | 0 | 0.05921 | 7.7623 | 0 | 0 | 0 | 0 | off_peak | 743.68 |  |  | 0 | 0 | 100 | 0 | 0
4852 | 703.96 | 0 | 28.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 703.96 | 0 | 0.05921 | 7.2446 | 0 | 0 | 0 | 0 | off_peak | 703.96 |  |  | 0 | 0 | 100 | 0 | 0
4853 | 650.19 | 0 | 28.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 650.19 | 0 | 0.05921 | 6.6533 | 0 | 0 | 0 | 0 | off_peak | 650.19 |  |  | 0 | 0 | 100 | 0 | 0
4854 | 698.6 | 0 | 28.2 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 18.9814 | 710.9624 | 0 | 0.05921 | 6.126 | 0 | 0 | 0 | 0 | off_peak | 698.6 | 0 | 100 | 0 | 0 | 100 | 0 | 0
4855 | 732.17 | 72.2823 | 28.7 | 11.5538 | 11.5538 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18.9814 | 720.6162 | 0 | 0.05921 | 5.6535 | 0 | 0 | 0 | 11.5538 | off_peak | 720.6162 |  |  | 1.58 | 0 | 98.42 | 65.3197 | 0
4856 | 721.38 | 274.755 | 29 | 43.8694 | 43.8694 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18.9814 | 677.5106 | 0 | 0.05921 | 5.2771 | 0 | 0 | 0 | 43.8694 | off_peak | 677.5106 |  |  | 6.08 | 0 | 93.92 | 231.5039 | 0
4857 | 733.11 | 443.882 | 29.2 | 70.8216 | 70.8216 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 30.5453 | 674.6508 | 0 | 0.05921 | 5.0233 | 0 | 0 | 0 | 70.8216 | off_peak | 662.2884 | 0 | 100 | 9.66 | 0 | 90.34 | 355.7548 | 0
4858 | 742.52 | 618.61 | 29.4 | 98.6274 | 98.6274 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30.5453 | 643.8926 | 0 | 0.05921 | 4.884 | 0 | 0 | 0 | 98.6274 | off_peak | 643.8926 |  |  | 13.28 | 0 | 86.72 | 481.6915 | 0
4859 | 742.97 | 525.74 | 29.6 | 83.7595 | 83.7595 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30.5453 | 659.2105 | 0 | 0.05921 | 4.8274 | 0 | 0 | 0 | 83.7595 | off_peak | 659.2105 |  |  | 11.27 | 0 | 88.73 | 404.3415 | 0
4860 | 747.81 | 670.769 | 29.8 | 106.7869 | 106.7869 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30.5453 | 641.0231 | 0 | 0.05921 | 4.844 | 0 | 0 | 0 | 106.7869 | off_peak | 641.0231 |  |  | 14.28 | 0 | 85.72 | 517.2756 | 0
4861 | 750.06 | 522.075 | 30.1 | 83.0233 | 83.0233 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30.5453 | 667.0367 | 0 | 0.05921 | 4.9815 | 0 | 0 | 0 | 83.0233 | off_peak | 667.0367 |  |  | 11.07 | 0 | 88.93 | 413.5816 | 0
4862 | 731.91 | 730.318 | 30.2 | 116.0967 | 116.0967 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30.5453 | 615.8133 | 0 | 0.05921 | 5.437 | 0 | 0 | 0 | 116.0967 | off_peak | 615.8133 |  |  | 15.86 | 0 | 84.14 | 631.2198 | 0
4863 | 690.15 | 645.149 | 30.3 | 102.52 | 102.52 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30.5453 | 587.63 | 0 | 0.05921 | 5.9793 | 0 | 0 | 0 | 102.52 | off_peak | 587.63 |  |  | 14.85 | 0 | 85.15 | 612.9933 | 0
4864 | 750.58 | 487.81 | 30.3 | 77.5174 | 77.5174 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30.5453 | 673.0626 | 0 | 0.05921 | 6.5717 | 0 | 0 | 0 | 77.5174 | off_peak | 673.0626 |  |  | 10.33 | 0 | 89.67 | 509.4215 | 0
4865 | 782.51 | 239.527 | 30 | 38.1049 | 38.1049 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30.5453 | 744.4051 | 0 | 0.05921 | 7.0964 | 0 | 0 | 0 | 38.1049 | off_peak | 744.4051 |  |  | 4.87 | 0 | 95.13 | 270.4088 | 0
4866 | 681.41 | 84.2858 | 29.7 | 13.4233 | 13.4233 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30.5453 | 667.9867 | 0 | 0.05921 | 7.7297 | 0 | 0 | 0 | 13.4233 | off_peak | 667.9867 |  |  | 1.97 | 0 | 98.03 | 103.7583 | 0
4867 | 668.68 | 54.5574 | 29.5 | 8.6951 | 8.6951 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30.5453 | 659.9849 | 0 | 0.05921 | 8.0831 | 0 | 0 | 0 | 8.6951 | off_peak | 659.9849 |  |  | 1.3 | 0 | 98.7 | 70.2833 | 0
4868 | 662.52 | 0 | 29 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30.5453 | 662.52 | 0 | 0.05921 | 8.4095 | 0 | 0 | 0 | 0 | off_peak | 662.52 |  |  | 0 | 0 | 100 | 0 | 0
4869 | 647.21 | 0 | 28.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30.5453 | 647.21 | 0 | 0.05921 | 8.633 | 0 | 0 | 0 | 0 | off_peak | 647.21 |  |  | 0 | 0 | 100 | 0 | 0
4870 | 646.35 | 0 | 28.5 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 42.1093 | 658.7124 | 0 | 0.05921 | 8.2525 | 0 | 0 | 0 | 0 | off_peak | 646.35 | 0 | 100 | 0 | 0 | 100 | 0 | 0
4871 | 643.86 | 0 | 28.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 42.1093 | 643.86 | 0 | 0.05921 | 8.0958 | 0 | 0 | 0 | 0 | off_peak | 643.86 |  |  | 0 | 0 | 100 | 0 | 0
4872 | 648.24 | 0 | 28.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 42.1093 | 648.24 | 0 | 0.05921 | 8.0762 | 0 | 0 | 0 | 0 | off_peak | 648.24 |  |  | 0 | 0 | 100 | 0 | 0
4873 | 652.36 | 0 | 28 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 42.1093 | 652.36 | 0 | 0.05921 | 7.8314 | 0 | 0 | 0 | 0 | off_peak | 652.36 |  |  | 0 | 0 | 100 | 0 | 0
4874 | 652.85 | 0 | 28 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 42.1093 | 652.85 | 0 | 0.05921 | 7.6306 | 0 | 0 | 0 | 0 | off_peak | 652.85 |  |  | 0 | 0 | 100 | 0 | 0
4875 | 624.95 | 0 | 27.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 42.1093 | 624.95 | 0 | 0.05921 | 7.4192 | 0 | 0 | 0 | 0 | off_peak | 624.95 |  |  | 0 | 0 | 100 | 0 | 0
4876 | 643.62 | 0 | 28 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 42.1093 | 643.62 | 0 | 0.05921 | 6.8905 | 0 | 0 | 0 | 0 | off_peak | 643.62 |  |  | 0 | 0 | 100 | 0 | 0
4877 | 646.32 | 0 | 28 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 42.1093 | 646.32 | 0 | 0.05921 | 6.4478 | 0 | 0 | 0 | 0 | off_peak | 646.32 |  |  | 0 | 0 | 100 | 0 | 0
4878 | 752.18 | 0 | 28.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 42.1093 | 752.18 | 0 | 0.05921 | 5.8405 | 0 | 0 | 0 | 0 | off_peak | 752.18 |  |  | 0 | 0 | 100 | 0 | 0
4879 | 720.08 | 63.002 | 28.8 | 10.0667 | 10.0667 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 42.1093 | 710.0133 | 0 | 0.05921 | 5.422 | 0 | 0 | 0 | 10.0667 | off_peak | 710.0133 |  |  | 1.4 | 0 | 98.6 | 54.582 | 0
4880 | 726.32 | 162.585 | 29.3 | 25.931 | 25.931 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 42.1093 | 700.389 | 0 | 0.05921 | 5.033 | 0 | 0 | 0 | 25.931 | off_peak | 700.389 |  |  | 3.57 | 0 | 96.43 | 130.5103 | 0
4881 | 764.03 | 305.469 | 29.6 | 48.6665 | 48.6665 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 42.1093 | 715.3635 | 0 | 0.05921 | 4.7632 | 0 | 0 | 0 | 48.6665 | off_peak | 715.3635 |  |  | 6.37 | 0 | 93.63 | 231.8077 | 0
4882 | 777.87 | 462.981 | 29.9 | 73.6799 | 73.6799 | 0 | 0 | 8.7006 | 8.7006 | 0 | 0 | 0 | 50.2479 | 712.8907 | 0 | 0.05921 | 4.6182 | 0 | 0 | 0 | 73.6799 | off_peak | 704.1901 | 0 | 100 | 9.47 | 0 | 90.53 | 340.268 | 0
4883 | 750.02 | 796.129 | 30.1 | 126.605 | 126.605 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50.2479 | 623.415 | 0 | 0.05921 | 4.5355 | 0 | 0 | 0 | 126.605 | off_peak | 623.415 |  |  | 16.88 | 0 | 83.12 | 574.2173 | 0
4884 | 747.89 | 866.144 | 30.2 | 137.6886 | 137.6886 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50.2479 | 610.2014 | 0 | 0.05921 | 4.5124 | 0 | 0 | 0 | 137.6886 | off_peak | 610.2014 |  |  | 18.41 | 0 | 81.59 | 621.3118 | 0
4885 | 747.76 | 571.327 | 30.3 | 90.789 | 90.789 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50.2479 | 656.971 | 0 | 0.05921 | 4.5634 | 0 | 0 | 0 | 90.789 | off_peak | 656.971 |  |  | 12.14 | 0 | 87.86 | 414.3073 | 0
4886 | 758.61 | 831.148 | 30.3 | 132.0769 | 132.0769 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50.2479 | 626.5331 | 0 | 0.05921 | 5.0747 | 0 | 0 | 0 | 132.0769 | off_peak | 626.5331 |  |  | 17.41 | 0 | 82.59 | 670.2463 | 0
4887 | 752.07 | 521.417 | 30.1 | 82.9187 | 82.9187 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50.2479 | 669.1513 | 0 | 0.05921 | 5.6785 | 0 | 0 | 0 | 82.9187 | off_peak | 669.1513 |  |  | 11.03 | 0 | 88.97 | 470.8509 | 0
4888 | 733.89 | 492.676 | 29.9 | 78.4056 | 78.4056 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50.2479 | 655.4844 | 0 | 0.05921 | 6.3123 | 0 | 0 | 0 | 78.4056 | off_peak | 655.4844 |  |  | 10.68 | 0 | 89.32 | 494.9223 | 0
4889 | 744.75 | 423.586 | 29.7 | 67.4599 | 67.4599 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50.2479 | 677.2901 | 0 | 0.05921 | 6.8169 | 0 | 0 | 0 | 67.4599 | off_peak | 677.2901 |  |  | 9.06 | 0 | 90.94 | 459.8692 | 0
4890 | 686.11 | 172.702 | 29.4 | 27.5346 | 27.5346 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 61.8119 | 670.9378 | 0 | 0.05921 | 7.4207 | 0 | 0 | 0 | 27.5346 | off_peak | 658.5754 | 0 | 100 | 4.01 | 0 | 95.99 | 204.3261 | 0
4891 | 628.55 | 46.9535 | 29.2 | 7.4915 | 7.4915 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 61.8119 | 621.0585 | 0 | 0.05921 | 7.7704 | 0 | 0 | 0 | 7.4915 | off_peak | 621.0585 |  |  | 1.19 | 0 | 98.81 | 58.2114 | 0
4892 | 655.63 | 0 | 28.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 61.8119 | 655.63 | 0 | 0.05921 | 8.002 | 0 | 0 | 0 | 0 | off_peak | 655.63 |  |  | 0 | 0 | 100 | 0 | 0
4893 | 631.43 | 0 | 28.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 61.8119 | 631.43 | 0 | 0.05921 | 8.0656 | 0 | 0 | 0 | 0 | off_peak | 631.43 |  |  | 0 | 0 | 100 | 0 | 0
4894 | 639.45 | 0 | 28.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 61.8119 | 639.45 | 0 | 0.05921 | 8.3186 | 0 | 0 | 0 | 0 | off_peak | 639.45 |  |  | 0 | 0 | 100 | 0 | 0
4895 | 632.43 | 0 | 28.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 61.8119 | 632.43 | 0 | 0.05921 | 8.4738 | 0 | 0 | 0 | 0 | off_peak | 632.43 |  |  | 0 | 0 | 100 | 0 | 0
4896 | 637.11 | 0 | 28 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 61.8119 | 637.11 | 0 | 0.05921 | 8.3537 | 0 | 0 | 0 | 0 | off_peak | 637.11 |  |  | 0 | 0 | 100 | 0 | 0
4897 | 607.1 | 0 | 27.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 61.8119 | 607.1 | 0 | 0.05921 | 8.1053 | 0 | 0 | 0 | 0 | off_peak | 607.1 |  |  | 0 | 0 | 100 | 0 | 0
4898 | 643.59 | 0 | 27.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 61.8119 | 643.59 | 0 | 0.05921 | 7.9288 | 0 | 0 | 0 | 0 | off_peak | 643.59 |  |  | 0 | 0 | 100 | 0 | 0
4899 | 610.88 | 0 | 27.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 61.8119 | 610.88 | 0 | 0.05921 | 7.6852 | 0 | 0 | 0 | 0 | off_peak | 610.88 |  |  | 0 | 0 | 100 | 0 | 0
4900 | 626.93 | 0 | 27.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 61.8119 | 626.93 | 0 | 0.05921 | 7.1562 | 0 | 0 | 0 | 0 | off_peak | 626.93 |  |  | 0 | 0 | 100 | 0 | 0
4901 | 622.78 | 0 | 27.4 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 73.3758 | 635.1424 | 0 | 0.05921 | 6.5178 | 0 | 0 | 0 | 0 | off_peak | 622.78 | 0 | 100 | 0 | 0 | 100 | 0 | 0
4902 | 704.49 | 0 | 27.6 | 0 | 0 | 0 | 0 | 0.79843 | 0.79843 | 0 | 0 | 0 | 74.1227 | 705.2884 | 0 | 0.05921 | 5.9277 | 0 | 0 | 0 | 0 | off_peak | 704.49 | 0 | 100 | 0 | 0 | 100 | 0 | 0
4903 | 782.56 | 89.5361 | 27.8 | 14.3586 | 14.3586 | 0 | 0 | 0.051567 | 0.051567 | 0 | 0 | 0 | 74.1709 | 768.2529 | 0 | 0.05921 | 5.4818 | 0 | 0 | 0 | 14.3586 | off_peak | 768.2014 | 0 | 100 | 1.83 | 0 | 98.17 | 78.7107 | 0
4904 | 844.77 | 53.2 | 28 | 8.5253 | 8.5253 | 0 | 0 | 0.0033305 | 0.0033305 | 0 | 0 | 0 | 74.174 | 836.248 | 0 | 0.05921 | 5.1176 | 0 | 0 | 0 | 8.5253 | off_peak | 836.2447 | 0 | 100 | 1.01 | 0 | 98.99 | 43.6296 | 0
4905 | 856.66 | 424.432 | 28.1 | 67.9906 | 67.9906 | 0 | 0 | 0.0002151 | 0.0002151 | 0 | 0 | 0 | 74.1742 | 788.6696 | 0 | 0.05921 | 4.8964 | 0 | 0 | 0 | 67.9906 | off_peak | 788.6694 | 0 | 100 | 7.94 | 0 | 92.06 | 332.9103 | 0
4906 | 893.65 | 494.324 | 28.2 | 79.158 | 79.158 | 0 | 0 | 1.3893e-05 | 1.3893e-05 | 0 | 0 | 0 | 74.1743 | 814.4921 | 0 | 0.05921 | 4.8027 | 0 | 0 | 0 | 79.158 | off_peak | 814.492 | 0 | 100 | 8.86 | 0 | 91.14 | 380.1742 | 0
4907 | 819.73 | 817.519 | 28.3 | 130.8647 | 130.8647 | 0 | 8.9726e-07 | 8.9726e-07 | 0 | 0 | 0 | 0 | 74.1743 | 688.8653 | 0 | 0.05921 | 4.9097 | 0 | 0 | 8.3931e-07 | 130.8647 | off_peak | 688.8653 | 100 | 0 | 15.96 | 0 | 84.04 | 642.501 | 0
4908 | 913.16 | 907.344 | 28.3 | 145.2435 | 145.2435 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1743 | 767.9165 | 0 | 0.05921 | 5.0954 | 0 | 0 | 8.9352e-07 | 145.2435 | off_peak | 767.9165 |  |  | 15.91 | 0 | 84.09 | 740.0749 | 0
4909 | 871.93 | 757.608 | 28.2 | 121.3186 | 121.3186 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1743 | 750.6114 | 0 | 0.088511 | 5.2118 | 0 | 0 | 8.9352e-07 | 121.3186 | on_peak | 750.6114 |  |  | 13.91 | 0 | 86.09 | 632.2841 | 0
4910 | 890.71 | 820.911 | 28.2 | 131.4556 | 131.4556 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1743 | 759.2544 | 0 | 0.088511 | 5.6605 | 0 | 0 | 8.9352e-07 | 131.4556 | on_peak | 759.2544 |  |  | 14.76 | 0 | 85.24 | 744.0996 | 0
4911 | 957.45 | 569.645 | 28.1 | 91.2526 | 91.2526 | 0 | 0 | 0 | 0 | 62.4453 | 62.4453 | 0 | 7.4174 | 803.7521 | 0 | 0.088511 | 6.0799 | 0 | 0 | 8.9352e-07 | 91.2526 | on_peak | 803.7521 |  |  | 9.53 | 6.52 | 83.95 | 554.8029 | 0
4912 | 876.52 | 386.639 | 28 | 61.9591 | 61.9591 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 814.5609 | 0 | 0.088511 | 6.5505 | 0 | 0 | 8.9352e-07 | 61.9591 | on_peak | 814.5609 |  |  | 7.07 | 0 | 92.93 | 405.8657 | 0
4913 | 849.48 | 374.738 | 28 | 60.0519 | 60.0519 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 789.4281 | 0 | 0.088511 | 7.0478 | 0 | 0 | 8.9352e-07 | 60.0519 | on_peak | 789.4281 |  |  | 7.07 | 0 | 92.93 | 423.2353 | 0
4914 | 861.18 | 133.144 | 28 | 21.3364 | 21.3364 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 839.8436 | 0 | 0.088511 | 7.6329 | 0 | 0 | 8.9352e-07 | 21.3364 | on_peak | 839.8436 |  |  | 2.48 | 0 | 97.52 | 162.8591 | 0
4915 | 837.74 | 59.8138 | 27.9 | 9.5887 | 9.5887 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 828.1513 | 0 | 0.088511 | 8.0957 | 0 | 0 | 8.9352e-07 | 9.5887 | on_peak | 828.1513 |  |  | 1.14 | 0 | 98.86 | 77.6268 | 0
4916 | 831.79 | 0 | 28 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 831.79 | 0 | 0.088511 | 8.3746 | 0 | 0 | 8.9352e-07 | 0 | on_peak | 831.79 |  |  | 0 | 0 | 100 | 0 | 0
4917 | 860.77 | 0 | 28.1 | 0 | 0 | 0 | 0 | 0 | 0 | 8.3581e-07 | 8.3581e-07 | 0 | 7.4174 | 860.77 | 0 | 0.088511 | 8.6272 | 8.3581e-07 | 0 | 0 | 8.3581e-07 | on_peak | 860.77 |  |  | 0 | 0 | 100 | 7.2107e-06 | 0
4918 | 798.18 | 0 | 28.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 798.18 | 0 | 0.05921 | 8.8056 | 0 | 0 | 0 | 0 | off_peak | 798.18 |  |  | 0 | 0 | 100 | 0 | 0
4919 | 806.92 | 0 | 28.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 806.92 | 0 | 0.05921 | 8.8977 | 0 | 0 | 0 | 0 | off_peak | 806.92 |  |  | 0 | 0 | 100 | 0 | 0
4920 | 826.02 | 0 | 27.9 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 18.9814 | 838.3824 | 0 | 0.05921 | 8.8849 | 0 | 0 | 0 | 0 | off_peak | 826.02 | 0 | 100 | 0 | 0 | 100 | 0 | 0
4921 | 739.97 | 0 | 27.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18.9814 | 739.97 | 0 | 0.05921 | 8.8702 | 0 | 0 | 0 | 0 | off_peak | 739.97 |  |  | 0 | 0 | 100 | 0 | 0
4922 | 679.95 | 0 | 27.4 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 30.5453 | 692.3124 | 0 | 0.05921 | 8.6126 | 0 | 0 | 0 | 0 | off_peak | 679.95 | 0 | 100 | 0 | 0 | 100 | 0 | 0
4923 | 639.34 | 0 | 27.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30.5453 | 639.34 | 0 | 0.05921 | 8.0457 | 0 | 0 | 0 | 0 | off_peak | 639.34 |  |  | 0 | 0 | 100 | 0 | 0
4924 | 643.82 | 0 | 27.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30.5453 | 643.82 | 0 | 0.05921 | 7.2695 | 0 | 0 | 0 | 0 | off_peak | 643.82 |  |  | 0 | 0 | 100 | 0 | 0
4925 | 634.61 | 0 | 27.3 | 0 | 0 | 0 | 0 | 8.7006 | 8.7006 | 0 | 0 | 0 | 38.684 | 643.3106 | 0 | 0.05921 | 6.5052 | 0 | 0 | 0 | 0 | off_peak | 634.61 | 0 | 100 | 0 | 0 | 100 | 0 | 0
4926 | 703.4 | 0 | 27.6 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 50.2479 | 715.7624 | 0 | 0.05921 | 5.95 | 0 | 0 | 0 | 0 | off_peak | 703.4 | 0 | 100 | 0 | 0 | 100 | 0 | 0
4927 | 785.48 | 92.2973 | 28.3 | 14.7745 | 14.7745 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 61.8119 | 783.0678 | 0 | 0.05921 | 5.4465 | 0 | 0 | 0 | 14.7745 | off_peak | 770.7055 | 0 | 100 | 1.88 | 0 | 98.12 | 80.4689 | 0
4928 | 906.47 | 288.594 | 28.7 | 46.1295 | 46.1295 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 73.3758 | 872.7029 | 0 | 0.05921 | 5.1033 | 0 | 0 | 0 | 46.1295 | off_peak | 860.3405 | 0 | 100 | 5.09 | 0 | 94.91 | 235.4107 | 0
4929 | 875.46 | 493.555 | 29 | 78.8045 | 78.8045 | 0 | 0 | 0.79843 | 0.79843 | 0 | 0 | 0 | 74.1227 | 797.4539 | 0 | 0.05921 | 4.8629 | 0 | 0 | 0 | 78.8045 | off_peak | 796.6555 | 0 | 100 | 9 | 0 | 91 | 383.2221 | 0
4930 | 859.82 | 620.194 | 29.3 | 98.9161 | 98.9161 | 0 | 0 | 0.051567 | 0.051567 | 0 | 0 | 0 | 74.1709 | 760.9554 | 0 | 0.05921 | 4.7718 | 0 | 0 | 0 | 98.9161 | off_peak | 760.9039 | 0 | 100 | 11.5 | 0 | 88.5 | 472.0096 | 0
4931 | 867.88 | 705.67 | 29.4 | 112.5077 | 112.5077 | 0 | 0 | 0.0033305 | 0.0033305 | 0 | 0 | 0 | 74.174 | 755.3756 | 0 | 0.05921 | 4.8586 | 0 | 0 | 0 | 112.5077 | off_peak | 755.3723 | 0 | 100 | 12.96 | 0 | 87.04 | 546.6278 | 0
4932 | 956.9 | 656.041 | 29.5 | 104.5569 | 104.5569 | 0 | 0 | 0.0002151 | 0.0002151 | 0 | 0 | 0 | 74.1742 | 852.3433 | 0 | 0.05921 | 5.0798 | 0 | 0 | 0 | 104.5569 | off_peak | 852.3431 | 0 | 100 | 10.93 | 0 | 89.07 | 531.1335 | 0
4933 | 878.57 | 771.347 | 29.5 | 122.9339 | 122.9339 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1742 | 755.6361 | 0 | 0.088511 | 5.1986 | 0 | 0 | 0 | 122.9339 | on_peak | 755.6361 |  |  | 13.99 | 0 | 86.01 | 639.0785 | 0
4934 | 943.81 | 817.174 | 29.4 | 130.2853 | 130.2853 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1742 | 813.5247 | 0 | 0.088511 | 5.5102 | 0 | 0 | 0 | 130.2853 | on_peak | 813.5247 |  |  | 13.8 | 0 | 86.2 | 717.9019 | 0
4935 | 986.76 | 467.909 | 29.3 | 74.6279 | 74.6279 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1742 | 912.1321 | 0 | 0.088511 | 5.8994 | 0 | 0 | 0 | 74.6279 | on_peak | 912.1321 |  |  | 7.56 | 0 | 92.44 | 440.2586 | 0
4936 | 842.57 | 55.1 | 29.2 | 8.7912 | 8.7912 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1742 | 833.7788 | 0 | 0.088511 | 6.4506 | 0 | 0 | 0 | 8.7912 | on_peak | 833.7788 |  |  | 1.04 | 0 | 98.96 | 56.7088 | 0
4937 | 883.02 | 328.542 | 29 | 52.4574 | 52.4574 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1742 | 830.5626 | 0 | 0.088511 | 7.0726 | 0 | 0 | 0 | 52.4574 | on_peak | 830.5626 |  |  | 5.94 | 0 | 94.06 | 371.0117 | 0
4938 | 871.9 | 263.785 | 28.8 | 42.1486 | 42.1486 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1742 | 829.7514 | 0 | 0.088511 | 7.7503 | 0 | 0 | 0 | 42.1486 | on_peak | 829.7514 |  |  | 4.83 | 0 | 95.17 | 326.6636 | 0
4939 | 854.58 | 56.2851 | 28.6 | 9 | 9 | 0 | 0 | 0 | 0 | 62.4453 | 62.4453 | 0 | 7.4174 | 783.1347 | 0 | 0.088511 | 8.082 | 0 | 0 | 0 | 9 | on_peak | 783.1347 |  |  | 1.05 | 7.31 | 91.64 | 72.7377 | 0
4940 | 860.48 | 0 | 28.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 860.48 | 0 | 0.088511 | 8.4149 | 0 | 0 | 0 | 0 | on_peak | 860.48 |  |  | 0 | 0 | 100 | 0 | 0
4941 | 832.98 | 0 | 28.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 832.98 | 0 | 0.088511 | 8.653 | 0 | 0 | 0 | 0 | on_peak | 832.98 |  |  | 0 | 0 | 100 | 0 | 0
4942 | 801.33 | 0 | 28.2 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 18.9814 | 813.6924 | 0 | 0.05921 | 8.7787 | 0 | 0 | 0 | 0 | off_peak | 801.33 | 0 | 100 | 0 | 0 | 100 | 0 | 0
4943 | 869.16 | 0 | 28.1 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 30.5453 | 881.5224 | 0 | 0.05921 | 8.8007 | 0 | 0 | 0 | 0 | off_peak | 869.16 | 0 | 100 | 0 | 0 | 100 | 0 | 0
4944 | 800.93 | 0 | 28.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30.5453 | 800.93 | 0 | 0.05921 | 8.8086 | 0 | 0 | 0 | 0 | off_peak | 800.93 |  |  | 0 | 0 | 100 | 0 | 0
4945 | 757.32 | 0 | 28 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30.5453 | 757.32 | 0 | 0.05921 | 8.7087 | 0 | 0 | 0 | 0 | off_peak | 757.32 |  |  | 0 | 0 | 100 | 0 | 0
4946 | 698.42 | 0 | 27.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30.5453 | 698.42 | 0 | 0.05921 | 8.5108 | 0 | 0 | 0 | 0 | off_peak | 698.42 |  |  | 0 | 0 | 100 | 0 | 0
4947 | 646.35 | 0 | 27.8 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 42.1093 | 658.7124 | 0 | 0.05921 | 8.1447 | 0 | 0 | 0 | 0 | off_peak | 646.35 | 0 | 100 | 0 | 0 | 100 | 0 | 0
4948 | 638.59 | 0 | 27.7 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 53.6732 | 650.9524 | 0 | 0.05921 | 7.4586 | 0 | 0 | 0 | 0 | off_peak | 638.59 | 0 | 100 | 0 | 0 | 100 | 0 | 0
4949 | 672.42 | 0 | 27.7 | 0 | 0 | 0 | 0 | 8.7006 | 8.7006 | 0 | 0 | 0 | 61.8119 | 681.1206 | 0 | 0.05921 | 6.6189 | 0 | 0 | 0 | 0 | off_peak | 672.42 | 0 | 100 | 0 | 0 | 100 | 0 | 0
4950 | 719.06 | 0 | 27.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 61.8119 | 719.06 | 0 | 0.05921 | 6.087 | 0 | 0 | 0 | 0 | off_peak | 719.06 |  |  | 0 | 0 | 100 | 0 | 0
4951 | 779.72 | 88.6788 | 28.2 | 14.2005 | 14.2005 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 61.8119 | 765.5195 | 0 | 0.05921 | 5.4985 | 0 | 0 | 0 | 14.2005 | off_peak | 765.5195 |  |  | 1.82 | 0 | 98.18 | 78.0806 | 0
4952 | 863.31 | 282.624 | 28.6 | 45.1917 | 45.1917 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 73.3758 | 830.4807 | 0 | 0.05921 | 5.1499 | 0 | 0 | 0 | 45.1917 | off_peak | 818.1183 | 0 | 100 | 5.23 | 0 | 94.77 | 232.7325 | 0
4953 | 863.28 | 487.959 | 28.9 | 77.9395 | 77.9395 | 0 | 0 | 0.79843 | 0.79843 | 0 | 0 | 0 | 74.1227 | 786.1389 | 0 | 0.05921 | 4.9215 | 0 | 0 | 0 | 77.9395 | off_peak | 785.3405 | 0 | 100 | 9.03 | 0 | 90.97 | 383.583 | 0
4954 | 905.46 | 586.292 | 29.2 | 93.5432 | 93.5432 | 0 | 0 | 0.051567 | 0.051567 | 0 | 0 | 0 | 74.1709 | 811.9684 | 0 | 0.05921 | 4.8199 | 0 | 0 | 0 | 93.5432 | off_peak | 811.9168 | 0 | 100 | 10.33 | 0 | 89.67 | 450.8723 | 0
4955 | 925.61 | 690.904 | 29.5 | 110.1132 | 110.1132 | 0 | 0 | 0.0033305 | 0.0033305 | 0 | 0 | 0 | 74.174 | 815.5001 | 0 | 0.05921 | 4.3894 | 0 | 0 | 0 | 110.1132 | off_peak | 815.4968 | 0 | 100 | 11.9 | 0 | 88.1 | 483.3328 | 0
4956 | 964.05 | 257.355 | 29.6 | 41.0011 | 41.0011 | 0 | 0 | 0.0002151 | 0.0002151 | 0 | 0 | 0 | 74.1742 | 923.0491 | 0 | 0.05921 | 5.1601 | 0 | 0 | 0 | 41.0011 | off_peak | 923.0489 | 0 | 100 | 4.25 | 0 | 95.75 | 211.5685 | 0
4957 | 927.53 | 546.458 | 29.7 | 87.0283 | 87.0283 | 0 | 0 | 0 | 0 | 62.4453 | 62.4453 | 0 | 7.4174 | 778.0564 | 0 | 0.088511 | 5.4006 | 0 | 0 | 0 | 87.0283 | on_peak | 778.0564 |  |  | 9.38 | 6.73 | 83.88 | 470.0011 | 0
4958 | 928.9 | 647.795 | 29.7 | 103.1672 | 103.1672 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 825.7328 | 0 | 0.088511 | 5.4858 | 0 | 0 | 0 | 103.1672 | on_peak | 825.7328 |  |  | 11.11 | 0 | 88.89 | 565.956 | 0
4959 | 931.82 | 750.511 | 29.7 | 119.5256 | 119.5256 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 812.2944 | 0 | 0.088511 | 5.6158 | 0 | 0 | 0 | 119.5256 | on_peak | 812.2944 |  |  | 12.83 | 0 | 87.17 | 671.2274 | 0
4960 | 851.72 | 658.116 | 29.6 | 104.8493 | 104.8493 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 746.8707 | 0 | 0.088511 | 5.9699 | 0 | 0 | 0 | 104.8493 | on_peak | 746.8707 |  |  | 12.31 | 0 | 87.69 | 625.9414 | 0
4961 | 853.72 | 473.216 | 29.3 | 75.4743 | 75.4743 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 778.2457 | 0 | 0.088511 | 6.3057 | 0 | 0 | 0 | 75.4743 | on_peak | 778.2457 |  |  | 8.84 | 0 | 91.16 | 475.9172 | 0
4962 | 919 | 270.471 | 29 | 43.1853 | 43.1853 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 875.8147 | 0 | 0.088511 | 6.7117 | 0 | 0 | 0 | 43.1853 | on_peak | 875.8147 |  |  | 4.7 | 0 | 95.3 | 289.8467 | 0
4963 | 823.32 | 78.3703 | 28.8 | 12.5223 | 12.5223 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 810.7977 | 0 | 0.088511 | 7.2716 | 0 | 0 | 0 | 12.5223 | on_peak | 810.7977 |  |  | 1.52 | 0 | 98.48 | 91.0577 | 0
4964 | 874.04 | 0 | 28.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 874.04 | 0 | 0.088511 | 7.4453 | 0 | 0 | 0 | 0 | on_peak | 874.04 |  |  | 0 | 0 | 100 | 0 | 0
4965 | 832.99 | 0 | 28.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 832.99 | 0 | 0.088511 | 7.7357 | 0 | 0 | 0 | 0 | on_peak | 832.99 |  |  | 0 | 0 | 100 | 0 | 0
4966 | 843.07 | 0 | 28.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 843.07 | 0 | 0.05921 | 7.8724 | 0 | 0 | 0 | 0 | off_peak | 843.07 |  |  | 0 | 0 | 100 | 0 | 0
4967 | 844.29 | 0 | 28.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 844.29 | 0 | 0.05921 | 8.0315 | 0 | 0 | 0 | 0 | off_peak | 844.29 |  |  | 0 | 0 | 100 | 0 | 0
4968 | 805.26 | 0 | 28 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 18.9814 | 817.6224 | 0 | 0.05921 | 8.105 | 0 | 0 | 0 | 0 | off_peak | 805.26 | 0 | 100 | 0 | 0 | 100 | 0 | 0
4969 | 728.39 | 0 | 27.9 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 30.5453 | 740.7524 | 0 | 0.05921 | 7.7985 | 0 | 0 | 0 | 0 | off_peak | 728.39 | 0 | 100 | 0 | 0 | 100 | 0 | 0
4970 | 752.4 | 0 | 27.8 | 0 | 0 | 0 | 0 | 8.7006 | 8.7006 | 0 | 0 | 0 | 38.684 | 761.1006 | 0 | 0.05921 | 7.743 | 0 | 0 | 0 | 0 | off_peak | 752.4 | 0 | 100 | 0 | 0 | 100 | 0 | 0
4971 | 703.17 | 0 | 27.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 38.684 | 703.17 | 0 | 0.05921 | 7.3849 | 0 | 0 | 0 | 0 | off_peak | 703.17 |  |  | 0 | 0 | 100 | 0 | 0
4972 | 691.71 | 0 | 27.7 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 50.2479 | 704.0724 | 0 | 0.05921 | 6.8326 | 0 | 0 | 0 | 0 | off_peak | 691.71 | 0 | 100 | 0 | 0 | 100 | 0 | 0
4973 | 702.35 | 0 | 27.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50.2479 | 702.35 | 0 | 0.05921 | 6.0659 | 0 | 0 | 0 | 0 | off_peak | 702.35 |  |  | 0 | 0 | 100 | 0 | 0
4974 | 751.2 | 0 | 27.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50.2479 | 751.2 | 0 | 0.05921 | 5.4996 | 0 | 0 | 0 | 0 | off_peak | 751.2 |  |  | 0 | 0 | 100 | 0 | 0
4975 | 797.43 | 92.0092 | 28.4 | 14.723 | 14.723 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 61.8119 | 795.0693 | 0 | 0.05921 | 5.0368 | 0 | 0 | 0 | 14.723 | off_peak | 782.707 | 0 | 100 | 1.85 | 0 | 98.15 | 74.1564 | 0
4976 | 857.44 | 290.403 | 28.8 | 46.4017 | 46.4017 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 73.3758 | 823.4007 | 0 | 0.05921 | 4.7107 | 0 | 0 | 0 | 46.4017 | off_peak | 811.0383 | 0 | 100 | 5.41 | 0 | 94.59 | 218.5854 | 0
4977 | 871.96 | 498.655 | 29 | 79.6188 | 78.8204 | 0 | 0.79843 | 0.79843 | 0 | 0 | 0 | 0 | 74.1227 | 793.1396 | 0 | 0.05921 | 4.464 | 0 | 0 | 0.74686 | 78.8204 | off_peak | 793.1396 | 100 | 0 | 9.04 | 0 | 90.96 | 351.8506 | 0
4978 | 918.41 | 541.25 | 29.3 | 86.3252 | 86.2736 | 0 | 0.051567 | 0.051567 | 0 | 0 | 0 | 0 | 74.1709 | 832.1364 | 0 | 0.05921 | 4.3786 | 0 | 0 | 0.7951 | 86.2736 | off_peak | 832.1364 | 100 | 0 | 9.39 | 0 | 90.61 | 377.7566 | 0
4979 | 885.21 | 824.761 | 29.6 | 131.3987 | 131.3953 | 0 | 0.0033305 | 0.0033305 | 0 | 0 | 0 | 0 | 74.174 | 753.8147 | 0 | 0.05921 | 4.5033 | 0 | 0 | 0.79822 | 131.3953 | off_peak | 753.8147 | 100 | 0 | 14.84 | 0 | 85.16 | 591.7122 | 0
4980 | 958.3 | 914.701 | 29.8 | 145.621 | 145.6208 | 0 | 0.0002151 | 0.0002151 | 0 | 0 | 0 | 0 | 74.1742 | 812.6792 | 0 | 0.05921 | 4.7552 | 0 | 0 | 0.79842 | 145.6208 | off_peak | 812.6792 | 100 | 0 | 15.2 | 0 | 84.8 | 692.4576 | 0
4981 | 855.84 | 418.889 | 29.9 | 66.663 | 66.663 | 0 | 0 | 0 | 0 | 62.4453 | 62.4453 | 0 | 7.4174 | 726.7318 | 0 | 0.088511 | 4.8639 | 0 | 0 | 0.79842 | 66.663 | on_peak | 726.7318 |  |  | 7.79 | 7.3 | 84.91 | 324.2418 | 0
4982 | 887.7 | 910.132 | 29.9 | 144.8405 | 144.8405 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 742.8595 | 0 | 0.088511 | 5.0166 | 0 | 0 | 0.79842 | 144.8405 | on_peak | 742.8595 |  |  | 16.32 | 0 | 83.68 | 726.6092 | 0
4983 | 898.94 | 788.719 | 29.8 | 125.5646 | 125.5646 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 773.3754 | 0 | 0.088511 | 5.3996 | 0 | 0 | 0.79842 | 125.5646 | on_peak | 773.3754 |  |  | 13.97 | 0 | 86.03 | 678.0012 | 0
4984 | 860.49 | 586.748 | 29.7 | 93.4449 | 93.4449 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 767.0451 | 0 | 0.088511 | 5.7991 | 0 | 0 | 0.79842 | 93.4449 | on_peak | 767.0451 |  |  | 10.86 | 0 | 89.14 | 541.8972 | 0
4985 | 832.36 | 458.548 | 29.4 | 73.1081 | 73.1081 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 759.2519 | 0 | 0.088511 | 6.278 | 0 | 0 | 0.79842 | 73.1081 | on_peak | 759.2519 |  |  | 8.78 | 0 | 91.22 | 458.9703 | 0
4986 | 878.21 | 267.802 | 29 | 42.7592 | 42.7592 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 835.4508 | 0 | 0.088511 | 6.7823 | 0 | 0 | 0.79842 | 42.7592 | on_peak | 835.4508 |  |  | 4.87 | 0 | 95.13 | 290.0057 | 0
4987 | 838.97 | 75.784 | 28.7 | 12.1135 | 12.1135 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 826.8565 | 0 | 0.088511 | 7.1186 | 0 | 0 | 0.79842 | 12.1135 | on_peak | 826.8565 |  |  | 1.44 | 0 | 98.56 | 86.2314 | 0
4988 | 841.23 | 0 | 28.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 841.23 | 0 | 0.088511 | 7.3015 | 0 | 0 | 0.79842 | 0 | on_peak | 841.23 |  |  | 0 | 0 | 100 | 0 | 0
4989 | 840.31 | 0 | 28 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 840.31 | 0 | 0.088511 | 7.513 | 0 | 0 | 0.79842 | 0 | on_peak | 840.31 |  |  | 0 | 0 | 100 | 0 | 0
4990 | 796 | 0 | 27.9 | 0 | 0 | 0 | 0 | 8.7006 | 8.7006 | 0 | 0 | 0 | 15.5561 | 804.7006 | 0 | 0.05921 | 7.7721 | 0 | 0 | 0.79842 | 0 | off_peak | 796 | 0 | 100 | 0 | 0 | 100 | 0 | 0
4991 | 843.25 | 0 | 27.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15.5561 | 843.25 | 0 | 0.05921 | 7.7034 | 0 | 0 | 0.79842 | 0 | off_peak | 843.25 |  |  | 0 | 0 | 100 | 0 | 0
4992 | 843.69 | 0 | 27.7 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 27.12 | 856.0524 | 0 | 0.05921 | 7.4874 | 0 | 0 | 0.79842 | 0 | off_peak | 843.69 | 0 | 100 | 0 | 0 | 100 | 0 | 0
4993 | 728.99 | 0 | 27.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27.12 | 728.99 | 0 | 0.05921 | 7.1745 | 0 | 0 | 0.79842 | 0 | off_peak | 728.99 |  |  | 0 | 0 | 100 | 0 | 0
4994 | 700.22 | 0 | 27.6 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 38.684 | 712.5824 | 0 | 0.05921 | 7.0924 | 0 | 0 | 0.79842 | 0 | off_peak | 700.22 | 0 | 100 | 0 | 0 | 100 | 0 | 0
4995 | 627.84 | 0 | 27.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 38.684 | 627.84 | 0 | 0.05921 | 6.8058 | 0 | 0 | 0.79842 | 0 | off_peak | 627.84 |  |  | 0 | 0 | 100 | 0 | 0
4996 | 644.3 | 0 | 27.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 38.684 | 644.3 | 0 | 0.05921 | 6.3455 | 0 | 0 | 0.79842 | 0 | off_peak | 644.3 |  |  | 0 | 0 | 100 | 0 | 0
4997 | 685.96 | 0 | 27.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 38.684 | 685.96 | 0 | 0.05921 | 5.8201 | 0 | 0 | 0.79842 | 0 | off_peak | 685.96 |  |  | 0 | 0 | 100 | 0 | 0
4998 | 710.25 | 0 | 27.7 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 50.2479 | 722.6124 | 0 | 0.05921 | 5.2911 | 0 | 0 | 0.79842 | 0 | off_peak | 710.25 | 0 | 100 | 0 | 0 | 100 | 0 | 0
4999 | 771.24 | 90.2758 | 28 | 14.4667 | 14.4667 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 61.8119 | 769.1356 | 0 | 0.05921 | 4.9044 | 0 | 0 | 0.79842 | 14.4667 | off_peak | 756.7733 | 0 | 100 | 1.88 | 0 | 98.12 | 70.9505 | 0
5000 | 859.14 | 288.85 | 28.3 | 46.2378 | 33.8754 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 0 | 73.3758 | 825.2646 | 0 | 0.05921 | 4.6473 | 0 | 0 | 12.3624 | 33.8754 | off_peak | 825.2646 | 100 | 0 | 3.94 | 0 | 96.06 | 157.4295 | 0
5001 | 864.63 | 496.453 | 28.6 | 79.3831 | 79.3831 | 0 | 0 | 0.79843 | 0.79843 | 0 | 0 | 0 | 74.1227 | 786.0454 | 0 | 0.05921 | 4.4718 | 0 | 0 | 12.3624 | 79.3831 | off_peak | 785.2469 | 0 | 100 | 9.18 | 0 | 90.82 | 354.9834 | 0
5002 | 838.14 | 617.285 | 28.9 | 98.5962 | 98.5962 | 0 | 0 | 0.051567 | 0.051567 | 0 | 0 | 0 | 74.1709 | 739.5954 | 0 | 0.05921 | 4.4485 | 0 | 0 | 12.3624 | 98.5962 | off_peak | 739.5438 | 0 | 100 | 11.76 | 0 | 88.24 | 438.6026 | 0
5003 | 829.32 | 774.076 | 29.3 | 123.4591 | 123.4558 | 0 | 0.0033305 | 0.0033305 | 0 | 0 | 0 | 0 | 74.174 | 705.8642 | 0 | 0.05921 | 4.5844 | 0 | 0 | 12.3655 | 123.4558 | off_peak | 705.8642 | 100 | 0 | 14.89 | 0 | 85.11 | 565.975 | 0
5004 | 879.06 | 911.568 | 29.6 | 145.2285 | 145.2285 | 0 | 0 | 0.0002151 | 0.0002151 | 0 | 0 | 0 | 74.1742 | 733.8317 | 0 | 0.05921 | 4.8198 | 0 | 0 | 12.3655 | 145.2285 | off_peak | 733.8315 | 0 | 100 | 16.52 | 0 | 83.48 | 699.9781 | 0
5005 | 834.92 | 585.769 | 29.8 | 93.2548 | 93.2548 | 0 | 0 | 0 | 0 | 62.4453 | 62.4453 | 0 | 7.4174 | 679.2199 | 0 | 0.088511 | 5.1215 | 11.5668 | 0 | 0 | 104.8216 | on_peak | 679.2199 |  |  | 11.17 | 7.48 | 81.35 | 536.8479 | 0
5006 | 889.96 | 430.849 | 30 | 68.5412 | 68.5412 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 821.4188 | 0 | 0.088511 | 5.3917 | 0 | 0 | 0 | 68.5412 | on_peak | 821.4188 |  |  | 7.7 | 0 | 92.3 | 369.5558 | 0
5007 | 857.28 | 802.167 | 30 | 127.6119 | 127.6119 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 729.6681 | 0 | 0.088511 | 5.7174 | 0 | 0 | 0 | 127.6119 | on_peak | 729.6681 |  |  | 14.89 | 0 | 85.11 | 729.6145 | 0
5008 | 815.03 | 654.505 | 29.8 | 104.1976 | 104.1976 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 710.8324 | 0 | 0.088511 | 6.0707 | 0 | 0 | 0 | 104.1976 | on_peak | 710.8324 |  |  | 12.78 | 0 | 87.22 | 632.5536 | 0
5009 | 803.74 | 448.247 | 29.6 | 71.4135 | 71.4135 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 732.3265 | 0 | 0.088511 | 6.5245 | 0 | 0 | 0 | 71.4135 | on_peak | 732.3265 |  |  | 8.89 | 0 | 91.11 | 465.934 | 0
5010 | 890.32 | 116.571 | 29.1 | 18.6058 | 18.6058 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 871.7142 | 0 | 0.088511 | 6.8764 | 0 | 0 | 0 | 18.6058 | on_peak | 871.7142 |  |  | 2.09 | 0 | 97.91 | 127.941 | 0
5011 | 812.14 | 73.642 | 28.8 | 11.7668 | 11.7668 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 800.3732 | 0 | 0.088511 | 7.0324 | 0 | 0 | 0 | 11.7668 | on_peak | 800.3732 |  |  | 1.45 | 0 | 98.55 | 82.7483 | 0
5012 | 887.33 | 0 | 28.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 887.33 | 0 | 0.088511 | 7.1853 | 0 | 0 | 0 | 0 | on_peak | 887.33 |  |  | 0 | 0 | 100 | 0 | 0
5013 | 837.61 | 0 | 27.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 837.61 | 0 | 0.088511 | 7.3471 | 0 | 0 | 0 | 0 | on_peak | 837.61 |  |  | 0 | 0 | 100 | 0 | 0
5014 | 777.48 | 0 | 27.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 777.48 | 0 | 0.05921 | 7.5708 | 0 | 0 | 0 | 0 | off_peak | 777.48 |  |  | 0 | 0 | 100 | 0 | 0
5015 | 857.51 | 0 | 27.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 857.51 | 0 | 0.05921 | 7.6357 | 0 | 0 | 0 | 0 | off_peak | 857.51 |  |  | 0 | 0 | 100 | 0 | 0
5016 | 803.58 | 0 | 27.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 803.58 | 0 | 0.05921 | 7.5217 | 0 | 0 | 0 | 0 | off_peak | 803.58 |  |  | 0 | 0 | 100 | 0 | 0
5017 | 714.78 | 0 | 27.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 714.78 | 0 | 0.05921 | 7.3444 | 0 | 0 | 0 | 0 | off_peak | 714.78 |  |  | 0 | 0 | 100 | 0 | 0
5018 | 662.83 | 0 | 27.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 662.83 | 0 | 0.05921 | 7.186 | 0 | 0 | 0 | 0 | off_peak | 662.83 |  |  | 0 | 0 | 100 | 0 | 0
5019 | 658.1 | 0 | 27.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 658.1 | 0 | 0.05921 | 6.9699 | 0 | 0 | 0 | 0 | off_peak | 658.1 |  |  | 0 | 0 | 100 | 0 | 0
5020 | 631.58 | 0 | 27.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 631.58 | 0 | 0.05921 | 6.5891 | 0 | 0 | 0 | 0 | off_peak | 631.58 |  |  | 0 | 0 | 100 | 0 | 0
5021 | 631.6 | 0 | 27.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 631.6 | 0 | 0.05921 | 6.0229 | 0 | 0 | 0 | 0 | off_peak | 631.6 |  |  | 0 | 0 | 100 | 0 | 0
5022 | 722.59 | 0 | 27.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 722.59 | 0 | 0.05921 | 5.5538 | 0 | 0 | 0 | 0 | off_peak | 722.59 |  |  | 0 | 0 | 100 | 0 | 0
5023 | 709.62 | 88.2644 | 27.8 | 14.1547 | 14.1547 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 695.4653 | 0 | 0.05921 | 5.1379 | 0 | 0 | 0 | 14.1547 | off_peak | 695.4653 |  |  | 1.99 | 0 | 98.01 | 72.7257 | 0
5024 | 751.08 | 171.118 | 28.2 | 27.4018 | 27.4018 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 723.6782 | 0 | 0.05921 | 4.8501 | 0 | 0 | 0 | 27.4018 | off_peak | 723.6782 |  |  | 3.65 | 0 | 96.35 | 132.9006 | 0
5025 | 776.15 | 450.705 | 28.4 | 72.1205 | 72.1205 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 704.0295 | 0 | 0.05921 | 4.6103 | 0 | 0 | 0 | 72.1205 | off_peak | 704.0295 |  |  | 9.29 | 0 | 90.71 | 332.4984 | 0
5026 | 773.23 | 673.77 | 28.7 | 107.6969 | 107.6969 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 665.5331 | 0 | 0.05921 | 4.488 | 0 | 0 | 0 | 107.6969 | off_peak | 665.5331 |  |  | 13.93 | 0 | 86.07 | 483.3434 | 0
5027 | 746.5 | 729.246 | 29.1 | 116.3941 | 116.3941 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 630.1059 | 0 | 0.05921 | 4.4674 | 0 | 0 | 0 | 116.3941 | off_peak | 630.1059 |  |  | 15.59 | 0 | 84.41 | 519.9783 | 0
5028 | 785.15 | 324.635 | 29.5 | 51.7389 | 51.7389 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 733.4111 | 0 | 0.05921 | 4.5225 | 0 | 0 | 0 | 51.7389 | off_peak | 733.4111 |  |  | 6.59 | 0 | 93.41 | 233.9899 | 0
5029 | 752.28 | 710.667 | 29.8 | 113.1386 | 113.1386 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 639.1414 | 0 | 0.05921 | 4.6488 | 0 | 0 | 0 | 113.1386 | off_peak | 639.1414 |  |  | 15.04 | 0 | 84.96 | 525.9559 | 0
5030 | 767.23 | 454.929 | 30 | 72.3719 | 72.3719 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 694.8581 | 0 | 0.05921 | 4.9608 | 0 | 0 | 0 | 72.3719 | off_peak | 694.8581 |  |  | 9.43 | 0 | 90.57 | 359.024 | 0
5031 | 754.16 | 678.33 | 30 | 107.9114 | 107.9114 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 646.2486 | 0 | 0.05921 | 5.4045 | 0 | 0 | 0 | 107.9114 | off_peak | 646.2486 |  |  | 14.31 | 0 | 85.69 | 583.2122 | 0
5032 | 721.58 | 434.114 | 29.8 | 69.1112 | 69.1112 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 652.4688 | 0 | 0.05921 | 6.0171 | 0 | 0 | 0 | 69.1112 | off_peak | 652.4688 |  |  | 9.58 | 0 | 90.42 | 415.8487 | 0
5033 | 711.03 | 473.539 | 29.5 | 75.4706 | 75.4706 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 635.5594 | 0 | 0.05921 | 6.673 | 0 | 0 | 0 | 75.4706 | off_peak | 635.5594 |  |  | 10.61 | 0 | 89.39 | 503.612 | 0
5034 | 666.82 | 266.833 | 29 | 42.6045 | 42.6045 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 624.2155 | 0 | 0.05921 | 7.3005 | 0 | 0 | 0 | 42.6045 | off_peak | 624.2155 |  |  | 6.39 | 0 | 93.61 | 311.0349 | 0
5035 | 644.85 | 74.4832 | 28.7 | 11.9056 | 11.9056 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 632.9444 | 0 | 0.05921 | 7.7852 | 0 | 0 | 0 | 11.9056 | off_peak | 632.9444 |  |  | 1.85 | 0 | 98.15 | 92.6866 | 0
5036 | 634.86 | 0 | 28.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 634.86 | 0 | 0.05921 | 8.0046 | 0 | 0 | 0 | 0 | off_peak | 634.86 |  |  | 0 | 0 | 100 | 0 | 0
5037 | 608.94 | 0 | 27.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 608.94 | 0 | 0.05921 | 8.38 | 0 | 0 | 0 | 0 | off_peak | 608.94 |  |  | 0 | 0 | 100 | 0 | 0
5038 | 601.96 | 0 | 27.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 601.96 | 0 | 0.05921 | 8.5484 | 0 | 0 | 0 | 0 | off_peak | 601.96 |  |  | 0 | 0 | 100 | 0 | 0
5039 | 590.65 | 0 | 27.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 590.65 | 0 | 0.05921 | 8.3927 | 0 | 0 | 0 | 0 | off_peak | 590.65 |  |  | 0 | 0 | 100 | 0 | 0
5040 | 596.25 | 0 | 27.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 596.25 | 0 | 0.05921 | 8.3438 | 0 | 0 | 0 | 0 | off_peak | 596.25 |  |  | 0 | 0 | 100 | 0 | 0
5041 | 601.73 | 0 | 27.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 601.73 | 0 | 0.05921 | 8.1426 | 0 | 0 | 0 | 0 | off_peak | 601.73 |  |  | 0 | 0 | 100 | 0 | 0
5042 | 625.37 | 0 | 27.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 625.37 | 0 | 0.05921 | 7.8782 | 0 | 0 | 0 | 0 | off_peak | 625.37 |  |  | 0 | 0 | 100 | 0 | 0
5043 | 602.19 | 0 | 27.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 602.19 | 0 | 0.05921 | 7.4485 | 0 | 0 | 0 | 0 | off_peak | 602.19 |  |  | 0 | 0 | 100 | 0 | 0
5044 | 602.25 | 0 | 27.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 602.25 | 0 | 0.05921 | 7.2231 | 0 | 0 | 0 | 0 | off_peak | 602.25 |  |  | 0 | 0 | 100 | 0 | 0
5045 | 622.14 | 0 | 27.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 622.14 | 0 | 0.05921 | 6.7215 | 0 | 0 | 0 | 0 | off_peak | 622.14 |  |  | 0 | 0 | 100 | 0 | 0
5046 | 679.67 | 0 | 27.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 679.67 | 0 | 0.05921 | 6.218 | 0 | 0 | 0 | 0 | off_peak | 679.67 |  |  | 0 | 0 | 100 | 0 | 0
5047 | 722.14 | 57.2812 | 28.1 | 9.176 | 9.176 | 0 | 0 | 8.7006 | 8.7006 | 0 | 0 | 0 | 15.5561 | 721.6646 | 0 | 0.05921 | 5.7261 | 0 | 0 | 0 | 9.176 | off_peak | 712.964 | 0 | 100 | 1.27 | 0 | 98.73 | 52.543 | 0
5048 | 702.16 | 284.835 | 28.6 | 45.5453 | 45.5453 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15.5561 | 656.6147 | 0 | 0.05921 | 5.3401 | 0 | 0 | 0 | 45.5453 | off_peak | 656.6147 |  |  | 6.49 | 0 | 93.51 | 243.2144 | 0
5049 | 763.49 | 467.778 | 28.9 | 74.7161 | 74.7161 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15.5561 | 688.7739 | 0 | 0.05921 | 5.0334 | 0 | 0 | 0 | 74.7161 | off_peak | 688.7739 |  |  | 9.79 | 0 | 90.21 | 376.0733 | 0
5050 | 735.98 | 676.013 | 29.1 | 107.8977 | 107.8977 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 27.12 | 640.4447 | 0 | 0.05921 | 4.8471 | 0 | 0 | 0 | 107.8977 | off_peak | 628.0823 | 0 | 100 | 14.66 | 0 | 85.34 | 522.9895 | 0
5051 | 759.07 | 820.336 | 29.4 | 130.7894 | 130.7894 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27.12 | 628.2806 | 0 | 0.05921 | 4.7499 | 0 | 0 | 0 | 130.7894 | off_peak | 628.2806 |  |  | 17.23 | 0 | 82.77 | 621.2398 | 0
5052 | 734.47 | 378.41 | 29.6 | 60.2873 | 60.2873 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27.12 | 674.1827 | 0 | 0.05921 | 4.6843 | 0 | 0 | 0 | 60.2873 | off_peak | 674.1827 |  |  | 8.21 | 0 | 91.79 | 282.4024 | 0
5053 | 735.58 | 463.198 | 29.8 | 73.7414 | 73.7414 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27.12 | 661.8386 | 0 | 0.05921 | 4.7068 | 0 | 0 | 0 | 73.7414 | off_peak | 661.8386 |  |  | 10.02 | 0 | 89.98 | 347.0898 | 0
5054 | 785.75 | 680.42 | 29.9 | 108.2836 | 108.2836 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27.12 | 677.4664 | 0 | 0.05921 | 4.9775 | 0 | 0 | 0 | 108.2836 | off_peak | 677.4664 |  |  | 13.78 | 0 | 86.22 | 538.9806 | 0
5055 | 753.88 | 803.221 | 29.9 | 127.8265 | 127.8265 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 38.684 | 638.4159 | 0 | 0.05921 | 5.3248 | 0 | 0 | 0 | 127.8265 | off_peak | 626.0535 | 0 | 100 | 16.96 | 0 | 83.04 | 680.655 | 0
5056 | 721.76 | 525.325 | 29.7 | 83.6627 | 83.6627 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 38.684 | 638.0973 | 0 | 0.05921 | 5.9243 | 0 | 0 | 0 | 83.6627 | off_peak | 638.0973 |  |  | 11.59 | 0 | 88.41 | 495.6442 | 0
5057 | 749.26 | 388.577 | 29.4 | 61.9524 | 61.9524 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 38.684 | 687.3076 | 0 | 0.05921 | 6.5952 | 0 | 0 | 0 | 61.9524 | off_peak | 687.3076 |  |  | 8.27 | 0 | 91.73 | 408.5908 | 0
5058 | 709.62 | 151.432 | 29 | 24.1787 | 24.1787 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 38.684 | 685.4413 | 0 | 0.05921 | 7.181 | 0 | 0 | 0 | 24.1787 | off_peak | 685.4413 |  |  | 3.41 | 0 | 96.59 | 173.6283 | 0
5059 | 680.68 | 31.4733 | 28.7 | 5.0308 | 5.0308 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 50.2479 | 688.0116 | 0 | 0.05921 | 7.7449 | 0 | 0 | 0 | 5.0308 | off_peak | 675.6492 | 0 | 100 | 0.74 | 0 | 99.26 | 38.963 | 0
5060 | 663.97 | 0 | 28.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50.2479 | 663.97 | 0 | 0.05921 | 8.0904 | 0 | 0 | 0 | 0 | off_peak | 663.97 |  |  | 0 | 0 | 100 | 0 | 0
5061 | 668.02 | 0 | 27.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50.2479 | 668.02 | 0 | 0.05921 | 8.3571 | 0 | 0 | 0 | 0 | off_peak | 668.02 |  |  | 0 | 0 | 100 | 0 | 0
5062 | 640.24 | 0 | 27.8 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 61.8119 | 652.6024 | 0 | 0.05921 | 8.7513 | 0 | 0 | 0 | 0 | off_peak | 640.24 | 0 | 100 | 0 | 0 | 100 | 0 | 0
5063 | 589.77 | 0 | 27.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 61.8119 | 589.77 | 0 | 0.05921 | 8.9811 | 0 | 0 | 0 | 0 | off_peak | 589.77 |  |  | 0 | 0 | 100 | 0 | 0
5064 | 604.79 | 0 | 27.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 61.8119 | 604.79 | 0 | 0.05921 | 8.8092 | 0 | 0 | 0 | 0 | off_peak | 604.79 |  |  | 0 | 0 | 100 | 0 | 0
5065 | 620.94 | 0 | 27.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 61.8119 | 620.94 | 0 | 0.05921 | 8.4827 | 0 | 0 | 0 | 0 | off_peak | 620.94 |  |  | 0 | 0 | 100 | 0 | 0
5066 | 606.06 | 0 | 27.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 61.8119 | 606.06 | 0 | 0.05921 | 8.3123 | 0 | 0 | 0 | 0 | off_peak | 606.06 |  |  | 0 | 0 | 100 | 0 | 0
5067 | 582.4 | 0 | 27.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 61.8119 | 582.4 | 0 | 0.05921 | 7.9912 | 0 | 0 | 0 | 0 | off_peak | 582.4 |  |  | 0 | 0 | 100 | 0 | 0
5068 | 591.98 | 0 | 27.8 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 73.3758 | 604.3424 | 0 | 0.05921 | 7.3997 | 0 | 0 | 0 | 0 | off_peak | 591.98 | 0 | 100 | 0 | 0 | 100 | 0 | 0
5069 | 601.91 | 0 | 27.8 | 0 | 0 | 0 | 0 | 0.79843 | 0.79843 | 0 | 0 | 0 | 74.1227 | 602.7084 | 0 | 0.05921 | 6.7986 | 0 | 0 | 0 | 0 | off_peak | 601.91 | 0 | 100 | 0 | 0 | 100 | 0 | 0
5070 | 723.22 | 0 | 28 | 0 | 0 | 0 | 0 | 0.051567 | 0.051567 | 0 | 0 | 0 | 74.1709 | 723.2716 | 0 | 0.05921 | 6.0784 | 0 | 0 | 0 | 0 | off_peak | 723.22 | 0 | 100 | 0 | 0 | 100 | 0 | 0
5071 | 790.44 | 23.75 | 28.3 | 3.8018 | 3.8018 | 0 | 0 | 0.0033305 | 0.0033305 | 0 | 0 | 0 | 74.174 | 786.6415 | 0 | 0.05921 | 5.5508 | 0 | 0 | 0 | 3.8018 | off_peak | 786.6382 | 0 | 100 | 0.48 | 0 | 99.52 | 21.103 | 0
5072 | 862.14 | 69.698 | 28.8 | 11.1366 | 11.1366 | 0 | 0 | 0.0002151 | 0.0002151 | 0 | 0 | 0 | 74.1742 | 851.0036 | 0 | 0.05921 | 5.1367 | 0 | 0 | 0 | 11.1366 | off_peak | 851.0034 | 0 | 100 | 1.29 | 0 | 98.71 | 57.2049 | 0
5073 | 846.65 | 87.9428 | 29.1 | 14.0365 | 14.0365 | 0 | 0 | 1.3893e-05 | 1.3893e-05 | 0 | 0 | 0 | 74.1743 | 832.6136 | 0 | 0.05921 | 4.8926 | 0 | 0 | 0 | 14.0365 | off_peak | 832.6135 | 0 | 100 | 1.66 | 0 | 98.34 | 68.6745 | 0
5074 | 866.19 | 162.919 | 29.4 | 25.9748 | 25.9748 | 0 | 0 | 8.9726e-07 | 8.9726e-07 | 0 | 0 | 0 | 74.1743 | 840.2152 | 0 | 0.05921 | 4.7925 | 0 | 0 | 0 | 25.9748 | off_peak | 840.2152 | 0 | 100 | 3 | 0 | 97 | 124.4836 | 0
5075 | 840.68 | 277.67 | 29.7 | 44.2214 | 44.2214 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1743 | 796.4586 | 0 | 0.05921 | 4.886 | 0 | 0 | 0 | 44.2214 | off_peak | 796.4586 |  |  | 5.26 | 0 | 94.74 | 216.0647 | 0
5076 | 915.14 | 194.716 | 29.9 | 30.9876 | 30.9876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1743 | 884.1524 | 0 | 0.05921 | 5.0831 | 0 | 0 | 0 | 30.9876 | off_peak | 884.1524 |  |  | 3.39 | 0 | 96.61 | 157.5115 | 0
5077 | 882.81 | 216.591 | 30 | 34.4562 | 34.4562 | 0 | 0 | 0 | 0 | 62.4453 | 62.4453 | 0 | 7.4174 | 785.9085 | 0 | 0.088511 | 5.2437 | 0 | 0 | 0 | 34.4562 | on_peak | 785.9085 |  |  | 3.9 | 7.07 | 89.02 | 180.6788 | 0
5078 | 918.78 | 394.233 | 30.1 | 62.6932 | 62.6932 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 856.0868 | 0 | 0.088511 | 5.4852 | 0 | 0 | 0 | 62.6932 | on_peak | 856.0868 |  |  | 6.82 | 0 | 93.18 | 343.8874 | 0
5079 | 943.28 | 257.303 | 30 | 40.9328 | 40.9328 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 902.3472 | 0 | 0.088511 | 5.8156 | 0 | 0 | 0 | 40.9328 | on_peak | 902.3472 |  |  | 4.34 | 0 | 95.66 | 238.0491 | 0
5080 | 844.37 | 252.961 | 29.8 | 40.2716 | 40.2716 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 804.0984 | 0 | 0.088511 | 6.3716 | 0 | 0 | 0 | 40.2716 | on_peak | 804.0984 |  |  | 4.77 | 0 | 95.23 | 256.5942 | 0
5081 | 881.83 | 99.3276 | 29.6 | 15.8246 | 15.8246 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 866.0054 | 0 | 0.088511 | 6.8464 | 0 | 0 | 0 | 15.8246 | on_peak | 866.0054 |  |  | 1.79 | 0 | 98.21 | 108.3414 | 0
5082 | 900.77 | 25.65 | 29.2 | 4.0925 | 4.0925 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 896.6775 | 0 | 0.088511 | 7.3437 | 0 | 0 | 0 | 4.0925 | on_peak | 896.6775 |  |  | 0.45 | 0 | 99.55 | 30.0538 | 0
5083 | 898.75 | 33.25 | 29 | 5.3089 | 5.3089 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 893.4411 | 0 | 0.088511 | 7.8253 | 0 | 0 | 0 | 5.3089 | on_peak | 893.4411 |  |  | 0.59 | 0 | 99.41 | 41.544 | 0
5084 | 887.89 | 0 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 887.89 | 0 | 0.088511 | 8.1503 | 0 | 0 | 0 | 0 | on_peak | 887.89 |  |  | 0 | 0 | 100 | 0 | 0
5085 | 871.14 | 0 | 29.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 871.14 | 0 | 0.088511 | 8.3732 | 0 | 0 | 0 | 0 | on_peak | 871.14 |  |  | 0 | 0 | 100 | 0 | 0
5086 | 856.17 | 0 | 29.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 856.17 | 0 | 0.05921 | 8.4156 | 0 | 0 | 0 | 0 | off_peak | 856.17 |  |  | 0 | 0 | 100 | 0 | 0
5087 | 872.31 | 0 | 29.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 872.31 | 0 | 0.05921 | 8.2402 | 0 | 0 | 0 | 0 | off_peak | 872.31 |  |  | 0 | 0 | 100 | 0 | 0
5088 | 853.22 | 0 | 29.4 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 18.9814 | 865.5824 | 0 | 0.05921 | 7.8999 | 0 | 0 | 0 | 0 | off_peak | 853.22 | 0 | 100 | 0 | 0 | 100 | 0 | 0
5089 | 789.24 | 0 | 29.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18.9814 | 789.24 | 0 | 0.05921 | 7.7104 | 0 | 0 | 0 | 0 | off_peak | 789.24 |  |  | 0 | 0 | 100 | 0 | 0
5090 | 757.5 | 0 | 29 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18.9814 | 757.5 | 0 | 0.05921 | 7.3136 | 0 | 0 | 0 | 0 | off_peak | 757.5 |  |  | 0 | 0 | 100 | 0 | 0
5091 | 695.39 | 0 | 28.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18.9814 | 695.39 | 0 | 0.05921 | 6.8051 | 0 | 0 | 0 | 0 | off_peak | 695.39 |  |  | 0 | 0 | 100 | 0 | 0
5092 | 688.11 | 0 | 28.8 | 0 | 0 | 0 | 0 | 8.7006 | 8.7006 | 0 | 0 | 0 | 27.12 | 696.8106 | 0 | 0.05921 | 6.3132 | 0 | 0 | 0 | 0 | off_peak | 688.11 | 0 | 100 | 0 | 0 | 100 | 0 | 0
5093 | 700.96 | 0 | 28.8 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 38.684 | 713.3224 | 0 | 0.05921 | 5.8131 | 0 | 0 | 0 | 0 | off_peak | 700.96 | 0 | 100 | 0 | 0 | 100 | 0 | 0
5094 | 746.76 | 0 | 29 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 50.2479 | 759.1224 | 0 | 0.05921 | 5.1773 | 0 | 0 | 0 | 0 | off_peak | 746.76 | 0 | 100 | 0 | 0 | 100 | 0 | 0
5095 | 761.96 | 79.2773 | 29.5 | 12.6349 | 12.6349 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 61.8119 | 761.6875 | 0 | 0.05921 | 4.6293 | 0 | 0 | 0 | 12.6349 | off_peak | 749.3251 | 0 | 100 | 1.66 | 0 | 98.34 | 58.4912 | 0
5096 | 849.47 | 199.001 | 29.9 | 31.6695 | 31.6695 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 73.3758 | 830.1629 | 0 | 0.05921 | 4.3479 | 0 | 0 | 0 | 31.6695 | off_peak | 817.8005 | 0 | 100 | 3.73 | 0 | 96.27 | 137.6972 | 0
5097 | 863.2 | 166.042 | 30.2 | 26.3953 | 26.3953 | 0 | 0 | 0.79843 | 0.79843 | 0 | 0 | 0 | 74.1227 | 837.6032 | 0 | 0.05921 | 4.1536 | 0 | 0 | 0 | 26.3953 | off_peak | 836.8047 | 0 | 100 | 3.06 | 0 | 96.94 | 109.6356 | 0
5098 | 933.45 | 603.034 | 30.6 | 95.722 | 95.722 | 0 | 0 | 0.051567 | 0.051567 | 0 | 0 | 0 | 74.1709 | 837.7795 | 0 | 0.05921 | 4.084 | 0 | 0 | 0 | 95.722 | off_peak | 837.728 | 0 | 100 | 10.25 | 0 | 89.75 | 390.9275 | 0
5099 | 919.63 | 766.727 | 31 | 121.5268 | 121.5268 | 0 | 0 | 0.0033305 | 0.0033305 | 0 | 0 | 0 | 74.174 | 798.1065 | 0 | 0.05921 | 4.219 | 0 | 0 | 0 | 121.5268 | off_peak | 798.1032 | 0 | 100 | 13.21 | 0 | 86.79 | 512.7268 | 0
5100 | 900.79 | 483.88 | 31.3 | 76.6107 | 76.6107 | 0 | 0 | 0.0002151 | 0.0002151 | 0 | 0 | 0 | 74.1742 | 824.1795 | 0 | 0.05921 | 4.4947 | 0 | 0 | 0 | 76.6107 | off_peak | 824.1793 | 0 | 100 | 8.5 | 0 | 91.5 | 344.3416 | 0
5101 | 881.94 | 909.507 | 31.5 | 143.8924 | 143.8924 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1742 | 738.0476 | 0 | 0.088511 | 4.7127 | 0 | 0 | 0 | 143.8924 | on_peak | 738.0476 |  |  | 16.32 | 0 | 83.68 | 678.1265 | 0
5102 | 956.79 | 123.5 | 31.6 | 19.5316 | 19.5316 | 0 | 0 | 0 | 0 | 38.0443 | 38.0443 | 0 | 33.5031 | 899.214 | 0 | 0.088511 | 4.9824 | 0 | 0 | 0 | 19.5316 | on_peak | 899.214 |  |  | 2.04 | 3.98 | 93.98 | 97.3153 | 0
5103 | 964.77 | 302.915 | 31.6 | 47.9063 | 47.9063 | 0 | 0 | 0 | 0 | 17.6497 | 17.6497 | 0 | 14.6348 | 899.214 | 0 | 0.088511 | 5.3108 | 0 | 0 | 0 | 47.9063 | on_peak | 899.214 |  |  | 4.97 | 1.83 | 93.21 | 254.4184 | 0
5104 | 853.73 | 347.51 | 31.4 | 54.9995 | 54.9995 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14.6348 | 798.7305 | 0 | 0.088511 | 5.8346 | 0 | 0 | 0 | 54.9995 | on_peak | 798.7305 |  |  | 6.44 | 0 | 93.56 | 320.9002 | 0
5105 | 826.13 | 338.388 | 31.1 | 53.615 | 53.615 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14.6348 | 772.515 | 0 | 0.088511 | 6.4072 | 0 | 0 | 0 | 53.615 | on_peak | 772.515 |  |  | 6.49 | 0 | 93.51 | 343.5243 | 0
5106 | 876.42 | 205.057 | 30.7 | 32.5376 | 32.5376 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14.6348 | 843.8824 | 0 | 0.088511 | 6.7912 | 0 | 0 | 0 | 32.5376 | on_peak | 843.8824 |  |  | 3.71 | 0 | 96.29 | 220.9677 | 0
5107 | 823.83 | 19 | 30.5 | 3.0171 | 3.0171 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14.6348 | 820.8129 | 0 | 0.088511 | 7.1514 | 0 | 0 | 0 | 3.0171 | on_peak | 820.8129 |  |  | 0.37 | 0 | 99.63 | 21.5761 | 0
5108 | 856.17 | 0 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14.6348 | 856.17 | 0 | 0.088511 | 7.304 | 0 | 0 | 0 | 0 | on_peak | 856.17 |  |  | 0 | 0 | 100 | 0 | 0
5109 | 842.73 | 0 | 29.9 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7513 | 6.7513 | 0 | 7.4174 | 835.9787 | 0 | 0.088511 | 7.4352 | 0 | 0 | 0 | 0 | on_peak | 835.9787 |  |  | 0 | 0.8 | 99.2 | 0 | 0
5110 | 799.18 | 0 | 29.7 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 18.9814 | 811.5424 | 0 | 0.05921 | 7.7741 | 0 | 0 | 0 | 0 | off_peak | 799.18 | 0 | 100 | 0 | 0 | 100 | 0 | 0
5111 | 832.88 | 0 | 29.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18.9814 | 832.88 | 0 | 0.05921 | 7.6997 | 0 | 0 | 0 | 0 | off_peak | 832.88 |  |  | 0 | 0 | 100 | 0 | 0
5112 | 794.19 | 0 | 29.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18.9814 | 794.19 | 0 | 0.05921 | 7.5146 | 0 | 0 | 0 | 0 | off_peak | 794.19 |  |  | 0 | 0 | 100 | 0 | 0
5113 | 790.19 | 0 | 29.4 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 30.5453 | 802.5524 | 0 | 0.05921 | 7.3455 | 0 | 0 | 0 | 0 | off_peak | 790.19 | 0 | 100 | 0 | 0 | 100 | 0 | 0
5114 | 659.76 | 0 | 29.3 | 0 | 0 | 0 | 0 | 8.7006 | 8.7006 | 0 | 0 | 0 | 38.684 | 668.4606 | 0 | 0.05921 | 7.166 | 0 | 0 | 0 | 0 | off_peak | 659.76 | 0 | 100 | 0 | 0 | 100 | 0 | 0
5115 | 634.98 | 0 | 29.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 38.684 | 634.98 | 0 | 0.05921 | 6.7772 | 0 | 0 | 0 | 0 | off_peak | 634.98 |  |  | 0 | 0 | 100 | 0 | 0
5116 | 638.61 | 0 | 29.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 38.684 | 638.61 | 0 | 0.05921 | 6.2554 | 0 | 0 | 0 | 0 | off_peak | 638.61 |  |  | 0 | 0 | 100 | 0 | 0
5117 | 647.99 | 0 | 29.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 38.684 | 647.99 | 0 | 0.05921 | 5.6827 | 0 | 0 | 0 | 0 | off_peak | 647.99 |  |  | 0 | 0 | 100 | 0 | 0
5118 | 701.72 | 0 | 29.2 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 50.2479 | 714.0824 | 0 | 0.05921 | 5.1232 | 0 | 0 | 0 | 0 | off_peak | 701.72 | 0 | 100 | 0 | 0 | 100 | 0 | 0
5119 | 716.75 | 42.8857 | 29.5 | 6.8349 | 6.8349 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 61.8119 | 722.2774 | 0 | 0.05921 | 4.6341 | 0 | 0 | 0 | 6.8349 | off_peak | 709.9151 | 0 | 100 | 0.95 | 0 | 99.05 | 31.6735 | 0
5120 | 825.2 | 177.374 | 29.8 | 28.2381 | 28.2381 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 73.3758 | 809.3243 | 0 | 0.05921 | 4.336 | 0 | 0 | 0 | 28.2381 | off_peak | 796.9619 | 0 | 100 | 3.42 | 0 | 96.58 | 122.441 | 0
5121 | 889.06 | 132.722 | 29.9 | 21.1217 | 21.1217 | 0 | 0 | 0.79843 | 0.79843 | 0 | 0 | 0 | 74.1227 | 868.7367 | 0 | 0.05921 | 4.1058 | 0 | 0 | 0 | 21.1217 | off_peak | 867.9383 | 0 | 100 | 2.38 | 0 | 97.62 | 86.7223 | 0
5122 | 883.93 | 345.293 | 30 | 54.9306 | 54.9306 | 0 | 0 | 0.051567 | 0.051567 | 0 | 0 | 0 | 74.1709 | 829.051 | 0 | 0.05921 | 4.0426 | 0 | 0 | 0 | 54.9306 | off_peak | 828.9994 | 0 | 100 | 6.21 | 0 | 93.79 | 222.0598 | 0
5123 | 848.57 | 343.883 | 30.2 | 54.6662 | 54.6662 | 0 | 0 | 0.0033305 | 0.0033305 | 0 | 0 | 0 | 74.174 | 793.9072 | 0 | 0.05921 | 4.1442 | 0 | 0 | 0 | 54.6662 | off_peak | 793.9038 | 0 | 100 | 6.44 | 0 | 93.56 | 226.5498 | 0
5124 | 871.28 | 477.221 | 30.3 | 75.8347 | 75.8347 | 0 | 0 | 0.0002151 | 0.0002151 | 0 | 0 | 0 | 74.1742 | 795.4455 | 0 | 0.05921 | 4.4263 | 0 | 0 | 0 | 75.8347 | off_peak | 795.4453 | 0 | 100 | 8.7 | 0 | 91.3 | 335.6674 | 0
5125 | 773.7 | 537.558 | 30.3 | 85.4228 | 85.4228 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1742 | 688.2772 | 0 | 0.088511 | 4.6632 | 0 | 0 | 0 | 85.4228 | on_peak | 688.2772 |  |  | 11.04 | 0 | 88.96 | 398.3415 | 0
5126 | 838.02 | 429.77 | 30.2 | 68.3194 | 68.3194 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1742 | 769.7006 | 0 | 0.088511 | 4.9665 | 0 | 0 | 0 | 68.3194 | on_peak | 769.7006 |  |  | 8.15 | 0 | 91.85 | 339.3084 | 0
5127 | 839.88 | 415.606 | 30.1 | 66.092 | 66.092 | 0 | 0 | 0 | 0 | 62.4453 | 62.4453 | 0 | 7.4174 | 711.3427 | 0 | 0.088511 | 5.3021 | 0 | 0 | 0 | 66.092 | on_peak | 711.3427 |  |  | 7.87 | 7.44 | 84.7 | 350.4285 | 0
5128 | 804.01 | 395.044 | 29.9 | 62.8682 | 62.8682 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 741.1418 | 0 | 0.088511 | 5.797 | 0 | 0 | 0 | 62.8682 | on_peak | 741.1418 |  |  | 7.82 | 0 | 92.18 | 364.4472 | 0
5129 | 758.43 | 307.281 | 29.6 | 48.9552 | 48.9552 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 709.4748 | 0 | 0.088511 | 6.4344 | 0 | 0 | 0 | 48.9552 | on_peak | 709.4748 |  |  | 6.45 | 0 | 93.55 | 314.9951 | 0
5130 | 788.07 | 153.621 | 29.3 | 24.5014 | 24.5014 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 763.5686 | 0 | 0.088511 | 7.0436 | 0 | 0 | 0 | 24.5014 | on_peak | 763.5686 |  |  | 3.11 | 0 | 96.89 | 172.5767 | 0
5131 | 753.09 | 42.0337 | 29.2 | 6.7065 | 6.7065 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 746.3835 | 0 | 0.088511 | 7.6296 | 0 | 0 | 0 | 6.7065 | on_peak | 746.3835 |  |  | 0.89 | 0 | 99.11 | 51.1677 | 0
5132 | 759.02 | 0 | 29 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 759.02 | 0 | 0.088511 | 7.8281 | 0 | 0 | 0 | 0 | on_peak | 759.02 |  |  | 0 | 0 | 100 | 0 | 0
5133 | 755.9 | 0 | 29 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 755.9 | 0 | 0.088511 | 7.9732 | 0 | 0 | 0 | 0 | on_peak | 755.9 |  |  | 0 | 0 | 100 | 0 | 0
5134 | 718.25 | 0 | 29 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 718.25 | 0 | 0.05921 | 8.3095 | 0 | 0 | 0 | 0 | off_peak | 718.25 |  |  | 0 | 0 | 100 | 0 | 0
5135 | 730.11 | 0 | 29 | 0 | 0 | 0 | 0 | 8.7006 | 8.7006 | 0 | 0 | 0 | 15.5561 | 738.8106 | 0 | 0.05921 | 8.2686 | 0 | 0 | 0 | 0 | off_peak | 730.11 | 0 | 100 | 0 | 0 | 100 | 0 | 0
5136 | 753.25 | 0 | 29 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15.5561 | 753.25 | 0 | 0.05921 | 8.0338 | 0 | 0 | 0 | 0 | off_peak | 753.25 |  |  | 0 | 0 | 100 | 0 | 0
5137 | 646.3 | 0 | 28.9 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 27.12 | 658.6624 | 0 | 0.05921 | 7.9402 | 0 | 0 | 0 | 0 | off_peak | 646.3 | 0 | 100 | 0 | 0 | 100 | 0 | 0
5138 | 560.61 | 0 | 28.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27.12 | 560.61 | 0 | 0.05921 | 7.7382 | 0 | 0 | 0 | 0 | off_peak | 560.61 |  |  | 0 | 0 | 100 | 0 | 0
5139 | 548.31 | 0 | 28.8 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 38.684 | 560.6724 | 0 | 0.05921 | 7.1543 | 0 | 0 | 0 | 0 | off_peak | 548.31 | 0 | 100 | 0 | 0 | 100 | 0 | 0
5140 | 575.73 | 0 | 28.8 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 50.2479 | 588.0924 | 0 | 0.05921 | 6.612 | 0 | 0 | 0 | 0 | off_peak | 575.73 | 0 | 100 | 0 | 0 | 100 | 0 | 0
5141 | 558.15 | 0 | 28.8 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 61.8119 | 570.5124 | 0 | 0.05921 | 5.8875 | 0 | 0 | 0 | 0 | off_peak | 558.15 | 0 | 100 | 0 | 0 | 100 | 0 | 0
5142 | 640.32 | 0 | 28.9 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 73.3758 | 652.6824 | 0 | 0.05921 | 5.4155 | 0 | 0 | 0 | 0 | off_peak | 640.32 | 0 | 100 | 0 | 0 | 100 | 0 | 0
5143 | 697.81 | 58.3424 | 29.1 | 9.312 | 9.312 | 0 | 0 | 0.79843 | 0.79843 | 0 | 0 | 0 | 74.1227 | 689.2965 | 0 | 0.05921 | 5.0413 | 0 | 0 | 0 | 9.312 | off_peak | 688.498 | 0 | 100 | 1.33 | 0 | 98.67 | 46.9443 | 0
5144 | 855.32 | 249.529 | 29.4 | 39.7834 | 39.7834 | 0 | 0 | 0.051567 | 0.051567 | 0 | 0 | 0 | 74.1709 | 815.5882 | 0 | 0.05921 | 4.7621 | 0 | 0 | 0 | 39.7834 | off_peak | 815.5366 | 0 | 100 | 4.65 | 0 | 95.35 | 189.4527 | 0
5145 | 863.1 | 379.892 | 29.6 | 60.5234 | 60.5234 | 0 | 0 | 0.0033305 | 0.0033305 | 0 | 0 | 0 | 74.174 | 802.58 | 0 | 0.05921 | 4.5163 | 0 | 0 | 0 | 60.5234 | off_peak | 802.5766 | 0 | 100 | 7.01 | 0 | 92.99 | 273.3407 | 0
5146 | 900.9 | 542.637 | 29.7 | 86.4198 | 86.4198 | 0 | 0 | 0.0002151 | 0.0002151 | 0 | 0 | 0 | 74.1742 | 814.4804 | 0 | 0.05921 | 4.4536 | 0 | 0 | 0 | 86.4198 | off_peak | 814.4802 | 0 | 100 | 9.59 | 0 | 90.41 | 384.8799 | 0
5147 | 841.52 | 565.897 | 29.7 | 90.1242 | 90.1242 | 0 | 0 | 1.4852e-05 | 1.4852e-05 | 0 | 0 | 0 | 74.1743 | 751.3958 | 0 | 0.05921 | 4.5866 | 0 | 0 | 0 | 90.1242 | off_peak | 751.3958 | 0 | 100 | 10.71 | 0 | 89.29 | 413.3652 | 0
5148 | 887.76 | 472.304 | 29.7 | 75.2186 | 75.2186 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1743 | 812.5414 | 0 | 0.05921 | 4.8682 | 0 | 0 | 0 | 75.2186 | off_peak | 812.5414 |  |  | 8.47 | 0 | 91.53 | 366.1793 | 0
5149 | 896.33 | 583.371 | 29.7 | 92.9071 | 92.9071 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1743 | 803.4229 | 0 | 0.088511 | 5.1362 | 0 | 0 | 0 | 92.9071 | on_peak | 803.4229 |  |  | 10.37 | 0 | 89.63 | 477.1884 | 0
5150 | 888.79 | 571.745 | 29.6 | 91.0889 | 91.0889 | 0 | 0 | 0 | 0 | 62.4453 | 62.4453 | 0 | 7.4174 | 735.2558 | 0 | 0.088511 | 5.3873 | 0 | 0 | 0 | 91.0889 | on_peak | 735.2558 |  |  | 10.25 | 7.03 | 82.73 | 490.7213 | 0
5151 | 900.66 | 491.719 | 29.6 | 78.3393 | 78.3393 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 822.3207 | 0 | 0.088511 | 5.5751 | 0 | 0 | 0 | 78.3393 | on_peak | 822.3207 |  |  | 8.7 | 0 | 91.3 | 436.7529 | 0
5152 | 815.51 | 460.187 | 29.4 | 73.3694 | 73.3694 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 742.1406 | 0 | 0.088511 | 5.992 | 0 | 0 | 0 | 73.3694 | on_peak | 742.1406 |  |  | 9 | 0 | 91 | 439.6271 | 0
5153 | 832.51 | 144.688 | 29.1 | 23.0935 | 23.0935 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 809.4165 | 0 | 0.088511 | 6.6214 | 0 | 0 | 0 | 23.0935 | on_peak | 809.4165 |  |  | 2.77 | 0 | 97.23 | 152.9106 | 0
5154 | 858.07 | 82.0768 | 28.6 | 13.1241 | 13.1241 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 844.9459 | 0 | 0.088511 | 7.2641 | 0 | 0 | 0 | 13.1241 | on_peak | 844.9459 |  |  | 1.53 | 0 | 98.47 | 95.3346 | 0
5155 | 826.11 | 19 | 28.4 | 3.0403 | 3.0403 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 823.0697 | 0 | 0.088511 | 7.7913 | 0 | 0 | 0 | 3.0403 | on_peak | 823.0697 |  |  | 0.37 | 0 | 99.63 | 23.688 | 0
5156 | 829.74 | 0 | 28 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 829.74 | 0 | 0.088511 | 8.0939 | 0 | 0 | 0 | 0 | on_peak | 829.74 |  |  | 0 | 0 | 100 | 0 | 0
5157 | 816.85 | 0 | 27.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 816.85 | 0 | 0.088511 | 8.2687 | 0 | 0 | 0 | 0 | on_peak | 816.85 |  |  | 0 | 0 | 100 | 0 | 0
5158 | 802.19 | 0 | 27.8 | 0 | 0 | 0 | 0 | 8.7006 | 8.7006 | 0 | 0 | 0 | 15.5561 | 810.8906 | 0 | 0.05921 | 8.2298 | 0 | 0 | 0 | 0 | off_peak | 802.19 | 0 | 100 | 0 | 0 | 100 | 0 | 0
5159 | 808.21 | 0 | 27.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15.5561 | 808.21 | 0 | 0.05921 | 8.1398 | 0 | 0 | 0 | 0 | off_peak | 808.21 |  |  | 0 | 0 | 100 | 0 | 0
5160 | 763.59 | 0 | 27.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15.5561 | 763.59 | 0 | 0.05921 | 8.0325 | 0 | 0 | 0 | 0 | off_peak | 763.59 |  |  | 0 | 0 | 100 | 0 | 0
5161 | 715.51 | 0 | 27.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15.5561 | 715.51 | 0 | 0.05921 | 8.0086 | 0 | 0 | 0 | 0 | off_peak | 715.51 |  |  | 0 | 0 | 100 | 0 | 0
5162 | 615.63 | 0 | 27.7 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 27.12 | 627.9924 | 0 | 0.05921 | 7.8974 | 0 | 0 | 0 | 0 | off_peak | 615.63 | 0 | 100 | 0 | 0 | 100 | 0 | 0
5163 | 621.79 | 0 | 27.7 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 38.684 | 634.1524 | 0 | 0.05921 | 7.4342 | 0 | 0 | 0 | 0 | off_peak | 621.79 | 0 | 100 | 0 | 0 | 100 | 0 | 0
5164 | 622.99 | 0 | 27.7 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 50.2479 | 635.3524 | 0 | 0.05921 | 6.924 | 0 | 0 | 0 | 0 | off_peak | 622.99 | 0 | 100 | 0 | 0 | 100 | 0 | 0
5165 | 649.31 | 0 | 27.9 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 61.8119 | 661.6724 | 0 | 0.05921 | 6.2064 | 0 | 0 | 0 | 0 | off_peak | 649.31 | 0 | 100 | 0 | 0 | 100 | 0 | 0
5166 | 690.39 | 0 | 28.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 61.8119 | 690.39 | 0 | 0.05921 | 5.5733 | 0 | 0 | 0 | 0 | off_peak | 690.39 |  |  | 0 | 0 | 100 | 0 | 0
5167 | 792.26 | 72.5217 | 28.5 | 11.6005 | 11.6005 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 73.3758 | 793.0219 | 0 | 0.05921 | 5.1848 | 0 | 0 | 0 | 11.6005 | off_peak | 780.6595 | 0 | 100 | 1.46 | 0 | 98.54 | 60.1463 | 0
5168 | 850.24 | 262.16 | 29 | 41.8584 | 41.8584 | 0 | 0 | 0.79843 | 0.79843 | 0 | 0 | 0 | 74.1227 | 809.1801 | 0 | 0.05921 | 4.8703 | 0 | 0 | 0 | 41.8584 | off_peak | 808.3816 | 0 | 100 | 4.92 | 0 | 95.08 | 203.8622 | 0
5169 | 925.28 | 470.403 | 29.2 | 75.0531 | 75.0531 | 0 | 0 | 0.051567 | 0.051567 | 0 | 0 | 0 | 74.1709 | 850.2785 | 0 | 0.05921 | 4.6596 | 0 | 0 | 0 | 75.0531 | off_peak | 850.2269 | 0 | 100 | 8.11 | 0 | 91.89 | 349.7149 | 0
5170 | 943.49 | 657.029 | 29.3 | 104.791 | 104.791 | 0 | 0 | 0.0033305 | 0.0033305 | 0 | 0 | 0 | 74.174 | 838.7023 | 0 | 0.05921 | 4.5452 | 0 | 0 | 0 | 104.791 | off_peak | 838.699 | 0 | 100 | 11.11 | 0 | 88.89 | 476.2943 | 0
5171 | 896.51 | 645.856 | 29.3 | 103.009 | 103.009 | 0 | 0 | 0.0002151 | 0.0002151 | 0 | 0 | 0 | 74.1742 | 793.5012 | 0 | 0.05921 | 4.5788 | 0 | 0 | 0 | 103.009 | off_peak | 793.501 | 0 | 100 | 11.49 | 0 | 88.51 | 471.6528 | 0
5172 | 935.07 | 342.316 | 29.1 | 54.6367 | 54.6367 | 0 | 0 | 1.3893e-05 | 1.3893e-05 | 0 | 0 | 0 | 74.1743 | 880.4333 | 0 | 0.05921 | 4.8303 | 0 | 0 | 0 | 54.6367 | off_peak | 880.4333 | 0 | 100 | 5.84 | 0 | 94.16 | 263.913 | 0
5173 | 826.89 | 137.75 | 29 | 21.9942 | 21.9942 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1743 | 804.8958 | 0 | 0.088511 | 5.155 | 0 | 0 | 0 | 21.9942 | on_peak | 804.8958 |  |  | 2.66 | 0 | 97.34 | 113.3802 | 0
5174 | 884.07 | 261.53 | 28.8 | 41.7883 | 41.7883 | 0 | 0 | 0 | 0 | 62.4453 | 62.4453 | 0 | 7.4174 | 779.8364 | 0 | 0.088511 | 5.4593 | 0 | 0 | 0 | 41.7883 | on_peak | 779.8364 |  |  | 4.73 | 7.06 | 88.21 | 228.134 | 0
5175 | 889.17 | 618.869 | 28.6 | 98.9575 | 98.9575 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 790.2125 | 0 | 0.088511 | 5.8977 | 0 | 0 | 0 | 98.9575 | on_peak | 790.2125 |  |  | 11.13 | 0 | 88.87 | 583.6207 | 0
5176 | 830.1 | 574.163 | 28.5 | 91.8424 | 91.8424 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 738.2576 | 0 | 0.088511 | 6.391 | 0 | 0 | 0 | 91.8424 | on_peak | 738.2576 |  |  | 11.06 | 0 | 88.94 | 586.9687 | 0
5177 | 844.89 | 414.463 | 28.4 | 66.3212 | 66.3212 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 778.5688 | 0 | 0.088511 | 6.8541 | 0 | 0 | 0 | 66.3212 | on_peak | 778.5688 |  |  | 7.85 | 0 | 92.15 | 454.5722 | 0
5178 | 834.8 | 245.705 | 28.3 | 39.3313 | 39.3313 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 795.4687 | 0 | 0.088511 | 7.3708 | 0 | 0 | 0 | 39.3313 | on_peak | 795.4687 |  |  | 4.71 | 0 | 95.29 | 289.9019 | 0
5179 | 825.32 | 47.3379 | 28.2 | 7.5804 | 7.5804 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 817.7396 | 0 | 0.088511 | 7.9719 | 0 | 0 | 0 | 7.5804 | on_peak | 817.7396 |  |  | 0.92 | 0 | 99.08 | 60.4303 | 0
5180 | 806.77 | 0 | 28.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 806.77 | 0 | 0.088511 | 8.4168 | 0 | 0 | 0 | 0 | on_peak | 806.77 |  |  | 0 | 0 | 100 | 0 | 0
5181 | 840.72 | 0 | 28.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 840.72 | 0 | 0.088511 | 8.5206 | 0 | 0 | 0 | 0 | on_peak | 840.72 |  |  | 0 | 0 | 100 | 0 | 0
5182 | 784.59 | 0 | 28.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 784.59 | 0 | 0.05921 | 8.7176 | 0 | 0 | 0 | 0 | off_peak | 784.59 |  |  | 0 | 0 | 100 | 0 | 0
5183 | 782.19 | 0 | 28.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 782.19 | 0 | 0.05921 | 8.6867 | 0 | 0 | 0 | 0 | off_peak | 782.19 |  |  | 0 | 0 | 100 | 0 | 0
5184 | 783.16 | 0 | 28.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 783.16 | 0 | 0.05921 | 8.5816 | 0 | 0 | 0 | 0 | off_peak | 783.16 |  |  | 0 | 0 | 100 | 0 | 0
5185 | 716.39 | 0 | 28.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 716.39 | 0 | 0.05921 | 8.452 | 0 | 0 | 0 | 0 | off_peak | 716.39 |  |  | 0 | 0 | 100 | 0 | 0
5186 | 646.46 | 0 | 28.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 646.46 | 0 | 0.05921 | 8.241 | 0 | 0 | 0 | 0 | off_peak | 646.46 |  |  | 0 | 0 | 100 | 0 | 0
5187 | 594.29 | 0 | 28.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 594.29 | 0 | 0.05921 | 7.727 | 0 | 0 | 0 | 0 | off_peak | 594.29 |  |  | 0 | 0 | 100 | 0 | 0
5188 | 628.74 | 0 | 28.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 628.74 | 0 | 0.05921 | 7.272 | 0 | 0 | 0 | 0 | off_peak | 628.74 |  |  | 0 | 0 | 100 | 0 | 0
5189 | 629.08 | 0 | 28.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 629.08 | 0 | 0.05921 | 6.7386 | 0 | 0 | 0 | 0 | off_peak | 629.08 |  |  | 0 | 0 | 100 | 0 | 0
5190 | 710.26 | 0 | 28.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 710.26 | 0 | 0.05921 | 6.1533 | 0 | 0 | 0 | 0 | off_peak | 710.26 |  |  | 0 | 0 | 100 | 0 | 0
5191 | 744.33 | 79.9684 | 28.9 | 12.773 | 12.773 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 731.557 | 0 | 0.05921 | 5.6849 | 0 | 0 | 0 | 12.773 | off_peak | 731.557 |  |  | 1.72 | 0 | 98.28 | 72.6138 | 0
5192 | 805.51 | 272.684 | 29.4 | 43.4751 | 43.4751 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 762.0349 | 0 | 0.05921 | 5.3465 | 0 | 0 | 0 | 43.4751 | off_peak | 762.0349 |  |  | 5.4 | 0 | 94.6 | 232.4376 | 0
5193 | 793.21 | 329.341 | 29.6 | 52.4697 | 52.4697 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 740.7403 | 0 | 0.05921 | 5.1042 | 0 | 0 | 0 | 52.4697 | off_peak | 740.7403 |  |  | 6.61 | 0 | 93.39 | 267.816 | 0
5194 | 794.26 | 489.048 | 29.8 | 77.8568 | 77.8568 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 716.4032 | 0 | 0.05921 | 4.9867 | 0 | 0 | 0 | 77.8568 | off_peak | 716.4032 |  |  | 9.8 | 0 | 90.2 | 388.2488 | 0
5195 | 798.79 | 263.567 | 30.1 | 41.9139 | 41.9139 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 756.8761 | 0 | 0.05921 | 4.9518 | 0 | 0 | 0 | 41.9139 | off_peak | 756.8761 |  |  | 5.25 | 0 | 94.75 | 207.5507 | 0
5196 | 776.56 | 504.715 | 30.4 | 80.1743 | 80.1743 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 696.3857 | 0 | 0.05921 | 5.0046 | 0 | 0 | 0 | 80.1743 | off_peak | 696.3857 |  |  | 10.32 | 0 | 89.68 | 401.2423 | 0
5197 | 773.82 | 636.094 | 30.6 | 100.9698 | 100.9698 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 672.8502 | 0 | 0.05921 | 5.1436 | 0 | 0 | 0 | 100.9698 | off_peak | 672.8502 |  |  | 13.05 | 0 | 86.95 | 519.3516 | 0
5198 | 746.94 | 724.111 | 30.8 | 114.8566 | 114.8566 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 632.0834 | 0 | 0.05921 | 5.6243 | 0 | 0 | 0 | 114.8566 | off_peak | 632.0834 |  |  | 15.38 | 0 | 84.62 | 645.9938 | 0
5199 | 725.54 | 687.222 | 30.8 | 109.0054 | 109.0054 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 616.5346 | 0 | 0.05921 | 6.0832 | 0 | 0 | 0 | 109.0054 | off_peak | 616.5346 |  |  | 15.02 | 0 | 84.98 | 663.0997 | 0
5200 | 685.56 | 635.662 | 30.8 | 100.8271 | 100.8271 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 584.7329 | 0 | 0.05921 | 6.6279 | 0 | 0 | 0 | 100.8271 | off_peak | 584.7329 |  |  | 14.71 | 0 | 85.29 | 668.2766 | 0
5201 | 724.39 | 449.07 | 30.6 | 71.2827 | 71.2827 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 18.9814 | 665.4697 | 0 | 0.05921 | 7.0979 | 0 | 0 | 0 | 71.2827 | off_peak | 653.1073 | 0 | 100 | 9.84 | 0 | 90.16 | 505.9571 | 0
5202 | 691.32 | 209.918 | 30.4 | 33.3456 | 33.3456 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18.9814 | 657.9744 | 0 | 0.05921 | 7.4329 | 0 | 0 | 0 | 33.3456 | off_peak | 657.9744 |  |  | 4.82 | 0 | 95.18 | 247.8534 | 0
5203 | 636.81 | 34.3103 | 30.2 | 5.4542 | 5.4542 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18.9814 | 631.3558 | 0 | 0.05921 | 7.6191 | 0 | 0 | 0 | 5.4542 | off_peak | 631.3558 |  |  | 0.86 | 0 | 99.14 | 41.5563 | 0
5204 | 653.56 | 0 | 29.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18.9814 | 653.56 | 0 | 0.05921 | 7.7691 | 0 | 0 | 0 | 0 | off_peak | 653.56 |  |  | 0 | 0 | 100 | 0 | 0
5205 | 633.79 | 0 | 29.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18.9814 | 633.79 | 0 | 0.05921 | 7.8472 | 0 | 0 | 0 | 0 | off_peak | 633.79 |  |  | 0 | 0 | 100 | 0 | 0
5206 | 639.07 | 0 | 29.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18.9814 | 639.07 | 0 | 0.05921 | 8.0894 | 0 | 0 | 0 | 0 | off_peak | 639.07 |  |  | 0 | 0 | 100 | 0 | 0
5207 | 638.27 | 0 | 28.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18.9814 | 638.27 | 0 | 0.05921 | 8.0533 | 0 | 0 | 0 | 0 | off_peak | 638.27 |  |  | 0 | 0 | 100 | 0 | 0
5208 | 623.32 | 0 | 28.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18.9814 | 623.32 | 0 | 0.05921 | 8.0246 | 0 | 0 | 0 | 0 | off_peak | 623.32 |  |  | 0 | 0 | 100 | 0 | 0
5209 | 640.68 | 0 | 28.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18.9814 | 640.68 | 0 | 0.05921 | 7.8905 | 0 | 0 | 0 | 0 | off_peak | 640.68 |  |  | 0 | 0 | 100 | 0 | 0
5210 | 626.41 | 0 | 28.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18.9814 | 626.41 | 0 | 0.05921 | 7.8059 | 0 | 0 | 0 | 0 | off_peak | 626.41 |  |  | 0 | 0 | 100 | 0 | 0
5211 | 632.59 | 0 | 28.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18.9814 | 632.59 | 0 | 0.05921 | 7.5718 | 0 | 0 | 0 | 0 | off_peak | 632.59 |  |  | 0 | 0 | 100 | 0 | 0
5212 | 615.67 | 0 | 28.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18.9814 | 615.67 | 0 | 0.05921 | 7.1061 | 0 | 0 | 0 | 0 | off_peak | 615.67 |  |  | 0 | 0 | 100 | 0 | 0
5213 | 661.79 | 0 | 28.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18.9814 | 661.79 | 0 | 0.05921 | 6.7125 | 0 | 0 | 0 | 0 | off_peak | 661.79 |  |  | 0 | 0 | 100 | 0 | 0
5214 | 695.15 | 0 | 28.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18.9814 | 695.15 | 0 | 0.05921 | 6.1274 | 0 | 0 | 0 | 0 | off_peak | 695.15 |  |  | 0 | 0 | 100 | 0 | 0
5215 | 755.7 | 80.6186 | 29.1 | 12.8674 | 12.8674 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18.9814 | 742.8326 | 0 | 0.05921 | 5.6479 | 0 | 0 | 0 | 12.8674 | off_peak | 742.8326 |  |  | 1.7 | 0 | 98.3 | 72.6734 | 0
5216 | 765.83 | 277.012 | 29.6 | 44.1328 | 44.1328 | 0 | 0 | 8.7006 | 8.7006 | 0 | 0 | 0 | 27.12 | 730.3978 | 0 | 0.05921 | 5.3036 | 0 | 0 | 0 | 44.1328 | off_peak | 721.6972 | 0 | 100 | 5.76 | 0 | 94.24 | 234.0617 | 0
5217 | 768.7 | 485.594 | 29.9 | 77.2786 | 77.2786 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27.12 | 691.4214 | 0 | 0.05921 | 5.0905 | 0 | 0 | 0 | 77.2786 | off_peak | 691.4214 |  |  | 10.05 | 0 | 89.95 | 393.3866 | 0
5218 | 773.8 | 670.882 | 30.2 | 106.6483 | 106.6483 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27.12 | 667.1517 | 0 | 0.05921 | 4.9537 | 0 | 0 | 0 | 106.6483 | off_peak | 667.1517 |  |  | 13.78 | 0 | 86.22 | 528.3047 | 0
5219 | 785.25 | 812.949 | 30.5 | 129.0901 | 129.0901 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 38.684 | 668.5223 | 0 | 0.05921 | 4.8876 | 0 | 0 | 0 | 129.0901 | off_peak | 656.1599 | 0 | 100 | 16.44 | 0 | 83.56 | 630.9368 | 0
5220 | 803.67 | 667.985 | 30.8 | 105.9541 | 105.9541 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 38.684 | 697.7159 | 0 | 0.05921 | 4.9042 | 0 | 0 | 0 | 105.9541 | off_peak | 697.7159 |  |  | 13.18 | 0 | 86.82 | 519.6187 | 0
5221 | 754.15 | 432.297 | 30.9 | 68.5446 | 68.5446 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 38.684 | 685.6054 | 0 | 0.05921 | 4.9984 | 0 | 0 | 0 | 68.5446 | off_peak | 685.6054 |  |  | 9.09 | 0 | 90.91 | 342.6148 | 0
5222 | 731.01 | 545.749 | 31 | 86.5017 | 86.5017 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 38.684 | 644.5083 | 0 | 0.05921 | 5.4162 | 0 | 0 | 0 | 86.5017 | off_peak | 644.5083 |  |  | 11.83 | 0 | 88.17 | 468.5089 | 0
5223 | 746.71 | 665.152 | 31 | 105.4271 | 105.4271 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 38.684 | 641.2829 | 0 | 0.05921 | 5.9333 | 0 | 0 | 0 | 105.4271 | off_peak | 641.2829 |  |  | 14.12 | 0 | 85.88 | 625.5355 | 0
5224 | 752.07 | 419.882 | 30.8 | 66.6006 | 66.6006 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 38.684 | 685.4694 | 0 | 0.05921 | 6.4725 | 0 | 0 | 0 | 66.6006 | off_peak | 685.4694 |  |  | 8.86 | 0 | 91.14 | 431.0696 | 0
5225 | 731.32 | 153.466 | 30.5 | 24.3692 | 24.3692 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 38.684 | 706.9508 | 0 | 0.05921 | 7.1014 | 0 | 0 | 0 | 24.3692 | off_peak | 706.9508 |  |  | 3.33 | 0 | 96.67 | 173.0552 | 0
5226 | 686.03 | 201.777 | 30.2 | 32.076 | 32.076 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 50.2479 | 666.3164 | 0 | 0.05921 | 7.6448 | 0 | 0 | 0 | 32.076 | off_peak | 653.954 | 0 | 100 | 4.68 | 0 | 95.32 | 245.2155 | 0
5227 | 629.14 | 42.3398 | 30 | 6.7356 | 6.7356 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50.2479 | 622.4044 | 0 | 0.05921 | 8.0584 | 0 | 0 | 0 | 6.7356 | off_peak | 622.4044 |  |  | 1.07 | 0 | 98.93 | 54.2783 | 0
5228 | 614.55 | 0 | 29.6 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 61.8119 | 626.9124 | 0 | 0.05921 | 8.2516 | 0 | 0 | 0 | 0 | off_peak | 614.55 | 0 | 100 | 0 | 0 | 100 | 0 | 0
5229 | 620.99 | 0 | 29.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 61.8119 | 620.99 | 0 | 0.05921 | 8.288 | 0 | 0 | 0 | 0 | off_peak | 620.99 |  |  | 0 | 0 | 100 | 0 | 0
5230 | 620.37 | 0 | 29.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 61.8119 | 620.37 | 0 | 0.05921 | 8.4856 | 0 | 0 | 0 | 0 | off_peak | 620.37 |  |  | 0 | 0 | 100 | 0 | 0
5231 | 630.33 | 0 | 29.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 61.8119 | 630.33 | 0 | 0.05921 | 8.7487 | 0 | 0 | 0 | 0 | off_peak | 630.33 |  |  | 0 | 0 | 100 | 0 | 0
5232 | 605.23 | 0 | 29.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 61.8119 | 605.23 | 0 | 0.05921 | 8.9716 | 0 | 0 | 0 | 0 | off_peak | 605.23 |  |  | 0 | 0 | 100 | 0 | 0
5233 | 617.98 | 0 | 29 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 61.8119 | 617.98 | 0 | 0.05921 | 8.8041 | 0 | 0 | 0 | 0 | off_peak | 617.98 |  |  | 0 | 0 | 100 | 0 | 0
5234 | 603.11 | 0 | 28.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 61.8119 | 603.11 | 0 | 0.05921 | 8.6397 | 0 | 0 | 0 | 0 | off_peak | 603.11 |  |  | 0 | 0 | 100 | 0 | 0
5235 | 638.35 | 0 | 28.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 61.8119 | 638.35 | 0 | 0.05921 | 8.3001 | 0 | 0 | 0 | 0 | off_peak | 638.35 |  |  | 0 | 0 | 100 | 0 | 0
5236 | 592.96 | 0 | 28.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 61.8119 | 592.96 | 0 | 0.05921 | 7.6856 | 0 | 0 | 0 | 0 | off_peak | 592.96 |  |  | 0 | 0 | 100 | 0 | 0
5237 | 665.82 | 0 | 28.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 61.8119 | 665.82 | 0 | 0.05921 | 6.8829 | 0 | 0 | 0 | 0 | off_peak | 665.82 |  |  | 0 | 0 | 100 | 0 | 0
5238 | 685.51 | 0 | 28.6 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 73.3758 | 697.8724 | 0 | 0.05921 | 6.3358 | 0 | 0 | 0 | 0 | off_peak | 685.51 | 0 | 100 | 0 | 0 | 100 | 0 | 0
5239 | 740.97 | 79.1276 | 29.1 | 12.6295 | 12.6295 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 73.3758 | 728.3405 | 0 | 0.05921 | 5.8421 | 0 | 0 | 0 | 12.6295 | off_peak | 728.3405 |  |  | 1.7 | 0 | 98.3 | 73.7821 | 0
5240 | 811.4 | 272.569 | 29.5 | 43.4408 | 43.4408 | 0 | 0 | 0.79843 | 0.79843 | 0 | 0 | 0 | 74.1227 | 768.7576 | 0 | 0.05921 | 5.5231 | 0 | 0 | 0 | 43.4408 | off_peak | 767.9592 | 0 | 100 | 5.35 | 0 | 94.65 | 239.9285 | 0
5241 | 880.71 | 480.046 | 29.9 | 76.3956 | 76.3956 | 0 | 0 | 0.051567 | 0.051567 | 0 | 0 | 0 | 74.1709 | 804.3659 | 0 | 0.05921 | 5.2905 | 0 | 0 | 0 | 76.3956 | off_peak | 804.3144 | 0 | 100 | 8.67 | 0 | 91.33 | 404.1689 | 0
5242 | 824.4 | 667.258 | 30.2 | 106.0722 | 106.0689 | 0 | 0.0033305 | 0.0033305 | 0 | 0 | 0 | 0 | 74.174 | 718.3311 | 0 | 0.05921 | 5.2171 | 0 | 0 | 0.0031154 | 106.0689 | off_peak | 718.3311 | 100 | 0 | 12.87 | 0 | 87.13 | 553.3711 | 0
5243 | 833.34 | 811.778 | 30.5 | 128.9042 | 128.904 | 0 | 0.0002151 | 0.0002151 | 0 | 0 | 0 | 0 | 74.1742 | 704.436 | 0 | 0.05921 | 5.3271 | 0 | 0 | 0.0033166 | 128.904 | off_peak | 704.436 | 100 | 0 | 15.47 | 0 | 84.53 | 686.6887 | 0
5244 | 890.2 | 903.687 | 30.8 | 143.3405 | 143.3405 | 0 | 0 | 1.3893e-05 | 1.3893e-05 | 0 | 0 | 0 | 74.1743 | 746.8595 | 0 | 0.05921 | 5.4982 | 0 | 0 | 0.0033166 | 143.3405 | off_peak | 746.8595 | 0 | 100 | 16.1 | 0 | 83.9 | 788.113 | 0
5245 | 812.82 | 931.615 | 31 | 147.6617 | 147.6617 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1743 | 665.1583 | 0 | 0.088511 | 5.6345 | 0 | 0 | 0.0033166 | 147.6617 | on_peak | 665.1583 |  |  | 18.17 | 0 | 81.83 | 832.0027 | 0
5246 | 871.48 | 895.124 | 31 | 141.8779 | 141.8779 | 0 | 0 | 0 | 0 | -8.3931e-07 | -8.3931e-07 | 0 | 74.1743 | 729.6021 | 0 | 0.088511 | 5.9465 | 0 | 0 | 0.0033166 | 141.8779 | on_peak | 729.6021 |  |  | 16.28 | 0 | 83.72 | 843.6733 | 0
5247 | 873.75 | 797.326 | 31 | 126.3768 | 126.3768 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1743 | 747.3732 | 0 | 0.088511 | 6.4105 | 0 | 0 | 0.0033166 | 126.3768 | on_peak | 747.3732 |  |  | 14.46 | 0 | 85.54 | 810.1387 | 0
5248 | 844.12 | 646.739 | 30.9 | 102.5464 | 102.5464 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1743 | 741.5736 | 0 | 0.088511 | 7.0774 | 0 | 0 | 0.0033166 | 102.5464 | on_peak | 741.5736 |  |  | 12.15 | 0 | 87.85 | 725.7613 | 0
5249 | 843.23 | 457.378 | 30.6 | 72.6015 | 72.6015 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1743 | 770.6285 | 0 | 0.088511 | 7.7249 | 0 | 0 | 0.0033166 | 72.6015 | on_peak | 770.6285 |  |  | 8.61 | 0 | 91.39 | 560.8366 | 0
5250 | 844.37 | 248.569 | 30.2 | 39.5144 | 39.5144 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1743 | 804.8556 | 0 | 0.088511 | 8.2406 | 0 | 0 | 0.0033166 | 39.5144 | on_peak | 804.8556 |  |  | 4.68 | 0 | 95.32 | 325.6235 | 0
5251 | 848.37 | 61.5389 | 30 | 9.7899 | 9.7899 | 0 | 0 | 0 | 0 | 62.4422 | 62.4422 | 0 | 7.4207 | 776.138 | 0 | 0.088511 | 8.712 | 0 | 0 | 0.0033166 | 9.7899 | on_peak | 776.138 |  |  | 1.15 | 7.36 | 91.49 | 85.2892 | 0
5252 | 855.88 | 0 | 29.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4207 | 855.88 | 0 | 0.088511 | 9.0542 | 0 | 0 | 0.0033166 | 0 | on_peak | 855.88 |  |  | 0 | 0 | 100 | 0 | 0
5253 | 830.24 | 0 | 29.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0031024 | 0.0031024 | 0 | 7.4174 | 830.2369 | 0 | 0.088511 | 8.9808 | 0.0031024 | 0 | 0 | 0.0031024 | on_peak | 830.2369 |  |  | 0 | 0 | 100 | 0.027862 | 0
5254 | 832.8 | 0 | 29.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 832.8 | 0 | 0.05921 | 8.8558 | 0 | 0 | 0 | 0 | off_peak | 832.8 |  |  | 0 | 0 | 100 | 0 | 0
5255 | 872.84 | 0 | 29.1 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 18.9814 | 885.2024 | 0 | 0.05921 | 8.967 | 0 | 0 | 0 | 0 | off_peak | 872.84 | 0 | 100 | 0 | 0 | 100 | 0 | 0
5256 | 816.46 | 0 | 29 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 30.5453 | 828.8224 | 0 | 0.05921 | 9.057 | 0 | 0 | 0 | 0 | off_peak | 816.46 | 0 | 100 | 0 | 0 | 100 | 0 | 0
5257 | 774.58 | 0 | 28.9 | 0 | 0 | 0 | 0 | 8.7006 | 8.7006 | 0 | 0 | 0 | 38.684 | 783.2806 | 0 | 0.05921 | 9.0684 | 0 | 0 | 0 | 0 | off_peak | 774.58 | 0 | 100 | 0 | 0 | 100 | 0 | 0
5258 | 704.44 | 0 | 28.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 38.684 | 704.44 | 0 | 0.05921 | 8.9796 | 0 | 0 | 0 | 0 | off_peak | 704.44 |  |  | 0 | 0 | 100 | 0 | 0
5259 | 687.58 | 0 | 28.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 38.684 | 687.58 | 0 | 0.05921 | 8.7383 | 0 | 0 | 0 | 0 | off_peak | 687.58 |  |  | 0 | 0 | 100 | 0 | 0
5260 | 686.76 | 0 | 28.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 38.684 | 686.76 | 0 | 0.05921 | 8.0899 | 0 | 0 | 0 | 0 | off_peak | 686.76 |  |  | 0 | 0 | 100 | 0 | 0
5261 | 656.25 | 0 | 28.7 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 50.2479 | 668.6124 | 0 | 0.05921 | 7.3993 | 0 | 0 | 0 | 0 | off_peak | 656.25 | 0 | 100 | 0 | 0 | 100 | 0 | 0
5262 | 705.35 | 0 | 28.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50.2479 | 705.35 | 0 | 0.05921 | 6.723 | 0 | 0 | 0 | 0 | off_peak | 705.35 |  |  | 0 | 0 | 100 | 0 | 0
5263 | 740.42 | 81.7191 | 29.2 | 13.0383 | 13.0383 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 61.8119 | 739.744 | 0 | 0.05921 | 6.204 | 0 | 0 | 0 | 13.0383 | off_peak | 727.3817 | 0 | 100 | 1.76 | 0 | 98.24 | 80.8895 | 0
5264 | 819.4 | 280.289 | 29.6 | 44.6549 | 32.2925 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 0 | 73.3758 | 787.1075 | 0 | 0.05921 | 5.8198 | 0 | 0 | 11.5639 | 32.2925 | off_peak | 787.1075 | 100 | 0 | 3.94 | 0 | 96.06 | 187.9349 | 0
5265 | 827.27 | 488.95 | 29.8 | 77.8412 | 77.8412 | 0 | 0 | 0.79843 | 0.79843 | 0 | 0 | 0 | 74.1227 | 750.2273 | 0 | 0.05921 | 5.5292 | 0 | 0 | 11.5639 | 77.8412 | off_peak | 749.4288 | 0 | 100 | 9.41 | 0 | 90.59 | 430.4016 | 0
5266 | 871.06 | 653.952 | 30.2 | 103.957 | 103.9055 | 0 | 0.051567 | 0.051567 | 0 | 0 | 0 | 0 | 74.1709 | 767.1545 | 0 | 0.05921 | 5.4057 | 0 | 0 | 11.6122 | 103.9055 | off_peak | 767.1545 | 100 | 0 | 11.93 | 0 | 88.07 | 561.6852 | 0
5267 | 852.8 | 501.124 | 30.5 | 79.5747 | 79.5714 | 0 | 0.0033305 | 0.0033305 | 0 | 0 | 0 | 0 | 74.174 | 773.2286 | 0 | 0.05921 | 5.4761 | 0 | 0 | 11.6153 | 79.5714 | off_peak | 773.2286 | 100 | 0 | 9.33 | 0 | 90.67 | 435.742 | 0
5268 | 889.01 | 854.529 | 30.7 | 135.593 | 135.593 | 0 | 0 | 0.0002151 | 0.0002151 | 0 | 0 | 0 | 74.1742 | 753.4172 | 0 | 0.05921 | 5.6944 | 0 | 0 | 11.6153 | 135.593 | off_peak | 753.417 | 0 | 100 | 15.25 | 0 | 84.75 | 772.1262 | 0
5269 | 862.69 | 935.417 | 30.8 | 148.3734 | 148.3734 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1742 | 714.3166 | 0 | 0.088511 | 5.8575 | 0 | 0 | 11.6153 | 148.3734 | on_peak | 714.3166 |  |  | 17.2 | 0 | 82.8 | 869.0992 | 0
5270 | 881.1 | 897.538 | 30.8 | 142.3652 | 142.3652 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1742 | 738.7348 | 0 | 0.088511 | 6.1756 | 0 | 0 | 11.6153 | 142.3652 | on_peak | 738.7348 |  |  | 16.16 | 0 | 83.84 | 879.1958 | 0
5271 | 831.85 | 799.5 | 30.8 | 126.8146 | 126.8146 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1742 | 705.0354 | 0 | 0.088511 | 6.6061 | 0 | 0 | 11.6153 | 126.8146 | on_peak | 705.0354 |  |  | 15.24 | 0 | 84.76 | 837.7454 | 0
5272 | 806.86 | 647.412 | 30.7 | 102.7286 | 102.7286 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1742 | 704.1314 | 0 | 0.088511 | 7.2062 | 0 | 0 | 11.6153 | 102.7286 | on_peak | 704.1314 |  |  | 12.73 | 0 | 87.27 | 740.2816 | 0
5273 | 835.68 | 457.523 | 30.5 | 72.6512 | 72.6512 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1742 | 763.0288 | 0 | 0.088511 | 7.7322 | 0 | 0 | 11.6153 | 72.6512 | on_peak | 763.0288 |  |  | 8.69 | 0 | 91.31 | 561.7517 | 0
5274 | 874.77 | 248.631 | 30.2 | 39.5242 | 39.5242 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1742 | 835.2458 | 0 | 0.088511 | 8.2542 | 0 | 0 | 11.6153 | 39.5242 | on_peak | 835.2458 |  |  | 4.52 | 0 | 95.48 | 326.2418 | 0
5275 | 808.22 | 60.2016 | 30 | 9.5771 | 9.5771 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1742 | 798.6429 | 0 | 0.088511 | 8.6262 | 0 | 0 | 11.6153 | 9.5771 | on_peak | 798.6429 |  |  | 1.18 | 0 | 98.82 | 82.6143 | 0
5276 | 845.54 | 0 | 29.5 | 0 | 0 | 0 | 0 | 0 | 0 | 62.4453 | 62.4453 | 0 | 7.4174 | 783.0947 | 0 | 0.088511 | 9.0003 | 10.8651 | 0 | 0 | 10.8651 | on_peak | 783.0947 |  |  | 0 | 7.39 | 92.61 | 97.7895 | 0
5277 | 800.84 | 0 | 29.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 800.84 | 0 | 0.088511 | 9.1783 | 0 | 0 | 0 | 0 | on_peak | 800.84 |  |  | 0 | 0 | 100 | 0 | 0
5278 | 788.13 | 0 | 29.3 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 18.9814 | 800.4924 | 0 | 0.05921 | 9.2545 | 0 | 0 | 0 | 0 | off_peak | 788.13 | 0 | 100 | 0 | 0 | 100 | 0 | 0
5279 | 798.93 | 0 | 29.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18.9814 | 798.93 | 0 | 0.05921 | 9.5411 | 0 | 0 | 0 | 0 | off_peak | 798.93 |  |  | 0 | 0 | 100 | 0 | 0
5280 | 765.69 | 0 | 29 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18.9814 | 765.69 | 0 | 0.05921 | 9.4332 | 0 | 0 | 0 | 0 | off_peak | 765.69 |  |  | 0 | 0 | 100 | 0 | 0
5281 | 715.25 | 0 | 28.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18.9814 | 715.25 | 0 | 0.05921 | 9.1974 | 0 | 0 | 0 | 0 | off_peak | 715.25 |  |  | 0 | 0 | 100 | 0 | 0
5282 | 616.02 | 0 | 28.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18.9814 | 616.02 | 0 | 0.05921 | 8.9087 | 0 | 0 | 0 | 0 | off_peak | 616.02 |  |  | 0 | 0 | 100 | 0 | 0
5283 | 579.08 | 0 | 28.8 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 30.5453 | 591.4424 | 0 | 0.05921 | 8.5001 | 0 | 0 | 0 | 0 | off_peak | 579.08 | 0 | 100 | 0 | 0 | 100 | 0 | 0
5284 | 547.62 | 0 | 28.8 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 42.1093 | 559.9824 | 0 | 0.05921 | 7.6565 | 0 | 0 | 0 | 0 | off_peak | 547.62 | 0 | 100 | 0 | 0 | 100 | 0 | 0
5285 | 575.27 | 0 | 28.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 42.1093 | 575.27 | 0 | 0.05921 | 6.8206 | 0 | 0 | 0 | 0 | off_peak | 575.27 |  |  | 0 | 0 | 100 | 0 | 0
5286 | 674.72 | 0 | 29.1 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 53.6732 | 687.0824 | 0 | 0.05921 | 6.3634 | 0 | 0 | 0 | 0 | off_peak | 674.72 | 0 | 100 | 0 | 0 | 100 | 0 | 0
5287 | 703.25 | 77.6385 | 29.6 | 12.3692 | 12.3692 | 0 | 0 | 8.7006 | 8.7006 | 0 | 0 | 0 | 61.8119 | 699.5815 | 0 | 0.05921 | 5.9987 | 0 | 0 | 0 | 12.3692 | off_peak | 690.8808 | 0 | 100 | 1.76 | 0 | 98.24 | 74.1993 | 0
5288 | 790.16 | 274.171 | 30 | 43.6162 | 43.6162 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 73.3758 | 758.9062 | 0 | 0.05921 | 5.7029 | 0 | 0 | 0 | 43.6162 | off_peak | 746.5438 | 0 | 100 | 5.52 | 0 | 94.48 | 248.7411 | 0
5289 | 836.98 | 403.114 | 30.3 | 64.0585 | 64.0585 | 0 | 0 | 0.79843 | 0.79843 | 0 | 0 | 0 | 74.1227 | 773.72 | 0 | 0.05921 | 5.4845 | 0 | 0 | 0 | 64.0585 | off_peak | 772.9215 | 0 | 100 | 7.65 | 0 | 92.35 | 351.3279 | 0
5290 | 883.76 | 456.026 | 30.6 | 72.3869 | 72.3869 | 0 | 0 | 0.051567 | 0.051567 | 0 | 0 | 0 | 74.1709 | 811.4247 | 0 | 0.05921 | 5.3892 | 0 | 0 | 0 | 72.3869 | off_peak | 811.3731 | 0 | 100 | 8.19 | 0 | 91.81 | 390.1093 | 0
5291 | 832.89 | 776.309 | 30.9 | 123.0909 | 123.0875 | 0 | 0.0033305 | 0.0033305 | 0 | 0 | 0 | 0 | 74.174 | 709.8025 | 0 | 0.05921 | 5.4578 | 0 | 0 | 0.0031154 | 123.0875 | off_peak | 709.8025 | 100 | 0 | 14.78 | 0 | 85.22 | 671.7837 | 0
5292 | 910.17 | 827.631 | 31 | 131.1802 | 131.18 | 0 | 0.0002151 | 0.0002151 | 0 | 0 | 0 | 0 | 74.1742 | 778.99 | 0 | 0.05921 | 5.6337 | 0 | 0 | 0.0033166 | 131.18 | off_peak | 778.99 | 100 | 0 | 14.41 | 0 | 85.59 | 739.0317 | 0
5293 | 849.44 | 929.2 | 31 | 147.2789 | 147.2789 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1742 | 702.1611 | 0 | 0.088511 | 5.7839 | 0 | 0 | 0.0033166 | 147.2789 | on_peak | 702.1611 |  |  | 17.34 | 0 | 82.66 | 851.8468 | 0
5294 | 853.22 | 890.789 | 30.9 | 141.2427 | 141.2427 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1742 | 711.9773 | 0 | 0.088511 | 6.1073 | 0 | 0 | 0.0033166 | 141.2427 | on_peak | 711.9773 |  |  | 16.55 | 0 | 83.45 | 862.6049 | 0
5295 | 909.56 | 784.805 | 30.8 | 124.4838 | 124.4838 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1742 | 785.0762 | 0 | 0.088511 | 6.5181 | 0 | 0 | 0.0033166 | 124.4838 | on_peak | 785.0762 |  |  | 13.69 | 0 | 86.31 | 811.4001 | 0
5296 | 824.62 | 642.923 | 30.5 | 102.0913 | 102.0913 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1742 | 722.5287 | 0 | 0.088511 | 7.0128 | 0 | 0 | 0.0033166 | 102.0913 | on_peak | 722.5287 |  |  | 12.38 | 0 | 87.62 | 715.9477 | 0
5297 | 828.74 | 454.416 | 30.2 | 72.2373 | 72.2373 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1742 | 756.5027 | 0 | 0.088511 | 7.5576 | 0 | 0 | 0.0033166 | 72.2373 | on_peak | 756.5027 |  |  | 8.72 | 0 | 91.28 | 545.9395 | 0
5298 | 830.23 | 247.078 | 29.9 | 39.3206 | 39.3206 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1742 | 790.9094 | 0 | 0.088511 | 8.0717 | 0 | 0 | 0.0033166 | 39.3206 | on_peak | 790.9094 |  |  | 4.74 | 0 | 95.26 | 317.3838 | 0
5299 | 828.55 | 50.5145 | 29.7 | 8.0449 | 8.0449 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1742 | 820.5051 | 0 | 0.088511 | 8.3748 | 0 | 0 | 0.0033166 | 8.0449 | on_peak | 820.5051 |  |  | 0.97 | 0 | 99.03 | 67.3747 | 0
5300 | 803.79 | 0 | 29.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1742 | 803.79 | 0 | 0.088511 | 8.8082 | 0 | 0 | 0.0033166 | 0 | on_peak | 803.79 |  |  | 0 | 0 | 100 | 0 | 0
5301 | 855.62 | 0 | 29.4 | 0 | 0 | 0 | 0 | 0 | 0 | 62.4453 | 62.4453 | 0 | 7.4174 | 793.1747 | 0 | 0.088511 | 9.1995 | 0.0031024 | 0 | 0 | 0.0031024 | on_peak | 793.1747 |  |  | 0 | 7.3 | 92.7 | 0.028541 | 0
5302 | 794.93 | 0 | 29.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 794.93 | 0 | 0.05921 | 9.121 | 0 | 0 | 0 | 0 | off_peak | 794.93 |  |  | 0 | 0 | 100 | 0 | 0
5303 | 843.4 | 0 | 29.3 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 18.9814 | 855.7624 | 0 | 0.05921 | 8.926 | 0 | 0 | 0 | 0 | off_peak | 843.4 | 0 | 100 | 0 | 0 | 100 | 0 | 0
5304 | 837.94 | 0 | 29.2 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 30.5453 | 850.3024 | 0 | 0.05921 | 8.8664 | 0 | 0 | 0 | 0 | off_peak | 837.94 | 0 | 100 | 0 | 0 | 100 | 0 | 0
5305 | 742.54 | 0 | 29 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 42.1093 | 754.9024 | 0 | 0.05921 | 8.8825 | 0 | 0 | 0 | 0 | off_peak | 742.54 | 0 | 100 | 0 | 0 | 100 | 0 | 0
5306 | 696.67 | 0 | 29 | 0 | 0 | 0 | 0 | 8.7006 | 8.7006 | 0 | 0 | 0 | 50.2479 | 705.3706 | 0 | 0.05921 | 8.6763 | 0 | 0 | 0 | 0 | off_peak | 696.67 | 0 | 100 | 0 | 0 | 100 | 0 | 0
5307 | 644.74 | 0 | 28.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50.2479 | 644.74 | 0 | 0.05921 | 8.3125 | 0 | 0 | 0 | 0 | off_peak | 644.74 |  |  | 0 | 0 | 100 | 0 | 0
5308 | 628.93 | 0 | 28.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50.2479 | 628.93 | 0 | 0.05921 | 7.6488 | 0 | 0 | 0 | 0 | off_peak | 628.93 |  |  | 0 | 0 | 100 | 0 | 0
5309 | 628.32 | 0 | 28.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50.2479 | 628.32 | 0 | 0.05921 | 6.9316 | 0 | 0 | 0 | 0 | off_peak | 628.32 |  |  | 0 | 0 | 100 | 0 | 0
5310 | 699.2 | 0 | 28.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50.2479 | 699.2 | 0 | 0.05921 | 6.3634 | 0 | 0 | 0 | 0 | off_peak | 699.2 |  |  | 0 | 0 | 100 | 0 | 0
5311 | 745.89 | 79.5752 | 29.2 | 12.6963 | 12.6963 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 61.8119 | 745.5561 | 0 | 0.05921 | 5.9317 | 0 | 0 | 0 | 12.6963 | off_peak | 733.1937 | 0 | 100 | 1.7 | 0 | 98.3 | 75.31 | 0
5312 | 768.67 | 278.374 | 29.6 | 44.3498 | 44.3498 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 73.3758 | 736.6826 | 0 | 0.05921 | 5.6056 | 0 | 0 | 0 | 44.3498 | off_peak | 724.3202 | 0 | 100 | 5.77 | 0 | 94.23 | 248.6062 | 0
5313 | 837.69 | 487.652 | 29.9 | 77.6061 | 77.6061 | 0 | 0 | 0.79843 | 0.79843 | 0 | 0 | 0 | 74.1227 | 760.8824 | 0 | 0.05921 | 5.3336 | 0 | 0 | 0 | 77.6061 | off_peak | 760.0839 | 0 | 100 | 9.26 | 0 | 90.74 | 413.9209 | 0
5314 | 859.29 | 673.496 | 30.3 | 107.0246 | 107.0246 | 0 | 0 | 0.051567 | 0.051567 | 0 | 0 | 0 | 74.1709 | 752.317 | 0 | 0.05921 | 5.1815 | 0 | 0 | 0 | 107.0246 | off_peak | 752.2654 | 0 | 100 | 12.46 | 0 | 87.54 | 554.549 | 0
5315 | 858.96 | 817.856 | 30.6 | 129.8216 | 129.8216 | 0 | 0 | 0.0033305 | 0.0033305 | 0 | 0 | 0 | 74.174 | 729.1417 | 0 | 0.05921 | 5.2861 | 0 | 0 | 0 | 129.8216 | off_peak | 729.1384 | 0 | 100 | 15.11 | 0 | 84.89 | 686.2463 | 0
5316 | 865.14 | 909.41 | 30.8 | 144.2483 | 144.2483 | 0 | 0 | 0.0002151 | 0.0002151 | 0 | 0 | 0 | 74.1742 | 720.8919 | 0 | 0.05921 | 5.5559 | 0 | 0 | 0 | 144.2483 | off_peak | 720.8917 | 0 | 100 | 16.67 | 0 | 83.33 | 801.429 | 0
5317 | 829.3 | 935.806 | 30.9 | 148.3806 | 148.3806 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1742 | 680.9194 | 0 | 0.088511 | 5.7652 | 0 | 0 | 0 | 148.3806 | on_peak | 680.9194 |  |  | 17.89 | 0 | 82.11 | 855.4375 | 0
5318 | 929 | 897.617 | 30.9 | 142.3254 | 142.3254 | 0 | 0 | 0 | 0 | 62.4453 | 62.4453 | 0 | 7.4174 | 724.2294 | 0 | 0.088511 | 5.9908 | 0 | 0 | 0 | 142.3254 | on_peak | 724.2294 |  |  | 15.32 | 6.72 | 77.96 | 852.6363 | 0
5319 | 881.73 | 799.632 | 30.8 | 126.8356 | 126.8356 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 754.8944 | 0 | 0.088511 | 6.3834 | 0 | 0 | 0 | 126.8356 | on_peak | 754.8944 |  |  | 14.38 | 0 | 85.62 | 809.6367 | 0
5320 | 866.14 | 647.912 | 30.6 | 102.8457 | 102.8457 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 763.2943 | 0 | 0.088511 | 6.9569 | 0 | 0 | 0 | 102.8457 | on_peak | 763.2943 |  |  | 11.87 | 0 | 88.13 | 715.4862 | 0
5321 | 838.39 | 456.743 | 30.4 | 72.554 | 72.554 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 765.836 | 0 | 0.088511 | 7.4956 | 0 | 0 | 0 | 72.554 | on_peak | 765.836 |  |  | 8.65 | 0 | 91.35 | 543.8337 | 0
5322 | 869.69 | 230.723 | 30 | 36.7043 | 36.7043 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 832.9857 | 0 | 0.088511 | 7.7495 | 0 | 0 | 0 | 36.7043 | on_peak | 832.9857 |  |  | 4.22 | 0 | 95.78 | 284.4414 | 0
5323 | 809.18 | 39.3419 | 29.7 | 6.2656 | 6.2656 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 802.9144 | 0 | 0.088511 | 8.3428 | 0 | 0 | 0 | 6.2656 | on_peak | 802.9144 |  |  | 0.77 | 0 | 99.23 | 52.2725 | 0
5324 | 871.94 | 0 | 29.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 871.94 | 0 | 0.088511 | 8.6804 | 0 | 0 | 0 | 0 | on_peak | 871.94 |  |  | 0 | 0 | 100 | 0 | 0
5325 | 842.7 | 0 | 29.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 842.7 | 0 | 0.088511 | 8.9415 | 0 | 0 | 0 | 0 | on_peak | 842.7 |  |  | 0 | 0 | 100 | 0 | 0
5326 | 812.32 | 0 | 29.1 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 18.9814 | 824.6824 | 0 | 0.05921 | 9.271 | 0 | 0 | 0 | 0 | off_peak | 812.32 | 0 | 100 | 0 | 0 | 100 | 0 | 0
5327 | 831.6 | 0 | 29 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 30.5453 | 843.9624 | 0 | 0.05921 | 9.0779 | 0 | 0 | 0 | 0 | off_peak | 831.6 | 0 | 100 | 0 | 0 | 100 | 0 | 0
5328 | 791.62 | 0 | 28.9 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 42.1093 | 803.9824 | 0 | 0.05921 | 8.5373 | 0 | 0 | 0 | 0 | off_peak | 791.62 | 0 | 100 | 0 | 0 | 100 | 0 | 0
5329 | 709.34 | 0 | 28.7 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 53.6732 | 721.7024 | 0 | 0.05921 | 8.3582 | 0 | 0 | 0 | 0 | off_peak | 709.34 | 0 | 100 | 0 | 0 | 100 | 0 | 0
5330 | 640.66 | 0 | 28.6 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 65.2371 | 653.0224 | 0 | 0.05921 | 8.0811 | 0 | 0 | 0 | 0 | off_peak | 640.66 | 0 | 100 | 0 | 0 | 100 | 0 | 0
5331 | 606.71 | 0 | 28.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 65.2371 | 606.71 | 0 | 0.05921 | 7.6097 | 0 | 0 | 0 | 0 | off_peak | 606.71 |  |  | 0 | 0 | 100 | 0 | 0
5332 | 568.95 | 0 | 28.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 65.2371 | 568.95 | 0 | 0.05921 | 7.1219 | 0 | 0 | 0 | 0 | off_peak | 568.95 |  |  | 0 | 0 | 100 | 0 | 0
5333 | 587.01 | 0 | 28.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 65.2371 | 587.01 | 0 | 0.05921 | 6.5854 | 0 | 0 | 0 | 0 | off_peak | 587.01 |  |  | 0 | 0 | 100 | 0 | 0
5334 | 689.67 | 0 | 28.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 65.2371 | 689.67 | 0 | 0.05921 | 5.9626 | 0 | 0 | 0 | 0 | off_peak | 689.67 |  |  | 0 | 0 | 100 | 0 | 0
5335 | 743.9 | 77.6051 | 29.1 | 12.3865 | 12.3865 | 0 | 0 | 8.9371 | 8.9371 | 0 | 0 | 0 | 73.597 | 740.4506 | 0 | 0.05921 | 5.5002 | 0 | 0 | 0 | 12.3865 | off_peak | 731.5135 | 0 | 100 | 1.67 | 0 | 98.33 | 68.1285 | 0
5336 | 836.18 | 275.222 | 29.5 | 43.8637 | 43.8637 | 0 | 0 | 0.57721 | 0.57721 | 0 | 0 | 0 | 74.137 | 792.8935 | 0 | 0.05921 | 5.206 | 0 | 0 | 0 | 43.8637 | off_peak | 792.3163 | 0 | 100 | 5.25 | 0 | 94.75 | 228.3521 | 0
5337 | 873.73 | 484.554 | 29.8 | 77.1413 | 77.1413 | 0 | 0 | 0.037279 | 0.037279 | 0 | 0 | 0 | 74.1718 | 796.626 | 0 | 0.05921 | 5.0016 | 0 | 0 | 0 | 77.1413 | off_peak | 796.5887 | 0 | 100 | 8.83 | 0 | 91.17 | 385.8316 | 0
5338 | 882.64 | 422.381 | 30 | 67.1941 | 67.1941 | 0 | 0 | 0.0024077 | 0.0024077 | 0 | 0 | 0 | 74.1741 | 815.4483 | 0 | 0.05921 | 4.9368 | 0 | 0 | 0 | 67.1941 | off_peak | 815.4459 | 0 | 100 | 7.61 | 0 | 92.39 | 331.7267 | 0
5339 | 855.01 | 644.242 | 30.3 | 102.3759 | 102.3759 | 0 | 0 | 0.0001555 | 0.0001555 | 0 | 0 | 0 | 74.1742 | 752.6343 | 0 | 0.05921 | 5.0632 | 0 | 0 | 0 | 102.3759 | off_peak | 752.6341 | 0 | 100 | 11.97 | 0 | 88.03 | 518.3503 | 0
5340 | 930.4 | 835.741 | 30.4 | 132.7581 | 132.7581 | 0 | 0 | 1.0043e-05 | 1.0043e-05 | 0 | 0 | 0 | 74.1743 | 797.642 | 0 | 0.05921 | 5.3013 | 0 | 0 | 0 | 132.7581 | off_peak | 797.6419 | 0 | 100 | 14.27 | 0 | 85.73 | 703.7884 | 0
5341 | 829.33 | 892.975 | 30.5 | 141.7976 | 141.7976 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1743 | 687.5324 | 0 | 0.088511 | 5.4246 | 0 | 0 | 0 | 141.7976 | on_peak | 687.5324 |  |  | 17.1 | 0 | 82.9 | 769.199 | 0
5342 | 908.29 | 897.304 | 30.5 | 142.4851 | 142.4851 | 0 | 0 | 0 | 0 | 62.4453 | 62.4453 | 0 | 7.4174 | 703.3597 | 0 | 0.088511 | 5.741 | 0 | 0 | 0 | 142.4851 | on_peak | 703.3597 |  |  | 15.69 | 6.88 | 77.44 | 818.0027 | 0
5343 | 865.76 | 797.516 | 30.4 | 126.686 | 126.686 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 739.074 | 0 | 0.088511 | 6.1707 | 0 | 0 | 0 | 126.686 | on_peak | 739.074 |  |  | 14.63 | 0 | 85.37 | 781.7461 | 0
5344 | 833.16 | 641.995 | 30.2 | 102.0563 | 102.0563 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 731.1037 | 0 | 0.088511 | 6.7287 | 0 | 0 | 0 | 102.0563 | on_peak | 731.1037 |  |  | 12.25 | 0 | 87.75 | 686.7016 | 0
5345 | 832.81 | 415.47 | 30 | 66.0946 | 66.0946 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 766.7154 | 0 | 0.088511 | 7.2396 | 0 | 0 | 0 | 66.0946 | on_peak | 766.7154 |  |  | 7.94 | 0 | 92.06 | 478.5018 | 0
5346 | 833.19 | 238.909 | 29.6 | 38.0623 | 38.0623 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 795.1277 | 0 | 0.088511 | 7.7839 | 0 | 0 | 0 | 38.0623 | on_peak | 795.1277 |  |  | 4.57 | 0 | 95.43 | 296.2727 | 0
5347 | 846.41 | 43.6259 | 29.3 | 6.958 | 6.958 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 839.452 | 0 | 0.088511 | 8.1568 | 0 | 0 | 0 | 6.958 | on_peak | 839.452 |  |  | 0.82 | 0 | 99.18 | 56.7549 | 0
5348 | 822.79 | 0 | 29 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 822.79 | 0 | 0.088511 | 8.5748 | 0 | 0 | 0 | 0 | on_peak | 822.79 |  |  | 0 | 0 | 100 | 0 | 0
5349 | 788.48 | 0 | 28.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 788.48 | 0 | 0.088511 | 8.8249 | 0 | 0 | 0 | 0 | on_peak | 788.48 |  |  | 0 | 0 | 100 | 0 | 0
5350 | 809.33 | 0 | 28.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 809.33 | 0 | 0.05921 | 9.0755 | 0 | 0 | 0 | 0 | off_peak | 809.33 |  |  | 0 | 0 | 100 | 0 | 0
5351 | 791.04 | 0 | 28.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 791.04 | 0 | 0.05921 | 9.3334 | 0 | 0 | 0 | 0 | off_peak | 791.04 |  |  | 0 | 0 | 100 | 0 | 0
5352 | 751.13 | 0 | 28.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 751.13 | 0 | 0.05921 | 9.4119 | 0 | 0 | 0 | 0 | off_peak | 751.13 |  |  | 0 | 0 | 100 | 0 | 0
5353 | 679.84 | 0 | 28.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 679.84 | 0 | 0.05921 | 9.3472 | 0 | 0 | 0 | 0 | off_peak | 679.84 |  |  | 0 | 0 | 100 | 0 | 0
5354 | 573.79 | 0 | 28.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 573.79 | 0 | 0.05921 | 9.0466 | 0 | 0 | 0 | 0 | off_peak | 573.79 |  |  | 0 | 0 | 100 | 0 | 0
5355 | 594.8 | 0 | 28.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 594.8 | 0 | 0.05921 | 8.4917 | 0 | 0 | 0 | 0 | off_peak | 594.8 |  |  | 0 | 0 | 100 | 0 | 0
5356 | 591.06 | 0 | 28.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 591.06 | 0 | 0.05921 | 7.8082 | 0 | 0 | 0 | 0 | off_peak | 591.06 |  |  | 0 | 0 | 100 | 0 | 0
5357 | 627.88 | 0 | 28.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 627.88 | 0 | 0.05921 | 7.2604 | 0 | 0 | 0 | 0 | off_peak | 627.88 |  |  | 0 | 0 | 100 | 0 | 0
5358 | 697.79 | 0 | 28.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 697.79 | 0 | 0.05921 | 6.677 | 0 | 0 | 0 | 0 | off_peak | 697.79 |  |  | 0 | 0 | 100 | 0 | 0
5359 | 705.97 | 48.8132 | 29 | 7.7939 | 7.7939 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 698.1761 | 0 | 0.05921 | 6.2178 | 0 | 0 | 0 | 7.7939 | off_peak | 698.1761 |  |  | 1.1 | 0 | 98.9 | 48.4607 | 0
5360 | 756.86 | 13.3 | 29.4 | 2.1205 | 2.1205 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 754.7395 | 0 | 0.05921 | 5.8376 | 0 | 0 | 0 | 2.1205 | off_peak | 754.7395 |  |  | 0.28 | 0 | 99.72 | 12.3786 | 0
5361 | 839.47 | 120.316 | 29.7 | 19.1614 | 19.1614 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 820.3086 | 0 | 0.05921 | 5.5766 | 0 | 0 | 0 | 19.1614 | off_peak | 820.3086 |  |  | 2.28 | 0 | 97.72 | 106.8562 | 0
5362 | 768.85 | 344.536 | 30 | 54.8102 | 54.8102 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 714.0398 | 0 | 0.05921 | 5.3685 | 0 | 0 | 0 | 54.8102 | off_peak | 714.0398 |  |  | 7.13 | 0 | 92.87 | 294.2489 | 0
5363 | 847.94 | 243.541 | 30.3 | 38.7009 | 38.7009 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 809.2391 | 0 | 0.05921 | 5.2698 | 0 | 0 | 0 | 38.7009 | off_peak | 809.2391 |  |  | 4.56 | 0 | 95.44 | 203.9447 | 0
5364 | 791.01 | 393.579 | 30.5 | 62.4974 | 62.4974 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 728.5126 | 0 | 0.05921 | 5.2757 | 0 | 0 | 0 | 62.4974 | off_peak | 728.5126 |  |  | 7.9 | 0 | 92.1 | 329.7196 | 0
5365 | 760.4 | 708.693 | 30.5 | 112.5351 | 112.5351 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 647.8649 | 0 | 0.05921 | 5.3396 | 0 | 0 | 0 | 112.5351 | off_peak | 647.8649 |  |  | 14.8 | 0 | 85.2 | 600.895 | 0
5366 | 777.5 | 739.369 | 30.5 | 117.4062 | 117.4062 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 660.0938 | 0 | 0.05921 | 5.7169 | 0 | 0 | 0 | 117.4062 | off_peak | 660.0938 |  |  | 15.1 | 0 | 84.9 | 671.2027 | 0
5367 | 743.47 | 680.759 | 30.4 | 108.1391 | 108.1391 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 635.3309 | 0 | 0.05921 | 6.1709 | 0 | 0 | 0 | 108.1391 | off_peak | 635.3309 |  |  | 14.55 | 0 | 85.45 | 667.3172 | 0
5368 | 774.87 | 588.193 | 30.2 | 93.5035 | 93.5035 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 18.9814 | 693.7289 | 0 | 0.05921 | 6.7541 | 0 | 0 | 0 | 93.5035 | off_peak | 681.3665 | 0 | 100 | 12.07 | 0 | 87.93 | 631.529 | 0
5369 | 744.69 | 311.873 | 29.8 | 49.6504 | 49.6504 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18.9814 | 695.0396 | 0 | 0.05921 | 7.3215 | 0 | 0 | 0 | 49.6504 | off_peak | 695.0396 |  |  | 6.67 | 0 | 93.33 | 363.5155 | 0
5370 | 673.61 | 188.72 | 29.3 | 30.0994 | 30.0994 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18.9814 | 643.5106 | 0 | 0.05921 | 7.7948 | 0 | 0 | 0 | 30.0994 | off_peak | 643.5106 |  |  | 4.47 | 0 | 95.53 | 234.6182 | 0
5371 | 607.67 | 51.6548 | 29.1 | 8.2446 | 8.2446 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18.9814 | 599.4254 | 0 | 0.05921 | 8.2495 | 0 | 0 | 0 | 8.2446 | off_peak | 599.4254 |  |  | 1.36 | 0 | 98.64 | 68.0136 | 0
5372 | 611.21 | 0 | 28.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18.9814 | 611.21 | 0 | 0.05921 | 8.6153 | 0 | 0 | 0 | 0 | off_peak | 611.21 |  |  | 0 | 0 | 100 | 0 | 0
5373 | 575.83 | 0 | 28.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18.9814 | 575.83 | 0 | 0.05921 | 8.8285 | 0 | 0 | 0 | 0 | off_peak | 575.83 |  |  | 0 | 0 | 100 | 0 | 0
5374 | 603.19 | 0 | 28.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18.9814 | 603.19 | 0 | 0.05921 | 9.0178 | 0 | 0 | 0 | 0 | off_peak | 603.19 |  |  | 0 | 0 | 100 | 0 | 0
5375 | 586.71 | 0 | 28.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18.9814 | 586.71 | 0 | 0.05921 | 9.2863 | 0 | 0 | 0 | 0 | off_peak | 586.71 |  |  | 0 | 0 | 100 | 0 | 0
5376 | 565.19 | 0 | 28.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18.9814 | 565.19 | 0 | 0.05921 | 9.3149 | 0 | 0 | 0 | 0 | off_peak | 565.19 |  |  | 0 | 0 | 100 | 0 | 0
5377 | 594.72 | 0 | 28.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18.9814 | 594.72 | 0 | 0.05921 | 8.9503 | 0 | 0 | 0 | 0 | off_peak | 594.72 |  |  | 0 | 0 | 100 | 0 | 0
5378 | 562.95 | 0 | 28 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18.9814 | 562.95 | 0 | 0.05921 | 8.66 | 0 | 0 | 0 | 0 | off_peak | 562.95 |  |  | 0 | 0 | 100 | 0 | 0
5379 | 595.26 | 0 | 27.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18.9814 | 595.26 | 0 | 0.05921 | 8.2627 | 0 | 0 | 0 | 0 | off_peak | 595.26 |  |  | 0 | 0 | 100 | 0 | 0
5380 | 552.52 | 0 | 27.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18.9814 | 552.52 | 0 | 0.05921 | 7.7919 | 0 | 0 | 0 | 0 | off_peak | 552.52 |  |  | 0 | 0 | 100 | 0 | 0
5381 | 595.12 | 0 | 27.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18.9814 | 595.12 | 0 | 0.05921 | 7.168 | 0 | 0 | 0 | 0 | off_peak | 595.12 |  |  | 0 | 0 | 100 | 0 | 0
5382 | 617.97 | 0 | 28.1 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 30.5453 | 630.3324 | 0 | 0.05921 | 6.5936 | 0 | 0 | 0 | 0 | off_peak | 617.97 | 0 | 100 | 0 | 0 | 100 | 0 | 0
5383 | 651.79 | 71.9521 | 28.5 | 11.5094 | 11.5094 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30.5453 | 640.2806 | 0 | 0.05921 | 6.0678 | 0 | 0 | 0 | 11.5094 | off_peak | 640.2806 |  |  | 1.77 | 0 | 98.23 | 69.8362 | 0
5384 | 706.59 | 267.199 | 28.9 | 42.6785 | 42.6785 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30.5453 | 663.9115 | 0 | 0.05921 | 5.6961 | 0 | 0 | 0 | 42.6785 | off_peak | 663.9115 |  |  | 6.04 | 0 | 93.96 | 243.0997 | 0
5385 | 735.49 | 463.567 | 29.3 | 73.9353 | 73.9353 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30.5453 | 661.5547 | 0 | 0.05921 | 5.4443 | 0 | 0 | 0 | 73.9353 | off_peak | 661.5547 |  |  | 10.05 | 0 | 89.95 | 402.5266 | 0
5386 | 738.34 | 655.569 | 29.7 | 104.4052 | 104.4052 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30.5453 | 633.9348 | 0 | 0.05921 | 5.285 | 0 | 0 | 0 | 104.4052 | off_peak | 633.9348 |  |  | 14.14 | 0 | 85.86 | 551.7815 | 0
5387 | 705.95 | 809.712 | 29.9 | 128.8594 | 128.8594 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30.5453 | 577.0906 | 0 | 0.05921 | 5.1736 | 0 | 0 | 0 | 128.8594 | off_peak | 577.0906 |  |  | 18.25 | 0 | 81.75 | 666.6622 | 0
5388 | 731.61 | 900.346 | 30.1 | 143.1781 | 143.1781 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 42.1093 | 600.7942 | 0 | 0.05921 | 5.1352 | 0 | 0 | 0 | 143.1781 | off_peak | 588.4319 | 0 | 100 | 19.57 | 0 | 80.43 | 735.2494 | 0
5389 | 715.28 | 807.315 | 30.1 | 128.3838 | 128.3838 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 42.1093 | 586.8962 | 0 | 0.05921 | 5.1364 | 0 | 0 | 0 | 128.3838 | off_peak | 586.8962 |  |  | 17.95 | 0 | 82.05 | 659.4306 | 0
5390 | 707.07 | 830.059 | 30 | 132.0491 | 132.0491 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 42.1093 | 575.0209 | 0 | 0.05921 | 5.4608 | 0 | 0 | 0 | 132.0491 | off_peak | 575.0209 |  |  | 18.68 | 0 | 81.32 | 721.0874 | 0
5391 | 723.52 | 791.395 | 29.9 | 125.9444 | 125.9444 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 53.6732 | 609.9379 | 0 | 0.05921 | 5.9287 | 0 | 0 | 0 | 125.9444 | off_peak | 597.5756 | 0 | 100 | 17.41 | 0 | 82.59 | 746.6839 | 0
5392 | 696.51 | 639.371 | 29.8 | 101.7883 | 101.7883 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 53.6732 | 594.7217 | 0 | 0.05921 | 6.5085 | 0 | 0 | 0 | 101.7883 | off_peak | 594.7217 |  |  | 14.61 | 0 | 85.39 | 662.4938 | 0
5393 | 691.62 | 447.881 | 29.6 | 71.3552 | 71.3552 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 53.6732 | 620.2648 | 0 | 0.05921 | 7.0567 | 0 | 0 | 0 | 71.3552 | off_peak | 620.2648 |  |  | 10.32 | 0 | 89.68 | 503.5336 | 0
5394 | 644.09 | 237.414 | 29.3 | 37.8657 | 37.8657 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 53.6732 | 606.2243 | 0 | 0.05921 | 7.5259 | 0 | 0 | 0 | 37.8657 | off_peak | 606.2243 |  |  | 5.88 | 0 | 94.12 | 284.9746 | 0
5395 | 608.21 | 51.0324 | 29.2 | 8.1422 | 8.1422 | 0 | 0 | 8.7006 | 8.7006 | 0 | 0 | 0 | 61.8119 | 608.7684 | 0 | 0.05921 | 7.9036 | 0 | 0 | 0 | 8.1422 | off_peak | 600.0678 | 0 | 100 | 1.34 | 0 | 98.66 | 64.3529 | 0
5396 | 580.3 | 0 | 29.1 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 73.3758 | 592.6624 | 0 | 0.05921 | 8.3066 | 0 | 0 | 0 | 0 | off_peak | 580.3 | 0 | 100 | 0 | 0 | 100 | 0 | 0
5397 | 568.89 | 0 | 29.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 73.3758 | 568.89 | 0 | 0.05921 | 8.5733 | 0 | 0 | 0 | 0 | off_peak | 568.89 |  |  | 0 | 0 | 100 | 0 | 0
5398 | 587.77 | 0 | 28.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 73.3758 | 587.77 | 0 | 0.05921 | 8.6059 | 0 | 0 | 0 | 0 | off_peak | 587.77 |  |  | 0 | 0 | 100 | 0 | 0
5399 | 544.6 | 0 | 28.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 73.3758 | 544.6 | 0 | 0.05921 | 8.525 | 0 | 0 | 0 | 0 | off_peak | 544.6 |  |  | 0 | 0 | 100 | 0 | 0
5400 | 565.68 | 0 | 28.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 73.3758 | 565.68 | 0 | 0.05921 | 8.4572 | 0 | 0 | 0 | 0 | off_peak | 565.68 |  |  | 0 | 0 | 100 | 0 | 0
5401 | 570.59 | 0 | 28.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 73.3758 | 570.59 | 0 | 0.05921 | 8.4116 | 0 | 0 | 0 | 0 | off_peak | 570.59 |  |  | 0 | 0 | 100 | 0 | 0
5402 | 584.88 | 0 | 27.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 73.3758 | 584.88 | 0 | 0.05921 | 8.1811 | 0 | 0 | 0 | 0 | off_peak | 584.88 |  |  | 0 | 0 | 100 | 0 | 0
5403 | 525.58 | 0 | 27.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 73.3758 | 525.58 | 0 | 0.05921 | 7.7026 | 0 | 0 | 0 | 0 | off_peak | 525.58 |  |  | 0 | 0 | 100 | 0 | 0
5404 | 557.86 | 0 | 27 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 73.3758 | 557.86 | 0 | 0.05921 | 7.256 | 0 | 0 | 0 | 0 | off_peak | 557.86 |  |  | 0 | 0 | 100 | 0 | 0
5405 | 570.12 | 0 | 27 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 73.3758 | 570.12 | 0 | 0.05921 | 6.6269 | 0 | 0 | 0 | 0 | off_peak | 570.12 |  |  | 0 | 0 | 100 | 0 | 0
5406 | 670.8 | 0 | 27.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 73.3758 | 670.8 | 0 | 0.05921 | 6.0144 | 0 | 0 | 0 | 0 | off_peak | 670.8 |  |  | 0 | 0 | 100 | 0 | 0
5407 | 691.73 | 44.1727 | 27.5 | 7.0916 | 7.0916 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 73.3758 | 684.6384 | 0 | 0.05921 | 5.5754 | 0 | 0 | 0 | 7.0916 | off_peak | 684.6384 |  |  | 1.03 | 0 | 98.97 | 39.5387 | 0
5408 | 821.02 | 252.427 | 27.9 | 40.4662 | 40.4662 | 0 | 0 | 0.79843 | 0.79843 | 0 | 0 | 0 | 74.1227 | 781.3522 | 0 | 0.05921 | 5.2789 | 0 | 0 | 0 | 40.4662 | off_peak | 780.5538 | 0 | 100 | 4.93 | 0 | 95.07 | 213.6168 | 0
5409 | 817.97 | 472.761 | 28.2 | 75.705 | 75.705 | 0 | 0 | 0.051567 | 0.051567 | 0 | 0 | 0 | 74.1709 | 742.3166 | 0 | 0.05921 | 5.1335 | 0 | 0 | 0 | 75.705 | off_peak | 742.265 | 0 | 100 | 9.26 | 0 | 90.74 | 388.6318 | 0
5410 | 847.97 | 661.823 | 28.4 | 105.903 | 105.903 | 0 | 0 | 0.0033305 | 0.0033305 | 0 | 0 | 0 | 74.174 | 742.0703 | 0 | 0.05921 | 5.0691 | 0 | 0 | 0 | 105.903 | off_peak | 742.067 | 0 | 100 | 12.49 | 0 | 87.51 | 536.8295 | 0
5411 | 807.7 | 727.136 | 28.4 | 116.3542 | 116.3542 | 0 | 0 | 0.0002151 | 0.0002151 | 0 | 0 | 0 | 74.1742 | 691.346 | 0 | 0.05921 | 5.2426 | 0 | 0 | 0 | 116.3542 | off_peak | 691.3458 | 0 | 100 | 14.41 | 0 | 85.59 | 609.9982 | 0
5412 | 923.51 | 825.597 | 28.3 | 132.1578 | 132.1578 | 0 | 0 | 1.3893e-05 | 1.3893e-05 | 0 | 0 | 0 | 74.1743 | 791.3522 | 0 | 0.05921 | 5.5112 | 0 | 0 | 0 | 132.1578 | off_peak | 791.3522 | 0 | 100 | 14.31 | 0 | 85.69 | 728.3425 | 0
5413 | 839.33 | 917.327 | 28.2 | 146.895 | 146.895 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1743 | 692.435 | 0 | 0.088511 | 5.6505 | 0 | 0 | 0 | 146.895 | on_peak | 692.435 |  |  | 17.5 | 0 | 82.5 | 830.0291 | 0
5414 | 905.79 | 857.404 | 28.1 | 137.3493 | 137.3493 | 0 | 0 | 0 | 0 | -8.3931e-07 | -8.3931e-07 | 0 | 74.1743 | 768.4407 | 0 | 0.088511 | 5.9128 | -8.3931e-07 | 0 | 8.9726e-07 | 137.3493 | on_peak | 768.4407 |  |  | 15.16 | 0 | 84.84 | 812.1184 | 0
5415 | 886.76 | 781.598 | 28 | 125.2514 | 125.2514 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1743 | 761.5086 | 0 | 0.088511 | 6.2967 | 8.3931e-07 | 0 | 0 | 125.2514 | on_peak | 761.5086 |  |  | 14.12 | 0 | 85.88 | 788.6711 | 0
5416 | 812.9 | 629.762 | 27.9 | 100.9563 | 100.9563 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1743 | 711.9437 | 0 | 0.088511 | 6.7636 | 0 | 0 | 0 | 100.9563 | on_peak | 711.9437 |  |  | 12.42 | 0 | 87.58 | 682.832 | 0
5417 | 888.59 | 438.394 | 27.7 | 70.3295 | 70.3295 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1743 | 818.2605 | 0 | 0.088511 | 7.3539 | 0 | 0 | 0 | 70.3295 | on_peak | 818.2605 |  |  | 7.91 | 0 | 92.09 | 517.1974 | 0
5418 | 870.27 | 229.017 | 27.6 | 36.7535 | 36.7535 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1743 | 833.5165 | 0 | 0.088511 | 7.9325 | 0 | 0 | 0 | 36.7535 | on_peak | 833.5165 |  |  | 4.22 | 0 | 95.78 | 291.5479 | 0
5419 | 843.4 | 46.7174 | 27.5 | 7.5001 | 7.5001 | 0 | 0 | 0 | 0 | 62.4453 | 62.4453 | 0 | 7.4174 | 773.4546 | 0 | 0.088511 | 8.2517 | 0 | 0 | 0 | 7.5001 | on_peak | 773.4546 |  |  | 0.89 | 7.4 | 91.71 | 61.8888 | 0
5420 | 873.66 | 0 | 27.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 873.66 | 0 | 0.088511 | 8.5946 | 0 | 0 | 0 | 0 | on_peak | 873.66 |  |  | 0 | 0 | 100 | 0 | 0
5421 | 836.44 | 0 | 27.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 836.44 | 0 | 0.088511 | 8.7805 | 0 | 0 | 0 | 0 | on_peak | 836.44 |  |  | 0 | 0 | 100 | 0 | 0
5422 | 826.97 | 0 | 27.8 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 18.9814 | 839.3324 | 0 | 0.05921 | 8.9952 | 0 | 0 | 0 | 0 | off_peak | 826.97 | 0 | 100 | 0 | 0 | 100 | 0 | 0
5423 | 820.53 | 0 | 27.9 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 30.5453 | 832.8924 | 0 | 0.05921 | 9.211 | 0 | 0 | 0 | 0 | off_peak | 820.53 | 0 | 100 | 0 | 0 | 100 | 0 | 0
5424 | 775.34 | 0 | 27.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30.5453 | 775.34 | 0 | 0.05921 | 9.0862 | 0 | 0 | 0 | 0 | off_peak | 775.34 |  |  | 0 | 0 | 100 | 0 | 0
5425 | 721.9 | 0 | 27.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30.5453 | 721.9 | 0 | 0.05921 | 8.8964 | 0 | 0 | 0 | 0 | off_peak | 721.9 |  |  | 0 | 0 | 100 | 0 | 0
5426 | 646.4 | 0 | 27.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30.5453 | 646.4 | 0 | 0.05921 | 8.6169 | 0 | 0 | 0 | 0 | off_peak | 646.4 |  |  | 0 | 0 | 100 | 0 | 0
5427 | 622.67 | 0 | 27.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30.5453 | 622.67 | 0 | 0.05921 | 8.1499 | 0 | 0 | 0 | 0 | off_peak | 622.67 |  |  | 0 | 0 | 100 | 0 | 0
5428 | 635.04 | 0 | 27.9 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 42.1093 | 647.4024 | 0 | 0.05921 | 7.5797 | 0 | 0 | 0 | 0 | off_peak | 635.04 | 0 | 100 | 0 | 0 | 100 | 0 | 0
5429 | 623.66 | 0 | 27.9 | 0 | 0 | 0 | 0 | 8.7006 | 8.7006 | 0 | 0 | 0 | 50.2479 | 632.3606 | 0 | 0.05921 | 6.9449 | 0 | 0 | 0 | 0 | off_peak | 623.66 | 0 | 100 | 0 | 0 | 100 | 0 | 0
5430 | 688.83 | 0 | 28.1 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 61.8119 | 701.1924 | 0 | 0.05921 | 6.2979 | 0 | 0 | 0 | 0 | off_peak | 688.83 | 0 | 100 | 0 | 0 | 100 | 0 | 0
5431 | 747.4 | 63.7952 | 28.4 | 10.2083 | 10.2083 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 73.3758 | 749.5541 | 0 | 0.05921 | 5.8582 | 0 | 0 | 0 | 10.2083 | off_peak | 737.1917 | 0 | 100 | 1.37 | 0 | 98.63 | 59.8029 | 0
5432 | 794.33 | 242.723 | 28.7 | 38.7974 | 38.7974 | 0 | 0 | 0.79843 | 0.79843 | 0 | 0 | 0 | 74.1227 | 756.3311 | 0 | 0.05921 | 5.5041 | 0 | 0 | 0 | 38.7974 | off_peak | 755.5326 | 0 | 100 | 4.88 | 0 | 95.12 | 213.5447 | 0
5433 | 840.34 | 456.742 | 28.9 | 72.9534 | 72.9534 | 0 | 0 | 0.051567 | 0.051567 | 0 | 0 | 0 | 74.1709 | 767.4382 | 0 | 0.05921 | 5.2731 | 0 | 0 | 0 | 72.9534 | off_peak | 767.3866 | 0 | 100 | 8.68 | 0 | 91.32 | 384.6886 | 0
5434 | 858.84 | 462.325 | 29 | 73.8181 | 73.8181 | 0 | 0 | 0.0033305 | 0.0033305 | 0 | 0 | 0 | 74.174 | 785.0252 | 0 | 0.05921 | 5.1785 | 0 | 0 | 0 | 73.8181 | off_peak | 785.0219 | 0 | 100 | 8.6 | 0 | 91.4 | 382.2676 | 0
5435 | 811.21 | 188.135 | 29 | 30.039 | 30.039 | 0 | 0 | 0.0002151 | 0.0002151 | 0 | 0 | 0 | 74.1742 | 781.1712 | 0 | 0.05921 | 5.2889 | 0 | 0 | 0 | 30.039 | off_peak | 781.171 | 0 | 100 | 3.7 | 0 | 96.3 | 158.872 | 0
5436 | 888.19 | 475.838 | 29 | 75.9757 | 75.9757 | 0 | 0 | 1.3893e-05 | 1.3893e-05 | 0 | 0 | 0 | 74.1743 | 812.2143 | 0 | 0.05921 | 5.5786 | 0 | 0 | 0 | 75.9757 | off_peak | 812.2143 | 0 | 100 | 8.55 | 0 | 91.45 | 423.8402 | 0
5437 | 865.88 | 853.631 | 29 | 136.2969 | 136.2969 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1743 | 729.5831 | 0 | 0.088511 | 5.6306 | 0 | 0 | 0 | 136.2969 | on_peak | 729.5831 |  |  | 15.74 | 0 | 84.26 | 767.4378 | 0
5438 | 923.43 | 420.598 | 28.9 | 67.1802 | 67.1802 | 0 | 0 | 0 | 0 | 62.4453 | 62.4453 | 0 | 7.4174 | 793.8045 | 0 | 0.088511 | 5.8902 | 0 | 0 | 0 | 67.1802 | on_peak | 793.8045 |  |  | 7.28 | 6.76 | 85.96 | 395.707 | 0
5439 | 938.04 | 507.391 | 28.8 | 81.0729 | 81.0729 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 856.9671 | 0 | 0.088511 | 6.2616 | 0 | 0 | 0 | 81.0729 | on_peak | 856.9671 |  |  | 8.64 | 0 | 91.36 | 507.6428 | 0
5440 | 810.47 | 639.311 | 28.7 | 102.1889 | 102.1889 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 708.2811 | 0 | 0.088511 | 6.778 | 0 | 0 | 0 | 102.1889 | on_peak | 708.2811 |  |  | 12.61 | 0 | 87.39 | 692.6329 | 0
5441 | 832.5 | 412.118 | 28.7 | 65.8738 | 65.8738 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 766.6262 | 0 | 0.088511 | 7.3895 | 0 | 0 | 0 | 65.8738 | on_peak | 766.6262 |  |  | 7.91 | 0 | 92.09 | 486.7744 | 0
5442 | 828.51 | 226.539 | 28.5 | 36.2369 | 36.2369 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 792.2731 | 0 | 0.088511 | 7.8893 | 0 | 0 | 0 | 36.2369 | on_peak | 792.2731 |  |  | 4.37 | 0 | 95.63 | 285.884 | 0
5443 | 790.57 | 47.887 | 28.4 | 7.6627 | 7.6627 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 782.9073 | 0 | 0.088511 | 8.4489 | 0 | 0 | 0 | 7.6627 | on_peak | 782.9073 |  |  | 0.97 | 0 | 99.03 | 64.7417 | 0
5444 | 829.48 | 0 | 28.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 829.48 | 0 | 0.088511 | 8.6474 | 0 | 0 | 0 | 0 | on_peak | 829.48 |  |  | 0 | 0 | 100 | 0 | 0
5445 | 821.18 | 0 | 28.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 821.18 | 0 | 0.088511 | 8.6274 | 0 | 0 | 0 | 0 | on_peak | 821.18 |  |  | 0 | 0 | 100 | 0 | 0
5446 | 764.39 | 0 | 28.3 | 0 | 0 | 0 | 0 | 8.7006 | 8.7006 | 0 | 0 | 0 | 15.5561 | 773.0906 | 0 | 0.05921 | 8.6039 | 0 | 0 | 0 | 0 | off_peak | 764.39 | 0 | 100 | 0 | 0 | 100 | 0 | 0
5447 | 799.73 | 0 | 28.3 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 27.12 | 812.0924 | 0 | 0.05921 | 8.545 | 0 | 0 | 0 | 0 | off_peak | 799.73 | 0 | 100 | 0 | 0 | 100 | 0 | 0
5448 | 790.62 | 0 | 28.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27.12 | 790.62 | 0 | 0.05921 | 8.4654 | 0 | 0 | 0 | 0 | off_peak | 790.62 |  |  | 0 | 0 | 100 | 0 | 0
5449 | 745.87 | 0 | 28.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27.12 | 745.87 | 0 | 0.05921 | 8.4749 | 0 | 0 | 0 | 0 | off_peak | 745.87 |  |  | 0 | 0 | 100 | 0 | 0
5450 | 659.5 | 0 | 28 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27.12 | 659.5 | 0 | 0.05921 | 8.2775 | 0 | 0 | 0 | 0 | off_peak | 659.5 |  |  | 0 | 0 | 100 | 0 | 0
5451 | 626.72 | 0 | 28 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 38.684 | 639.0824 | 0 | 0.05921 | 7.8401 | 0 | 0 | 0 | 0 | off_peak | 626.72 | 0 | 100 | 0 | 0 | 100 | 0 | 0
5452 | 609.08 | 0 | 28 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 50.2479 | 621.4424 | 0 | 0.05921 | 7.2581 | 0 | 0 | 0 | 0 | off_peak | 609.08 | 0 | 100 | 0 | 0 | 100 | 0 | 0
5453 | 620.18 | 0 | 28.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50.2479 | 620.18 | 0 | 0.05921 | 6.5663 | 0 | 0 | 0 | 0 | off_peak | 620.18 |  |  | 0 | 0 | 100 | 0 | 0
5454 | 712.16 | 0 | 28.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50.2479 | 712.16 | 0 | 0.05921 | 5.9398 | 0 | 0 | 0 | 0 | off_peak | 712.16 |  |  | 0 | 0 | 100 | 0 | 0
5455 | 757.8 | 52.7814 | 28.5 | 8.4428 | 8.4428 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 61.8119 | 761.7195 | 0 | 0.05921 | 5.5192 | 0 | 0 | 0 | 8.4428 | off_peak | 749.3572 | 0 | 100 | 1.11 | 0 | 98.89 | 46.5979 | 0
5456 | 818.02 | 227.172 | 28.9 | 36.2852 | 36.2852 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 73.3758 | 794.0972 | 0 | 0.05921 | 5.198 | 0 | 0 | 0 | 36.2852 | off_peak | 781.7348 | 0 | 100 | 4.44 | 0 | 95.56 | 188.6119 | 0
5457 | 854.29 | 479.337 | 29.2 | 76.4785 | 76.4785 | 0 | 0 | 0.79843 | 0.79843 | 0 | 0 | 0 | 74.1227 | 778.6099 | 0 | 0.05921 | 5.0076 | 0 | 0 | 0 | 76.4785 | off_peak | 777.8115 | 0 | 100 | 8.95 | 0 | 91.05 | 382.9716 | 0
5458 | 832.37 | 570.345 | 29.5 | 90.8991 | 90.8991 | 0 | 0 | 0.051567 | 0.051567 | 0 | 0 | 0 | 74.1709 | 741.5225 | 0 | 0.05921 | 4.9075 | 0 | 0 | 0 | 90.8991 | off_peak | 741.4709 | 0 | 100 | 10.92 | 0 | 89.08 | 446.0915 | 0
5459 | 879.13 | 701.386 | 29.9 | 111.6202 | 111.6202 | 0 | 0 | 0.0033305 | 0.0033305 | 0 | 0 | 0 | 74.174 | 767.5131 | 0 | 0.05921 | 4.9974 | 0 | 0 | 0 | 111.6202 | off_peak | 767.5098 | 0 | 100 | 12.7 | 0 | 87.3 | 557.8085 | 0
5460 | 895.73 | 741.559 | 30.2 | 117.8837 | 117.8837 | 0 | 0 | 0.0002151 | 0.0002151 | 0 | 0 | 0 | 74.1742 | 777.8465 | 0 | 0.05921 | 5.2518 | 0 | 0 | 0 | 117.8837 | off_peak | 777.8463 | 0 | 100 | 13.16 | 0 | 86.84 | 619.0965 | 0
5461 | 840.08 | 425.751 | 30.4 | 67.6309 | 67.6309 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1742 | 772.4491 | 0 | 0.088511 | 5.2974 | 0 | 0 | 0 | 67.6309 | on_peak | 772.4491 |  |  | 8.05 | 0 | 91.95 | 358.267 | 0
5462 | 873.59 | 465.752 | 30.5 | 73.9579 | 73.9579 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1742 | 799.6321 | 0 | 0.088511 | 5.51 | 0 | 0 | 0 | 73.9579 | on_peak | 799.6321 |  |  | 8.47 | 0 | 91.53 | 407.5108 | 0
5463 | 872.32 | 410.769 | 30.5 | 65.227 | 65.227 | 0 | 0 | 0 | 0 | 62.4453 | 62.4453 | 0 | 7.4174 | 744.6477 | 0 | 0.088511 | 5.8605 | 0 | 0 | 0 | 65.227 | on_peak | 744.6477 |  |  | 7.48 | 7.16 | 85.36 | 382.2632 | 0
5464 | 799.63 | 623.95 | 30.3 | 99.1513 | 99.1513 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 700.4787 | 0 | 0.088511 | 6.4511 | 0 | 0 | 0 | 99.1513 | on_peak | 700.4787 |  |  | 12.4 | 0 | 87.6 | 639.633 | 0
5465 | 810.87 | 449.864 | 29.9 | 71.5924 | 71.5924 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 739.2776 | 0 | 0.088511 | 6.9715 | 0 | 0 | 0 | 71.5924 | on_peak | 739.2776 |  |  | 8.83 | 0 | 91.17 | 499.1057 | 0
5466 | 818.23 | 236.922 | 29.5 | 37.7596 | 37.7596 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 780.4704 | 0 | 0.088511 | 7.3899 | 0 | 0 | 0 | 37.7596 | on_peak | 780.4704 |  |  | 4.61 | 0 | 95.39 | 279.0388 | 0
5467 | 792.26 | 47.8552 | 29.2 | 7.6353 | 7.6353 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 784.6247 | 0 | 0.088511 | 7.8463 | 0 | 0 | 0 | 7.6353 | on_peak | 784.6247 |  |  | 0.96 | 0 | 99.04 | 59.9087 | 0
5468 | 827.41 | 0 | 28.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 827.41 | 0 | 0.088511 | 8.1472 | 0 | 0 | 0 | 0 | on_peak | 827.41 |  |  | 0 | 0 | 100 | 0 | 0
5469 | 784.84 | 0 | 28.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 784.84 | 0 | 0.088511 | 8.029 | 0 | 0 | 0 | 0 | on_peak | 784.84 |  |  | 0 | 0 | 100 | 0 | 0
5470 | 758.35 | 0 | 28.7 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 18.9814 | 770.7124 | 0 | 0.05921 | 7.9183 | 0 | 0 | 0 | 0 | off_peak | 758.35 | 0 | 100 | 0 | 0 | 100 | 0 | 0
5471 | 806.42 | 0 | 28.6 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 30.5453 | 818.7824 | 0 | 0.05921 | 7.9199 | 0 | 0 | 0 | 0 | off_peak | 806.42 | 0 | 100 | 0 | 0 | 100 | 0 | 0
5472 | 775.08 | 0 | 28.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30.5453 | 775.08 | 0 | 0.05921 | 7.8753 | 0 | 0 | 0 | 0 | off_peak | 775.08 |  |  | 0 | 0 | 100 | 0 | 0
5473 | 706.22 | 0 | 28.5 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 42.1093 | 718.5824 | 0 | 0.05921 | 7.7131 | 0 | 0 | 0 | 0 | off_peak | 706.22 | 0 | 100 | 0 | 0 | 100 | 0 | 0
5474 | 628.84 | 0 | 28.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 42.1093 | 628.84 | 0 | 0.05921 | 7.3065 | 0 | 0 | 0 | 0 | off_peak | 628.84 |  |  | 0 | 0 | 100 | 0 | 0
5475 | 609.94 | 0 | 28.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 42.1093 | 609.94 | 0 | 0.05921 | 6.8551 | 0 | 0 | 0 | 0 | off_peak | 609.94 |  |  | 0 | 0 | 100 | 0 | 0
5476 | 579.14 | 0 | 28.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 42.1093 | 579.14 | 0 | 0.05921 | 6.2966 | 0 | 0 | 0 | 0 | off_peak | 579.14 |  |  | 0 | 0 | 100 | 0 | 0
5477 | 594.73 | 0 | 28.4 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 53.6732 | 607.0924 | 0 | 0.05921 | 5.8115 | 0 | 0 | 0 | 0 | off_peak | 594.73 | 0 | 100 | 0 | 0 | 100 | 0 | 0
5478 | 688.36 | 0 | 28.6 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 65.2371 | 700.7224 | 0 | 0.05921 | 5.1794 | 0 | 0 | 0 | 0 | off_peak | 688.36 | 0 | 100 | 0 | 0 | 100 | 0 | 0
5479 | 745.07 | 68.8592 | 28.9 | 10.9986 | 10.9986 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 65.2371 | 734.0714 | 0 | 0.05921 | 4.7536 | 0 | 0 | 0 | 10.9986 | off_peak | 734.0714 |  |  | 1.48 | 0 | 98.52 | 52.2823 | 0
5480 | 860.47 | 264.34 | 29.3 | 42.1602 | 42.1602 | 0 | 0 | 8.9371 | 8.9371 | 0 | 0 | 0 | 73.597 | 827.2469 | 0 | 0.05921 | 4.4784 | 0 | 0 | 0 | 42.1602 | off_peak | 818.3098 | 0 | 100 | 4.9 | 0 | 95.1 | 188.8115 | 0
5481 | 913.02 | 475.231 | 29.5 | 75.7402 | 75.7402 | 0 | 0 | 0.57721 | 0.57721 | 0 | 0 | 0 | 74.137 | 837.857 | 0 | 0.05921 | 4.3343 | 0 | 0 | 0 | 75.7402 | off_peak | 837.2798 | 0 | 100 | 8.3 | 0 | 91.7 | 328.2807 | 0
5482 | 894.15 | 558.789 | 29.7 | 88.9922 | 88.9549 | 0 | 0.037279 | 0.037279 | 0 | 0 | 0 | 0 | 74.1718 | 805.1951 | 0 | 0.05921 | 4.2753 | 0 | 0 | 0.034872 | 88.9549 | off_peak | 805.1951 | 100 | 0 | 9.95 | 0 | 90.05 | 380.3078 | 0
5483 | 852.98 | 674.118 | 29.9 | 107.2807 | 107.2783 | 0 | 0.0024077 | 0.0024077 | 0 | 0 | 0 | 0 | 74.1741 | 745.7017 | 0 | 0.05921 | 4.4528 | 0 | 0 | 0.037124 | 107.2783 | off_peak | 745.7017 | 100 | 0 | 12.58 | 0 | 87.42 | 477.6838 | 0
5484 | 948.93 | 790.449 | 30.1 | 125.7017 | 125.7017 | 0 | 0 | 0.0001555 | 0.0001555 | 0 | 0 | 0 | 74.1742 | 823.2285 | 0 | 0.05921 | 4.8004 | 0 | 0 | 0.037124 | 125.7017 | off_peak | 823.2283 | 0 | 100 | 13.25 | 0 | 86.75 | 603.4192 | 0
5485 | 915.7 | 717.883 | 30.1 | 114.1618 | 114.1618 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1742 | 801.5382 | 0 | 0.088511 | 4.8613 | 0 | 0 | 0.037124 | 114.1618 | on_peak | 801.5382 |  |  | 12.47 | 0 | 87.53 | 554.9743 | 0
5486 | 928.17 | 873.261 | 30.1 | 138.8709 | 138.8709 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1742 | 789.2991 | 0 | 0.088511 | 4.9721 | 0 | 0 | 0.037124 | 138.8709 | on_peak | 789.2991 |  |  | 14.96 | 0 | 85.04 | 690.4745 | 0
5487 | 972.24 | 788.157 | 30 | 125.3832 | 125.3832 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1742 | 846.8568 | 0 | 0.088511 | 5.1737 | 0 | 0 | 0.037124 | 125.3832 | on_peak | 846.8568 |  |  | 12.9 | 0 | 87.1 | 648.6924 | 0
5488 | 900.47 | 634.129 | 29.9 | 100.9168 | 100.9168 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1742 | 799.5532 | 0 | 0.088511 | 5.6746 | 0 | 0 | 0.037124 | 100.9168 | on_peak | 799.5532 |  |  | 11.21 | 0 | 88.79 | 572.6616 | 0
5489 | 873.75 | 432.429 | 29.7 | 68.8682 | 68.8682 | 0 | 0 | 0 | 0 | 0.034726 | 0.034726 | 0 | 74.1371 | 804.8471 | 0 | 0.088511 | 6.4077 | 0.034726 | 0 | 0 | 68.9029 | on_peak | 804.8471 |  |  | 7.88 | 0 | 92.11 | 441.5059 | 0
5490 | 890.09 | 139.662 | 29.5 | 22.2587 | 22.2587 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1371 | 867.8313 | 0 | 0.088511 | 7.0286 | 0 | 0 | 0 | 22.2587 | on_peak | 867.8313 |  |  | 2.5 | 0 | 97.5 | 156.4476 | 0
5491 | 817.23 | 18.05 | 29.3 | 2.8788 | 2.8788 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1371 | 814.3512 | 0 | 0.088511 | 7.7496 | 0 | 0 | 0 | 2.8788 | on_peak | 814.3512 |  |  | 0.35 | 0 | 99.65 | 22.3098 | 0
5492 | 893.97 | 0 | 29.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1371 | 893.97 | 0 | 0.088511 | 7.9341 | 0 | 0 | 0 | 0 | on_peak | 893.97 |  |  | 0 | 0 | 100 | 0 | 0
5493 | 868.36 | 0 | 29.1 | 0 | 0 | 0 | 0 | 0 | 0 | 62.4106 | 62.4106 | 0 | 7.4174 | 805.9494 | 0 | 0.088511 | 7.8248 | 0 | 0 | 0 | 0 | on_peak | 805.9494 |  |  | 0 | 7.19 | 92.81 | 0 | 0
5494 | 802.27 | 0 | 29.1 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 18.9814 | 814.6324 | 0 | 0.05921 | 7.5385 | 0 | 0 | 0 | 0 | off_peak | 802.27 | 0 | 100 | 0 | 0 | 100 | 0 | 0
5495 | 835.78 | 0 | 29 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18.9814 | 835.78 | 0 | 0.05921 | 7.3968 | 0 | 0 | 0 | 0 | off_peak | 835.78 |  |  | 0 | 0 | 100 | 0 | 0
5496 | 795.45 | 0 | 28.8 | 0 | 0 | 0 | 0 | 8.7006 | 8.7006 | 0 | 0 | 0 | 27.12 | 804.1506 | 0 | 0.05921 | 7.1678 | 0 | 0 | 0 | 0 | off_peak | 795.45 | 0 | 100 | 0 | 0 | 100 | 0 | 0
5497 | 756.98 | 0 | 28.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27.12 | 756.98 | 0 | 0.05921 | 7.0782 | 0 | 0 | 0 | 0 | off_peak | 756.98 |  |  | 0 | 0 | 100 | 0 | 0
5498 | 711.05 | 0 | 28.6 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 38.684 | 723.4124 | 0 | 0.05921 | 6.974 | 0 | 0 | 0 | 0 | off_peak | 711.05 | 0 | 100 | 0 | 0 | 100 | 0 | 0
5499 | 621.96 | 0 | 28.5 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 50.2479 | 634.3224 | 0 | 0.05921 | 6.6098 | 0 | 0 | 0 | 0 | off_peak | 621.96 | 0 | 100 | 0 | 0 | 100 | 0 | 0
5500 | 657.38 | 0 | 28.5 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 61.8119 | 669.7424 | 0 | 0.05921 | 6.1081 | 0 | 0 | 0 | 0 | off_peak | 657.38 | 0 | 100 | 0 | 0 | 100 | 0 | 0
5501 | 641.62 | 0 | 28.5 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 73.3758 | 653.9824 | 0 | 0.05921 | 5.4833 | 0 | 0 | 0 | 0 | off_peak | 641.62 | 0 | 100 | 0 | 0 | 100 | 0 | 0
5502 | 741.98 | 0 | 28.6 | 0 | 0 | 0 | 0 | 0.79843 | 0.79843 | 0 | 0 | 0 | 74.1227 | 742.7784 | 0 | 0.05921 | 5.001 | 0 | 0 | 0 | 0 | off_peak | 741.98 | 0 | 100 | 0 | 0 | 100 | 0 | 0
5503 | 824.71 | 67.4604 | 29.1 | 10.7673 | 10.7673 | 0 | 0 | 0.051567 | 0.051567 | 0 | 0 | 0 | 74.1709 | 813.9943 | 0 | 0.05921 | 4.6145 | 0 | 0 | 0 | 10.7673 | off_peak | 813.9427 | 0 | 100 | 1.31 | 0 | 98.69 | 49.6852 | 0
5504 | 839.56 | 264.347 | 29.5 | 42.1305 | 42.1305 | 0 | 0 | 0.0033305 | 0.0033305 | 0 | 0 | 0 | 74.174 | 797.4329 | 0 | 0.05921 | 4.3323 | 0 | 0 | 0 | 42.1305 | off_peak | 797.4295 | 0 | 100 | 5.02 | 0 | 94.98 | 182.522 | 0
5505 | 918.22 | 472.933 | 29.9 | 75.2637 | 75.2637 | 0 | 0 | 0.0002151 | 0.0002151 | 0 | 0 | 0 | 74.1742 | 842.9566 | 0 | 0.05921 | 4.1422 | 0 | 0 | 0 | 75.2637 | off_peak | 842.9563 | 0 | 100 | 8.2 | 0 | 91.8 | 311.7554 | 0
5506 | 880.15 | 617.057 | 30.2 | 98.0919 | 98.0919 | 0 | 0 | 1.3893e-05 | 1.3893e-05 | 0 | 0 | 0 | 74.1743 | 782.0581 | 0 | 0.05921 | 4.098 | 0 | 0 | 0 | 98.0919 | off_peak | 782.0581 | 0 | 100 | 11.14 | 0 | 88.86 | 401.9813 | 0
5507 | 844.63 | 503.91 | 30.5 | 80.0171 | 80.0171 | 0 | 0 | 8.9726e-07 | 8.9726e-07 | 0 | 0 | 0 | 74.1743 | 764.6129 | 0 | 0.05921 | 4.3275 | 0 | 0 | 0 | 80.0171 | off_peak | 764.6129 | 0 | 100 | 9.47 | 0 | 90.53 | 346.2753 | 0
5508 | 924.29 | 612.166 | 30.6 | 97.1716 | 97.1716 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1743 | 827.1184 | 0 | 0.05921 | 4.6471 | 0 | 0 | 0 | 97.1716 | off_peak | 827.1184 |  |  | 10.51 | 0 | 89.49 | 451.5656 | 0
5509 | 875.66 | 671.396 | 30.7 | 106.5343 | 106.5343 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1743 | 769.1257 | 0 | 0.088511 | 4.7578 | 0 | 0 | 0 | 106.5343 | on_peak | 769.1257 |  |  | 12.17 | 0 | 87.83 | 506.8732 | 0
5510 | 908.86 | 876.127 | 30.6 | 139.0712 | 139.0712 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1743 | 769.7888 | 0 | 0.088511 | 4.8945 | 0 | 0 | 0 | 139.0712 | on_peak | 769.7888 |  |  | 15.3 | 0 | 84.7 | 680.6788 | 0
5511 | 953.14 | 225.888 | 30.5 | 35.8693 | 35.8693 | 0 | 0 | 0 | 0 | 62.4453 | 62.4453 | 0 | 7.4174 | 854.8254 | 0 | 0.088511 | 5.1283 | 0 | 0 | 0 | 35.8693 | on_peak | 854.8254 |  |  | 3.76 | 6.55 | 89.69 | 183.9477 | 0
5512 | 869.78 | 588.183 | 30.4 | 93.4333 | 93.4333 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 776.3467 | 0 | 0.088511 | 5.4097 | 0 | 0 | 0 | 93.4333 | on_peak | 776.3467 |  |  | 10.74 | 0 | 89.26 | 505.4463 | 0
5513 | 872.38 | 397.852 | 30.1 | 63.2687 | 63.2687 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 809.1113 | 0 | 0.088511 | 5.8204 | 0 | 0 | 0 | 63.2687 | on_peak | 809.1113 |  |  | 7.25 | 0 | 92.75 | 368.2504 | 0
5514 | 896.18 | 224.629 | 29.8 | 35.7611 | 35.7611 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 860.4189 | 0 | 0.088511 | 6.1756 | 0 | 0 | 0 | 35.7611 | on_peak | 860.4189 |  |  | 3.99 | 0 | 96.01 | 220.8446 | 0
5515 | 842.31 | 20.9654 | 29.5 | 3.3414 | 3.3414 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 838.9686 | 0 | 0.088511 | 6.7045 | 0 | 0 | 0 | 3.3414 | on_peak | 838.9686 |  |  | 0.4 | 0 | 99.6 | 22.4024 | 0
5516 | 855.96 | 0 | 29.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 855.96 | 0 | 0.088511 | 7.0274 | 0 | 0 | 0 | 0 | on_peak | 855.96 |  |  | 0 | 0 | 100 | 0 | 0
5517 | 879.64 | 0 | 29 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 879.64 | 0 | 0.088511 | 7.2654 | 0 | 0 | 0 | 0 | on_peak | 879.64 |  |  | 0 | 0 | 100 | 0 | 0
5518 | 812.34 | 0 | 28.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 812.34 | 0 | 0.05921 | 7.4918 | 0 | 0 | 0 | 0 | off_peak | 812.34 |  |  | 0 | 0 | 100 | 0 | 0
5519 | 835.44 | 0 | 28.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 835.44 | 0 | 0.05921 | 7.5046 | 0 | 0 | 0 | 0 | off_peak | 835.44 |  |  | 0 | 0 | 100 | 0 | 0
5520 | 805.32 | 0 | 28.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 805.32 | 0 | 0.05921 | 7.3859 | 0 | 0 | 0 | 0 | off_peak | 805.32 |  |  | 0 | 0 | 100 | 0 | 0
5521 | 714 | 0 | 28.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 714 | 0 | 0.05921 | 7.3166 | 0 | 0 | 0 | 0 | off_peak | 714 |  |  | 0 | 0 | 100 | 0 | 0
5522 | 607.72 | 0 | 28.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 607.72 | 0 | 0.05921 | 7.2098 | 0 | 0 | 0 | 0 | off_peak | 607.72 |  |  | 0 | 0 | 100 | 0 | 0
5523 | 611.31 | 0 | 28.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 611.31 | 0 | 0.05921 | 6.8545 | 0 | 0 | 0 | 0 | off_peak | 611.31 |  |  | 0 | 0 | 100 | 0 | 0
5524 | 622.87 | 0 | 28.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 622.87 | 0 | 0.05921 | 6.4108 | 0 | 0 | 0 | 0 | off_peak | 622.87 |  |  | 0 | 0 | 100 | 0 | 0
5525 | 635.54 | 0 | 28.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 635.54 | 0 | 0.05921 | 5.7987 | 0 | 0 | 0 | 0 | off_peak | 635.54 |  |  | 0 | 0 | 100 | 0 | 0
5526 | 699.62 | 0 | 28.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 699.62 | 0 | 0.05921 | 5.2883 | 0 | 0 | 0 | 0 | off_peak | 699.62 |  |  | 0 | 0 | 100 | 0 | 0
5527 | 763.43 | 46.0441 | 28.9 | 7.3544 | 7.3544 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 18.9814 | 768.438 | 0 | 0.05921 | 4.9156 | 0 | 0 | 0 | 7.3544 | off_peak | 756.0756 | 0 | 100 | 0.96 | 0 | 99.04 | 36.1511 | 0
5528 | 753.31 | 238.699 | 29.4 | 38.0567 | 38.0567 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 30.5453 | 727.6157 | 0 | 0.05921 | 4.6381 | 0 | 0 | 0 | 38.0567 | off_peak | 715.2533 | 0 | 100 | 5.05 | 0 | 94.95 | 176.5094 | 0
5529 | 788.44 | 217.703 | 29.7 | 34.6712 | 34.6712 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 42.1093 | 766.1312 | 0 | 0.05921 | 4.3873 | 0 | 0 | 0 | 34.6712 | off_peak | 753.7688 | 0 | 100 | 4.4 | 0 | 95.6 | 152.1141 | 0
5530 | 787.86 | 147.687 | 30.1 | 23.486 | 23.486 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 53.6732 | 776.7363 | 0 | 0.05921 | 4.2673 | 0 | 0 | 0 | 23.486 | off_peak | 764.374 | 0 | 100 | 2.98 | 0 | 97.02 | 100.221 | 0
5531 | 758.63 | 176.572 | 30.4 | 28.0486 | 28.0486 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 53.6732 | 730.5814 | 0 | 0.05921 | 4.2504 | 0 | 0 | 0 | 28.0486 | off_peak | 730.5814 |  |  | 3.7 | 0 | 96.3 | 119.2178 | 0
5532 | 821.31 | 416.725 | 30.7 | 66.1242 | 66.1242 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 53.6732 | 755.1858 | 0 | 0.05921 | 4.3366 | 0 | 0 | 0 | 66.1242 | off_peak | 755.1858 |  |  | 8.05 | 0 | 91.95 | 286.753 | 0
5533 | 746.07 | 851.472 | 30.9 | 135.0087 | 135.0087 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 53.6732 | 611.0613 | 0 | 0.05921 | 4.4627 | 0 | 0 | 0 | 135.0087 | off_peak | 611.0613 |  |  | 18.1 | 0 | 81.9 | 602.5065 | 0
5534 | 715.21 | 750.569 | 30.9 | 119.0096 | 119.0096 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 53.6732 | 596.2004 | 0 | 0.05921 | 4.7341 | 0 | 0 | 0 | 119.0096 | off_peak | 596.2004 |  |  | 16.64 | 0 | 83.36 | 563.4069 | 0
5535 | 727.59 | 201.444 | 30.9 | 31.9408 | 31.9408 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 53.6732 | 695.6492 | 0 | 0.05921 | 5.1238 | 0 | 0 | 0 | 31.9408 | off_peak | 695.6492 |  |  | 4.39 | 0 | 95.61 | 163.6596 | 0
5536 | 744.77 | 22.8 | 30.7 | 3.6178 | 3.6178 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 53.6732 | 741.1522 | 0 | 0.05921 | 5.7546 | 0 | 0 | 0 | 3.6178 | off_peak | 741.1522 |  |  | 0.49 | 0 | 99.51 | 20.819 | 0
5537 | 733.79 | 84.2078 | 30.4 | 13.3765 | 13.3765 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 53.6732 | 720.4135 | 0 | 0.05921 | 6.3604 | 0 | 0 | 0 | 13.3765 | off_peak | 720.4135 |  |  | 1.82 | 0 | 98.18 | 85.0799 | 0
5538 | 643.84 | 55.0103 | 29.9 | 8.7545 | 8.7545 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 53.6732 | 635.0855 | 0 | 0.05921 | 6.738 | 0 | 0 | 0 | 8.7545 | off_peak | 635.0855 |  |  | 1.36 | 0 | 98.64 | 58.9878 | 0
5539 | 630.79 | 21.8838 | 29.6 | 3.4865 | 3.4865 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 53.6732 | 627.3035 | 0 | 0.05921 | 7.1478 | 0 | 0 | 0 | 3.4865 | off_peak | 627.3035 |  |  | 0.55 | 0 | 99.45 | 24.9206 | 0
5540 | 600.92 | 0 | 29 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 53.6732 | 600.92 | 0 | 0.05921 | 7.6276 | 0 | 0 | 0 | 0 | off_peak | 600.92 |  |  | 0 | 0 | 100 | 0 | 0
5541 | 571.67 | 0 | 28.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 53.6732 | 571.67 | 0 | 0.05921 | 8.0352 | 0 | 0 | 0 | 0 | off_peak | 571.67 |  |  | 0 | 0 | 100 | 0 | 0
5542 | 569.22 | 0 | 28.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 53.6732 | 569.22 | 0 | 0.05921 | 8.2424 | 0 | 0 | 0 | 0 | off_peak | 569.22 |  |  | 0 | 0 | 100 | 0 | 0
5543 | 592.7 | 0 | 28.4 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 65.2371 | 605.0624 | 0 | 0.05921 | 8.2908 | 0 | 0 | 0 | 0 | off_peak | 592.7 | 0 | 100 | 0 | 0 | 100 | 0 | 0
5544 | 585.25 | 0 | 28.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 65.2371 | 585.25 | 0 | 0.05921 | 8.0229 | 0 | 0 | 0 | 0 | off_peak | 585.25 |  |  | 0 | 0 | 100 | 0 | 0
5545 | 568.92 | 0 | 28.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 65.2371 | 568.92 | 0 | 0.05921 | 7.9049 | 0 | 0 | 0 | 0 | off_peak | 568.92 |  |  | 0 | 0 | 100 | 0 | 0
5546 | 587.55 | 0 | 28.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 65.2371 | 587.55 | 0 | 0.05921 | 7.7691 | 0 | 0 | 0 | 0 | off_peak | 587.55 |  |  | 0 | 0 | 100 | 0 | 0
5547 | 572.22 | 0 | 28.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 65.2371 | 572.22 | 0 | 0.05921 | 7.2745 | 0 | 0 | 0 | 0 | off_peak | 572.22 |  |  | 0 | 0 | 100 | 0 | 0
5548 | 584.48 | 0 | 28 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 65.2371 | 584.48 | 0 | 0.05921 | 6.7221 | 0 | 0 | 0 | 0 | off_peak | 584.48 |  |  | 0 | 0 | 100 | 0 | 0
5549 | 599.48 | 0 | 27.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 65.2371 | 599.48 | 0 | 0.05921 | 6.1142 | 0 | 0 | 0 | 0 | off_peak | 599.48 |  |  | 0 | 0 | 100 | 0 | 0
5550 | 658.9 | 0 | 28 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 65.2371 | 658.9 | 0 | 0.05921 | 5.6009 | 0 | 0 | 0 | 0 | off_peak | 658.9 |  |  | 0 | 0 | 100 | 0 | 0
5551 | 711.36 | 37.2692 | 28.3 | 5.9659 | 5.9659 | 0 | 0 | 8.9371 | 8.9371 | 0 | 0 | 0 | 73.597 | 714.3312 | 0 | 0.05921 | 5.1619 | 0 | 0 | 0 | 5.9659 | off_peak | 705.3941 | 0 | 100 | 0.84 | 0 | 99.16 | 30.7951 | 0
5552 | 748.49 | 86.9221 | 28.7 | 13.8938 | 13.8938 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 73.597 | 734.5962 | 0 | 0.05921 | 4.8489 | 0 | 0 | 0 | 13.8938 | off_peak | 734.5962 |  |  | 1.86 | 0 | 98.14 | 67.3702 | 0
5553 | 755.96 | 402.277 | 29.2 | 64.1835 | 64.1835 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 73.597 | 691.7765 | 0 | 0.05921 | 4.6117 | 0 | 0 | 0 | 64.1835 | off_peak | 691.7765 |  |  | 8.49 | 0 | 91.51 | 295.9968 | 0
5554 | 729.46 | 585.295 | 29.8 | 93.1793 | 93.1793 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 73.597 | 636.2807 | 0 | 0.05921 | 4.4751 | 0 | 0 | 0 | 93.1793 | off_peak | 636.2807 |  |  | 12.77 | 0 | 87.23 | 416.986 | 0
5555 | 725.02 | 451.504 | 30.4 | 71.7217 | 71.7217 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 73.597 | 653.2983 | 0 | 0.05921 | 4.4511 | 0 | 0 | 0 | 71.7217 | off_peak | 653.2983 |  |  | 9.89 | 0 | 90.11 | 319.2374 | 0
5556 | 729.86 | 108.3 | 30.9 | 17.172 | 17.172 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 73.597 | 712.688 | 0 | 0.05921 | 4.5015 | 0 | 0 | 0 | 17.172 | off_peak | 712.688 |  |  | 2.35 | 0 | 97.65 | 77.2997 | 0
5557 | 704.83 | 196.321 | 31.3 | 31.0827 | 31.0827 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 73.597 | 673.7473 | 0 | 0.05921 | 4.5752 | 0 | 0 | 0 | 31.0827 | off_peak | 673.7473 |  |  | 4.41 | 0 | 95.59 | 142.2094 | 0
5558 | 703.77 | 201.616 | 31.4 | 31.9093 | 31.9093 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 73.597 | 671.8607 | 0 | 0.05921 | 4.8034 | 0 | 0 | 0 | 31.9093 | off_peak | 671.8607 |  |  | 4.53 | 0 | 95.47 | 153.272 | 0
5559 | 724.07 | 264.812 | 31.5 | 41.8957 | 41.8957 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 73.597 | 682.1743 | 0 | 0.05921 | 5.1746 | 0 | 0 | 0 | 41.8957 | off_peak | 682.1743 |  |  | 5.79 | 0 | 94.21 | 216.7924 | 0
5560 | 733.73 | 573.761 | 31.3 | 90.8412 | 90.8412 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 73.597 | 642.8888 | 0 | 0.05921 | 5.7609 | 0 | 0 | 0 | 90.8412 | off_peak | 642.8888 |  |  | 12.38 | 0 | 87.62 | 523.3245 | 0
5561 | 708.87 | 192.311 | 31 | 30.4814 | 30.4814 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 73.597 | 678.3886 | 0 | 0.05921 | 6.2295 | 0 | 0 | 0 | 30.4814 | off_peak | 678.3886 |  |  | 4.3 | 0 | 95.7 | 189.8853 | 0
5562 | 653.22 | 211.854 | 30.4 | 33.6532 | 33.6532 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 73.597 | 619.5668 | 0 | 0.05921 | 6.4889 | 0 | 0 | 0 | 33.6532 | off_peak | 619.5668 |  |  | 5.15 | 0 | 94.85 | 218.3713 | 0
5563 | 608.26 | 36.1024 | 30 | 5.7433 | 5.7433 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 73.597 | 602.5167 | 0 | 0.05921 | 6.751 | 0 | 0 | 0 | 5.7433 | off_peak | 602.5167 |  |  | 0.94 | 0 | 99.06 | 38.7732 | 0
5564 | 595.99 | 0 | 29.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 73.597 | 595.99 | 0 | 0.05921 | 6.97 | 0 | 0 | 0 | 0 | off_peak | 595.99 |  |  | 0 | 0 | 100 | 0 | 0
5565 | 579.25 | 0 | 29.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 73.597 | 579.25 | 0 | 0.05921 | 7.0431 | 0 | 0 | 0 | 0 | off_peak | 579.25 |  |  | 0 | 0 | 100 | 0 | 0
5566 | 612.23 | 0 | 28.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 73.597 | 612.23 | 0 | 0.05921 | 7.198 | 0 | 0 | 0 | 0 | off_peak | 612.23 |  |  | 0 | 0 | 100 | 0 | 0
5567 | 600.95 | 0 | 28.8 | 0 | 0 | 0 | 0 | 0.57721 | 0.57721 | 0 | 0 | 0 | 74.137 | 601.5272 | 0 | 0.05921 | 7.2891 | 0 | 0 | 0 | 0 | off_peak | 600.95 | 0 | 100 | 0 | 0 | 100 | 0 | 0
5568 | 611.96 | 0 | 28.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.137 | 611.96 | 0 | 0.05921 | 7.2999 | 0 | 0 | 0 | 0 | off_peak | 611.96 |  |  | 0 | 0 | 100 | 0 | 0
5569 | 608.47 | 0 | 28.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.137 | 608.47 | 0 | 0.05921 | 7.3974 | 0 | 0 | 0 | 0 | off_peak | 608.47 |  |  | 0 | 0 | 100 | 0 | 0
5570 | 598.98 | 0 | 28.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.137 | 598.98 | 0 | 0.05921 | 7.3981 | 0 | 0 | 0 | 0 | off_peak | 598.98 |  |  | 0 | 0 | 100 | 0 | 0
5571 | 633.97 | 0 | 28.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.137 | 633.97 | 0 | 0.05921 | 7.0577 | 0 | 0 | 0 | 0 | off_peak | 633.97 |  |  | 0 | 0 | 100 | 0 | 0
5572 | 583.16 | 0 | 28 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.137 | 583.16 | 0 | 0.05921 | 6.5921 | 0 | 0 | 0 | 0 | off_peak | 583.16 |  |  | 0 | 0 | 100 | 0 | 0
5573 | 631.72 | 0 | 27.9 | 0 | 0 | 0 | 0 | 0.037279 | 0.037279 | 0 | 0 | 0 | 74.1718 | 631.7573 | 0 | 0.05921 | 6.1149 | 0 | 0 | 0 | 0 | off_peak | 631.72 | 0 | 100 | 0 | 0 | 100 | 0 | 0
5574 | 753.78 | 0 | 28.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1718 | 753.78 | 0 | 0.05921 | 0 | 0 | 0 | 0 | 0 | off_peak | 753.78 |  |  | 0 | 0 | 100 | 0 | 0
5575 | 771.99 | 39.1664 | 28.7 | 6.2604 | 6.2604 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1718 | 765.7296 | 0 | 0.05921 | 0 | 0 | 0 | 0 | 6.2604 | off_peak | 765.7296 |  |  | 0.81 | 0 | 99.19 | 0 | 0
5576 | 825.67 | 174.935 | 29.2 | 27.911 | 27.911 | 0 | 0 | 0.0024077 | 0.0024077 | 0 | 0 | 0 | 74.1741 | 797.7614 | 0 | 0.05921 | 0 | 0 | 0 | 0 | 27.911 | off_peak | 797.759 | 0 | 100 | 3.38 | 0 | 96.62 | 0 | 0
5577 | 907.7 | 445.804 | 29.6 | 71.0243 | 71.0241 | 0 | 0.0001555 | 0.0001555 | 0 | 0 | 0 | 0 | 74.1742 | 836.6759 | 0 | 0.05921 | 0 | 0 | 0 | 0.00014546 | 71.0241 | off_peak | 836.6759 | 100 | 0 | 7.82 | 0 | 92.18 | 0 | 0
5578 | 937.46 | 637.928 | 30.1 | 101.4469 | 101.4469 | 0 | 0 | 1.0043e-05 | 1.0043e-05 | 0 | 0 | 0 | 74.1743 | 836.0131 | 0 | 0.05921 | 0 | 0 | 0 | 0.00014546 | 101.4469 | off_peak | 836.0131 | 0 | 100 | 10.82 | 0 | 89.18 | 0 | 0
5579 | 877.2 | 780.808 | 30.4 | 124.0319 | 124.0319 | 0 | 6.4865e-07 | 6.4865e-07 | 0 | 0 | 0 | 0 | 74.1743 | 753.1681 | 0 | 0.05921 | 0 | 0 | 0 | 0.00014607 | 124.0319 | off_peak | 753.1681 | 100 | 0 | 14.14 | 0 | 85.86 | 0 | 0
5580 | 929.37 | 630.987 | 30.7 | 100.1223 | 100.1223 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1743 | 829.2477 | 0 | 0.05921 | 0 | 0 | 0 | 0.00014611 | 100.1223 | off_peak | 829.2477 |  |  | 10.77 | 0 | 89.23 | 0 | 0
5581 | 865.59 | 761.977 | 30.9 | 120.8184 | 120.8184 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1743 | 744.7716 | 0 | 0.088511 | 0 | 0 | 0 | 0.00014611 | 120.8184 | on_peak | 744.7716 |  |  | 13.96 | 0 | 86.04 | 0 | 0
5582 | 902.12 | 833.828 | 30.9 | 132.211 | 132.211 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1743 | 769.909 | 0 | 0.088511 | 0 | 0 | 0 | 0.00014611 | 132.211 | on_peak | 769.909 |  |  | 14.66 | 0 | 85.34 | 0 | 0
5583 | 946.15 | 730.953 | 30.8 | 115.9419 | 115.9419 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1743 | 830.2081 | 0 | 0.088511 | 0 | 0 | 0 | 0.00014611 | 115.9419 | on_peak | 830.2081 |  |  | 12.25 | 0 | 87.75 | 0 | 0
5584 | 894.5 | 535.734 | 30.7 | 85.008 | 85.008 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1743 | 809.492 | 0 | 0.088511 | 0 | 0 | 0 | 0.00014611 | 85.008 | on_peak | 809.492 |  |  | 9.5 | 0 | 90.5 | 0 | 0
5585 | 889.1 | 261.674 | 30.4 | 41.5671 | 41.5671 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1743 | 847.5329 | 0 | 0.088511 | 0 | 0 | 0 | 0.00014611 | 41.5671 | on_peak | 847.5329 |  |  | 4.68 | 0 | 95.32 | 0 | 0
5586 | 887.99 | 152.44 | 30 | 24.2508 | 24.2508 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1743 | 863.7392 | 0 | 0.088511 | 0 | 0 | 0 | 0.00014611 | 24.2508 | on_peak | 863.7392 |  |  | 2.73 | 0 | 97.27 | 0 | 0
5587 | 832.15 | 25.0266 | 29.7 | 3.9857 | 3.9857 | 0 | 0 | 0 | 0 | 61.6793 | 61.6793 | 0 | 8.2363 | 766.485 | 0 | 0.088511 | 0 | 0 | 0 | 0.00014611 | 3.9857 | on_peak | 766.485 |  |  | 0.48 | 7.41 | 92.11 | 0 | 0
5588 | 899.98 | 0 | 29.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0.76596 | 0.76596 | 0 | 7.4174 | 899.214 | 0 | 0.088511 | 0 | 0.00013667 | 0 | 0 | 0.00013667 | on_peak | 899.214 |  |  | 0 | 0.09 | 99.91 | 0 | 0
5589 | 871.84 | 0 | 29.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 871.84 | 0 | 0.088511 | 0 | 0 | 0 | 0 | 0 | on_peak | 871.84 |  |  | 0 | 0 | 100 | 0 | 0
5590 | 869.1 | 0 | 29.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 869.1 | 0 | 0.05921 | 0 | 0 | 0 | 0 | 0 | off_peak | 869.1 |  |  | 0 | 0 | 100 | 0 | 0
5591 | 847.59 | 0 | 29.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 847.59 | 0 | 0.05921 | 0 | 0 | 0 | 0 | 0 | off_peak | 847.59 |  |  | 0 | 0 | 100 | 0 | 0
5592 | 799.36 | 0 | 29 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 799.36 | 0 | 0.05921 | 0 | 0 | 0 | 0 | 0 | off_peak | 799.36 |  |  | 0 | 0 | 100 | 0 | 0
5593 | 752.98 | 0 | 28.9 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 18.9814 | 765.3424 | 0 | 0.05921 | 0 | 0 | 0 | 0 | 0 | off_peak | 752.98 | 0 | 100 | 0 | 0 | 100 | 0 | 0
5594 | 643.07 | 0 | 28.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18.9814 | 643.07 | 0 | 0.05921 | 0 | 0 | 0 | 0 | 0 | off_peak | 643.07 |  |  | 0 | 0 | 100 | 0 | 0
5595 | 611.43 | 0 | 28.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18.9814 | 611.43 | 0 | 0.05921 | 0 | 0 | 0 | 0 | 0 | off_peak | 611.43 |  |  | 0 | 0 | 100 | 0 | 0
5596 | 624.09 | 0 | 28.8 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 30.5453 | 636.4524 | 0 | 0.05921 | 0 | 0 | 0 | 0 | 0 | off_peak | 624.09 | 0 | 100 | 0 | 0 | 100 | 0 | 0
5597 | 643.72 | 0 | 28.9 | 0 | 0 | 0 | 0 | 8.7006 | 8.7006 | 0 | 0 | 0 | 38.684 | 652.4206 | 0 | 0.05921 | 0 | 0 | 0 | 0 | 0 | off_peak | 643.72 | 0 | 100 | 0 | 0 | 100 | 0 | 0
5598 | 724.31 | 0 | 29 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 50.2479 | 736.6724 | 0 | 0.05921 | 5.9781 | 0 | 0 | 0 | 0 | off_peak | 724.31 | 0 | 100 | 0 | 0 | 100 | 0 | 0
5599 | 806.95 | 60.2634 | 29.4 | 9.608 | 9.608 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 61.8119 | 809.7043 | 0 | 0.05921 | 5.4827 | 0 | 0 | 0 | 9.608 | off_peak | 797.342 | 0 | 100 | 1.19 | 0 | 98.81 | 52.6782 | 0
5600 | 844.24 | 239.027 | 29.8 | 38.0533 | 38.0533 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 73.3758 | 818.5491 | 0 | 0.05921 | 5.1795 | 0 | 0 | 0 | 38.0533 | off_peak | 806.1867 | 0 | 100 | 4.51 | 0 | 95.49 | 197.0971 | 0
5601 | 892.61 | 403.3 | 30.1 | 64.1351 | 64.1351 | 0 | 0 | 0.79843 | 0.79843 | 0 | 0 | 0 | 74.1227 | 829.2734 | 0 | 0.05921 | 4.9898 | 0 | 0 | 0 | 64.1351 | off_peak | 828.4749 | 0 | 100 | 7.19 | 0 | 92.81 | 320.0228 | 0
5602 | 919 | 527.938 | 30.4 | 83.8633 | 83.8633 | 0 | 0 | 0.051567 | 0.051567 | 0 | 0 | 0 | 74.1709 | 835.1882 | 0 | 0.05921 | 4.8992 | 0 | 0 | 0 | 83.8633 | off_peak | 835.1367 | 0 | 100 | 9.13 | 0 | 90.87 | 410.8645 | 0
5603 | 852.9 | 795.268 | 30.7 | 126.1898 | 126.1898 | 0 | 0 | 0.0033305 | 0.0033305 | 0 | 0 | 0 | 74.174 | 726.7136 | 0 | 0.05921 | 5.0702 | 0 | 0 | 0 | 126.1898 | off_peak | 726.7102 | 0 | 100 | 14.8 | 0 | 85.2 | 639.8054 | 0
5604 | 955.43 | 861.407 | 30.9 | 136.5839 | 136.5839 | 0 | 0 | 0.0002151 | 0.0002151 | 0 | 0 | 0 | 74.1742 | 818.8463 | 0 | 0.05921 | 5.3666 | 0 | 0 | 0 | 136.5839 | off_peak | 818.8461 | 0 | 100 | 14.3 | 0 | 85.7 | 732.9908 | 0
5605 | 893.79 | 816.178 | 30.9 | 129.4125 | 129.4125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1742 | 764.3775 | 0 | 0.088511 | 5.4776 | 0 | 0 | 0 | 129.4125 | on_peak | 764.3775 |  |  | 14.48 | 0 | 85.52 | 708.8669 | 0
5606 | 939.42 | 875.823 | 30.9 | 138.8697 | 138.8697 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1742 | 800.5503 | 0 | 0.088511 | 5.5884 | 0 | 0 | 0 | 138.8697 | on_peak | 800.5503 |  |  | 14.78 | 0 | 85.22 | 776.0545 | 0
5607 | 907.83 | 763.941 | 30.7 | 121.2189 | 121.2189 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1742 | 786.6111 | 0 | 0.088511 | 5.8602 | 0 | 0 | 0 | 121.2189 | on_peak | 786.6111 |  |  | 13.35 | 0 | 86.65 | 710.3621 | 0
5608 | 874.11 | 619.89 | 30.5 | 98.4338 | 98.4338 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1742 | 775.6762 | 0 | 0.088511 | 6.1984 | 0 | 0 | 0 | 98.4338 | on_peak | 775.6762 |  |  | 11.26 | 0 | 88.74 | 610.1347 | 0
5609 | 908.34 | 416.032 | 30.2 | 66.1355 | 66.1355 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1742 | 842.2045 | 0 | 0.088511 | 6.6042 | 0 | 0 | 0 | 66.1355 | on_peak | 842.2045 |  |  | 7.28 | 0 | 92.72 | 436.771 | 0
5610 | 922.14 | 192.042 | 29.9 | 30.562 | 30.562 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1742 | 891.578 | 0 | 0.088511 | 7.1484 | 0 | 0 | 0 | 30.562 | on_peak | 891.578 |  |  | 3.31 | 0 | 96.69 | 218.4686 | 0
5611 | 929.74 | 27.2295 | 29.8 | 4.335 | 4.335 | 0 | 0 | 0 | 0 | 26.191 | 26.191 | 0 | 46.1749 | 899.214 | 0 | 0.088511 | 7.6132 | 0 | 0 | 0 | 4.335 | on_peak | 899.214 |  |  | 0.47 | 2.82 | 96.72 | 33.0027 | 0
5612 | 916.78 | 0 | 29.6 | 0 | 0 | 0 | 0 | 0 | 0 | 36.2543 | 36.2543 | 0 | 7.4174 | 880.5257 | 0 | 0.088511 | 8.0291 | 0 | 0 | 0 | 0 | on_peak | 880.5257 |  |  | 0 | 3.95 | 96.05 | 0 | 0
5613 | 881.01 | 0 | 29.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 881.01 | 0 | 0.088511 | 8.2772 | 0 | 0 | 0 | 0 | on_peak | 881.01 |  |  | 0 | 0 | 100 | 0 | 0
5614 | 870.11 | 0 | 29.5 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 18.9814 | 882.4724 | 0 | 0.05921 | 8.6774 | 0 | 0 | 0 | 0 | off_peak | 870.11 | 0 | 100 | 0 | 0 | 100 | 0 | 0
5615 | 895.09 | 0 | 29.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18.9814 | 895.09 | 0 | 0.05921 | 8.8301 | 0 | 0 | 0 | 0 | off_peak | 895.09 |  |  | 0 | 0 | 100 | 0 | 0
5616 | 864.43 | 0 | 29.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18.9814 | 864.43 | 0 | 0.05921 | 9.0041 | 0 | 0 | 0 | 0 | off_peak | 864.43 |  |  | 0 | 0 | 100 | 0 | 0
5617 | 830.42 | 0 | 29.1 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 30.5453 | 842.7824 | 0 | 0.05921 | 8.9328 | 0 | 0 | 0 | 0 | off_peak | 830.42 | 0 | 100 | 0 | 0 | 100 | 0 | 0
5618 | 745.19 | 0 | 29 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30.5453 | 745.19 | 0 | 0.05921 | 8.6465 | 0 | 0 | 0 | 0 | off_peak | 745.19 |  |  | 0 | 0 | 100 | 0 | 0
5619 | 691.91 | 0 | 28.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30.5453 | 691.91 | 0 | 0.05921 | 8.1206 | 0 | 0 | 0 | 0 | off_peak | 691.91 |  |  | 0 | 0 | 100 | 0 | 0
5620 | 686.8 | 0 | 28.8 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 42.1093 | 699.1624 | 0 | 0.05921 | 7.442 | 0 | 0 | 0 | 0 | off_peak | 686.8 | 0 | 100 | 0 | 0 | 100 | 0 | 0
5621 | 679.4 | 0 | 28.8 | 0 | 0 | 0 | 0 | 8.7006 | 8.7006 | 0 | 0 | 0 | 50.2479 | 688.1006 | 0 | 0.05921 | 6.6356 | 0 | 0 | 0 | 0 | off_peak | 679.4 | 0 | 100 | 0 | 0 | 100 | 0 | 0
5622 | 759.29 | 0 | 28.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50.2479 | 759.29 | 0 | 0.05921 | 5.9727 | 0 | 0 | 0 | 0 | off_peak | 759.29 |  |  | 0 | 0 | 100 | 0 | 0
5623 | 844.38 | 44.2166 | 29.2 | 7.0548 | 7.0548 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 61.8119 | 849.6876 | 0 | 0.05921 | 5.4808 | 0 | 0 | 0 | 7.0548 | off_peak | 837.3252 | 0 | 100 | 0.84 | 0 | 99.16 | 38.666 | 0
5624 | 896.05 | 235.413 | 29.6 | 37.5054 | 37.5054 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 73.3758 | 870.907 | 0 | 0.05921 | 5.0947 | 0 | 0 | 0 | 37.5054 | off_peak | 858.5446 | 0 | 100 | 4.19 | 0 | 95.81 | 191.0804 | 0
5625 | 907.22 | 447.019 | 29.9 | 71.1396 | 71.1396 | 0 | 0 | 0.79843 | 0.79843 | 0 | 0 | 0 | 74.1227 | 836.8788 | 0 | 0.05921 | 4.8563 | 0 | 0 | 0 | 71.1396 | off_peak | 836.0804 | 0 | 100 | 7.84 | 0 | 92.16 | 345.4751 | 0
5626 | 917.46 | 636.267 | 30.1 | 101.1828 | 101.1828 | 0 | 0 | 0.051567 | 0.051567 | 0 | 0 | 0 | 74.1709 | 816.3288 | 0 | 0.05921 | 4.7756 | 0 | 0 | 0 | 101.1828 | off_peak | 816.2772 | 0 | 100 | 11.03 | 0 | 88.97 | 483.2107 | 0
5627 | 935.13 | 785.316 | 30.3 | 124.7938 | 124.7938 | 0 | 0 | 0.0033305 | 0.0033305 | 0 | 0 | 0 | 74.174 | 810.3395 | 0 | 0.05921 | 4.9151 | 0 | 0 | 0 | 124.7938 | off_peak | 810.3362 | 0 | 100 | 13.35 | 0 | 86.65 | 613.3716 | 0
5628 | 965.48 | 876.013 | 30.4 | 139.1553 | 139.1553 | 0 | 0 | 0.0002151 | 0.0002151 | 0 | 0 | 0 | 74.1742 | 826.3249 | 0 | 0.05921 | 5.2467 | 0 | 0 | 0 | 139.1553 | off_peak | 826.3247 | 0 | 100 | 14.41 | 0 | 85.59 | 730.1007 | 0
5629 | 901.57 | 905.315 | 30.5 | 143.7571 | 143.7571 | 0 | 0 | 1.3893e-05 | 1.3893e-05 | 0 | 0 | 0 | 74.1743 | 757.8129 | 0 | 0.088511 | 5.3312 | 0 | 0 | 0 | 143.7571 | on_peak | 757.8129 | 0 | 100 | 15.95 | 0 | 84.05 | 766.4027 | 0
5630 | 928.84 | 868.97 | 30.5 | 137.9858 | 137.9858 | 0 | 8.9726e-07 | 8.9726e-07 | 0 | 0 | 0 | 0 | 74.1743 | 790.8542 | 0 | 0.088511 | 5.4487 | 0 | 0 | 8.3931e-07 | 137.9858 | on_peak | 790.8542 | 100 | 0 | 14.86 | 0 | 85.14 | 751.8488 | 0
5631 | 959.62 | 765.787 | 30.4 | 121.6458 | 121.6458 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1743 | 837.9742 | 0 | 0.088511 | 5.6731 | 0 | 0 | 8.9352e-07 | 121.6458 | on_peak | 837.9742 |  |  | 12.68 | 0 | 87.32 | 690.1068 | 0
5632 | 919.08 | 607.761 | 30.3 | 96.5787 | 96.5787 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1743 | 822.5013 | 0 | 0.088511 | 6.2025 | 0 | 0 | 8.9352e-07 | 96.5787 | on_peak | 822.5013 |  |  | 10.51 | 0 | 89.49 | 599.0337 | 0
5633 | 900.78 | 356.379 | 30.1 | 56.6734 | 56.6734 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1743 | 844.1066 | 0 | 0.088511 | 6.6371 | 0 | 0 | 8.9374e-07 | 56.6734 | on_peak | 844.1066 |  |  | 6.29 | 0 | 93.71 | 376.1484 | 0
5634 | 953.64 | 70.0921 | 29.8 | 11.1587 | 11.1587 | 0 | 0 | 0 | 0 | 43.2672 | 43.2672 | 0 | 27.9196 | 899.214 | 0 | 0.088511 | 7.2607 | 0 | 0 | 8.9374e-07 | 11.1587 | on_peak | 899.214 |  |  | 1.17 | 4.54 | 94.29 | 81.0196 | 0
5635 | 892.87 | 22.6167 | 29.6 | 3.6032 | 0 | 0 | 3.6032 | 9.9473 | 6.344 | 0 | 0 | 0 | 37.2244 | 899.214 | 0 | 0.088511 | 7.8354 | 0 | 0 | 3.3705 | 0 | on_peak | 892.87 | 36.22 | 63.78 | 0 | 0 | 100 | 0 | 0
5636 | 915.73 | 0 | 29.4 | 0 | 0 | 0 | 0 | 0 | 0 | 16.516 | 16.516 | 0 | 19.5681 | 899.214 | 0 | 0.088511 | 8.2034 | 3.1528 | 0 | 0 | 3.1528 | on_peak | 899.214 |  |  | 0 | 1.8 | 98.2 | 25.8641 | 0
5637 | 910.58 | 0 | 29.3 | 0 | 0 | 0 | 0 | 0 | 0 | 11.366 | 11.366 | 0 | 7.4174 | 899.214 | 0 | 0.088511 | 8.55 | 0 | 0 | 0 | 0 | on_peak | 899.214 |  |  | 0 | 1.25 | 98.75 | 0 | 0
5638 | 852.32 | 0 | 29.2 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 18.9814 | 864.6824 | 0 | 0.05921 | 8.8436 | 0 | 0 | 0 | 0 | off_peak | 852.32 | 0 | 100 | 0 | 0 | 100 | 0 | 0
5639 | 896.5 | 0 | 29.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18.9814 | 896.5 | 0 | 0.05921 | 9.027 | 0 | 0 | 0 | 0 | off_peak | 896.5 |  |  | 0 | 0 | 100 | 0 | 0
5640 | 896.68 | 0 | 29 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18.9814 | 896.68 | 0 | 0.05921 | 9.1829 | 0 | 0 | 0 | 0 | off_peak | 896.68 |  |  | 0 | 0 | 100 | 0 | 0
5641 | 827.32 | 0 | 28.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18.9814 | 827.32 | 0 | 0.05921 | 9.0509 | 0 | 0 | 0 | 0 | off_peak | 827.32 |  |  | 0 | 0 | 100 | 0 | 0
5642 | 720.13 | 0 | 28.8 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 30.5453 | 732.4924 | 0 | 0.05921 | 8.7845 | 0 | 0 | 0 | 0 | off_peak | 720.13 | 0 | 100 | 0 | 0 | 100 | 0 | 0
5643 | 719.52 | 0 | 28.7 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 42.1093 | 731.8824 | 0 | 0.05921 | 8.2683 | 0 | 0 | 0 | 0 | off_peak | 719.52 | 0 | 100 | 0 | 0 | 100 | 0 | 0
5644 | 664.53 | 0 | 28.6 | 0 | 0 | 0 | 0 | 8.7006 | 8.7006 | 0 | 0 | 0 | 50.2479 | 673.2306 | 0 | 0.05921 | 7.5326 | 0 | 0 | 0 | 0 | off_peak | 664.53 | 0 | 100 | 0 | 0 | 100 | 0 | 0
5645 | 728.18 | 0 | 28.5 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 61.8119 | 740.5424 | 0 | 0.05921 | 6.8575 | 0 | 0 | 0 | 0 | off_peak | 728.18 | 0 | 100 | 0 | 0 | 100 | 0 | 0
5646 | 777.98 | 0 | 28.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 61.8119 | 777.98 | 0 | 0.05921 | 6.1225 | 0 | 0 | 0 | 0 | off_peak | 777.98 |  |  | 0 | 0 | 100 | 0 | 0
5647 | 817.8 | 46.4938 | 28.8 | 7.429 | 7.429 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 61.8119 | 810.371 | 0 | 0.05921 | 5.6026 | 0 | 0 | 0 | 7.429 | off_peak | 810.371 |  |  | 0.91 | 0 | 99.09 | 41.6217 | 0
5648 | 901.12 | 175.546 | 29.3 | 27.9982 | 27.9982 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 73.3758 | 885.4842 | 0 | 0.05921 | 5.2648 | 0 | 0 | 0 | 27.9982 | off_peak | 873.1218 | 0 | 100 | 3.11 | 0 | 96.89 | 147.4058 | 0
5649 | 863.54 | 427.936 | 29.6 | 68.1776 | 68.1776 | 0 | 0 | 0.79843 | 0.79843 | 0 | 0 | 0 | 74.1227 | 796.1608 | 0 | 0.05921 | 4.9866 | 0 | 0 | 0 | 68.1776 | off_peak | 795.3624 | 0 | 100 | 7.9 | 0 | 92.1 | 339.9741 | 0
5650 | 890.75 | 552.112 | 29.9 | 87.8644 | 87.8644 | 0 | 0 | 0.051567 | 0.051567 | 0 | 0 | 0 | 74.1709 | 802.9372 | 0 | 0.05921 | 4.8559 | 0 | 0 | 0 | 87.8644 | off_peak | 802.8856 | 0 | 100 | 9.86 | 0 | 90.14 | 426.6624 | 0
5651 | 882 | 611.056 | 30.2 | 97.138 | 97.1346 | 0 | 0.0033305 | 0.0033305 | 0 | 0 | 0 | 0 | 74.174 | 784.8654 | 0 | 0.05921 | 5.0053 | 0 | 0 | 0.0031154 | 97.1346 | off_peak | 784.8654 | 100 | 0 | 11.01 | 0 | 88.99 | 486.1834 | 0
5652 | 893.38 | 526.358 | 30.3 | 83.643 | 83.643 | 0 | 0 | 0.0002151 | 0.0002151 | 0 | 0 | 0 | 74.1742 | 809.7372 | 0 | 0.05921 | 5.3385 | 0 | 0 | 0.0031154 | 83.643 | off_peak | 809.737 | 0 | 100 | 9.36 | 0 | 90.64 | 446.5283 | 0
5653 | 836.89 | 635.942 | 30.4 | 101.0198 | 101.0198 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1742 | 735.8702 | 0 | 0.088511 | 5.508 | 0 | 0 | 0.0031154 | 101.0198 | on_peak | 735.8702 |  |  | 12.07 | 0 | 87.93 | 556.4196 | 0
5654 | 941.72 | 343.143 | 30.3 | 54.5285 | 54.5285 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1742 | 887.1915 | 0 | 0.088511 | 5.6529 | 0 | 0 | 0.0031154 | 54.5285 | on_peak | 887.1915 |  |  | 5.79 | 0 | 94.21 | 308.2453 | 0
5655 | 945.41 | 728.527 | 30.1 | 115.8545 | 115.8545 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1742 | 829.5555 | 0 | 0.088511 | 5.986 | 0 | 0 | 0.0031154 | 115.8545 | on_peak | 829.5555 |  |  | 12.25 | 0 | 87.75 | 693.5065 | 0
5656 | 859.73 | 576.535 | 29.8 | 91.7847 | 91.7847 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1742 | 767.9453 | 0 | 0.088511 | 6.5033 | 0 | 0 | 0.0031154 | 91.7847 | on_peak | 767.9453 |  |  | 10.68 | 0 | 89.32 | 596.9058 | 0
5657 | 860.68 | 387.607 | 29.6 | 61.7525 | 61.7525 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1742 | 798.9275 | 0 | 0.088511 | 6.9928 | 0 | 0 | 0.0031154 | 61.7525 | on_peak | 798.9275 |  |  | 7.17 | 0 | 92.83 | 431.8213 | 0
5658 | 850.29 | 181.042 | 29.2 | 28.8854 | 28.8854 | 0 | 0 | 0 | 0 | 62.4453 | 62.4453 | 0 | 7.4174 | 758.9594 | 0 | 0.088511 | 7.446 | 0.0029142 | 0 | 0 | 28.8883 | on_peak | 758.9594 |  |  | 3.4 | 7.34 | 89.26 | 215.1013 | 0
5659 | 825.96 | 21.412 | 29.1 | 3.4175 | 3.4175 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 822.5425 | 0 | 0.088511 | 7.8643 | 0 | 0 | 0 | 3.4175 | on_peak | 822.5425 |  |  | 0.41 | 0 | 99.59 | 26.8766 | 0
5660 | 858.98 | 0 | 28.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 858.98 | 0 | 0.088511 | 8.1733 | 0 | 0 | 0 | 0 | on_peak | 858.98 |  |  | 0 | 0 | 100 | 0 | 0
5661 | 811.8 | 0 | 28.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 811.8 | 0 | 0.088511 | 8.0295 | 0 | 0 | 0 | 0 | on_peak | 811.8 |  |  | 0 | 0 | 100 | 0 | 0
5662 | 789.61 | 0 | 28.9 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 18.9814 | 801.9724 | 0 | 0.05921 | 8.2856 | 0 | 0 | 0 | 0 | off_peak | 789.61 | 0 | 100 | 0 | 0 | 100 | 0 | 0
5663 | 818.53 | 0 | 28.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18.9814 | 818.53 | 0 | 0.05921 | 8.1766 | 0 | 0 | 0 | 0 | off_peak | 818.53 |  |  | 0 | 0 | 100 | 0 | 0
5664 | 793.98 | 0 | 28.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18.9814 | 793.98 | 0 | 0.05921 | 8.1495 | 0 | 0 | 0 | 0 | off_peak | 793.98 |  |  | 0 | 0 | 100 | 0 | 0
5665 | 749.14 | 0 | 28.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18.9814 | 749.14 | 0 | 0.05921 | 8.1725 | 0 | 0 | 0 | 0 | off_peak | 749.14 |  |  | 0 | 0 | 100 | 0 | 0
5666 | 701.71 | 0 | 28.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18.9814 | 701.71 | 0 | 0.05921 | 7.9927 | 0 | 0 | 0 | 0 | off_peak | 701.71 |  |  | 0 | 0 | 100 | 0 | 0
5667 | 659.86 | 0 | 28.2 | 0 | 0 | 0 | 0 | 0.75266 | 0.75266 | 0 | 0 | 0 | 19.6854 | 660.6127 | 0 | 0.05921 | 7.5055 | 0 | 0 | 0 | 0 | off_peak | 659.86 | 0 | 100 | 0 | 0 | 100 | 0 | 0
5668 | 669.31 | 0 | 28.1 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 31.2494 | 681.6724 | 0 | 0.05921 | 6.9448 | 0 | 0 | 0 | 0 | off_peak | 669.31 | 0 | 100 | 0 | 0 | 100 | 0 | 0
5669 | 608.4 | 0 | 28 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 42.8133 | 620.7624 | 0 | 0.05921 | 6.2015 | 0 | 0 | 0 | 0 | off_peak | 608.4 | 0 | 100 | 0 | 0 | 100 | 0 | 0
5670 | 750.78 | 0 | 28 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 54.3772 | 763.1424 | 0 | 0.05921 | 5.5475 | 0 | 0 | 0 | 0 | off_peak | 750.78 | 0 | 100 | 0 | 0 | 100 | 0 | 0
5671 | 771.68 | 49.6513 | 28.3 | 7.948 | 0 | 0 | 7.948 | 7.948 | 0 | 0 | 0 | 0 | 61.8119 | 771.68 | 0 | 0.05921 | 5.0027 | 0 | 0 | 7.4346 | 0 | off_peak | 771.68 | 100 | 0 | 0 | 0 | 100 | 0 | 0
5672 | 842.28 | 196.63 | 28.6 | 31.4412 | 31.4412 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 73.3758 | 823.2011 | 0 | 0.05921 | 4.6378 | 0 | 0 | 7.4346 | 31.4412 | off_peak | 810.8388 | 0 | 100 | 3.73 | 0 | 96.27 | 145.8186 | 0
5673 | 860.72 | 421.711 | 28.9 | 67.358 | 67.358 | 0 | 0 | 0.79843 | 0.79843 | 0 | 0 | 0 | 74.1227 | 794.1604 | 0 | 0.05921 | 4.3594 | 0 | 0 | 7.4346 | 67.358 | off_peak | 793.362 | 0 | 100 | 7.83 | 0 | 92.17 | 293.6372 | 0
5674 | 894.35 | 628.541 | 29.1 | 100.3207 | 100.2692 | 0 | 0.051567 | 0.051567 | 0 | 0 | 0 | 0 | 74.1709 | 794.0808 | 0 | 0.05921 | 4.2762 | 0 | 0 | 7.4829 | 100.2692 | off_peak | 794.0808 | 100 | 0 | 11.21 | 0 | 88.79 | 428.7692 | 0
5675 | 883.94 | 742.778 | 29.3 | 118.4673 | 118.4673 | 0 | 0 | 0.0033305 | 0.0033305 | 0 | 0 | 0 | 74.174 | 765.476 | 0 | 0.05921 | 4.4521 | 0 | 0 | 7.4829 | 118.4673 | off_peak | 765.4727 | 0 | 100 | 13.4 | 0 | 86.6 | 527.426 | 0
5676 | 908.57 | 848.23 | 29.5 | 135.1872 | 135.1872 | 0 | 0 | 0.0002151 | 0.0002151 | 0 | 0 | 0 | 74.1742 | 773.383 | 0 | 0.05921 | 4.8221 | 0 | 0 | 7.4829 | 135.1872 | off_peak | 773.3828 | 0 | 100 | 14.88 | 0 | 85.12 | 651.8879 | 0
5677 | 845.78 | 900.345 | 29.6 | 143.4405 | 143.4405 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1742 | 702.3395 | 0 | 0.088511 | 4.9386 | 0 | 0 | 7.4829 | 143.4405 | on_peak | 702.3395 |  |  | 16.96 | 0 | 83.04 | 708.3988 | 0
5678 | 874.02 | 856.117 | 29.6 | 136.3942 | 136.3942 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1742 | 737.6258 | 0 | 0.088511 | 5.0824 | 0 | 0 | 7.4829 | 136.3942 | on_peak | 737.6258 |  |  | 15.61 | 0 | 84.39 | 693.2035 | 0
5679 | 886.03 | 765.027 | 29.5 | 121.9266 | 121.9266 | 0 | 0 | 0 | 0 | 62.4453 | 62.4453 | 0 | 7.4174 | 701.6581 | 0 | 0.088511 | 5.3238 | 6.9996 | 0 | 0 | 128.9262 | on_peak | 701.6581 |  |  | 13.76 | 7.05 | 79.19 | 686.3774 | 0
5680 | 839 | 560.253 | 29.3 | 89.356 | 89.356 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 749.644 | 0 | 0.088511 | 5.7454 | 0 | 0 | 0 | 89.356 | on_peak | 749.644 |  |  | 10.65 | 0 | 89.35 | 513.3824 | 0
5681 | 820.01 | 380.824 | 28.9 | 60.8273 | 60.8273 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 759.1827 | 0 | 0.088511 | 6.2247 | 0 | 0 | 0 | 60.8273 | on_peak | 759.1827 |  |  | 7.42 | 0 | 92.58 | 378.6316 | 0
5682 | 833.79 | 197.354 | 28.5 | 31.5685 | 31.5685 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 802.2215 | 0 | 0.088511 | 6.7434 | 0 | 0 | 0 | 31.5685 | on_peak | 802.2215 |  |  | 3.79 | 0 | 96.21 | 212.8801 | 0
5683 | 775.78 | 26.2455 | 28.2 | 4.2028 | 4.2028 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 771.5772 | 0 | 0.088511 | 7.2767 | 0 | 0 | 0 | 4.2028 | on_peak | 771.5772 |  |  | 0.54 | 0 | 99.46 | 30.5826 | 0
5684 | 829.69 | 0 | 28 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 829.69 | 0 | 0.088511 | 7.7103 | 0 | 0 | 0 | 0 | on_peak | 829.69 |  |  | 0 | 0 | 100 | 0 | 0
5685 | 775.61 | 0 | 28 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 775.61 | 0 | 0.088511 | 8.0602 | 0 | 0 | 0 | 0 | on_peak | 775.61 |  |  | 0 | 0 | 100 | 0 | 0
5686 | 775.05 | 0 | 27.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 775.05 | 0 | 0.05921 | 8.4701 | 0 | 0 | 0 | 0 | off_peak | 775.05 |  |  | 0 | 0 | 100 | 0 | 0
5687 | 774.71 | 0 | 27.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 774.71 | 0 | 0.05921 | 8.717 | 0 | 0 | 0 | 0 | off_peak | 774.71 |  |  | 0 | 0 | 100 | 0 | 0
5688 | 758.11 | 0 | 27.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 758.11 | 0 | 0.05921 | 8.8478 | 0 | 0 | 0 | 0 | off_peak | 758.11 |  |  | 0 | 0 | 100 | 0 | 0
5689 | 715.32 | 0 | 28 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 715.32 | 0 | 0.05921 | 8.7377 | 0 | 0 | 0 | 0 | off_peak | 715.32 |  |  | 0 | 0 | 100 | 0 | 0
5690 | 654.09 | 0 | 28 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 654.09 | 0 | 0.05921 | 8.384 | 0 | 0 | 0 | 0 | off_peak | 654.09 |  |  | 0 | 0 | 100 | 0 | 0
5691 | 609.35 | 0 | 28 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 609.35 | 0 | 0.05921 | 7.8547 | 0 | 0 | 0 | 0 | off_peak | 609.35 |  |  | 0 | 0 | 100 | 0 | 0
5692 | 612.22 | 0 | 27.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 612.22 | 0 | 0.05921 | 7.2709 | 0 | 0 | 0 | 0 | off_peak | 612.22 |  |  | 0 | 0 | 100 | 0 | 0
5693 | 630.25 | 0 | 27.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 630.25 | 0 | 0.05921 | 6.6909 | 0 | 0 | 0 | 0 | off_peak | 630.25 |  |  | 0 | 0 | 100 | 0 | 0
5694 | 723.07 | 0 | 27.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 723.07 | 0 | 0.05921 | 6.0237 | 0 | 0 | 0 | 0 | off_peak | 723.07 |  |  | 0 | 0 | 100 | 0 | 0
5695 | 715.09 | 58.775 | 27.8 | 9.4256 | 9.4256 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 705.6644 | 0 | 0.05921 | 5.4213 | 0 | 0 | 0 | 9.4256 | off_peak | 705.6644 |  |  | 1.32 | 0 | 98.68 | 51.0987 | 0
5696 | 746.56 | 252.929 | 28.1 | 40.5172 | 40.5172 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 706.0428 | 0 | 0.05921 | 5.0261 | 0 | 0 | 0 | 40.5172 | off_peak | 706.0428 |  |  | 5.43 | 0 | 94.57 | 203.6417 | 0
5697 | 792.53 | 465.064 | 28.3 | 74.4453 | 74.4453 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 718.0847 | 0 | 0.05921 | 4.6893 | 0 | 0 | 0 | 74.4453 | off_peak | 718.0847 |  |  | 9.39 | 0 | 90.61 | 349.0991 | 0
5698 | 797.18 | 503.666 | 28.6 | 80.5364 | 80.5364 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 716.6436 | 0 | 0.05921 | 4.5019 | 0 | 0 | 0 | 80.5364 | off_peak | 716.6436 |  |  | 10.1 | 0 | 89.9 | 362.5658 | 0
5699 | 749.66 | 762.646 | 29.2 | 121.6806 | 121.6806 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 627.9794 | 0 | 0.05921 | 4.4306 | 0 | 0 | 0 | 121.6806 | off_peak | 627.9794 |  |  | 16.23 | 0 | 83.77 | 539.1196 | 0
5700 | 781.6 | 693.359 | 29.6 | 110.4641 | 110.4641 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 18.9814 | 683.4983 | 0 | 0.05921 | 4.4464 | 0 | 0 | 0 | 110.4641 | off_peak | 671.1359 | 0 | 100 | 14.13 | 0 | 85.87 | 491.165 | 0
5701 | 786.02 | 815.8 | 29.9 | 129.8283 | 129.8283 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18.9814 | 656.1917 | 0 | 0.05921 | 4.5706 | 0 | 0 | 0 | 129.8283 | off_peak | 656.1917 |  |  | 16.52 | 0 | 83.48 | 593.3977 | 0
5702 | 772.48 | 875.297 | 30.1 | 139.1947 | 139.1947 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18.9814 | 633.2853 | 0 | 0.05921 | 4.9596 | 0 | 0 | 0 | 139.1947 | off_peak | 633.2853 |  |  | 18.02 | 0 | 81.98 | 690.3564 | 0
5703 | 749.09 | 735.039 | 30.2 | 116.8472 | 116.8472 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18.9814 | 632.2428 | 0 | 0.05921 | 5.3815 | 0 | 0 | 0 | 116.8472 | off_peak | 632.2428 |  |  | 15.6 | 0 | 84.4 | 628.8128 | 0
5704 | 796.41 | 613.188 | 30 | 97.5484 | 97.5484 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18.9814 | 698.8616 | 0 | 0.05921 | 5.8783 | 0 | 0 | 0 | 97.5484 | off_peak | 698.8616 |  |  | 12.25 | 0 | 87.75 | 573.4168 | 0
5705 | 755.46 | 416.496 | 29.8 | 66.3064 | 66.3064 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18.9814 | 689.1536 | 0 | 0.05921 | 6.4762 | 0 | 0 | 0 | 66.3064 | off_peak | 689.1536 |  |  | 8.78 | 0 | 91.22 | 429.4128 | 0
5706 | 703.7 | 194.511 | 29.4 | 31.0117 | 31.0117 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18.9814 | 672.6883 | 0 | 0.05921 | 7.1335 | 0 | 0 | 0 | 31.0117 | off_peak | 672.6883 |  |  | 4.41 | 0 | 95.59 | 221.221 | 0
5707 | 619.3 | 23.8401 | 29.2 | 3.8037 | 0 | 0 | 3.8037 | 3.8037 | 0 | 0 | 0 | 0 | 22.5394 | 619.3 | 0 | 0.05921 | 7.5637 | 0 | 0 | 3.558 | 0 | off_peak | 619.3 | 100 | 0 | 0 | 0 | 100 | 0 | 0
5708 | 619.54 | 0 | 28.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22.5394 | 619.54 | 0 | 0.05921 | 7.9557 | 0 | 0 | 3.558 | 0 | off_peak | 619.54 |  |  | 0 | 0 | 100 | 0 | 0
5709 | 591.25 | 0 | 28.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22.5394 | 591.25 | 0 | 0.05921 | 8.1975 | 0 | 0 | 3.558 | 0 | off_peak | 591.25 |  |  | 0 | 0 | 100 | 0 | 0
5710 | 595.47 | 0 | 28.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22.5394 | 595.47 | 0 | 0.05921 | 8.4479 | 0 | 0 | 3.558 | 0 | off_peak | 595.47 |  |  | 0 | 0 | 100 | 0 | 0
5711 | 600.21 | 0 | 28.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22.5394 | 600.21 | 0 | 0.05921 | 8.5996 | 0 | 0 | 3.558 | 0 | off_peak | 600.21 |  |  | 0 | 0 | 100 | 0 | 0
5712 | 594.56 | 0 | 28.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22.5394 | 594.56 | 0 | 0.05921 | 8.8243 | 0 | 0 | 3.558 | 0 | off_peak | 594.56 |  |  | 0 | 0 | 100 | 0 | 0
5713 | 594.31 | 0 | 28.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22.5394 | 594.31 | 0 | 0.05921 | 8.6503 | 0 | 0 | 3.558 | 0 | off_peak | 594.31 |  |  | 0 | 0 | 100 | 0 | 0
5714 | 583.03 | 0 | 28.6 | 0 | 0 | 0 | 0 | 4.8969 | 4.8969 | 0 | 0 | 0 | 27.12 | 587.9269 | 0 | 0.05921 | 8.4255 | 0 | 0 | 3.558 | 0 | off_peak | 583.03 | 0 | 100 | 0 | 0 | 100 | 0 | 0
5715 | 604.13 | 0 | 28.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27.12 | 604.13 | 0 | 0.05921 | 7.9367 | 0 | 0 | 3.558 | 0 | off_peak | 604.13 |  |  | 0 | 0 | 100 | 0 | 0
5716 | 604.29 | 0 | 28.5 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 38.684 | 616.6524 | 0 | 0.05921 | 7.3534 | 0 | 0 | 3.558 | 0 | off_peak | 604.29 | 0 | 100 | 0 | 0 | 100 | 0 | 0
5717 | 592.88 | 0 | 28.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 38.684 | 592.88 | 0 | 0.05921 | 6.6839 | 0 | 0 | 3.558 | 0 | off_peak | 592.88 |  |  | 0 | 0 | 100 | 0 | 0
5718 | 714.82 | 0 | 28.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 38.684 | 714.82 | 0 | 0.05921 | 5.9852 | 0 | 0 | 3.558 | 0 | off_peak | 714.82 |  |  | 0 | 0 | 100 | 0 | 0
5719 | 749.15 | 59.0142 | 28.8 | 9.4295 | 9.4295 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 38.684 | 739.7205 | 0 | 0.05921 | 5.495 | 0 | 0 | 3.558 | 9.4295 | off_peak | 739.7205 |  |  | 1.26 | 0 | 98.74 | 51.8147 | 0
5720 | 803.37 | 254.432 | 29.1 | 40.6096 | 40.6096 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 38.684 | 762.7604 | 0 | 0.05921 | 5.1132 | 0 | 0 | 3.558 | 40.6096 | off_peak | 762.7604 |  |  | 5.05 | 0 | 94.95 | 207.6448 | 0
5721 | 767.15 | 466.56 | 29.4 | 74.3855 | 74.3855 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 50.2479 | 705.1269 | 0 | 0.05921 | 4.8043 | 0 | 0 | 3.558 | 74.3855 | off_peak | 692.7645 | 0 | 100 | 9.7 | 0 | 90.3 | 357.3711 | 0
5722 | 780.56 | 655.131 | 29.7 | 104.3355 | 104.3355 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50.2479 | 676.2245 | 0 | 0.05921 | 4.6419 | 0 | 0 | 3.558 | 104.3355 | off_peak | 676.2245 |  |  | 13.37 | 0 | 86.63 | 484.313 | 0
5723 | 759.57 | 759.45 | 30 | 120.8163 | 120.8163 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50.2479 | 638.7537 | 0 | 0.05921 | 4.5455 | 0 | 0 | 3.558 | 120.8163 | off_peak | 638.7537 |  |  | 15.91 | 0 | 84.09 | 549.167 | 0
5724 | 794.9 | 823.94 | 30.2 | 130.9796 | 130.9796 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50.2479 | 663.9204 | 0 | 0.05921 | 4.5118 | 0 | 0 | 3.558 | 130.9796 | off_peak | 663.9204 |  |  | 16.48 | 0 | 83.52 | 590.9563 | 0
5725 | 775.3 | 871.492 | 30.3 | 138.488 | 138.488 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50.2479 | 636.812 | 0 | 0.05921 | 4.6024 | 0 | 0 | 3.558 | 138.488 | off_peak | 636.812 |  |  | 17.86 | 0 | 82.14 | 637.3725 | 0
5726 | 753.68 | 815.436 | 30.3 | 129.5802 | 129.5802 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 61.8119 | 636.4622 | 0 | 0.05921 | 4.9927 | 0 | 0 | 3.558 | 129.5802 | off_peak | 624.0998 | 0 | 100 | 17.19 | 0 | 82.81 | 646.9608 | 0
5727 | 751.05 | 710.631 | 30.3 | 112.9257 | 112.9257 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 61.8119 | 638.1243 | 0 | 0.05921 | 5.4129 | 0 | 0 | 3.558 | 112.9257 | off_peak | 638.1243 |  |  | 15.04 | 0 | 84.96 | 611.2603 | 0
5728 | 737.32 | 601.03 | 30.1 | 95.5792 | 95.5792 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 61.8119 | 641.7408 | 0 | 0.05921 | 6.0712 | 0 | 0 | 3.558 | 95.5792 | off_peak | 641.7408 |  |  | 12.96 | 0 | 87.04 | 580.2801 | 0
5729 | 732.5 | 404.294 | 29.9 | 64.3403 | 64.3403 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 73.3758 | 680.5221 | 0 | 0.05921 | 6.7505 | 0 | 0 | 3.558 | 64.3403 | off_peak | 668.1597 | 0 | 100 | 8.78 | 0 | 91.22 | 434.3304 | 0
5730 | 675.44 | 194.541 | 29.5 | 31.0051 | 31.0051 | 0 | 0 | 0.79843 | 0.79843 | 0 | 0 | 0 | 74.1227 | 645.2333 | 0 | 0.05921 | 7.2987 | 0 | 0 | 3.558 | 31.0051 | off_peak | 644.4349 | 0 | 100 | 4.59 | 0 | 95.41 | 226.2964 | 0
5731 | 605.13 | 21.6076 | 29.3 | 3.4462 | 3.4462 | 0 | 0 | 0.051567 | 0.051567 | 0 | 0 | 0 | 74.1709 | 601.7353 | 0 | 0.05921 | 7.8329 | 0 | 0 | 3.558 | 3.4462 | off_peak | 601.6838 | 0 | 100 | 0.57 | 0 | 99.43 | 26.9942 | 0
5732 | 561.43 | 0 | 29.1 | 0 | 0 | 0 | 0 | 0.0033305 | 0.0033305 | 0 | 0 | 0 | 74.174 | 561.4333 | 0 | 0.05921 | 8.1431 | 0 | 0 | 3.558 | 0 | off_peak | 561.43 | 0 | 100 | 0 | 0 | 100 | 0 | 0
5733 | 540.13 | 0 | 29.1 | 0 | 0 | 0 | 0 | 0.0002151 | 0.0002151 | 0 | 0 | 0 | 74.1742 | 540.1302 | 0 | 0.05921 | 8.4176 | 0 | 0 | 3.558 | 0 | off_peak | 540.13 | 0 | 100 | 0 | 0 | 100 | 0 | 0
5734 | 512.96 | 0 | 29 | 0 | 0 | 0 | 0 | 1.4852e-05 | 1.4852e-05 | 0 | 0 | 0 | 74.1743 | 512.96 | 0 | 0.05921 | 8.5809 | 0 | 0 | 3.558 | 0 | off_peak | 512.96 | 0 | 100 | 0 | 0 | 100 | 0 | 0
5735 | 520.41 | 0 | 28.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1743 | 520.41 | 0 | 0.05921 | 8.639 | 0 | 0 | 3.558 | 0 | off_peak | 520.41 |  |  | 0 | 0 | 100 | 0 | 0
5736 | 525.34 | 0 | 28.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1743 | 525.34 | 0 | 0.05921 | 8.5035 | 0 | 0 | 3.558 | 0 | off_peak | 525.34 |  |  | 0 | 0 | 100 | 0 | 0
5737 | 532.39 | 0 | 28.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1743 | 532.39 | 0 | 0.05921 | 8.3768 | 0 | 0 | 3.558 | 0 | off_peak | 532.39 |  |  | 0 | 0 | 100 | 0 | 0
5738 | 547.05 | 0 | 28.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1743 | 547.05 | 0 | 0.05921 | 8.2428 | 0 | 0 | 3.558 | 0 | off_peak | 547.05 |  |  | 0 | 0 | 100 | 0 | 0
5739 | 513.44 | 0 | 28.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1743 | 513.44 | 0 | 0.05921 | 7.7652 | 0 | 0 | 3.558 | 0 | off_peak | 513.44 |  |  | 0 | 0 | 100 | 0 | 0
5740 | 522.12 | 0 | 28.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1743 | 522.12 | 0 | 0.05921 | 7.1642 | 0 | 0 | 3.558 | 0 | off_peak | 522.12 |  |  | 0 | 0 | 100 | 0 | 0
5741 | 539.43 | 0 | 28.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1743 | 539.43 | 0 | 0.05921 | 6.4991 | 0 | 0 | 3.558 | 0 | off_peak | 539.43 |  |  | 0 | 0 | 100 | 0 | 0
5742 | 644.58 | 0 | 28.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1743 | 644.58 | 0 | 0.05921 | 5.8496 | 0 | 0 | 3.558 | 0 | off_peak | 644.58 |  |  | 0 | 0 | 100 | 0 | 0
5743 | 784.33 | 56.8505 | 28.8 | 9.0838 | 9.0838 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1743 | 775.2462 | 0 | 0.05921 | 5.4058 | 0 | 0 | 3.558 | 9.0838 | off_peak | 775.2462 |  |  | 1.16 | 0 | 98.84 | 49.1054 | 0
5744 | 787.58 | 249.666 | 29.2 | 39.8344 | 39.8344 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1743 | 747.7456 | 0 | 0.05921 | 5.0866 | 0 | 0 | 3.558 | 39.8344 | off_peak | 747.7456 |  |  | 5.06 | 0 | 94.94 | 202.6217 | 0
5745 | 816.91 | 355.012 | 29.5 | 56.5803 | 56.5803 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1743 | 760.3297 | 0 | 0.05921 | 4.8938 | 0 | 0 | 3.558 | 56.5803 | off_peak | 760.3297 |  |  | 6.93 | 0 | 93.07 | 276.8938 | 0
5746 | 846.35 | 642.394 | 29.7 | 102.307 | 102.307 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1743 | 744.043 | 0 | 0.05921 | 4.8747 | 0 | 0 | 3.558 | 102.307 | off_peak | 744.043 |  |  | 12.09 | 0 | 87.91 | 498.7122 | 0
5747 | 828.63 | 778.959 | 29.9 | 123.9653 | 123.9653 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1743 | 704.6647 | 0 | 0.05921 | 5.0686 | 0 | 0 | 3.558 | 123.9653 | off_peak | 704.6647 |  |  | 14.96 | 0 | 85.04 | 628.3261 | 0
5748 | 891.86 | 819.702 | 30.1 | 130.3537 | 130.3537 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1743 | 761.5063 | 0 | 0.05921 | 5.4102 | 0 | 0 | 3.558 | 130.3537 | off_peak | 761.5063 |  |  | 14.62 | 0 | 85.38 | 705.2436 | 0
5749 | 884.38 | 890.86 | 30.1 | 141.6696 | 141.6696 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1743 | 742.7104 | 0 | 0.088511 | 5.597 | 0 | 0 | 3.558 | 141.6696 | on_peak | 742.7104 |  |  | 16.02 | 0 | 83.98 | 792.9288 | 0
5750 | 897.8 | 765.948 | 30.1 | 121.8054 | 121.8054 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1743 | 775.9946 | 0 | 0.088511 | 5.8348 | 0 | 0 | 3.558 | 121.8054 | on_peak | 775.9946 |  |  | 13.57 | 0 | 86.43 | 710.7065 | 0
5751 | 872.59 | 748.805 | 30.1 | 119.0792 | 119.0792 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1743 | 753.5108 | 0 | 0.088511 | 6.1498 | 0 | 0 | 3.558 | 119.0792 | on_peak | 753.5108 |  |  | 13.65 | 0 | 86.35 | 732.3137 | 0
5752 | 830.03 | 593.281 | 29.9 | 94.4161 | 94.4161 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1743 | 735.6139 | 0 | 0.088511 | 6.6184 | 0 | 0 | 3.558 | 94.4161 | on_peak | 735.6139 |  |  | 11.38 | 0 | 88.62 | 624.8851 | 0
5753 | 831.96 | 400.959 | 29.7 | 63.8563 | 63.8563 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1743 | 768.1037 | 0 | 0.088511 | 7.0053 | 0 | 0 | 3.558 | 63.8563 | on_peak | 768.1037 |  |  | 7.68 | 0 | 92.32 | 447.331 | 0
5754 | 898.66 | 189.512 | 29.3 | 30.2257 | 30.2257 | 0 | 0 | 0 | 0 | 59.1171 | 59.1171 | 0 | 10.9755 | 809.3173 | 0 | 0.088511 | 7.4214 | 0 | 0 | 3.558 | 30.2257 | on_peak | 809.3173 |  |  | 3.36 | 6.58 | 90.06 | 224.3158 | 0
5755 | 834 | 18.2314 | 29.1 | 2.9099 | 2.9099 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10.9755 | 831.0901 | 0 | 0.088511 | 7.6372 | 0 | 0 | 3.558 | 2.9099 | on_peak | 831.0901 |  |  | 0.35 | 0 | 99.65 | 22.2234 | 0
5756 | 852.88 | 0 | 28.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10.9755 | 852.88 | 0 | 0.088511 | 7.7476 | 0 | 0 | 3.558 | 0 | on_peak | 852.88 |  |  | 0 | 0 | 100 | 0 | 0
5757 | 859.19 | 0 | 28.8 | 0 | 0 | 0 | 0 | 0 | 0 | 3.3282 | 3.3282 | 0 | 7.4174 | 855.8618 | 0 | 0.088511 | 8.0412 | 3.3282 | 0 | 0 | 3.3282 | on_peak | 855.8618 |  |  | 0 | 0.39 | 99.61 | 26.763 | 0
5758 | 793.29 | 0 | 28.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 793.29 | 0 | 0.05921 | 8.3292 | 0 | 0 | 0 | 0 | off_peak | 793.29 |  |  | 0 | 0 | 100 | 0 | 0
5759 | 847.16 | 0 | 28.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 847.16 | 0 | 0.05921 | 8.2813 | 0 | 0 | 0 | 0 | off_peak | 847.16 |  |  | 0 | 0 | 100 | 0 | 0
5760 | 808.66 | 0 | 28.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 808.66 | 0 | 0.05921 | 8.4038 | 0 | 0 | 0 | 0 | off_peak | 808.66 |  |  | 0 | 0 | 100 | 0 | 0
5761 | 737.32 | 0 | 28.4 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 18.9814 | 749.6824 | 0 | 0.05921 | 8.293 | 0 | 0 | 0 | 0 | off_peak | 737.32 | 0 | 100 | 0 | 0 | 100 | 0 | 0
5762 | 691.14 | 0 | 28.3 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 30.5453 | 703.5024 | 0 | 0.05921 | 8.1632 | 0 | 0 | 0 | 0 | off_peak | 691.14 | 0 | 100 | 0 | 0 | 100 | 0 | 0
5763 | 623.19 | 0 | 28.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30.5453 | 623.19 | 0 | 0.05921 | 7.6782 | 0 | 0 | 0 | 0 | off_peak | 623.19 |  |  | 0 | 0 | 100 | 0 | 0
5764 | 639.4 | 0 | 28.1 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 42.1093 | 651.7624 | 0 | 0.05921 | 7.0485 | 0 | 0 | 0 | 0 | off_peak | 639.4 | 0 | 100 | 0 | 0 | 100 | 0 | 0
5765 | 618.79 | 0 | 28 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 53.6732 | 631.1524 | 0 | 0.05921 | 6.352 | 0 | 0 | 0 | 0 | off_peak | 618.79 | 0 | 100 | 0 | 0 | 100 | 0 | 0
5766 | 709 | 0 | 28.1 | 0 | 0 | 0 | 0 | 8.7006 | 8.7006 | 0 | 0 | 0 | 61.8119 | 717.7006 | 0 | 0.05921 | 5.6528 | 0 | 0 | 0 | 0 | off_peak | 709 | 0 | 100 | 0 | 0 | 100 | 0 | 0
5767 | 798.81 | 56.9235 | 28.4 | 9.1087 | 9.1087 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 61.8119 | 789.7013 | 0 | 0.05921 | 5.251 | 0 | 0 | 0 | 9.1087 | off_peak | 789.7013 |  |  | 1.14 | 0 | 98.86 | 47.8296 | 0
5768 | 798.01 | 231.768 | 28.8 | 37.0328 | 37.0328 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 73.3758 | 773.3396 | 0 | 0.05921 | 4.9326 | 0 | 0 | 0 | 37.0328 | off_peak | 760.9772 | 0 | 100 | 4.64 | 0 | 95.36 | 182.6696 | 0
5769 | 816.39 | 461.951 | 29.1 | 73.7315 | 72.933 | 0 | 0.79843 | 0.79843 | 0 | 0 | 0 | 0 | 74.1227 | 743.457 | 0 | 0.05921 | 4.7226 | 0 | 0 | 0.74686 | 72.933 | off_peak | 743.457 | 100 | 0 | 8.93 | 0 | 91.07 | 344.4312 | 0
5770 | 848.52 | 648.018 | 29.3 | 103.3538 | 103.3538 | 0 | 0 | 0.051567 | 0.051567 | 0 | 0 | 0 | 74.1709 | 745.2177 | 0 | 0.05921 | 4.6967 | 0 | 0 | 0.74686 | 103.3538 | off_peak | 745.1662 | 0 | 100 | 12.18 | 0 | 87.82 | 485.4227 | 0
5771 | 852.44 | 719.461 | 29.5 | 114.6645 | 114.6645 | 0 | 0 | 0.0033305 | 0.0033305 | 0 | 0 | 0 | 74.174 | 737.7788 | 0 | 0.05921 | 4.9231 | 0 | 0 | 0.74686 | 114.6645 | off_peak | 737.7755 | 0 | 100 | 13.45 | 0 | 86.55 | 564.5075 | 0
5772 | 875.12 | 558.37 | 29.7 | 88.9254 | 88.9254 | 0 | 0 | 0.0002151 | 0.0002151 | 0 | 0 | 0 | 74.1742 | 786.1948 | 0 | 0.05921 | 5.3052 | 0 | 0 | 0.74686 | 88.9254 | off_peak | 786.1946 | 0 | 100 | 10.16 | 0 | 89.84 | 471.77 | 0
5773 | 856.92 | 727.757 | 29.9 | 115.8169 | 115.8169 | 0 | 0 | 0 | 0 | 61.7467 | 61.7467 | 0 | 8.1643 | 679.3564 | 0 | 0.088511 | 5.5719 | 0 | 0 | 0.74686 | 115.8169 | on_peak | 679.3564 |  |  | 13.52 | 7.21 | 79.28 | 645.3168 | 0
5774 | 868.95 | 760.691 | 30 | 121.0138 | 121.0138 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.1643 | 747.9362 | 0 | 0.088511 | 5.8707 | 0 | 0 | 0.74686 | 121.0138 | on_peak | 747.9362 |  |  | 13.93 | 0 | 86.07 | 710.4404 | 0
5775 | 840.65 | 702.226 | 30 | 111.7129 | 111.7129 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.1643 | 728.9371 | 0 | 0.088511 | 6.3016 | 0 | 0 | 0.74686 | 111.7129 | on_peak | 728.9371 |  |  | 13.29 | 0 | 86.71 | 703.9736 | 0
5776 | 783.43 | 577.005 | 30 | 91.7923 | 91.7923 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.1643 | 691.6377 | 0 | 0.088511 | 6.7364 | 0 | 0 | 0.74686 | 91.7923 | on_peak | 691.6377 |  |  | 11.72 | 0 | 88.28 | 618.3501 | 0
5777 | 795.93 | 380.9 | 29.8 | 60.6395 | 60.6395 | 0 | 0 | 0 | 0 | 0.69863 | 0.69863 | 0 | 7.4174 | 734.5918 | 0 | 0.088511 | 7.0924 | 0.69863 | 0 | 0 | 61.3382 | on_peak | 734.5918 |  |  | 7.62 | 0.09 | 92.29 | 435.0377 | 0
5778 | 811.49 | 186.826 | 29.5 | 29.7755 | 29.7755 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 781.7145 | 0 | 0.088511 | 7.5878 | 0 | 0 | 0 | 29.7755 | on_peak | 781.7145 |  |  | 3.67 | 0 | 96.33 | 225.9311 | 0
5779 | 767.07 | 19.7973 | 29.3 | 3.1575 | 3.1575 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 763.9125 | 0 | 0.088511 | 8.0145 | 0 | 0 | 0 | 3.1575 | on_peak | 763.9125 |  |  | 0.41 | 0 | 99.59 | 25.3059 | 0
5780 | 783.01 | 0 | 29 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 783.01 | 0 | 0.088511 | 8.089 | 0 | 0 | 0 | 0 | on_peak | 783.01 |  |  | 0 | 0 | 100 | 0 | 0
5781 | 780.16 | 0 | 28.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 780.16 | 0 | 0.088511 | 8.2647 | 0 | 0 | 0 | 0 | on_peak | 780.16 |  |  | 0 | 0 | 100 | 0 | 0
5782 | 746.37 | 0 | 28.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 746.37 | 0 | 0.05921 | 8.329 | 0 | 0 | 0 | 0 | off_peak | 746.37 |  |  | 0 | 0 | 100 | 0 | 0
5783 | 773.82 | 0 | 28.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 773.82 | 0 | 0.05921 | 7.9467 | 0 | 0 | 0 | 0 | off_peak | 773.82 |  |  | 0 | 0 | 100 | 0 | 0
5784 | 755.99 | 0 | 28.3 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 18.9814 | 768.3524 | 0 | 0.05921 | 7.5222 | 0 | 0 | 0 | 0 | off_peak | 755.99 | 0 | 100 | 0 | 0 | 100 | 0 | 0
5785 | 719.02 | 0 | 28.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18.9814 | 719.02 | 0 | 0.05921 | 7.3979 | 0 | 0 | 0 | 0 | off_peak | 719.02 |  |  | 0 | 0 | 100 | 0 | 0
5786 | 626.71 | 0 | 28 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 30.5453 | 639.0724 | 0 | 0.05921 | 7.26 | 0 | 0 | 0 | 0 | off_peak | 626.71 | 0 | 100 | 0 | 0 | 100 | 0 | 0
5787 | 622.28 | 0 | 27.9 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 42.1093 | 634.6424 | 0 | 0.05921 | 6.8334 | 0 | 0 | 0 | 0 | off_peak | 622.28 | 0 | 100 | 0 | 0 | 100 | 0 | 0
5788 | 618.19 | 0 | 27.9 | 0 | 0 | 0 | 0 | 8.7006 | 8.7006 | 0 | 0 | 0 | 50.2479 | 626.8906 | 0 | 0.05921 | 6.4064 | 0 | 0 | 0 | 0 | off_peak | 618.19 | 0 | 100 | 0 | 0 | 100 | 0 | 0
5789 | 627.31 | 0 | 28 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50.2479 | 627.31 | 0 | 0.05921 | 6.01 | 0 | 0 | 0 | 0 | off_peak | 627.31 |  |  | 0 | 0 | 100 | 0 | 0
5790 | 677.44 | 0 | 28.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50.2479 | 677.44 | 0 | 0.05921 | 5.5515 | 0 | 0 | 0 | 0 | off_peak | 677.44 |  |  | 0 | 0 | 100 | 0 | 0
5791 | 746.03 | 49.894 | 28.6 | 7.9781 | 7.9781 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 61.8119 | 750.4143 | 0 | 0.05921 | 5.3089 | 0 | 0 | 0 | 7.9781 | off_peak | 738.0519 | 0 | 100 | 1.07 | 0 | 98.93 | 42.3551 | 0
5792 | 847.17 | 245.857 | 29.1 | 39.241 | 39.241 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 73.3758 | 820.2914 | 0 | 0.05921 | 5.1376 | 0 | 0 | 0 | 39.241 | off_peak | 807.929 | 0 | 100 | 4.63 | 0 | 95.37 | 201.6051 | 0
5793 | 875.82 | 457.827 | 29.5 | 72.9665 | 72.9665 | 0 | 0 | 0.79843 | 0.79843 | 0 | 0 | 0 | 74.1227 | 803.652 | 0 | 0.05921 | 5.0714 | 0 | 0 | 0 | 72.9665 | off_peak | 802.8535 | 0 | 100 | 8.33 | 0 | 91.67 | 370.0407 | 0
5794 | 901 | 638.45 | 29.9 | 101.6044 | 101.6044 | 0 | 0 | 0.051567 | 0.051567 | 0 | 0 | 0 | 74.1709 | 799.4472 | 0 | 0.05921 | 5.0897 | 0 | 0 | 0 | 101.6044 | off_peak | 799.3956 | 0 | 100 | 11.28 | 0 | 88.72 | 517.1382 | 0
5795 | 815.68 | 767.972 | 30.2 | 122.0825 | 122.0825 | 0 | 0 | 0.0033305 | 0.0033305 | 0 | 0 | 0 | 74.174 | 693.6008 | 0 | 0.05921 | 5.3134 | 0 | 0 | 0 | 122.0825 | off_peak | 693.5975 | 0 | 100 | 14.97 | 0 | 85.03 | 648.6748 | 0
5796 | 859.28 | 858.654 | 30.4 | 136.3978 | 136.3978 | 0 | 0 | 0.0002151 | 0.0002151 | 0 | 0 | 0 | 74.1742 | 722.8824 | 0 | 0.05921 | 5.6006 | 0 | 0 | 0 | 136.3978 | off_peak | 722.8822 | 0 | 100 | 15.87 | 0 | 84.13 | 763.915 | 0
5797 | 841.9 | 771.258 | 30.6 | 122.4249 | 122.4249 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1742 | 719.4751 | 0 | 0.088511 | 5.7322 | 0 | 0 | 0 | 122.4249 | on_peak | 719.4751 |  |  | 14.54 | 0 | 85.46 | 701.7654 | 0
5798 | 879.89 | 697.458 | 30.6 | 110.7104 | 110.7104 | 0 | 0 | 0 | 0 | 62.4453 | 62.4453 | 0 | 7.4174 | 706.7344 | 0 | 0.088511 | 6.0982 | 0 | 0 | 0 | 110.7104 | on_peak | 706.7344 |  |  | 12.58 | 7.1 | 80.32 | 675.1365 | 0
5799 | 907.59 | 625.47 | 30.5 | 99.3199 | 99.3199 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 808.2701 | 0 | 0.088511 | 6.5491 | 0 | 0 | 0 | 99.3199 | on_peak | 808.2701 |  |  | 10.94 | 0 | 89.06 | 650.4527 | 0
5800 | 836.84 | 273.165 | 30.2 | 43.4243 | 43.4243 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 793.4157 | 0 | 0.088511 | 6.9004 | 0 | 0 | 0 | 43.4243 | on_peak | 793.4157 |  |  | 5.19 | 0 | 94.81 | 299.6442 | 0
5801 | 853.28 | 342.992 | 29.8 | 54.6045 | 54.6045 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 798.6755 | 0 | 0.088511 | 7.2506 | 0 | 0 | 0 | 54.6045 | on_peak | 798.6755 |  |  | 6.4 | 0 | 93.6 | 395.9174 | 0
5802 | 871.33 | 97.904 | 29.3 | 15.6149 | 15.6149 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 855.7151 | 0 | 0.088511 | 7.3499 | 0 | 0 | 0 | 15.6149 | on_peak | 855.7151 |  |  | 1.79 | 0 | 98.21 | 114.7679 | 0
5803 | 834.55 | 7.6 | 29 | 1.2135 | 1.2135 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 833.3365 | 0 | 0.088511 | 7.4936 | 0 | 0 | 0 | 1.2135 | on_peak | 833.3365 |  |  | 0.15 | 0 | 99.85 | 9.0933 | 0
5804 | 841.72 | 0 | 28.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 841.72 | 0 | 0.088511 | 7.6807 | 0 | 0 | 0 | 0 | on_peak | 841.72 |  |  | 0 | 0 | 100 | 0 | 0
5805 | 817.94 | 0 | 28.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 817.94 | 0 | 0.088511 | 7.9036 | 0 | 0 | 0 | 0 | on_peak | 817.94 |  |  | 0 | 0 | 100 | 0 | 0
5806 | 812.63 | 0 | 28.2 | 0 | 0 | 0 | 0 | 8.7006 | 8.7006 | 0 | 0 | 0 | 15.5561 | 821.3306 | 0 | 0.05921 | 8.0878 | 0 | 0 | 0 | 0 | off_peak | 812.63 | 0 | 100 | 0 | 0 | 100 | 0 | 0
5807 | 873.28 | 0 | 28.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15.5561 | 873.28 | 0 | 0.05921 | 8.2537 | 0 | 0 | 0 | 0 | off_peak | 873.28 |  |  | 0 | 0 | 100 | 0 | 0
5808 | 807.49 | 0 | 28 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15.5561 | 807.49 | 0 | 0.05921 | 8.4092 | 0 | 0 | 0 | 0 | off_peak | 807.49 |  |  | 0 | 0 | 100 | 0 | 0
5809 | 687.14 | 0 | 27.9 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 27.12 | 699.5024 | 0 | 0.05921 | 8.3019 | 0 | 0 | 0 | 0 | off_peak | 687.14 | 0 | 100 | 0 | 0 | 100 | 0 | 0
5810 | 678.78 | 0 | 27.8 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 38.684 | 691.1424 | 0 | 0.05921 | 8.1695 | 0 | 0 | 0 | 0 | off_peak | 678.78 | 0 | 100 | 0 | 0 | 100 | 0 | 0
5811 | 663.91 | 0 | 27.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 38.684 | 663.91 | 0 | 0.05921 | 7.6717 | 0 | 0 | 0 | 0 | off_peak | 663.91 |  |  | 0 | 0 | 100 | 0 | 0
5812 | 657.17 | 0 | 27.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 38.684 | 657.17 | 0 | 0.05921 | 7.0668 | 0 | 0 | 0 | 0 | off_peak | 657.17 |  |  | 0 | 0 | 100 | 0 | 0
5813 | 677.52 | 0 | 27.7 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 50.2479 | 689.8824 | 0 | 0.05921 | 6.4523 | 0 | 0 | 0 | 0 | off_peak | 677.52 | 0 | 100 | 0 | 0 | 100 | 0 | 0
5814 | 715.2 | 0 | 27.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50.2479 | 715.2 | 0 | 0.05921 | 5.8716 | 0 | 0 | 0 | 0 | off_peak | 715.2 |  |  | 0 | 0 | 100 | 0 | 0
5815 | 781.78 | 35.2444 | 28 | 5.6479 | 5.6479 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 61.8119 | 788.4944 | 0 | 0.05921 | 5.4535 | 0 | 0 | 0 | 5.6479 | off_peak | 776.1321 | 0 | 100 | 0.72 | 0 | 99.28 | 30.801 | 0
5816 | 821.09 | 228.568 | 28.5 | 36.5615 | 36.5615 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 73.3758 | 796.8909 | 0 | 0.05921 | 5.1695 | 0 | 0 | 0 | 36.5615 | off_peak | 784.5285 | 0 | 100 | 4.45 | 0 | 95.55 | 189.0057 | 0
5817 | 837.36 | 449.065 | 28.9 | 71.7271 | 71.7271 | 0 | 0 | 0.79843 | 0.79843 | 0 | 0 | 0 | 74.1227 | 766.4313 | 0 | 0.05921 | 4.9752 | 0 | 0 | 0 | 71.7271 | off_peak | 765.6329 | 0 | 100 | 8.57 | 0 | 91.43 | 356.8561 | 0
5818 | 841.93 | 629.456 | 29.4 | 100.3566 | 100.3566 | 0 | 0 | 0.051567 | 0.051567 | 0 | 0 | 0 | 74.1709 | 741.6249 | 0 | 0.05921 | 4.8916 | 0 | 0 | 0 | 100.3566 | off_peak | 741.5734 | 0 | 100 | 11.92 | 0 | 88.08 | 490.9029 | 0
5819 | 855.99 | 730.757 | 29.9 | 116.2944 | 116.2944 | 0 | 0 | 0.0033305 | 0.0033305 | 0 | 0 | 0 | 74.174 | 739.699 | 0 | 0.05921 | 5.0489 | 0 | 0 | 0 | 116.2944 | off_peak | 739.6956 | 0 | 100 | 13.59 | 0 | 86.41 | 587.1588 | 0
5820 | 894.73 | 864 | 30.3 | 137.2974 | 137.2974 | 0 | 0 | 0.0002151 | 0.0002151 | 0 | 0 | 0 | 74.1742 | 757.4328 | 0 | 0.05921 | 5.3885 | 0 | 0 | 0 | 137.2974 | off_peak | 757.4326 | 0 | 100 | 15.35 | 0 | 84.65 | 739.8268 | 0
5821 | 904.53 | 584.997 | 30.6 | 92.859 | 92.859 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1742 | 811.671 | 0 | 0.088511 | 5.5218 | 0 | 0 | 0 | 92.859 | on_peak | 811.671 |  |  | 10.27 | 0 | 89.73 | 512.7481 | 0
5822 | 902.55 | 264.359 | 30.8 | 41.9319 | 41.9319 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1742 | 860.6181 | 0 | 0.088511 | 5.637 | 0 | 0 | 0 | 41.9319 | on_peak | 860.6181 |  |  | 4.65 | 0 | 95.35 | 236.3721 | 0
5823 | 880.42 | 267.011 | 30.9 | 42.337 | 42.337 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1742 | 838.083 | 0 | 0.088511 | 5.9661 | 0 | 0 | 0 | 42.337 | on_peak | 838.083 |  |  | 4.81 | 0 | 95.19 | 252.5879 | 0
5824 | 833.47 | 198.873 | 30.8 | 31.5447 | 31.5447 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1742 | 801.9253 | 0 | 0.088511 | 6.4929 | 0 | 0 | 0 | 31.5447 | on_peak | 801.9253 |  |  | 3.78 | 0 | 96.22 | 204.8157 | 0
5825 | 829.49 | 144.195 | 30.5 | 22.8971 | 22.8971 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1742 | 806.5929 | 0 | 0.088511 | 7.0586 | 0 | 0 | 0 | 22.8971 | on_peak | 806.5929 |  |  | 2.76 | 0 | 97.24 | 161.621 | 0
5826 | 833.32 | 104.234 | 30 | 16.582 | 16.582 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1742 | 816.738 | 0 | 0.088511 | 7.5019 | 0 | 0 | 0 | 16.582 | on_peak | 816.738 |  |  | 1.99 | 0 | 98.01 | 124.3957 | 0
5827 | 820.4 | 9.5 | 29.7 | 1.513 | 1.513 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1742 | 818.887 | 0 | 0.088511 | 7.9436 | 0 | 0 | 0 | 1.513 | on_peak | 818.887 |  |  | 0.18 | 0 | 99.82 | 12.0184 | 0
5828 | 840.44 | 0 | 29.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1742 | 840.44 | 0 | 0.088511 | 8.2626 | 0 | 0 | 0 | 0 | on_peak | 840.44 |  |  | 0 | 0 | 100 | 0 | 0
5829 | 832.8 | 0 | 29.3 | 0 | 0 | 0 | 0 | 0 | 0 | 62.4453 | 62.4453 | 0 | 7.4174 | 770.3547 | 0 | 0.088511 | 8.5905 | 0 | 0 | 0 | 0 | on_peak | 770.3547 |  |  | 0 | 7.5 | 92.5 | 0 | 0
5830 | 782.73 | 0 | 29.1 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 18.9814 | 795.0924 | 0 | 0.05921 | 8.6336 | 0 | 0 | 0 | 0 | off_peak | 782.73 | 0 | 100 | 0 | 0 | 100 | 0 | 0
5831 | 836.68 | 0 | 29 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18.9814 | 836.68 | 0 | 0.05921 | 8.4962 | 0 | 0 | 0 | 0 | off_peak | 836.68 |  |  | 0 | 0 | 100 | 0 | 0
5832 | 777.14 | 0 | 28.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18.9814 | 777.14 | 0 | 0.05921 | 8.0896 | 0 | 0 | 0 | 0 | off_peak | 777.14 |  |  | 0 | 0 | 100 | 0 | 0
5833 | 747.15 | 0 | 28.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18.9814 | 747.15 | 0 | 0.05921 | 7.8722 | 0 | 0 | 0 | 0 | off_peak | 747.15 |  |  | 0 | 0 | 100 | 0 | 0
5834 | 721 | 0 | 28.6 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 30.5453 | 733.3624 | 0 | 0.05921 | 7.6008 | 0 | 0 | 0 | 0 | off_peak | 721 | 0 | 100 | 0 | 0 | 100 | 0 | 0
5835 | 629.13 | 0 | 28.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30.5453 | 629.13 | 0 | 0.05921 | 7.127 | 0 | 0 | 0 | 0 | off_peak | 629.13 |  |  | 0 | 0 | 100 | 0 | 0
5836 | 657.94 | 0 | 28.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30.5453 | 657.94 | 0 | 0.05921 | 6.6121 | 0 | 0 | 0 | 0 | off_peak | 657.94 |  |  | 0 | 0 | 100 | 0 | 0
5837 | 667.3 | 0 | 28.5 | 0 | 0 | 0 | 0 | 8.7006 | 8.7006 | 0 | 0 | 0 | 38.684 | 676.0006 | 0 | 0.05921 | 5.8682 | 0 | 0 | 0 | 0 | off_peak | 667.3 | 0 | 100 | 0 | 0 | 100 | 0 | 0
5838 | 745.71 | 0 | 28.5 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 50.2479 | 758.0724 | 0 | 0.05921 | 5.4292 | 0 | 0 | 0 | 0 | off_peak | 745.71 | 0 | 100 | 0 | 0 | 100 | 0 | 0
5839 | 756.74 | 38.5604 | 28.7 | 6.1636 | 6.1636 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 61.8119 | 762.9388 | 0 | 0.05921 | 5.0519 | 0 | 0 | 0 | 6.1636 | off_peak | 750.5764 | 0 | 100 | 0.81 | 0 | 99.19 | 31.1377 | 0
5840 | 792.01 | 173.034 | 29.1 | 27.6178 | 27.6178 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 73.3758 | 776.7546 | 0 | 0.05921 | 4.7367 | 0 | 0 | 0 | 27.6178 | off_peak | 764.3922 | 0 | 100 | 3.49 | 0 | 96.51 | 130.8173 | 0
5841 | 840.19 | 362.108 | 29.4 | 57.7323 | 57.7323 | 0 | 0 | 0.79843 | 0.79843 | 0 | 0 | 0 | 74.1227 | 783.2561 | 0 | 0.05921 | 4.5515 | 0 | 0 | 0 | 57.7323 | off_peak | 782.4577 | 0 | 100 | 6.87 | 0 | 93.13 | 262.7684 | 0
5842 | 832.55 | 652.244 | 29.8 | 103.8377 | 103.7861 | 0 | 0.051567 | 0.051567 | 0 | 0 | 0 | 0 | 74.1709 | 728.7639 | 0 | 0.05921 | 4.4891 | 0 | 0 | 0.048237 | 103.7861 | off_peak | 728.7639 | 100 | 0 | 12.47 | 0 | 87.53 | 465.9028 | 0
5843 | 869.47 | 694.141 | 30.1 | 110.3862 | 110.3862 | 0 | 0 | 0.0033305 | 0.0033305 | 0 | 0 | 0 | 74.174 | 759.0871 | 0 | 0.05921 | 4.6961 | 0 | 0 | 0.048237 | 110.3862 | off_peak | 759.0838 | 0 | 100 | 12.7 | 0 | 87.3 | 518.3856 | 0
5844 | 854.92 | 880.814 | 30.4 | 139.9179 | 139.9179 | 0 | 0 | 0.0002151 | 0.0002151 | 0 | 0 | 0 | 74.1742 | 715.0023 | 0 | 0.05921 | 5.0089 | 0 | 0 | 0.048237 | 139.9179 | off_peak | 715.0021 | 0 | 100 | 16.37 | 0 | 83.63 | 700.8372 | 0
5845 | 900.65 | 901.81 | 30.6 | 143.148 | 143.148 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1742 | 757.502 | 0 | 0.088511 | 5.1511 | 0 | 0 | 0.048237 | 143.148 | on_peak | 757.502 |  |  | 15.89 | 0 | 84.11 | 737.3637 | 0
5846 | 858.09 | 856.214 | 30.8 | 135.8105 | 135.8105 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1742 | 722.2795 | 0 | 0.088511 | 5.4194 | 0 | 0 | 0.048237 | 135.8105 | on_peak | 722.2795 |  |  | 15.83 | 0 | 84.17 | 736.0089 | 0
5847 | 876.25 | 749.089 | 31 | 118.7312 | 118.7312 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1742 | 757.5188 | 0 | 0.088511 | 5.8877 | 0 | 0 | 0.048237 | 118.7312 | on_peak | 757.5188 |  |  | 13.55 | 0 | 86.45 | 699.0479 | 0
5848 | 836.8 | 365.373 | 30.8 | 57.9545 | 57.9545 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1742 | 778.8455 | 0 | 0.088511 | 6.4704 | 0 | 0 | 0.048237 | 57.9545 | on_peak | 778.8455 |  |  | 6.93 | 0 | 93.07 | 374.9881 | 0
5849 | 811.57 | 389.859 | 30.3 | 61.9521 | 61.9521 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1742 | 749.6179 | 0 | 0.088511 | 7.0874 | 0 | 0 | 0.048237 | 61.9521 | on_peak | 749.6179 |  |  | 7.63 | 0 | 92.37 | 439.0788 | 0
5850 | 887.77 | 84.3656 | 29.7 | 13.436 | 13.436 | 0 | 0 | 0 | 0 | 21.5585 | 21.5585 | 0 | 51.1272 | 852.7755 | 0 | 0.088511 | 7.5637 | 0 | 0 | 0.048237 | 13.436 | on_peak | 852.7755 |  |  | 1.51 | 2.43 | 96.06 | 101.6256 | 0
5851 | 815.27 | 8.55 | 29.3 | 1.3637 | 1.3637 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 51.1272 | 813.9063 | 0 | 0.088511 | 8.1053 | 0 | 0 | 0.048237 | 1.3637 | on_peak | 813.9063 |  |  | 0.17 | 0 | 99.83 | 11.0528 | 0
5852 | 839.89 | 0 | 28.5 | 0 | 0 | 0 | 0 | 0 | 0 | 40.8868 | 40.8868 | 0 | 7.4174 | 799.0032 | 0 | 0.088511 | 8.5812 | 0.045121 | 0 | 0 | 0.045121 | on_peak | 799.0032 |  |  | 0 | 4.87 | 95.13 | 0.38719 | 0
5853 | 793.51 | 0 | 28.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 793.51 | 0 | 0.088511 | 8.5942 | 0 | 0 | 0 | 0 | on_peak | 793.51 |  |  | 0 | 0 | 100 | 0 | 0
5854 | 785.52 | 0 | 27.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 785.52 | 0 | 0.05921 | 8.6211 | 0 | 0 | 0 | 0 | off_peak | 785.52 |  |  | 0 | 0 | 100 | 0 | 0
5855 | 774.69 | 0 | 27.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 774.69 | 0 | 0.05921 | 8.7489 | 0 | 0 | 0 | 0 | off_peak | 774.69 |  |  | 0 | 0 | 100 | 0 | 0
5856 | 737.14 | 0 | 27.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 737.14 | 0 | 0.05921 | 8.7101 | 0 | 0 | 0 | 0 | off_peak | 737.14 |  |  | 0 | 0 | 100 | 0 | 0
5857 | 673.19 | 0 | 27.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 673.19 | 0 | 0.05921 | 8.4147 | 0 | 0 | 0 | 0 | off_peak | 673.19 |  |  | 0 | 0 | 100 | 0 | 0
5858 | 645.58 | 0 | 27.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 645.58 | 0 | 0.05921 | 8.1341 | 0 | 0 | 0 | 0 | off_peak | 645.58 |  |  | 0 | 0 | 100 | 0 | 0
5859 | 636.02 | 0 | 27.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 636.02 | 0 | 0.05921 | 7.5963 | 0 | 0 | 0 | 0 | off_peak | 636.02 |  |  | 0 | 0 | 100 | 0 | 0
5860 | 625.84 | 0 | 27.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 625.84 | 0 | 0.05921 | 7.0801 | 0 | 0 | 0 | 0 | off_peak | 625.84 |  |  | 0 | 0 | 100 | 0 | 0
5861 | 637.2 | 0 | 27.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 637.2 | 0 | 0.05921 | 6.2386 | 0 | 0 | 0 | 0 | off_peak | 637.2 |  |  | 0 | 0 | 100 | 0 | 0
5862 | 676.21 | 0 | 27.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 676.21 | 0 | 0.05921 | 5.5205 | 0 | 0 | 0 | 0 | off_peak | 676.21 |  |  | 0 | 0 | 100 | 0 | 0
5863 | 686.43 | 37.5102 | 28.1 | 6.0088 | 6.0088 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 680.4212 | 0 | 0.05921 | 5.0241 | 0 | 0 | 0 | 6.0088 | off_peak | 680.4212 |  |  | 0.88 | 0 | 99.12 | 30.1893 | 0
5864 | 718.12 | 168.218 | 28.6 | 26.8981 | 26.8981 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 691.2219 | 0 | 0.05921 | 4.6629 | 0 | 0 | 0 | 26.8981 | off_peak | 691.2219 |  |  | 3.75 | 0 | 96.25 | 125.4246 | 0
5865 | 809.38 | 360.51 | 29.1 | 57.5406 | 57.5406 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 751.8394 | 0 | 0.05921 | 4.4417 | 0 | 0 | 0 | 57.5406 | off_peak | 751.8394 |  |  | 7.11 | 0 | 92.89 | 255.5781 | 0
5866 | 769.96 | 165.707 | 29.5 | 26.4097 | 26.4097 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 743.5503 | 0 | 0.05921 | 4.3126 | 0 | 0 | 0 | 26.4097 | off_peak | 743.5503 |  |  | 3.43 | 0 | 96.57 | 113.895 | 0
5867 | 725.35 | 83.6 | 29.8 | 13.3092 | 13.3092 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 712.0408 | 0 | 0.05921 | 4.2776 | 0 | 0 | 0 | 13.3092 | off_peak | 712.0408 |  |  | 1.83 | 0 | 98.17 | 56.9313 | 0
5868 | 777.14 | 312.141 | 30.1 | 49.6384 | 49.6384 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 727.5016 | 0 | 0.05921 | 4.3326 | 0 | 0 | 0 | 49.6384 | off_peak | 727.5016 |  |  | 6.39 | 0 | 93.61 | 215.0629 | 0
5869 | 734.2 | 763.753 | 30.3 | 121.3673 | 121.3673 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 612.8327 | 0 | 0.05921 | 4.4988 | 0 | 0 | 0 | 121.3673 | off_peak | 612.8327 |  |  | 16.53 | 0 | 83.47 | 546.0034 | 0
5870 | 717.45 | 805.902 | 30.4 | 128.0181 | 128.0181 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 589.4319 | 0 | 0.05921 | 4.9161 | 0 | 0 | 0 | 128.0181 | off_peak | 589.4319 |  |  | 17.84 | 0 | 82.16 | 629.3507 | 0
5871 | 735.61 | 569.756 | 30.4 | 90.5062 | 90.5062 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 645.1038 | 0 | 0.05921 | 5.4498 | 0 | 0 | 0 | 90.5062 | off_peak | 645.1038 |  |  | 12.3 | 0 | 87.7 | 493.2364 | 0
5872 | 720.41 | 482.553 | 30.4 | 76.6539 | 76.6539 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 643.7561 | 0 | 0.05921 | 6.0069 | 0 | 0 | 0 | 76.6539 | off_peak | 643.7561 |  |  | 10.64 | 0 | 89.36 | 460.4554 | 0
5873 | 713.56 | 231.462 | 30 | 36.8219 | 36.8219 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 676.7381 | 0 | 0.05921 | 6.2004 | 0 | 0 | 0 | 36.8219 | off_peak | 676.7381 |  |  | 5.16 | 0 | 94.84 | 228.3094 | 0
5874 | 632.58 | 174.877 | 29.5 | 27.8711 | 27.8711 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 604.7089 | 0 | 0.05921 | 6.404 | 0 | 0 | 0 | 27.8711 | off_peak | 604.7089 |  |  | 4.41 | 0 | 95.59 | 178.486 | 0
5875 | 548.3 | 11.3643 | 29.3 | 1.8125 | 1.8125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 546.4875 | 0 | 0.05921 | 6.6017 | 0 | 0 | 0 | 1.8125 | off_peak | 546.4875 |  |  | 0.33 | 0 | 99.67 | 11.9658 | 0
5876 | 579.45 | 0 | 28.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 579.45 | 0 | 0.05921 | 6.8928 | 0 | 0 | 0 | 0 | off_peak | 579.45 |  |  | 0 | 0 | 100 | 0 | 0
5877 | 549.33 | 0 | 28.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 549.33 | 0 | 0.05921 | 7.1075 | 0 | 0 | 0 | 0 | off_peak | 549.33 |  |  | 0 | 0 | 100 | 0 | 0
5878 | 548.64 | 0 | 28.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 548.64 | 0 | 0.05921 | 7.3633 | 0 | 0 | 0 | 0 | off_peak | 548.64 |  |  | 0 | 0 | 100 | 0 | 0
5879 | 529.68 | 0 | 27.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 529.68 | 0 | 0.05921 | 7.6765 | 0 | 0 | 0 | 0 | off_peak | 529.68 |  |  | 0 | 0 | 100 | 0 | 0
5880 | 557.16 | 0 | 27.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 557.16 | 0 | 0.05921 | 7.7801 | 0 | 0 | 0 | 0 | off_peak | 557.16 |  |  | 0 | 0 | 100 | 0 | 0
5881 | 571.76 | 0 | 27.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 571.76 | 0 | 0.05921 | 7.5503 | 0 | 0 | 0 | 0 | off_peak | 571.76 |  |  | 0 | 0 | 100 | 0 | 0
5882 | 553.44 | 0 | 27.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 553.44 | 0 | 0.05921 | 7.3559 | 0 | 0 | 0 | 0 | off_peak | 553.44 |  |  | 0 | 0 | 100 | 0 | 0
5883 | 552.78 | 0 | 27.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 552.78 | 0 | 0.05921 | 6.8803 | 0 | 0 | 0 | 0 | off_peak | 552.78 |  |  | 0 | 0 | 100 | 0 | 0
5884 | 551.43 | 0 | 27 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 18.9814 | 563.7924 | 0 | 0.05921 | 6.396 | 0 | 0 | 0 | 0 | off_peak | 551.43 | 0 | 100 | 0 | 0 | 100 | 0 | 0
5885 | 556.35 | 0 | 27 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 30.5453 | 568.7124 | 0 | 0.05921 | 5.7949 | 0 | 0 | 0 | 0 | off_peak | 556.35 | 0 | 100 | 0 | 0 | 100 | 0 | 0
5886 | 606.87 | 0 | 27 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 42.1093 | 619.2324 | 0 | 0.05921 | 5.2226 | 0 | 0 | 0 | 0 | off_peak | 606.87 | 0 | 100 | 0 | 0 | 100 | 0 | 0
5887 | 637.82 | 49.2097 | 27.2 | 7.9088 | 7.9088 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 42.1093 | 629.9112 | 0 | 0.05921 | 4.8107 | 0 | 0 | 0 | 7.9088 | off_peak | 629.9112 |  |  | 1.24 | 0 | 98.76 | 38.0469 | 0
5888 | 709.15 | 243.158 | 27.4 | 39.0513 | 39.0513 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 53.6732 | 682.4611 | 0 | 0.05921 | 4.5011 | 0 | 0 | 0 | 39.0513 | off_peak | 670.0987 | 0 | 100 | 5.51 | 0 | 94.49 | 175.7744 | 0
5889 | 704.74 | 457.077 | 27.6 | 73.3534 | 73.3534 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 53.6732 | 631.3866 | 0 | 0.05921 | 4.2528 | 0 | 0 | 0 | 73.3534 | off_peak | 631.3866 |  |  | 10.41 | 0 | 89.59 | 311.9545 | 0
5890 | 716.16 | 646.983 | 28 | 103.6793 | 103.6793 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 53.6732 | 612.4807 | 0 | 0.05921 | 4.092 | 0 | 0 | 0 | 103.6793 | off_peak | 612.4807 |  |  | 14.48 | 0 | 85.52 | 424.2559 | 0
5891 | 676.82 | 780.678 | 28.4 | 124.9218 | 124.9218 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 53.6732 | 551.8982 | 0 | 0.05921 | 4.0109 | 0 | 0 | 0 | 124.9218 | off_peak | 551.8982 |  |  | 18.46 | 0 | 81.54 | 501.0517 | 0
5892 | 695.64 | 710.426 | 28.7 | 113.556 | 113.556 | 0 | 0 | 1.3242 | 1.3242 | 0 | 0 | 0 | 54.9118 | 583.4081 | 0 | 0.05921 | 4.0227 | 0 | 0 | 0 | 113.556 | off_peak | 582.084 | 0 | 100 | 16.32 | 0 | 83.68 | 456.8057 | 0
5893 | 685.1 | 800.216 | 28.9 | 127.8149 | 127.8149 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 54.9118 | 557.2851 | 0 | 0.05921 | 4.1297 | 0 | 0 | 0 | 127.8149 | off_peak | 557.2851 |  |  | 18.66 | 0 | 81.34 | 527.84 | 0
5894 | 697.43 | 692.67 | 29 | 110.5967 | 110.5967 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 54.9118 | 586.8333 | 0 | 0.05921 | 4.4735 | 0 | 0 | 0 | 110.5967 | off_peak | 586.8333 |  |  | 15.86 | 0 | 84.14 | 494.7501 | 0
5895 | 692.51 | 659.074 | 29.1 | 105.1941 | 105.1941 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 54.9118 | 587.3159 | 0 | 0.05921 | 4.8859 | 0 | 0 | 0 | 105.1941 | off_peak | 587.3159 |  |  | 15.19 | 0 | 84.81 | 513.9659 | 0
5896 | 704.96 | 367.659 | 29.1 | 58.6816 | 58.6816 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 66.4758 | 658.6407 | 0 | 0.05921 | 5.3166 | 0 | 0 | 0 | 58.6816 | off_peak | 646.2784 | 0 | 100 | 8.32 | 0 | 91.68 | 311.9847 | 0
5897 | 660.32 | 267.552 | 28.8 | 42.7505 | 42.7505 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 66.4758 | 617.5695 | 0 | 0.05921 | 5.6996 | 0 | 0 | 0 | 42.7505 | off_peak | 617.5695 |  |  | 6.47 | 0 | 93.53 | 243.6623 | 0
5898 | 610.81 | 68.1635 | 28.4 | 10.9073 | 10.9073 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 66.4758 | 599.9027 | 0 | 0.05921 | 6.1653 | 0 | 0 | 0 | 10.9073 | off_peak | 599.9027 |  |  | 1.79 | 0 | 98.21 | 67.2474 | 0
5899 | 585.8 | 4.75 | 28.2 | 0.76064 | 0.76064 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 66.4758 | 585.0394 | 0 | 0.05921 | 6.4472 | 0 | 0 | 0 | 0.76064 | off_peak | 585.0394 |  |  | 0.13 | 0 | 99.87 | 4.9039 | 0
5900 | 563.08 | 0 | 27.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 66.4758 | 563.08 | 0 | 0.05921 | 6.8249 | 0 | 0 | 0 | 0 | off_peak | 563.08 |  |  | 0 | 0 | 100 | 0 | 0
5901 | 559.93 | 0 | 27.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 66.4758 | 559.93 | 0 | 0.05921 | 7.1528 | 0 | 0 | 0 | 0 | off_peak | 559.93 |  |  | 0 | 0 | 100 | 0 | 0
5902 | 575.31 | 0 | 27.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 66.4758 | 575.31 | 0 | 0.05921 | 7.3061 | 0 | 0 | 0 | 0 | off_peak | 575.31 |  |  | 0 | 0 | 100 | 0 | 0
5903 | 567.42 | 0 | 27.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 66.4758 | 567.42 | 0 | 0.05921 | 7.5378 | 0 | 0 | 0 | 0 | off_peak | 567.42 |  |  | 0 | 0 | 100 | 0 | 0
5904 | 569.13 | 0 | 27 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 66.4758 | 569.13 | 0 | 0.05921 | 7.5426 | 0 | 0 | 0 | 0 | off_peak | 569.13 |  |  | 0 | 0 | 100 | 0 | 0
5905 | 543.93 | 0 | 26.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 66.4758 | 543.93 | 0 | 0.05921 | 7.5307 | 0 | 0 | 0 | 0 | off_peak | 543.93 |  |  | 0 | 0 | 100 | 0 | 0
5906 | 568.12 | 0 | 26.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 66.4758 | 568.12 | 0 | 0.05921 | 7.2794 | 0 | 0 | 0 | 0 | off_peak | 568.12 |  |  | 0 | 0 | 100 | 0 | 0
5907 | 562.59 | 0 | 26.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 66.4758 | 562.59 | 0 | 0.05921 | 6.8266 | 0 | 0 | 0 | 0 | off_peak | 562.59 |  |  | 0 | 0 | 100 | 0 | 0
5908 | 581.66 | 0 | 26.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 66.4758 | 581.66 | 0 | 0.05921 | 6.4108 | 0 | 0 | 0 | 0 | off_peak | 581.66 |  |  | 0 | 0 | 100 | 0 | 0
5909 | 572.46 | 0 | 26.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 66.4758 | 572.46 | 0 | 0.05921 | 5.8189 | 0 | 0 | 0 | 0 | off_peak | 572.46 |  |  | 0 | 0 | 100 | 0 | 0
5910 | 621.45 | 0 | 26.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 66.4758 | 621.45 | 0 | 0.05921 | 5.2934 | 0 | 0 | 0 | 0 | off_peak | 621.45 |  |  | 0 | 0 | 100 | 0 | 0
5911 | 621.5 | 47.6294 | 26.6 | 7.6715 | 7.6715 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 66.4758 | 613.8285 | 0 | 0.05921 | 4.8121 | 0 | 0 | 0 | 7.6715 | off_peak | 613.8285 |  |  | 1.23 | 0 | 98.77 | 36.9161 | 0
5912 | 610.58 | 238.885 | 26.9 | 38.4347 | 38.4347 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 66.4758 | 572.1453 | 0 | 0.05921 | 4.4796 | 0 | 0 | 0 | 38.4347 | off_peak | 572.1453 |  |  | 6.29 | 0 | 93.71 | 172.1727 | 0
5913 | 633.93 | 341.612 | 27.1 | 54.9228 | 54.9228 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 66.4758 | 579.0072 | 0 | 0.05921 | 4.287 | 0 | 0 | 0 | 54.9228 | off_peak | 579.0072 |  |  | 8.66 | 0 | 91.34 | 235.4514 | 0
5914 | 615.91 | 512.578 | 27.4 | 82.3202 | 82.3202 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 66.4758 | 533.5898 | 0 | 0.05921 | 4.177 | 0 | 0 | 0 | 82.3202 | off_peak | 533.5898 |  |  | 13.37 | 0 | 86.63 | 343.852 | 0
5915 | 651.59 | 713.086 | 27.8 | 114.3555 | 114.3555 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 66.4758 | 537.2345 | 0 | 0.05921 | 4.1953 | 0 | 0 | 0 | 114.3555 | off_peak | 537.2345 |  |  | 17.55 | 0 | 82.45 | 479.7513 | 0
5916 | 669.15 | 875.136 | 28 | 140.2409 | 140.2409 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 66.4758 | 528.9091 | 0 | 0.05921 | 4.2299 | 0 | 0 | 0 | 140.2409 | off_peak | 528.9091 |  |  | 20.96 | 0 | 79.04 | 593.2023 | 0
5917 | 634.46 | 796.136 | 28.1 | 127.5347 | 127.5347 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 66.4758 | 506.9253 | 0 | 0.05921 | 4.3371 | 0 | 0 | 0 | 127.5347 | on_peak | 506.9253 |  |  | 20.1 | 0 | 79.9 | 553.1344 | 0
5918 | 652.43 | 690.948 | 28.1 | 110.6844 | 110.6844 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 66.4758 | 541.7456 | 0 | 0.05921 | 4.5858 | 0 | 0 | 0 | 110.6844 | on_peak | 541.7456 |  |  | 16.96 | 0 | 83.04 | 507.5713 | 0
5919 | 619.54 | 553.657 | 28 | 88.7238 | 88.7238 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 66.4758 | 530.8162 | 0 | 0.05921 | 4.9519 | 0 | 0 | 0 | 88.7238 | on_peak | 530.8162 |  |  | 14.32 | 0 | 85.68 | 439.3481 | 0
5920 | 616.76 | 579.957 | 27.8 | 93.006 | 93.006 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 66.4758 | 523.754 | 0 | 0.05921 | 5.4699 | 0 | 0 | 0 | 93.006 | on_peak | 523.754 |  |  | 15.08 | 0 | 84.92 | 508.7325 | 0
5921 | 609.8 | 372.123 | 27.6 | 59.7197 | 59.7197 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 66.4758 | 550.0803 | 0 | 0.05921 | 6.1221 | 0 | 0 | 0 | 59.7197 | on_peak | 550.0803 |  |  | 9.79 | 0 | 90.21 | 365.6096 | 0
5922 | 577.47 | 48.6841 | 27.3 | 7.8215 | 7.8215 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 66.4758 | 569.6485 | 0 | 0.05921 | 6.6152 | 0 | 0 | 0 | 7.8215 | on_peak | 569.6485 |  |  | 1.35 | 0 | 98.65 | 51.7407 | 0
5923 | 593.66 | 1.9 | 27.2 | 0.30536 | 0.30536 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 66.4758 | 593.3546 | 0 | 0.05921 | 7.0427 | 0 | 0 | 0 | 0.30536 | on_peak | 593.3546 |  |  | 0.05 | 0 | 99.95 | 2.1506 | 0
5924 | 585.57 | 0 | 27 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 66.4758 | 585.57 | 0 | 0.05921 | 7.3157 | 0 | 0 | 0 | 0 | on_peak | 585.57 |  |  | 0 | 0 | 100 | 0 | 0
5925 | 609.09 | 0 | 27 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 66.4758 | 609.09 | 0 | 0.05921 | 7.6477 | 0 | 0 | 0 | 0 | on_peak | 609.09 |  |  | 0 | 0 | 100 | 0 | 0
5926 | 566.2 | 0 | 27 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 66.4758 | 566.2 | 0 | 0.05921 | 7.8743 | 0 | 0 | 0 | 0 | off_peak | 566.2 |  |  | 0 | 0 | 100 | 0 | 0
5927 | 585.4 | 0 | 26.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 66.4758 | 585.4 | 0 | 0.05921 | 8.0733 | 0 | 0 | 0 | 0 | off_peak | 585.4 |  |  | 0 | 0 | 100 | 0 | 0
5928 | 568.81 | 0 | 26.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 66.4758 | 568.81 | 0 | 0.05921 | 8.3327 | 0 | 0 | 0 | 0 | off_peak | 568.81 |  |  | 0 | 0 | 100 | 0 | 0
5929 | 587.08 | 0 | 26.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 66.4758 | 587.08 | 0 | 0.05921 | 8.372 | 0 | 0 | 0 | 0 | off_peak | 587.08 |  |  | 0 | 0 | 100 | 0 | 0
5930 | 584.8 | 0 | 26.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 66.4758 | 584.8 | 0 | 0.05921 | 8.124 | 0 | 0 | 0 | 0 | off_peak | 584.8 |  |  | 0 | 0 | 100 | 0 | 0
5931 | 568.15 | 0 | 26.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 66.4758 | 568.15 | 0 | 0.05921 | 7.5193 | 0 | 0 | 0 | 0 | off_peak | 568.15 |  |  | 0 | 0 | 100 | 0 | 0
5932 | 604.26 | 0 | 26.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 66.4758 | 604.26 | 0 | 0.05921 | 6.8646 | 0 | 0 | 0 | 0 | off_peak | 604.26 |  |  | 0 | 0 | 100 | 0 | 0
5933 | 569.48 | 0 | 26.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 66.4758 | 569.48 | 0 | 0.05921 | 5.9837 | 0 | 0 | 0 | 0 | off_peak | 569.48 |  |  | 0 | 0 | 100 | 0 | 0
5934 | 690.76 | 0 | 26.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 66.4758 | 690.76 | 0 | 0.05921 | 5.3109 | 0 | 0 | 0 | 0 | off_peak | 690.76 |  |  | 0 | 0 | 100 | 0 | 0
5935 | 776.82 | 47.8141 | 26.7 | 7.6985 | 0 | 0 | 7.6985 | 7.6985 | 0 | 0 | 0 | 0 | 73.677 | 776.82 | 0 | 0.05921 | 4.7938 | 0 | 0 | 7.2013 | 0 | off_peak | 776.82 | 100 | 0 | 0 | 0 | 100 | 0 | 0
5936 | 872.59 | 241.789 | 26.9 | 38.9019 | 38.9019 | 0 | 0 | 0.49721 | 0.49721 | 0 | 0 | 0 | 74.1421 | 834.1853 | 0 | 0.05921 | 4.461 | 0 | 0 | 7.2013 | 38.9019 | off_peak | 833.6881 | 0 | 100 | 4.46 | 0 | 95.54 | 173.5417 | 0
5937 | 873.49 | 454.608 | 27.1 | 73.0897 | 73.0897 | 0 | 0 | 0.032113 | 0.032113 | 0 | 0 | 0 | 74.1722 | 800.4324 | 0 | 0.05921 | 4.258 | 0 | 0 | 7.2013 | 73.0897 | off_peak | 800.4003 | 0 | 100 | 8.37 | 0 | 91.63 | 311.2155 | 0
5938 | 822.46 | 643.615 | 27.4 | 103.3648 | 103.3648 | 0 | 0 | 0.002074 | 0.002074 | 0 | 0 | 0 | 74.1741 | 719.0973 | 0 | 0.05921 | 4.1767 | 0 | 0 | 7.2013 | 103.3648 | off_peak | 719.0952 | 0 | 100 | 12.57 | 0 | 87.43 | 431.7288 | 0
5939 | 798.71 | 789.656 | 27.6 | 126.7269 | 126.7269 | 0 | 0 | 0.00013395 | 0.00013395 | 0 | 0 | 0 | 74.1742 | 671.9832 | 0 | 0.05921 | 4.342 | 0 | 0 | 7.2013 | 126.7269 | off_peak | 671.9831 | 0 | 100 | 15.87 | 0 | 84.13 | 550.2449 | 0
5940 | 865.98 | 877.734 | 27.8 | 140.7596 | 140.7596 | 0 | 0 | 8.6514e-06 | 8.6514e-06 | 0 | 0 | 0 | 74.1743 | 725.2204 | 0 | 0.05921 | 4.6983 | 0 | 0 | 7.2013 | 140.7596 | off_peak | 725.2204 | 0 | 100 | 16.25 | 0 | 83.75 | 661.3279 | 0
5941 | 833.65 | 897.909 | 27.8 | 143.995 | 143.995 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1743 | 689.655 | 0 | 0.088511 | 4.8843 | 0 | 0 | 7.2013 | 143.995 | on_peak | 689.655 |  |  | 17.27 | 0 | 82.73 | 703.3101 | 0
5942 | 863.82 | 791.084 | 27.8 | 126.8638 | 126.8638 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1743 | 736.9562 | 0 | 0.088511 | 5.0414 | 0 | 0 | 7.2013 | 126.8638 | on_peak | 736.9562 |  |  | 14.69 | 0 | 85.31 | 639.5704 | 0
5943 | 853.42 | 739.611 | 27.7 | 118.6524 | 118.6524 | 0 | 0 | 0 | 0 | 62.4453 | 62.4453 | 0 | 7.4174 | 672.3223 | 0 | 0.088511 | 5.2763 | 6.7362 | 0 | 0 | 125.3885 | on_peak | 672.3223 |  |  | 13.9 | 7.32 | 78.78 | 661.5883 | 0
5944 | 790.04 | 512.896 | 27.6 | 82.3114 | 82.3114 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 707.7286 | 0 | 0.088511 | 5.7105 | 0 | 0 | 0 | 82.3114 | on_peak | 707.7286 |  |  | 10.42 | 0 | 89.58 | 470.0435 | 0
5945 | 809.94 | 14.25 | 27.4 | 2.2886 | 2.2886 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 807.6514 | 0 | 0.088511 | 6.2476 | 0 | 0 | 0 | 2.2886 | on_peak | 807.6514 |  |  | 0.28 | 0 | 99.72 | 14.2979 | 0
5946 | 836.07 | 7.6 | 27.1 | 1.2219 | 1.2219 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 834.8481 | 0 | 0.088511 | 6.7724 | 0 | 0 | 0 | 1.2219 | on_peak | 834.8481 |  |  | 0.15 | 0 | 99.85 | 8.2751 | 0
5947 | 829.21 | 0 | 27 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 829.21 | 0 | 0.088511 | 7.4141 | 0 | 0 | 0 | 0 | on_peak | 829.21 |  |  | 0 | 0 | 100 | 0 | 0
5948 | 839.2 | 0 | 26.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 839.2 | 0 | 0.088511 | 7.8512 | 0 | 0 | 0 | 0 | on_peak | 839.2 |  |  | 0 | 0 | 100 | 0 | 0
5949 | 791.38 | 0 | 26.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 791.38 | 0 | 0.088511 | 8.1302 | 0 | 0 | 0 | 0 | on_peak | 791.38 |  |  | 0 | 0 | 100 | 0 | 0
5950 | 811.62 | 0 | 26.8 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 18.9814 | 823.9824 | 0 | 0.05921 | 8.4208 | 0 | 0 | 0 | 0 | off_peak | 811.62 | 0 | 100 | 0 | 0 | 100 | 0 | 0
5951 | 809.67 | 0 | 26.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18.9814 | 809.67 | 0 | 0.05921 | 8.5598 | 0 | 0 | 0 | 0 | off_peak | 809.67 |  |  | 0 | 0 | 100 | 0 | 0
5952 | 816.09 | 0 | 26.7 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 30.5453 | 828.4524 | 0 | 0.05921 | 8.74 | 0 | 0 | 0 | 0 | off_peak | 816.09 | 0 | 100 | 0 | 0 | 100 | 0 | 0
5953 | 733.51 | 0 | 26.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30.5453 | 733.51 | 0 | 0.05921 | 8.7825 | 0 | 0 | 0 | 0 | off_peak | 733.51 |  |  | 0 | 0 | 100 | 0 | 0
5954 | 658.85 | 0 | 26.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30.5453 | 658.85 | 0 | 0.05921 | 8.4932 | 0 | 0 | 0 | 0 | off_peak | 658.85 |  |  | 0 | 0 | 100 | 0 | 0
5955 | 621.08 | 0 | 26.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30.5453 | 621.08 | 0 | 0.05921 | 7.8251 | 0 | 0 | 0 | 0 | off_peak | 621.08 |  |  | 0 | 0 | 100 | 0 | 0
5956 | 662.76 | 0 | 26.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30.5453 | 662.76 | 0 | 0.05921 | 7.0342 | 0 | 0 | 0 | 0 | off_peak | 662.76 |  |  | 0 | 0 | 100 | 0 | 0
5957 | 646.64 | 0 | 26.2 | 0 | 0 | 0 | 0 | 8.7006 | 8.7006 | 0 | 0 | 0 | 38.684 | 655.3406 | 0 | 0.05921 | 6.1821 | 0 | 0 | 0 | 0 | off_peak | 646.64 | 0 | 100 | 0 | 0 | 100 | 0 | 0
5958 | 704.19 | 0 | 26.2 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 50.2479 | 716.5524 | 0 | 0.05921 | 5.5043 | 0 | 0 | 0 | 0 | off_peak | 704.19 | 0 | 100 | 0 | 0 | 100 | 0 | 0
5959 | 770.15 | 47.6356 | 26.2 | 7.6836 | 7.6836 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 61.8119 | 774.8287 | 0 | 0.05921 | 5.0076 | 0 | 0 | 0 | 7.6836 | off_peak | 762.4664 | 0 | 100 | 1 | 0 | 99 | 38.4768 | 0
5960 | 840.7 | 242.69 | 26.5 | 39.1035 | 39.1035 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 73.3758 | 813.9589 | 0 | 0.05921 | 4.6231 | 0 | 0 | 0 | 39.1035 | off_peak | 801.5965 | 0 | 100 | 4.65 | 0 | 95.35 | 180.7799 | 0
5961 | 862.35 | 364.504 | 26.8 | 58.667 | 58.667 | 0 | 0 | 0.79843 | 0.79843 | 0 | 0 | 0 | 74.1227 | 804.4814 | 0 | 0.05921 | 4.3503 | 0 | 0 | 0 | 58.667 | off_peak | 803.683 | 0 | 100 | 6.8 | 0 | 93.2 | 255.2176 | 0
5962 | 851.33 | 643.157 | 27.3 | 103.3287 | 103.3287 | 0 | 0 | 0.051567 | 0.051567 | 0 | 0 | 0 | 74.1709 | 748.0528 | 0 | 0.05921 | 4.2493 | 0 | 0 | 0 | 103.3287 | off_peak | 748.0013 | 0 | 100 | 12.14 | 0 | 87.86 | 439.0778 | 0
5963 | 826.45 | 676.438 | 27.8 | 108.4784 | 108.4784 | 0 | 0 | 0.0033305 | 0.0033305 | 0 | 0 | 0 | 74.174 | 717.975 | 0 | 0.05921 | 4.3993 | 0 | 0 | 0 | 108.4784 | off_peak | 717.9716 | 0 | 100 | 13.13 | 0 | 86.87 | 477.2251 | 0
5964 | 903.98 | 773.725 | 28.3 | 123.8544 | 123.8542 | 0 | 0.0002151 | 0.0002151 | 0 | 0 | 0 | 0 | 74.1742 | 780.1258 | 0 | 0.05921 | 4.7206 | 0 | 0 | 0.00020121 | 123.8542 | off_peak | 780.1258 | 100 | 0 | 13.7 | 0 | 86.3 | 584.666 | 0
5965 | 818.86 | 581.387 | 28.7 | 92.9302 | 92.9302 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1742 | 725.9298 | 0 | 0.088511 | 4.9345 | 0 | 0 | 0.00020121 | 92.9302 | on_peak | 725.9298 |  |  | 11.35 | 0 | 88.65 | 458.5617 | 0
5966 | 866.14 | 723.037 | 28.9 | 115.4875 | 115.4875 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1742 | 750.6525 | 0 | 0.088511 | 5.064 | 0 | 0 | 0.00020121 | 115.4875 | on_peak | 750.6525 |  |  | 13.33 | 0 | 86.67 | 584.8256 | 0
5967 | 848.3 | 302.103 | 28.9 | 48.2536 | 48.2536 | 0 | 0 | 0 | 0 | 62.4453 | 62.4453 | 0 | 7.4174 | 737.6012 | 0 | 0.088511 | 5.2417 | 0.00018821 | 0 | 0 | 48.2537 | on_peak | 737.6012 |  |  | 5.69 | 7.36 | 86.95 | 252.9339 | 0
5968 | 827.34 | 229.038 | 28.8 | 36.5966 | 36.5966 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 790.7434 | 0 | 0.088511 | 5.6593 | 0 | 0 | 0 | 36.5966 | on_peak | 790.7434 |  |  | 4.42 | 0 | 95.58 | 207.1127 | 0
5969 | 829.12 | 188.364 | 28.6 | 30.1195 | 30.1195 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 799.0005 | 0 | 0.088511 | 6.308 | 0 | 0 | 0 | 30.1195 | on_peak | 799.0005 |  |  | 3.63 | 0 | 96.37 | 189.9935 | 0
5970 | 814.92 | 16.15 | 28.3 | 2.5852 | 2.5852 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 812.3348 | 0 | 0.088511 | 6.8711 | 0 | 0 | 0 | 2.5852 | on_peak | 812.3348 |  |  | 0.32 | 0 | 99.68 | 17.7633 | 0
5971 | 828.95 | 0 | 28.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 828.95 | 0 | 0.088511 | 7.4862 | 0 | 0 | 0 | 0 | on_peak | 828.95 |  |  | 0 | 0 | 100 | 0 | 0
5972 | 823.47 | 0 | 27.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 823.47 | 0 | 0.088511 | 7.9118 | 0 | 0 | 0 | 0 | on_peak | 823.47 |  |  | 0 | 0 | 100 | 0 | 0
5973 | 784.55 | 0 | 27.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 784.55 | 0 | 0.088511 | 8.178 | 0 | 0 | 0 | 0 | on_peak | 784.55 |  |  | 0 | 0 | 100 | 0 | 0
5974 | 780.24 | 0 | 27.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 780.24 | 0 | 0.05921 | 8.3895 | 0 | 0 | 0 | 0 | off_peak | 780.24 |  |  | 0 | 0 | 100 | 0 | 0
5975 | 818.07 | 0 | 27.2 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 18.9814 | 830.4324 | 0 | 0.05921 | 8.6329 | 0 | 0 | 0 | 0 | off_peak | 818.07 | 0 | 100 | 0 | 0 | 100 | 0 | 0
5976 | 804.37 | 0 | 26.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18.9814 | 804.37 | 0 | 0.05921 | 8.8568 | 0 | 0 | 0 | 0 | off_peak | 804.37 |  |  | 0 | 0 | 100 | 0 | 0
5977 | 736.86 | 0 | 26.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18.9814 | 736.86 | 0 | 0.05921 | 8.7756 | 0 | 0 | 0 | 0 | off_peak | 736.86 |  |  | 0 | 0 | 100 | 0 | 0
5978 | 654.95 | 0 | 26.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18.9814 | 654.95 | 0 | 0.05921 | 8.5091 | 0 | 0 | 0 | 0 | off_peak | 654.95 |  |  | 0 | 0 | 100 | 0 | 0
5979 | 620.01 | 0 | 26.3 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 30.5453 | 632.3724 | 0 | 0.05921 | 7.8924 | 0 | 0 | 0 | 0 | off_peak | 620.01 | 0 | 100 | 0 | 0 | 100 | 0 | 0
5980 | 652.22 | 0 | 26.2 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 42.1093 | 664.5824 | 0 | 0.05921 | 7.0602 | 0 | 0 | 0 | 0 | off_peak | 652.22 | 0 | 100 | 0 | 0 | 100 | 0 | 0
5981 | 641.36 | 0 | 26.2 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 53.6732 | 653.7224 | 0 | 0.05921 | 6.1186 | 0 | 0 | 0 | 0 | off_peak | 641.36 | 0 | 100 | 0 | 0 | 100 | 0 | 0
5982 | 694.33 | 0 | 26.3 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 65.2371 | 706.6924 | 0 | 0.05921 | 5.4526 | 0 | 0 | 0 | 0 | off_peak | 694.33 | 0 | 100 | 0 | 0 | 100 | 0 | 0
5983 | 725.73 | 48.5023 | 26.6 | 7.8121 | 7.8121 | 0 | 0 | 8.9371 | 8.9371 | 0 | 0 | 0 | 73.597 | 726.855 | 0 | 0.05921 | 4.9838 | 0 | 0 | 0 | 7.8121 | off_peak | 717.9179 | 0 | 100 | 1.08 | 0 | 98.92 | 38.9337 | 0
5984 | 810.86 | 244.347 | 27 | 39.2992 | 39.2992 | 0 | 0 | 0.57721 | 0.57721 | 0 | 0 | 0 | 74.137 | 772.138 | 0 | 0.05921 | 4.6566 | 0 | 0 | 0 | 39.2992 | off_peak | 771.5608 | 0 | 100 | 4.85 | 0 | 95.15 | 183.0007 | 0
5985 | 806.3 | 458.603 | 27.4 | 73.6518 | 73.6518 | 0 | 0 | 0.037279 | 0.037279 | 0 | 0 | 0 | 74.1718 | 732.6855 | 0 | 0.05921 | 4.4449 | 0 | 0 | 0 | 73.6518 | off_peak | 732.6482 | 0 | 100 | 9.13 | 0 | 90.87 | 327.3736 | 0
5986 | 840.26 | 441.891 | 27.9 | 70.839 | 70.839 | 0 | 0 | 0.0024077 | 0.0024077 | 0 | 0 | 0 | 74.1741 | 769.4234 | 0 | 0.05921 | 4.3455 | 0 | 0 | 0 | 70.839 | off_peak | 769.421 | 0 | 100 | 8.43 | 0 | 91.57 | 307.832 | 0
5987 | 830.31 | 716.699 | 28.4 | 114.6841 | 114.6841 | 0 | 0 | 0.0001555 | 0.0001555 | 0 | 0 | 0 | 74.1742 | 715.626 | 0 | 0.05921 | 4.5146 | 0 | 0 | 0 | 114.6841 | off_peak | 715.6259 | 0 | 100 | 13.81 | 0 | 86.19 | 517.7552 | 0
5988 | 879.55 | 875.277 | 29 | 139.753 | 139.753 | 0 | 0 | 1.0043e-05 | 1.0043e-05 | 0 | 0 | 0 | 74.1743 | 739.797 | 0 | 0.05921 | 4.8657 | 0 | 0 | 0 | 139.753 | off_peak | 739.797 | 0 | 100 | 15.89 | 0 | 84.11 | 679.9956 | 0
5989 | 836.98 | 895.892 | 29.4 | 142.8356 | 142.8356 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1743 | 694.1444 | 0 | 0.088511 | 4.9896 | 0 | 0 | 0 | 142.8356 | on_peak | 694.1444 |  |  | 17.07 | 0 | 82.93 | 712.6951 | 0
5990 | 879.95 | 837.999 | 29.7 | 133.4588 | 133.4588 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1743 | 746.4912 | 0 | 0.088511 | 5.1018 | 0 | 0 | 0 | 133.4588 | on_peak | 746.4912 |  |  | 15.17 | 0 | 84.83 | 680.8757 | 0
5991 | 848.66 | 728.594 | 29.8 | 115.9926 | 115.9926 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1743 | 732.6674 | 0 | 0.088511 | 5.2283 | 0 | 0 | 0 | 115.9926 | on_peak | 732.6674 |  |  | 13.67 | 0 | 86.33 | 606.4386 | 0
5992 | 863.16 | 565.207 | 29.6 | 90.0472 | 90.0472 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1743 | 773.1128 | 0 | 0.088511 | 5.6014 | 0 | 0 | 0 | 90.0472 | on_peak | 773.1128 |  |  | 10.43 | 0 | 89.57 | 504.3875 | 0
5993 | 866.45 | 366.027 | 29.3 | 58.3785 | 58.3785 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1743 | 808.0715 | 0 | 0.088511 | 6.3288 | 0 | 0 | 0 | 58.3785 | on_peak | 808.0715 |  |  | 6.74 | 0 | 93.26 | 369.4655 | 0
5994 | 876.38 | 155.586 | 28.8 | 24.8601 | 24.8601 | 0 | 0 | 0 | 0 | 62.4453 | 62.4453 | 0 | 7.4174 | 789.0746 | 0 | 0.088511 | 7.0703 | 0 | 0 | 0 | 24.8601 | on_peak | 789.0746 |  |  | 2.84 | 7.13 | 90.04 | 175.769 | 0
5995 | 843.11 | 0 | 28.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 843.11 | 0 | 0.088511 | 7.7 | 0 | 0 | 0 | 0 | on_peak | 843.11 |  |  | 0 | 0 | 100 | 0 | 0
5996 | 813.83 | 0 | 28 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 813.83 | 0 | 0.088511 | 8.042 | 0 | 0 | 0 | 0 | on_peak | 813.83 |  |  | 0 | 0 | 100 | 0 | 0
5997 | 842.43 | 0 | 27.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 842.43 | 0 | 0.088511 | 8.4138 | 0 | 0 | 0 | 0 | on_peak | 842.43 |  |  | 0 | 0 | 100 | 0 | 0
5998 | 808.37 | 0 | 27.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 808.37 | 0 | 0.05921 | 8.6588 | 0 | 0 | 0 | 0 | off_peak | 808.37 |  |  | 0 | 0 | 100 | 0 | 0
5999 | 832.81 | 0 | 27.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 832.81 | 0 | 0.05921 | 8.8352 | 0 | 0 | 0 | 0 | off_peak | 832.81 |  |  | 0 | 0 | 100 | 0 | 0
6000 | 770.88 | 0 | 27.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 770.88 | 0 | 0.05921 | 8.9071 | 0 | 0 | 0 | 0 | off_peak | 770.88 |  |  | 0 | 0 | 100 | 0 | 0
6001 | 752.49 | 0 | 27.2 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 18.9814 | 764.8524 | 0 | 0.05921 | 8.7321 | 0 | 0 | 0 | 0 | off_peak | 752.49 | 0 | 100 | 0 | 0 | 100 | 0 | 0
6002 | 683.57 | 0 | 27 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18.9814 | 683.57 | 0 | 0.05921 | 8.4392 | 0 | 0 | 0 | 0 | off_peak | 683.57 |  |  | 0 | 0 | 100 | 0 | 0
6003 | 636.03 | 0 | 26.8 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 30.5453 | 648.3924 | 0 | 0.05921 | 7.8676 | 0 | 0 | 0 | 0 | off_peak | 636.03 | 0 | 100 | 0 | 0 | 100 | 0 | 0
6004 | 663.98 | 0 | 26.6 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 42.1093 | 676.3424 | 0 | 0.05921 | 7.1435 | 0 | 0 | 0 | 0 | off_peak | 663.98 | 0 | 100 | 0 | 0 | 100 | 0 | 0
6005 | 652.33 | 0 | 26.5 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 53.6732 | 664.6924 | 0 | 0.05921 | 6.1863 | 0 | 0 | 0 | 0 | off_peak | 652.33 | 0 | 100 | 0 | 0 | 100 | 0 | 0
6006 | 734.85 | 0 | 26.5 | 0 | 0 | 0 | 0 | 8.7006 | 8.7006 | 0 | 0 | 0 | 61.8119 | 743.5506 | 0 | 0.05921 | 5.5553 | 0 | 0 | 0 | 0 | off_peak | 734.85 | 0 | 100 | 0 | 0 | 100 | 0 | 0
6007 | 780.12 | 33.5016 | 26.8 | 5.3921 | 5.3921 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 61.8119 | 774.7279 | 0 | 0.05921 | 5.0413 | 0 | 0 | 0 | 5.3921 | off_peak | 774.7279 |  |  | 0.69 | 0 | 99.31 | 27.1831 | 0
6008 | 800.77 | 172.966 | 27.2 | 27.7986 | 27.7986 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 73.3758 | 785.3338 | 0 | 0.05921 | 4.6882 | 0 | 0 | 0 | 27.7986 | off_peak | 772.9714 | 0 | 100 | 3.47 | 0 | 96.53 | 130.3245 | 0
6009 | 795.68 | 446.992 | 27.7 | 71.7089 | 71.7089 | 0 | 0 | 0.79843 | 0.79843 | 0 | 0 | 0 | 74.1227 | 724.7696 | 0 | 0.05921 | 4.4346 | 0 | 0 | 0 | 71.7089 | off_peak | 723.9711 | 0 | 100 | 9.01 | 0 | 90.99 | 317.9982 | 0
6010 | 825.37 | 511.611 | 28.4 | 81.8665 | 81.8665 | 0 | 0 | 0.051567 | 0.051567 | 0 | 0 | 0 | 74.1709 | 743.555 | 0 | 0.05921 | 4.3292 | 0 | 0 | 0 | 81.8665 | off_peak | 743.5035 | 0 | 100 | 9.92 | 0 | 90.08 | 354.4175 | 0
6011 | 849.12 | 766.034 | 29 | 122.3105 | 122.3105 | 0 | 0 | 0.0033305 | 0.0033305 | 0 | 0 | 0 | 74.174 | 726.8128 | 0 | 0.05921 | 4.4651 | 0 | 0 | 0 | 122.3105 | off_peak | 726.8095 | 0 | 100 | 14.4 | 0 | 85.6 | 546.1289 | 0
6012 | 898.96 | 850.472 | 29.6 | 135.4949 | 135.4949 | 0 | 0 | 0.0002151 | 0.0002151 | 0 | 0 | 0 | 74.1742 | 763.4653 | 0 | 0.05921 | 4.7919 | 0 | 0 | 0 | 135.4949 | off_peak | 763.4651 | 0 | 100 | 15.07 | 0 | 84.93 | 649.2753 | 0
6013 | 900.61 | 807.399 | 30.1 | 128.3972 | 128.3972 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1742 | 772.2128 | 0 | 0.088511 | 4.9253 | 0 | 0 | 0 | 128.3972 | on_peak | 772.2128 |  |  | 14.26 | 0 | 85.74 | 632.3968 | 0
6014 | 863.7 | 831.412 | 30.3 | 132.1189 | 132.1189 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1742 | 731.5811 | 0 | 0.088511 | 5.0917 | 0 | 0 | 0 | 132.1189 | on_peak | 731.5811 |  |  | 15.3 | 0 | 84.7 | 672.7149 | 0
6015 | 896.27 | 718.844 | 30.4 | 114.1889 | 114.1889 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1742 | 782.0811 | 0 | 0.088511 | 5.3438 | 0 | 0 | 0 | 114.1889 | on_peak | 782.0811 |  |  | 12.74 | 0 | 87.26 | 610.2042 | 0
6016 | 872.55 | 492.011 | 30.3 | 78.185 | 78.185 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1742 | 794.365 | 0 | 0.088511 | 5.8503 | 0 | 0 | 0 | 78.185 | on_peak | 794.365 |  |  | 8.96 | 0 | 91.04 | 457.4068 | 0
6017 | 832.68 | 320.209 | 30 | 50.9401 | 50.9401 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1742 | 781.7399 | 0 | 0.088511 | 6.4385 | 0 | 0 | 0 | 50.9401 | on_peak | 781.7399 |  |  | 6.12 | 0 | 93.88 | 327.9779 | 0
6018 | 896.44 | 129.765 | 29.5 | 20.6814 | 20.6814 | 0 | 0 | 0 | 0 | 22.9831 | 22.9831 | 0 | 49.6043 | 852.7755 | 0 | 0.088511 | 6.964 | 0 | 0 | 0 | 20.6814 | on_peak | 852.7755 |  |  | 2.31 | 2.56 | 95.13 | 144.0244 | 0
6019 | 851.67 | 0 | 29.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 49.6043 | 851.67 | 0 | 0.088511 | 7.2002 | 0 | 0 | 0 | 0 | on_peak | 851.67 |  |  | 0 | 0 | 100 | 0 | 0
6020 | 798.56 | 0 | 28.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 49.6043 | 798.56 | 0 | 0.088511 | 7.5383 | 0 | 0 | 0 | 0 | on_peak | 798.56 |  |  | 0 | 0 | 100 | 0 | 0
6021 | 801.87 | 0 | 28.4 | 0 | 0 | 0 | 0 | 0 | 0 | 39.4622 | 39.4622 | 0 | 7.4174 | 762.4078 | 0 | 0.088511 | 7.7794 | 0 | 0 | 0 | 0 | on_peak | 762.4078 |  |  | 0 | 4.92 | 95.08 | 0 | 0
6022 | 795.68 | 0 | 28.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 795.68 | 0 | 0.05921 | 7.8028 | 0 | 0 | 0 | 0 | off_peak | 795.68 |  |  | 0 | 0 | 100 | 0 | 0
6023 | 794.88 | 0 | 27.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 794.88 | 0 | 0.05921 | 7.8228 | 0 | 0 | 0 | 0 | off_peak | 794.88 |  |  | 0 | 0 | 100 | 0 | 0
6024 | 784.47 | 0 | 27.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 784.47 | 0 | 0.05921 | 7.6583 | 0 | 0 | 0 | 0 | off_peak | 784.47 |  |  | 0 | 0 | 100 | 0 | 0
6025 | 696.78 | 0 | 27 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 696.78 | 0 | 0.05921 | 7.4173 | 0 | 0 | 0 | 0 | off_peak | 696.78 |  |  | 0 | 0 | 100 | 0 | 0
6026 | 639.43 | 0 | 26.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 639.43 | 0 | 0.05921 | 7.1571 | 0 | 0 | 0 | 0 | off_peak | 639.43 |  |  | 0 | 0 | 100 | 0 | 0
6027 | 627.91 | 0 | 26.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 627.91 | 0 | 0.05921 | 6.6478 | 0 | 0 | 0 | 0 | off_peak | 627.91 |  |  | 0 | 0 | 100 | 0 | 0
6028 | 629.9 | 0 | 26.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 629.9 | 0 | 0.05921 | 6.1479 | 0 | 0 | 0 | 0 | off_peak | 629.9 |  |  | 0 | 0 | 100 | 0 | 0
6029 | 643.58 | 0 | 25.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 643.58 | 0 | 0.05921 | 5.6465 | 0 | 0 | 0 | 0 | off_peak | 643.58 |  |  | 0 | 0 | 100 | 0 | 0
6030 | 704.76 | 0 | 25.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 704.76 | 0 | 0.05921 | 4.9269 | 0 | 0 | 0 | 0 | off_peak | 704.76 |  |  | 0 | 0 | 100 | 0 | 0
6031 | 744.25 | 13.3 | 26.1 | 2.1461 | 2.1461 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 742.1039 | 0 | 0.05921 | 4.5025 | 0 | 0 | 0 | 2.1461 | off_peak | 742.1039 |  |  | 0.29 | 0 | 99.71 | 9.6628 | 0
6032 | 782.92 | 23.75 | 26.6 | 3.8253 | 3.8253 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 779.0947 | 0 | 0.05921 | 4.2092 | 0 | 0 | 0 | 3.8253 | off_peak | 779.0947 |  |  | 0.49 | 0 | 99.51 | 16.1014 | 0
6033 | 757.33 | 57.95 | 27.3 | 9.3102 | 9.3102 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 748.0198 | 0 | 0.05921 | 4.0026 | 0 | 0 | 0 | 9.3102 | off_peak | 748.0198 |  |  | 1.23 | 0 | 98.77 | 37.2653 | 0
6034 | 792.35 | 128.919 | 28 | 20.6593 | 20.6593 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 771.6907 | 0 | 0.05921 | 3.8922 | 0 | 0 | 0 | 20.6593 | off_peak | 771.6907 |  |  | 2.61 | 0 | 97.39 | 80.4109 | 0
6035 | 799.18 | 498.254 | 28.7 | 79.642 | 79.642 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 719.538 | 0 | 0.05921 | 3.8593 | 0 | 0 | 0 | 79.642 | off_peak | 719.538 |  |  | 9.97 | 0 | 90.03 | 307.3636 | 0
6036 | 798.61 | 228.789 | 29.4 | 36.4767 | 36.4767 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 762.1333 | 0 | 0.05921 | 3.9556 | 0 | 0 | 0 | 36.4767 | off_peak | 762.1333 |  |  | 4.57 | 0 | 95.43 | 144.287 | 0
6037 | 752.08 | 38.95 | 29.9 | 6.1986 | 6.1986 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 745.8814 | 0 | 0.05921 | 4.0625 | 0 | 0 | 0 | 6.1986 | off_peak | 745.8814 |  |  | 0.82 | 0 | 99.18 | 25.1819 | 0
6038 | 750.5 | 191.797 | 30.3 | 30.4783 | 30.4783 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 720.0217 | 0 | 0.05921 | 4.3311 | 0 | 0 | 0 | 30.4783 | off_peak | 720.0217 |  |  | 4.06 | 0 | 95.94 | 132.0039 | 0
6039 | 756.24 | 190.553 | 30.6 | 30.2473 | 30.2473 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 725.9927 | 0 | 0.05921 | 4.6058 | 0 | 0 | 0 | 30.2473 | off_peak | 725.9927 |  |  | 4 | 0 | 96 | 139.3127 | 0
6040 | 727.28 | 102.6 | 30.6 | 16.2861 | 16.2861 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 710.9939 | 0 | 0.05921 | 5.1025 | 0 | 0 | 0 | 16.2861 | off_peak | 710.9939 |  |  | 2.24 | 0 | 97.76 | 83.1006 | 0
6041 | 749.04 | 65.55 | 30.5 | 10.4088 | 10.4088 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 738.6312 | 0 | 0.05921 | 5.7759 | 0 | 0 | 0 | 10.4088 | off_peak | 738.6312 |  |  | 1.39 | 0 | 98.61 | 60.1205 | 0
6042 | 690.72 | 21.85 | 30.2 | 3.4734 | 3.4734 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 687.2466 | 0 | 0.05921 | 6.2644 | 0 | 0 | 0 | 3.4734 | off_peak | 687.2466 |  |  | 0.5 | 0 | 99.5 | 21.7591 | 0
6043 | 661.11 | 0 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 661.11 | 0 | 0.05921 | 6.8276 | 0 | 0 | 0 | 0 | off_peak | 661.11 |  |  | 0 | 0 | 100 | 0 | 0
6044 | 675.79 | 0 | 29.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 675.79 | 0 | 0.05921 | 6.9964 | 0 | 0 | 0 | 0 | off_peak | 675.79 |  |  | 0 | 0 | 100 | 0 | 0
6045 | 608.33 | 0 | 29.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 608.33 | 0 | 0.05921 | 7.1354 | 0 | 0 | 0 | 0 | off_peak | 608.33 |  |  | 0 | 0 | 100 | 0 | 0
6046 | 615.44 | 0 | 28.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 615.44 | 0 | 0.05921 | 6.9826 | 0 | 0 | 0 | 0 | off_peak | 615.44 |  |  | 0 | 0 | 100 | 0 | 0
6047 | 641.36 | 0 | 28.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 641.36 | 0 | 0.05921 | 7.2158 | 0 | 0 | 0 | 0 | off_peak | 641.36 |  |  | 0 | 0 | 100 | 0 | 0
6048 | 648.01 | 0 | 28 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 648.01 | 0 | 0.05921 | 7.4864 | 0 | 0 | 0 | 0 | off_peak | 648.01 |  |  | 0 | 0 | 100 | 0 | 0
6049 | 639.63 | 0 | 27.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 639.63 | 0 | 0.05921 | 7.4054 | 0 | 0 | 0 | 0 | off_peak | 639.63 |  |  | 0 | 0 | 100 | 0 | 0
6050 | 625.91 | 0 | 27.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 625.91 | 0 | 0.05921 | 7.1845 | 0 | 0 | 0 | 0 | off_peak | 625.91 |  |  | 0 | 0 | 100 | 0 | 0
6051 | 623.46 | 0 | 26.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 623.46 | 0 | 0.05921 | 6.7257 | 0 | 0 | 0 | 0 | off_peak | 623.46 |  |  | 0 | 0 | 100 | 0 | 0
6052 | 652.09 | 0 | 26.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 652.09 | 0 | 0.05921 | 6.2321 | 0 | 0 | 0 | 0 | off_peak | 652.09 |  |  | 0 | 0 | 100 | 0 | 0
6053 | 644.76 | 0 | 26.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 644.76 | 0 | 0.05921 | 5.6137 | 0 | 0 | 0 | 0 | off_peak | 644.76 |  |  | 0 | 0 | 100 | 0 | 0
6054 | 687.49 | 0 | 26.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 687.49 | 0 | 0.05921 | 5.129 | 0 | 0 | 0 | 0 | off_peak | 687.49 |  |  | 0 | 0 | 100 | 0 | 0
6055 | 700.12 | 13.3 | 26.5 | 2.143 | 2.143 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 697.977 | 0 | 0.05921 | 4.688 | 0 | 0 | 0 | 2.143 | off_peak | 697.977 |  |  | 0.31 | 0 | 99.69 | 10.0462 | 0
6056 | 752.5 | 19 | 27 | 3.0558 | 3.0558 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 749.4442 | 0 | 0.05921 | 4.3517 | 0 | 0 | 0 | 3.0558 | off_peak | 749.4442 |  |  | 0.41 | 0 | 99.59 | 13.2982 | 0
6057 | 712.66 | 42.75 | 27.6 | 6.8607 | 6.8607 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 705.7993 | 0 | 0.05921 | 4.1528 | 0 | 0 | 0 | 6.8607 | off_peak | 705.7993 |  |  | 0.96 | 0 | 99.04 | 28.4913 | 0
6058 | 748.34 | 93.1 | 28.2 | 14.9085 | 14.9085 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 733.4315 | 0 | 0.05921 | 4.0126 | 0 | 0 | 0 | 14.9085 | off_peak | 733.4315 |  |  | 1.99 | 0 | 98.01 | 59.8213 | 0
6059 | 736.85 | 89.3 | 28.9 | 14.2635 | 14.2635 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 722.5865 | 0 | 0.05921 | 3.975 | 0 | 0 | 0 | 14.2635 | off_peak | 722.5865 |  |  | 1.94 | 0 | 98.06 | 56.698 | 0
6060 | 743.32 | 78.85 | 29.5 | 12.5668 | 12.5668 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 730.7532 | 0 | 0.05921 | 4.0141 | 0 | 0 | 0 | 12.5668 | off_peak | 730.7532 |  |  | 1.69 | 0 | 98.31 | 50.4448 | 0
6061 | 745.81 | 87.4 | 30 | 13.9039 | 13.9039 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 731.9061 | 0 | 0.05921 | 4.1309 | 0 | 0 | 0 | 13.9039 | off_peak | 731.9061 |  |  | 1.86 | 0 | 98.14 | 57.436 | 0
6062 | 723.59 | 56.05 | 30.3 | 8.9069 | 8.9069 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 714.6831 | 0 | 0.05921 | 4.4152 | 0 | 0 | 0 | 8.9069 | off_peak | 714.6831 |  |  | 1.23 | 0 | 98.77 | 39.3253 | 0
6063 | 743.05 | 78.85 | 30.4 | 12.5254 | 12.5254 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 730.5246 | 0 | 0.05921 | 4.7567 | 0 | 0 | 0 | 12.5254 | off_peak | 730.5246 |  |  | 1.69 | 0 | 98.31 | 59.5799 | 0
6064 | 752.8 | 57.95 | 30.4 | 9.2054 | 9.2054 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 743.5946 | 0 | 0.05921 | 5.3695 | 0 | 0 | 0 | 9.2054 | off_peak | 743.5946 |  |  | 1.22 | 0 | 98.78 | 49.4287 | 0
6065 | 710.22 | 38.95 | 30.3 | 6.1895 | 6.1895 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 704.0305 | 0 | 0.05921 | 6.095 | 0 | 0 | 0 | 6.1895 | off_peak | 704.0305 |  |  | 0.87 | 0 | 99.13 | 37.7253 | 0
6066 | 704.31 | 10.45 | 29.8 | 1.6636 | 1.6636 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 702.6464 | 0 | 0.05921 | 6.8304 | 0 | 0 | 0 | 1.6636 | off_peak | 702.6464 |  |  | 0.24 | 0 | 99.76 | 11.3633 | 0
6067 | 616.43 | 0 | 29.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 616.43 | 0 | 0.05921 | 7.354 | 0 | 0 | 0 | 0 | off_peak | 616.43 |  |  | 0 | 0 | 100 | 0 | 0
6068 | 645 | 0 | 29 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 645 | 0 | 0.05921 | 7.4975 | 0 | 0 | 0 | 0 | off_peak | 645 |  |  | 0 | 0 | 100 | 0 | 0
6069 | 594.71 | 0 | 28.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 594.71 | 0 | 0.05921 | 7.5925 | 0 | 0 | 0 | 0 | off_peak | 594.71 |  |  | 0 | 0 | 100 | 0 | 0
6070 | 634.01 | 0 | 28.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 634.01 | 0 | 0.05921 | 8.0175 | 0 | 0 | 0 | 0 | off_peak | 634.01 |  |  | 0 | 0 | 100 | 0 | 0
6071 | 597.17 | 0 | 28 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 597.17 | 0 | 0.05921 | 8.1386 | 0 | 0 | 0 | 0 | off_peak | 597.17 |  |  | 0 | 0 | 100 | 0 | 0
6072 | 621.12 | 0 | 27.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 621.12 | 0 | 0.05921 | 8.3795 | 0 | 0 | 0 | 0 | off_peak | 621.12 |  |  | 0 | 0 | 100 | 0 | 0
6073 | 627.21 | 0 | 27.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 627.21 | 0 | 0.05921 | 8.3081 | 0 | 0 | 0 | 0 | off_peak | 627.21 |  |  | 0 | 0 | 100 | 0 | 0
6074 | 617.51 | 0 | 27 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 617.51 | 0 | 0.05921 | 8.0232 | 0 | 0 | 0 | 0 | off_peak | 617.51 |  |  | 0 | 0 | 100 | 0 | 0
6075 | 625.1 | 0 | 26.7 | 0 | 0 | 0 | 0 | 8.7006 | 8.7006 | 0 | 0 | 0 | 15.5561 | 633.8006 | 0 | 0.05921 | 7.452 | 0 | 0 | 0 | 0 | off_peak | 625.1 | 0 | 100 | 0 | 0 | 100 | 0 | 0
6076 | 611.32 | 0 | 26.5 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 27.12 | 623.6824 | 0 | 0.05921 | 6.8293 | 0 | 0 | 0 | 0 | off_peak | 611.32 | 0 | 100 | 0 | 0 | 100 | 0 | 0
6077 | 613.7 | 0 | 26.4 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 38.684 | 626.0624 | 0 | 0.05921 | 6.0642 | 0 | 0 | 0 | 0 | off_peak | 613.7 | 0 | 100 | 0 | 0 | 100 | 0 | 0
6078 | 741.16 | 0 | 26.5 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 50.2479 | 753.5224 | 0 | 0.05921 | 5.4696 | 0 | 0 | 0 | 0 | off_peak | 741.16 | 0 | 100 | 0 | 0 | 100 | 0 | 0
6079 | 830.46 | 28.4613 | 26.8 | 4.5809 | 4.5809 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 61.8119 | 838.2415 | 0 | 0.05921 | 4.954 | 0 | 0 | 0 | 4.5809 | off_peak | 825.8791 | 0 | 100 | 0.55 | 0 | 99.45 | 22.6938 | 0
6080 | 795.93 | 217.558 | 27.2 | 34.9653 | 34.9653 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 73.3758 | 773.3271 | 0 | 0.05921 | 4.6129 | 0 | 0 | 0 | 34.9653 | off_peak | 760.9647 | 0 | 100 | 4.39 | 0 | 95.61 | 161.291 | 0
6081 | 793.13 | 428.748 | 27.6 | 68.8071 | 68.8071 | 0 | 0 | 0.79843 | 0.79843 | 0 | 0 | 0 | 74.1227 | 725.1214 | 0 | 0.05921 | 4.4028 | 0 | 0 | 0 | 68.8071 | off_peak | 724.3229 | 0 | 100 | 8.68 | 0 | 91.32 | 302.946 | 0
6082 | 787.65 | 580.433 | 28.1 | 92.9808 | 92.9808 | 0 | 0 | 0.051567 | 0.051567 | 0 | 0 | 0 | 74.1709 | 694.7208 | 0 | 0.05921 | 4.3541 | 0 | 0 | 0 | 92.9808 | off_peak | 694.6692 | 0 | 100 | 11.8 | 0 | 88.2 | 404.8522 | 0
6083 | 838.67 | 737.019 | 28.6 | 117.8497 | 117.8497 | 0 | 0 | 0.0033305 | 0.0033305 | 0 | 0 | 0 | 74.174 | 720.8236 | 0 | 0.05921 | 4.5278 | 0 | 0 | 0 | 117.8497 | off_peak | 720.8203 | 0 | 100 | 14.05 | 0 | 85.95 | 533.5954 | 0
6084 | 853.39 | 844.475 | 29.1 | 134.7857 | 134.7857 | 0 | 0 | 0.0002151 | 0.0002151 | 0 | 0 | 0 | 74.1742 | 718.6045 | 0 | 0.05921 | 4.8727 | 0 | 0 | 0 | 134.7857 | off_peak | 718.6043 | 0 | 100 | 15.79 | 0 | 84.21 | 656.7709 | 0
6085 | 813.49 | 864.63 | 29.4 | 137.8514 | 137.8514 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1742 | 675.6386 | 0 | 0.088511 | 4.9998 | 0 | 0 | 0 | 137.8514 | on_peak | 675.6386 |  |  | 16.95 | 0 | 83.05 | 689.2244 | 0
6086 | 844.5 | 834.426 | 29.6 | 132.9385 | 132.9385 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1742 | 711.5615 | 0 | 0.088511 | 5.186 | 0 | 0 | 0 | 132.9385 | on_peak | 711.5615 |  |  | 15.74 | 0 | 84.26 | 689.4135 | 0
6087 | 897.97 | 722.927 | 29.8 | 115.0904 | 115.0904 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1742 | 782.8796 | 0 | 0.088511 | 5.4776 | 0 | 0 | 0 | 115.0904 | on_peak | 782.8796 |  |  | 12.82 | 0 | 87.18 | 630.4155 | 0
6088 | 809.34 | 557.256 | 29.9 | 88.683 | 88.683 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1742 | 720.657 | 0 | 0.088511 | 5.9417 | 0 | 0 | 0 | 88.683 | on_peak | 720.657 |  |  | 10.96 | 0 | 89.04 | 526.9303 | 0
6089 | 825.05 | 225.721 | 29.8 | 35.9349 | 35.9349 | 0 | 0 | 0 | 0 | 62.4453 | 62.4453 | 0 | 7.4174 | 726.6698 | 0 | 0.088511 | 6.5925 | 0 | 0 | 0 | 35.9349 | on_peak | 726.6698 |  |  | 4.36 | 7.57 | 88.08 | 236.9022 | 0
6090 | 830.53 | 140.947 | 29.4 | 22.4717 | 22.4717 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 808.0583 | 0 | 0.088511 | 7.2292 | 0 | 0 | 0 | 22.4717 | on_peak | 808.0583 |  |  | 2.71 | 0 | 97.29 | 162.4525 | 0
6091 | 831.76 | 0 | 29.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 831.76 | 0 | 0.088511 | 7.9094 | 0 | 0 | 0 | 0 | on_peak | 831.76 |  |  | 0 | 0 | 100 | 0 | 0
6092 | 833.41 | 0 | 28.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 833.41 | 0 | 0.088511 | 8.1985 | 0 | 0 | 0 | 0 | on_peak | 833.41 |  |  | 0 | 0 | 100 | 0 | 0
6093 | 799.98 | 0 | 28.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 799.98 | 0 | 0.088511 | 8.498 | 0 | 0 | 0 | 0 | on_peak | 799.98 |  |  | 0 | 0 | 100 | 0 | 0
6094 | 814.06 | 0 | 28.3 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 18.9814 | 826.4224 | 0 | 0.05921 | 8.742 | 0 | 0 | 0 | 0 | off_peak | 814.06 | 0 | 100 | 0 | 0 | 100 | 0 | 0
6095 | 790.17 | 0 | 27.9 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 30.5453 | 802.5324 | 0 | 0.05921 | 8.8497 | 0 | 0 | 0 | 0 | off_peak | 790.17 | 0 | 100 | 0 | 0 | 100 | 0 | 0
6096 | 796.37 | 0 | 27.5 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 42.1093 | 808.7324 | 0 | 0.05921 | 8.9631 | 0 | 0 | 0 | 0 | off_peak | 796.37 | 0 | 100 | 0 | 0 | 100 | 0 | 0
6097 | 730.77 | 0 | 27.2 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 53.6732 | 743.1324 | 0 | 0.05921 | 8.7831 | 0 | 0 | 0 | 0 | off_peak | 730.77 | 0 | 100 | 0 | 0 | 100 | 0 | 0
6098 | 644.23 | 0 | 26.9 | 0 | 0 | 0 | 0 | 8.7006 | 8.7006 | 0 | 0 | 0 | 61.8119 | 652.9306 | 0 | 0.05921 | 8.4624 | 0 | 0 | 0 | 0 | off_peak | 644.23 | 0 | 100 | 0 | 0 | 100 | 0 | 0
6099 | 639.62 | 0 | 26.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 61.8119 | 639.62 | 0 | 0.05921 | 7.9368 | 0 | 0 | 0 | 0 | off_peak | 639.62 |  |  | 0 | 0 | 100 | 0 | 0
6100 | 634.55 | 0 | 26.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 61.8119 | 634.55 | 0 | 0.05921 | 7.3116 | 0 | 0 | 0 | 0 | off_peak | 634.55 |  |  | 0 | 0 | 100 | 0 | 0
6101 | 656.25 | 0 | 26.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 61.8119 | 656.25 | 0 | 0.05921 | 6.5632 | 0 | 0 | 0 | 0 | off_peak | 656.25 |  |  | 0 | 0 | 100 | 0 | 0
6102 | 712.05 | 0 | 26.2 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 73.3758 | 724.4124 | 0 | 0.05921 | 5.8704 | 0 | 0 | 0 | 0 | off_peak | 712.05 | 0 | 100 | 0 | 0 | 100 | 0 | 0
6103 | 738.98 | 41.6967 | 26.5 | 6.7184 | 6.7184 | 0 | 0 | 0.79843 | 0.79843 | 0 | 0 | 0 | 74.1227 | 733.06 | 0 | 0.05921 | 5.3313 | 0 | 0 | 0 | 6.7184 | off_peak | 732.2616 | 0 | 100 | 0.91 | 0 | 99.09 | 35.8174 | 0
6104 | 805.61 | 235.939 | 27 | 37.9469 | 37.9469 | 0 | 0 | 0.051567 | 0.051567 | 0 | 0 | 0 | 74.1709 | 767.7146 | 0 | 0.05921 | 4.9682 | 0 | 0 | 0 | 37.9469 | off_peak | 767.6631 | 0 | 100 | 4.71 | 0 | 95.29 | 188.5276 | 0
6105 | 824.07 | 450.662 | 27.5 | 72.3502 | 72.3502 | 0 | 0 | 0.0033305 | 0.0033305 | 0 | 0 | 0 | 74.174 | 751.7232 | 0 | 0.05921 | 4.7509 | 0 | 0 | 0 | 72.3502 | off_peak | 751.7198 | 0 | 100 | 8.78 | 0 | 91.22 | 343.7313 | 0
6106 | 847.65 | 640.184 | 28.2 | 102.5151 | 102.5151 | 0 | 0 | 0.0002151 | 0.0002151 | 0 | 0 | 0 | 74.1742 | 745.1351 | 0 | 0.05921 | 4.6705 | 0 | 0 | 0 | 102.5151 | off_peak | 745.1349 | 0 | 100 | 12.09 | 0 | 87.91 | 478.7915 | 0
6107 | 802.89 | 790.497 | 28.9 | 126.2625 | 126.2625 | 0 | 0 | 1.4852e-05 | 1.4852e-05 | 0 | 0 | 0 | 74.1743 | 676.6275 | 0 | 0.05921 | 4.8085 | 0 | 0 | 0 | 126.2625 | off_peak | 676.6275 | 0 | 100 | 15.73 | 0 | 84.27 | 607.1338 | 0
6108 | 830.62 | 839.662 | 29.6 | 133.7727 | 133.7727 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1743 | 696.8473 | 0 | 0.05921 | 5.1333 | 0 | 0 | 0 | 133.7727 | off_peak | 696.8473 |  |  | 16.11 | 0 | 83.89 | 686.6916 | 0
6109 | 865.83 | 894.191 | 30.1 | 142.1993 | 142.1993 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1743 | 723.6307 | 0 | 0.088511 | 5.2591 | 0 | 0 | 0 | 142.1993 | on_peak | 723.6307 |  |  | 16.42 | 0 | 83.58 | 747.8338 | 0
6110 | 871.85 | 811.868 | 30.5 | 128.9185 | 128.9185 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1743 | 742.9315 | 0 | 0.088511 | 5.3787 | 0 | 0 | 0 | 128.9185 | on_peak | 742.9315 |  |  | 14.79 | 0 | 85.21 | 693.4098 | 0
6111 | 852.2 | 730.261 | 30.7 | 115.8747 | 115.8747 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1743 | 736.3253 | 0 | 0.088511 | 5.6102 | 0 | 0 | 0 | 115.8747 | on_peak | 736.3253 |  |  | 13.6 | 0 | 86.4 | 650.0829 | 0
6112 | 793.8 | 563.918 | 30.7 | 89.4801 | 89.4801 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1743 | 704.3199 | 0 | 0.088511 | 6.0504 | 0 | 0 | 0 | 89.4801 | on_peak | 704.3199 |  |  | 11.27 | 0 | 88.73 | 541.3928 | 0
6113 | 814.61 | 361.22 | 30.4 | 57.3801 | 57.3801 | 0 | 0 | 0 | 0 | 62.4453 | 62.4453 | 0 | 7.4174 | 694.7846 | 0 | 0.088511 | 6.7485 | 0 | 0 | 0 | 57.3801 | on_peak | 694.7846 |  |  | 7.04 | 7.67 | 85.29 | 387.2303 | 0
6114 | 816.54 | 147.371 | 29.9 | 23.453 | 23.453 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 793.087 | 0 | 0.088511 | 7.4205 | 0 | 0 | 0 | 23.453 | on_peak | 793.087 |  |  | 2.87 | 0 | 97.13 | 174.0333 | 0
6115 | 834.23 | 0 | 29.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 834.23 | 0 | 0.088511 | 7.9497 | 0 | 0 | 0 | 0 | on_peak | 834.23 |  |  | 0 | 0 | 100 | 0 | 0
6116 | 810.02 | 0 | 29 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 810.02 | 0 | 0.088511 | 8.1351 | 0 | 0 | 0 | 0 | on_peak | 810.02 |  |  | 0 | 0 | 100 | 0 | 0
6117 | 775.29 | 0 | 28.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 775.29 | 0 | 0.088511 | 8.3241 | 0 | 0 | 0 | 0 | on_peak | 775.29 |  |  | 0 | 0 | 100 | 0 | 0
6118 | 780.94 | 0 | 28.3 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 18.9814 | 793.3024 | 0 | 0.05921 | 8.4413 | 0 | 0 | 0 | 0 | off_peak | 780.94 | 0 | 100 | 0 | 0 | 100 | 0 | 0
6119 | 800.14 | 0 | 28 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18.9814 | 800.14 | 0 | 0.05921 | 8.6896 | 0 | 0 | 0 | 0 | off_peak | 800.14 |  |  | 0 | 0 | 100 | 0 | 0
6120 | 770.1 | 0 | 27.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18.9814 | 770.1 | 0 | 0.05921 | 8.6082 | 0 | 0 | 0 | 0 | off_peak | 770.1 |  |  | 0 | 0 | 100 | 0 | 0
6121 | 714.38 | 0 | 27.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18.9814 | 714.38 | 0 | 0.05921 | 8.526 | 0 | 0 | 0 | 0 | off_peak | 714.38 |  |  | 0 | 0 | 100 | 0 | 0
6122 | 650.11 | 0 | 27.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18.9814 | 650.11 | 0 | 0.05921 | 8.2895 | 0 | 0 | 0 | 0 | off_peak | 650.11 |  |  | 0 | 0 | 100 | 0 | 0
6123 | 602.05 | 0 | 27 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18.9814 | 602.05 | 0 | 0.05921 | 7.8156 | 0 | 0 | 0 | 0 | off_peak | 602.05 |  |  | 0 | 0 | 100 | 0 | 0
6124 | 613.48 | 0 | 26.7 | 0 | 0 | 0 | 0 | 8.7006 | 8.7006 | 0 | 0 | 0 | 27.12 | 622.1806 | 0 | 0.05921 | 7.1729 | 0 | 0 | 0 | 0 | off_peak | 613.48 | 0 | 100 | 0 | 0 | 100 | 0 | 0
6125 | 639.41 | 0 | 26.6 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 38.684 | 651.7724 | 0 | 0.05921 | 6.4147 | 0 | 0 | 0 | 0 | off_peak | 639.41 | 0 | 100 | 0 | 0 | 100 | 0 | 0
6126 | 674.7 | 0 | 26.5 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 50.2479 | 687.0624 | 0 | 0.05921 | 5.8268 | 0 | 0 | 0 | 0 | off_peak | 674.7 | 0 | 100 | 0 | 0 | 100 | 0 | 0
6127 | 708.12 | 41.0823 | 26.6 | 6.617 | 6.617 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 61.8119 | 713.8654 | 0 | 0.05921 | 5.2917 | 0 | 0 | 0 | 6.617 | off_peak | 701.503 | 0 | 100 | 0.93 | 0 | 99.07 | 35.0153 | 0
6128 | 781.76 | 233.373 | 27.1 | 37.5206 | 37.5206 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 73.3758 | 756.6018 | 0 | 0.05921 | 4.9634 | 0 | 0 | 0 | 37.5206 | off_peak | 744.2394 | 0 | 100 | 4.8 | 0 | 95.2 | 186.2293 | 0
6129 | 800.94 | 444.841 | 27.8 | 71.3378 | 71.3378 | 0 | 0 | 0.79843 | 0.79843 | 0 | 0 | 0 | 74.1227 | 730.4006 | 0 | 0.05921 | 4.7435 | 0 | 0 | 0 | 71.3378 | off_peak | 729.6022 | 0 | 100 | 8.91 | 0 | 91.09 | 338.3932 | 0
6130 | 823.1 | 632.658 | 28.5 | 101.1992 | 101.1992 | 0 | 0 | 0.051567 | 0.051567 | 0 | 0 | 0 | 74.1709 | 721.9524 | 0 | 0.05921 | 4.6903 | 0 | 0 | 0 | 101.1992 | off_peak | 721.9008 | 0 | 100 | 12.29 | 0 | 87.71 | 474.6508 | 0
6131 | 807.27 | 773.23 | 29.2 | 123.3693 | 123.3693 | 0 | 0 | 0.0033305 | 0.0033305 | 0 | 0 | 0 | 74.174 | 683.9041 | 0 | 0.05921 | 4.8474 | 0 | 0 | 0 | 123.3693 | off_peak | 683.9007 | 0 | 100 | 15.28 | 0 | 84.72 | 598.0213 | 0
6132 | 894.96 | 183.35 | 29.8 | 29.1894 | 29.1894 | 0 | 0 | 0.0002151 | 0.0002151 | 0 | 0 | 0 | 74.1742 | 865.7708 | 0 | 0.05921 | 5.2122 | 0 | 0 | 0 | 29.1894 | off_peak | 865.7706 | 0 | 100 | 3.26 | 0 | 96.74 | 152.1417 | 0
6133 | 852.75 | 471.451 | 30.3 | 74.9178 | 74.9178 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1742 | 777.8322 | 0 | 0.088511 | 5.3189 | 0 | 0 | 0 | 74.9178 | on_peak | 777.8322 |  |  | 8.79 | 0 | 91.21 | 398.4796 | 0
6134 | 838.52 | 566.448 | 30.7 | 89.8816 | 89.8816 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1742 | 748.6384 | 0 | 0.088511 | 5.4575 | 0 | 0 | 0 | 89.8816 | on_peak | 748.6384 |  |  | 10.72 | 0 | 89.28 | 490.5303 | 0
6135 | 858.83 | 26.6 | 30.9 | 4.2177 | 4.2177 | 0 | 0 | 0 | 0 | 1.8368 | 1.8368 | 0 | 72.2106 | 852.7755 | 0 | 0.088511 | 5.6947 | 0 | 0 | 0 | 4.2177 | on_peak | 852.7755 |  |  | 0.49 | 0.21 | 99.3 | 24.0182 | 0
6136 | 843.91 | 405.1 | 30.9 | 64.2323 | 64.2323 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 72.2106 | 779.6777 | 0 | 0.088511 | 6.1011 | 0 | 0 | 0 | 64.2323 | on_peak | 779.6777 |  |  | 7.61 | 0 | 92.39 | 391.8864 | 0
6137 | 818.71 | 77.3593 | 30.7 | 12.275 | 12.275 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 72.2106 | 806.435 | 0 | 0.088511 | 6.6326 | 0 | 0 | 0 | 12.275 | on_peak | 806.435 |  |  | 1.5 | 0 | 98.5 | 81.415 | 0
6138 | 826.85 | 39.9 | 30.3 | 6.3405 | 6.3405 | 0 | 0 | 0 | 0 | 42.254 | 42.254 | 0 | 27.0392 | 778.2555 | 0 | 0.088511 | 7.254 | 0 | 0 | 0 | 6.3405 | on_peak | 778.2555 |  |  | 0.77 | 5.11 | 94.12 | 45.994 | 0
6139 | 796.17 | 0 | 29.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27.0392 | 796.17 | 0 | 0.088511 | 7.7656 | 0 | 0 | 0 | 0 | on_peak | 796.17 |  |  | 0 | 0 | 100 | 0 | 0
6140 | 871.13 | 0 | 29.4 | 0 | 0 | 0 | 0 | 0 | 0 | 18.3545 | 18.3545 | 0 | 7.4174 | 852.7755 | 0 | 0.088511 | 8.2757 | 0 | 0 | 0 | 0 | on_peak | 852.7755 |  |  | 0 | 2.11 | 97.89 | 0 | 0
6141 | 805.11 | 0 | 29 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 805.11 | 0 | 0.088511 | 8.4298 | 0 | 0 | 0 | 0 | on_peak | 805.11 |  |  | 0 | 0 | 100 | 0 | 0
6142 | 804.61 | 0 | 28.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 804.61 | 0 | 0.05921 | 8.7309 | 0 | 0 | 0 | 0 | off_peak | 804.61 |  |  | 0 | 0 | 100 | 0 | 0
6143 | 822.29 | 0 | 28.1 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 18.9814 | 834.6524 | 0 | 0.05921 | 8.7082 | 0 | 0 | 0 | 0 | off_peak | 822.29 | 0 | 100 | 0 | 0 | 100 | 0 | 0
6144 | 776.54 | 0 | 27.6 | 0 | 0 | 0 | 0 | 8.7006 | 8.7006 | 0 | 0 | 0 | 27.12 | 785.2406 | 0 | 0.05921 | 8.6463 | 0 | 0 | 0 | 0 | off_peak | 776.54 | 0 | 100 | 0 | 0 | 100 | 0 | 0
6145 | 702.12 | 0 | 27.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27.12 | 702.12 | 0 | 0.05921 | 8.4986 | 0 | 0 | 0 | 0 | off_peak | 702.12 |  |  | 0 | 0 | 100 | 0 | 0
6146 | 687.63 | 0 | 26.8 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 38.684 | 699.9924 | 0 | 0.05921 | 8.2569 | 0 | 0 | 0 | 0 | off_peak | 687.63 | 0 | 100 | 0 | 0 | 100 | 0 | 0
6147 | 630.36 | 0 | 26.5 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 50.2479 | 642.7224 | 0 | 0.05921 | 7.9308 | 0 | 0 | 0 | 0 | off_peak | 630.36 | 0 | 100 | 0 | 0 | 100 | 0 | 0
6148 | 647.31 | 0 | 26.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50.2479 | 647.31 | 0 | 0.05921 | 7.2144 | 0 | 0 | 0 | 0 | off_peak | 647.31 |  |  | 0 | 0 | 100 | 0 | 0
6149 | 642.26 | 0 | 26.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50.2479 | 642.26 | 0 | 0.05921 | 6.4771 | 0 | 0 | 0 | 0 | off_peak | 642.26 |  |  | 0 | 0 | 100 | 0 | 0
6150 | 702.53 | 0 | 26.2 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 61.8119 | 714.8924 | 0 | 0.05921 | 5.8154 | 0 | 0 | 0 | 0 | off_peak | 702.53 | 0 | 100 | 0 | 0 | 100 | 0 | 0
6151 | 789.64 | 38.5882 | 26.6 | 6.2153 | 6.2153 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 61.8119 | 783.4247 | 0 | 0.05921 | 5.3034 | 0 | 0 | 0 | 6.2153 | off_peak | 783.4247 |  |  | 0.79 | 0 | 99.21 | 32.9622 | 0
6152 | 825.19 | 228.427 | 27.2 | 36.7121 | 36.7121 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 73.3758 | 800.8403 | 0 | 0.05921 | 4.9574 | 0 | 0 | 0 | 36.7121 | off_peak | 788.4779 | 0 | 100 | 4.45 | 0 | 95.55 | 181.9949 | 0
6153 | 863.42 | 439.182 | 27.8 | 70.4303 | 70.4303 | 0 | 0 | 0.79843 | 0.79843 | 0 | 0 | 0 | 74.1227 | 793.7881 | 0 | 0.05921 | 4.7528 | 0 | 0 | 0 | 70.4303 | off_peak | 792.9897 | 0 | 100 | 8.16 | 0 | 91.84 | 334.7438 | 0
6154 | 819.34 | 625.83 | 28.4 | 100.1435 | 100.1435 | 0 | 0 | 0.051567 | 0.051567 | 0 | 0 | 0 | 74.1709 | 719.2481 | 0 | 0.05921 | 4.6588 | 0 | 0 | 0 | 100.1435 | off_peak | 719.1965 | 0 | 100 | 12.22 | 0 | 87.78 | 466.5447 | 0
6155 | 814.01 | 768.375 | 29 | 122.6843 | 122.6843 | 0 | 0 | 0.0033305 | 0.0033305 | 0 | 0 | 0 | 74.174 | 691.329 | 0 | 0.05921 | 4.82 | 0 | 0 | 0 | 122.6843 | off_peak | 691.3257 | 0 | 100 | 15.07 | 0 | 84.93 | 591.3379 | 0
6156 | 838.84 | 689.367 | 29.6 | 109.8281 | 109.8281 | 0 | 0 | 0.0002151 | 0.0002151 | 0 | 0 | 0 | 74.1742 | 729.0121 | 0 | 0.05921 | 5.1397 | 0 | 0 | 0 | 109.8281 | off_peak | 729.0119 | 0 | 100 | 13.09 | 0 | 86.91 | 564.4806 | 0
6157 | 843.87 | 871.284 | 30 | 138.6073 | 138.6073 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1742 | 705.2627 | 0 | 0.088511 | 5.2327 | 0 | 0 | 0 | 138.6073 | on_peak | 705.2627 |  |  | 16.43 | 0 | 83.57 | 725.2965 | 0
6158 | 875.74 | 824.198 | 30.4 | 130.9244 | 130.9244 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1742 | 744.8156 | 0 | 0.088511 | 5.4182 | 0 | 0 | 0 | 130.9244 | on_peak | 744.8156 |  |  | 14.95 | 0 | 85.05 | 709.3772 | 0
6159 | 883.78 | 709.699 | 30.6 | 112.6534 | 112.6534 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1742 | 771.1266 | 0 | 0.088511 | 5.6516 | 0 | 0 | 0 | 112.6534 | on_peak | 771.1266 |  |  | 12.75 | 0 | 87.25 | 636.6704 | 0
6160 | 845.87 | 544.566 | 30.7 | 86.4094 | 86.4094 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1742 | 759.4606 | 0 | 0.088511 | 6.0815 | 0 | 0 | 0 | 86.4094 | on_peak | 759.4606 |  |  | 10.22 | 0 | 89.78 | 525.5029 | 0
6161 | 858.56 | 343.288 | 30.5 | 54.5115 | 54.5115 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1742 | 804.0485 | 0 | 0.088511 | 6.6052 | 0 | 0 | 0 | 54.5115 | on_peak | 804.0485 |  |  | 6.35 | 0 | 93.65 | 360.0592 | 0
6162 | 897.3 | 133.342 | 30.1 | 21.2048 | 21.2048 | 0 | 0 | 0 | 0 | 23.3197 | 23.3197 | 0 | 49.2445 | 852.7755 | 0 | 0.088511 | 7.1944 | 0 | 0 | 0 | 21.2048 | on_peak | 852.7755 |  |  | 2.36 | 2.6 | 95.04 | 152.5568 | 0
6163 | 832.42 | 0 | 29.8 | 0 | 0 | 0 | 0 | 0 | 0 | 22.8012 | 22.8012 | 0 | 24.869 | 809.6188 | 0 | 0.088511 | 7.688 | 0 | 0 | 0 | 0 | on_peak | 809.6188 |  |  | 0 | 2.74 | 97.26 | 0 | 0
6164 | 869.1 | 0 | 29.3 | 0 | 0 | 0 | 0 | 0 | 0 | 16.3245 | 16.3245 | 0 | 7.4174 | 852.7755 | 0 | 0.088511 | 8.0735 | 0 | 0 | 0 | 0 | on_peak | 852.7755 |  |  | 0 | 1.88 | 98.12 | 0 | 0
6165 | 842.65 | 0 | 29 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 842.65 | 0 | 0.088511 | 8.3711 | 0 | 0 | 0 | 0 | on_peak | 842.65 |  |  | 0 | 0 | 100 | 0 | 0
6166 | 795.98 | 0 | 28.8 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 18.9814 | 808.3424 | 0 | 0.05921 | 8.5781 | 0 | 0 | 0 | 0 | off_peak | 795.98 | 0 | 100 | 0 | 0 | 100 | 0 | 0
6167 | 846.49 | 0 | 28.6 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 30.5453 | 858.8524 | 0 | 0.05921 | 8.66 | 0 | 0 | 0 | 0 | off_peak | 846.49 | 0 | 100 | 0 | 0 | 100 | 0 | 0
6168 | 820.52 | 0 | 28.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30.5453 | 820.52 | 0 | 0.05921 | 8.712 | 0 | 0 | 0 | 0 | off_peak | 820.52 |  |  | 0 | 0 | 100 | 0 | 0
6169 | 751.74 | 0 | 28.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30.5453 | 751.74 | 0 | 0.05921 | 8.494 | 0 | 0 | 0 | 0 | off_peak | 751.74 |  |  | 0 | 0 | 100 | 0 | 0
6170 | 674.24 | 0 | 27.9 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 42.1093 | 686.6024 | 0 | 0.05921 | 8.2251 | 0 | 0 | 0 | 0 | off_peak | 674.24 | 0 | 100 | 0 | 0 | 100 | 0 | 0
6171 | 642.92 | 0 | 27.7 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 53.6732 | 655.2824 | 0 | 0.05921 | 7.7216 | 0 | 0 | 0 | 0 | off_peak | 642.92 | 0 | 100 | 0 | 0 | 100 | 0 | 0
6172 | 645.39 | 0 | 27.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 53.6732 | 645.39 | 0 | 0.05921 | 7.0895 | 0 | 0 | 0 | 0 | off_peak | 645.39 |  |  | 0 | 0 | 100 | 0 | 0
6173 | 665.55 | 0 | 27.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 53.6732 | 665.55 | 0 | 0.05921 | 6.3656 | 0 | 0 | 0 | 0 | off_peak | 665.55 |  |  | 0 | 0 | 100 | 0 | 0
6174 | 737.96 | 0 | 26.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 53.6732 | 737.96 | 0 | 0.05921 | 5.73 | 0 | 0 | 0 | 0 | off_peak | 737.96 |  |  | 0 | 0 | 100 | 0 | 0
6175 | 805.81 | 39.3217 | 27.1 | 6.322 | 6.322 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 65.2371 | 811.8504 | 0 | 0.05921 | 5.2236 | 0 | 0 | 0 | 6.322 | off_peak | 799.488 | 0 | 100 | 0.78 | 0 | 99.22 | 33.0232 | 0
6176 | 818.1 | 231.072 | 27.5 | 37.0968 | 37.0968 | 0 | 0 | 8.9371 | 8.9371 | 0 | 0 | 0 | 73.597 | 789.9403 | 0 | 0.05921 | 4.8871 | 0 | 0 | 0 | 37.0968 | off_peak | 781.0032 | 0 | 100 | 4.53 | 0 | 95.47 | 181.294 | 0
6177 | 895.77 | 442.85 | 28.1 | 70.9411 | 70.9411 | 0 | 0 | 0.57721 | 0.57721 | 0 | 0 | 0 | 74.137 | 825.4061 | 0 | 0.05921 | 4.6459 | 0 | 0 | 0 | 70.9411 | off_peak | 824.8289 | 0 | 100 | 7.92 | 0 | 92.08 | 329.5843 | 0
6178 | 898.5 | 631.966 | 28.7 | 101.0148 | 101.0148 | 0 | 0 | 0.037279 | 0.037279 | 0 | 0 | 0 | 74.1718 | 797.5225 | 0 | 0.05921 | 4.5644 | 0 | 0 | 0 | 101.0148 | off_peak | 797.4852 | 0 | 100 | 11.24 | 0 | 88.76 | 461.0746 | 0
6179 | 869.06 | 776.685 | 29.4 | 123.8299 | 123.8299 | 0 | 0 | 0.0024077 | 0.0024077 | 0 | 0 | 0 | 74.1741 | 745.2325 | 0 | 0.05921 | 4.7084 | 0 | 0 | 0 | 123.8299 | off_peak | 745.2301 | 0 | 100 | 14.25 | 0 | 85.75 | 583.0404 | 0
6180 | 977.68 | 861.585 | 30 | 137.0644 | 137.0644 | 0 | 0 | 0.0001555 | 0.0001555 | 0 | 0 | 0 | 74.1742 | 840.6158 | 0 | 0.05921 | 5.0604 | 0 | 0 | 0 | 137.0644 | off_peak | 840.6156 | 0 | 100 | 14.02 | 0 | 85.98 | 693.5979 | 0
6181 | 870.61 | 880.65 | 30.5 | 139.8405 | 139.8405 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1742 | 730.7695 | 0 | 0.088511 | 5.2252 | 0 | 0 | 0 | 139.8405 | on_peak | 730.7695 |  |  | 16.06 | 0 | 83.94 | 730.7015 | 0
6182 | 946.99 | 832.87 | 30.8 | 132.1077 | 132.1077 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1742 | 814.8823 | 0 | 0.088511 | 5.4299 | 0 | 0 | 0 | 132.1077 | on_peak | 814.8823 |  |  | 13.95 | 0 | 86.05 | 717.3289 | 0
6183 | 891.67 | 719.277 | 31 | 114.006 | 114.006 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1742 | 777.664 | 0 | 0.088511 | 5.8054 | 0 | 0 | 0 | 114.006 | on_peak | 777.664 |  |  | 12.79 | 0 | 87.21 | 661.8534 | 0
6184 | 862.67 | 553.332 | 31 | 87.7036 | 87.7036 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1742 | 774.9664 | 0 | 0.088511 | 6.1973 | 0 | 0 | 0 | 87.7036 | on_peak | 774.9664 |  |  | 10.17 | 0 | 89.83 | 543.5214 | 0
6185 | 854.01 | 349.532 | 30.8 | 55.4419 | 55.4419 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1742 | 798.5681 | 0 | 0.088511 | 6.5901 | 0 | 0 | 0 | 55.4419 | on_peak | 798.5681 |  |  | 6.49 | 0 | 93.51 | 365.3676 | 0
6186 | 857.44 | 137.664 | 30.4 | 21.868 | 21.868 | 0 | 0 | 0 | 0 | 57.0308 | 57.0308 | 0 | 13.2057 | 778.5412 | 0 | 0.088511 | 6.9811 | 0 | 0 | 0 | 21.868 | on_peak | 778.5412 |  |  | 2.55 | 6.65 | 90.8 | 152.6631 | 0
6187 | 858.19 | 0 | 30.2 | 0 | 0 | 0 | 0 | 0 | 0 | 5.4145 | 5.4145 | 0 | 7.4174 | 852.7755 | 0 | 0.088511 | 7.2953 | 0 | 0 | 0 | 0 | on_peak | 852.7755 |  |  | 0 | 0.63 | 99.37 | 0 | 0
6188 | 802.22 | 0 | 29.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 802.22 | 0 | 0.088511 | 7.5313 | 0 | 0 | 0 | 0 | on_peak | 802.22 |  |  | 0 | 0 | 100 | 0 | 0
6189 | 804.62 | 0 | 29.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 804.62 | 0 | 0.088511 | 7.8177 | 0 | 0 | 0 | 0 | on_peak | 804.62 |  |  | 0 | 0 | 100 | 0 | 0
6190 | 808.65 | 0 | 29.4 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 18.9814 | 821.0124 | 0 | 0.05921 | 7.986 | 0 | 0 | 0 | 0 | off_peak | 808.65 | 0 | 100 | 0 | 0 | 100 | 0 | 0
6191 | 771.64 | 0 | 29.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18.9814 | 771.64 | 0 | 0.05921 | 8.2002 | 0 | 0 | 0 | 0 | off_peak | 771.64 |  |  | 0 | 0 | 100 | 0 | 0
6192 | 780.36 | 0 | 28.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18.9814 | 780.36 | 0 | 0.05921 | 8.2955 | 0 | 0 | 0 | 0 | off_peak | 780.36 |  |  | 0 | 0 | 100 | 0 | 0
6193 | 727.78 | 0 | 28.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18.9814 | 727.78 | 0 | 0.05921 | 8.0107 | 0 | 0 | 0 | 0 | off_peak | 727.78 |  |  | 0 | 0 | 100 | 0 | 0
6194 | 640.29 | 0 | 28.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18.9814 | 640.29 | 0 | 0.05921 | 7.7217 | 0 | 0 | 0 | 0 | off_peak | 640.29 |  |  | 0 | 0 | 100 | 0 | 0
6195 | 627.19 | 0 | 28.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18.9814 | 627.19 | 0 | 0.05921 | 7.1397 | 0 | 0 | 0 | 0 | off_peak | 627.19 |  |  | 0 | 0 | 100 | 0 | 0
6196 | 646.02 | 0 | 28 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18.9814 | 646.02 | 0 | 0.05921 | 6.664 | 0 | 0 | 0 | 0 | off_peak | 646.02 |  |  | 0 | 0 | 100 | 0 | 0
6197 | 620.32 | 0 | 28 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18.9814 | 620.32 | 0 | 0.05921 | 6.041 | 0 | 0 | 0 | 0 | off_peak | 620.32 |  |  | 0 | 0 | 100 | 0 | 0
6198 | 702.21 | 0 | 28 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18.9814 | 702.21 | 0 | 0.05921 | 5.5254 | 0 | 0 | 0 | 0 | off_peak | 702.21 |  |  | 0 | 0 | 100 | 0 | 0
6199 | 772.25 | 38.5866 | 28.4 | 6.1745 | 6.1745 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18.9814 | 766.0755 | 0 | 0.05921 | 5.1164 | 0 | 0 | 0 | 6.1745 | off_peak | 766.0755 |  |  | 0.8 | 0 | 99.2 | 31.5911 | 0
6200 | 751.02 | 230.767 | 29 | 36.8459 | 36.8459 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18.9814 | 714.1741 | 0 | 0.05921 | 4.7419 | 0 | 0 | 0 | 36.8459 | off_peak | 714.1741 |  |  | 4.91 | 0 | 95.09 | 174.7212 | 0
6201 | 856.5 | 443.706 | 29.5 | 70.7159 | 70.7159 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18.9814 | 785.7841 | 0 | 0.05921 | 4.5142 | 0 | 0 | 0 | 70.7159 | off_peak | 785.7841 |  |  | 8.26 | 0 | 91.74 | 319.2252 | 0
6202 | 772.19 | 374.872 | 30 | 59.6361 | 59.6361 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18.9814 | 712.5539 | 0 | 0.05921 | 4.4008 | 0 | 0 | 0 | 59.6361 | off_peak | 712.5539 |  |  | 7.72 | 0 | 92.28 | 262.4468 | 0
6203 | 753.39 | 358.48 | 30.5 | 56.9239 | 56.9239 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18.9814 | 696.4661 | 0 | 0.05921 | 4.3664 | 0 | 0 | 0 | 56.9239 | off_peak | 696.4661 |  |  | 7.56 | 0 | 92.44 | 248.5546 | 0
6204 | 818.24 | 863.209 | 30.8 | 136.92 | 136.92 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18.9814 | 681.32 | 0 | 0.05921 | 4.4501 | 0 | 0 | 0 | 136.92 | off_peak | 681.32 |  |  | 16.73 | 0 | 83.27 | 609.3144 | 0
6205 | 745.64 | 879.623 | 31.1 | 139.3696 | 139.3696 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18.9814 | 606.2704 | 0 | 0.05921 | 4.6338 | 0 | 0 | 0 | 139.3696 | off_peak | 606.2704 |  |  | 18.69 | 0 | 81.31 | 645.8139 | 0
6206 | 733.91 | 744.421 | 31.2 | 117.9045 | 117.9045 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18.9814 | 616.0055 | 0 | 0.05921 | 4.8755 | 0 | 0 | 0 | 117.9045 | off_peak | 616.0055 |  |  | 16.07 | 0 | 83.93 | 574.8412 | 0
6207 | 740.72 | 713.313 | 31.2 | 112.9775 | 112.9775 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18.9814 | 627.7425 | 0 | 0.05921 | 5.2888 | 0 | 0 | 0 | 112.9775 | off_peak | 627.7425 |  |  | 15.25 | 0 | 84.75 | 597.5182 | 0
6208 | 704.65 | 544.786 | 31 | 86.349 | 86.349 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18.9814 | 618.301 | 0 | 0.05921 | 5.8363 | 0 | 0 | 0 | 86.349 | off_peak | 618.301 |  |  | 12.25 | 0 | 87.75 | 503.9578 | 0
6209 | 709.66 | 340.315 | 30.7 | 53.9997 | 53.9997 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18.9814 | 655.6603 | 0 | 0.05921 | 6.5141 | 0 | 0 | 0 | 53.9997 | off_peak | 655.6603 |  |  | 7.61 | 0 | 92.39 | 351.757 | 0
6210 | 686.33 | 128.418 | 30 | 20.4292 | 20.4292 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18.9814 | 665.9008 | 0 | 0.05921 | 7.0777 | 0 | 0 | 0 | 20.4292 | off_peak | 665.9008 |  |  | 2.98 | 0 | 97.02 | 144.5925 | 0
6211 | 635.06 | 0 | 29.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18.9814 | 635.06 | 0 | 0.05921 | 7.373 | 0 | 0 | 0 | 0 | off_peak | 635.06 |  |  | 0 | 0 | 100 | 0 | 0
6212 | 610.34 | 0 | 29 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18.9814 | 610.34 | 0 | 0.05921 | 7.3652 | 0 | 0 | 0 | 0 | off_peak | 610.34 |  |  | 0 | 0 | 100 | 0 | 0
6213 | 624.77 | 0 | 28.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18.9814 | 624.77 | 0 | 0.05921 | 7.5527 | 0 | 0 | 0 | 0 | off_peak | 624.77 |  |  | 0 | 0 | 100 | 0 | 0
6214 | 639.78 | 0 | 28.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18.9814 | 639.78 | 0 | 0.05921 | 7.6327 | 0 | 0 | 0 | 0 | off_peak | 639.78 |  |  | 0 | 0 | 100 | 0 | 0
6215 | 611.55 | 0 | 28.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18.9814 | 611.55 | 0 | 0.05921 | 7.655 | 0 | 0 | 0 | 0 | off_peak | 611.55 |  |  | 0 | 0 | 100 | 0 | 0
6216 | 656.74 | 0 | 28.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18.9814 | 656.74 | 0 | 0.05921 | 7.4815 | 0 | 0 | 0 | 0 | off_peak | 656.74 |  |  | 0 | 0 | 100 | 0 | 0
6217 | 630.37 | 0 | 28.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18.9814 | 630.37 | 0 | 0.05921 | 7.3633 | 0 | 0 | 0 | 0 | off_peak | 630.37 |  |  | 0 | 0 | 100 | 0 | 0
6218 | 635.78 | 0 | 28.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18.9814 | 635.78 | 0 | 0.05921 | 7.1671 | 0 | 0 | 0 | 0 | off_peak | 635.78 |  |  | 0 | 0 | 100 | 0 | 0
6219 | 647.87 | 0 | 28.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18.9814 | 647.87 | 0 | 0.05921 | 6.7053 | 0 | 0 | 0 | 0 | off_peak | 647.87 |  |  | 0 | 0 | 100 | 0 | 0
6220 | 645.01 | 0 | 28.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18.9814 | 645.01 | 0 | 0.05921 | 6.2789 | 0 | 0 | 0 | 0 | off_peak | 645.01 |  |  | 0 | 0 | 100 | 0 | 0
6221 | 627.42 | 0 | 28.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18.9814 | 627.42 | 0 | 0.05921 | 5.7318 | 0 | 0 | 0 | 0 | off_peak | 627.42 |  |  | 0 | 0 | 100 | 0 | 0
6222 | 672.84 | 0 | 28.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18.9814 | 672.84 | 0 | 0.05921 | 5.2919 | 0 | 0 | 0 | 0 | off_peak | 672.84 |  |  | 0 | 0 | 100 | 0 | 0
6223 | 703.42 | 35.0116 | 28.6 | 5.5984 | 5.5984 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18.9814 | 697.8216 | 0 | 0.05921 | 4.9062 | 0 | 0 | 0 | 5.5984 | off_peak | 697.8216 |  |  | 0.8 | 0 | 99.2 | 27.4669 | 0
6224 | 738.35 | 223.078 | 29.1 | 35.6052 | 35.6052 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18.9814 | 702.7448 | 0 | 0.05921 | 4.5965 | 0 | 0 | 0 | 35.6052 | off_peak | 702.7448 |  |  | 4.82 | 0 | 95.18 | 163.6591 | 0
6225 | 715.86 | 432.274 | 29.5 | 68.8939 | 68.8939 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18.9814 | 646.9661 | 0 | 0.05921 | 4.3644 | 0 | 0 | 0 | 68.8939 | off_peak | 646.9661 |  |  | 9.62 | 0 | 90.38 | 300.678 | 0
6226 | 754.53 | 619.499 | 29.9 | 98.5885 | 98.5885 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18.9814 | 655.9415 | 0 | 0.05921 | 4.2445 | 0 | 0 | 0 | 98.5885 | off_peak | 655.9415 |  |  | 13.07 | 0 | 86.93 | 418.4541 | 0
6227 | 741.58 | 769.61 | 30.2 | 122.3429 | 122.3429 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18.9814 | 619.2371 | 0 | 0.05921 | 4.1871 | 0 | 0 | 0 | 122.3429 | off_peak | 619.2371 |  |  | 16.5 | 0 | 83.5 | 512.2636 | 0
6228 | 730.14 | 853.079 | 30.5 | 135.4625 | 135.4625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18.9814 | 594.6775 | 0 | 0.05921 | 4.2204 | 0 | 0 | 0 | 135.4625 | off_peak | 594.6775 |  |  | 18.55 | 0 | 81.45 | 571.7112 | 0
6229 | 728.08 | 870.403 | 30.6 | 138.1626 | 138.1626 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18.9814 | 589.9174 | 0 | 0.05921 | 4.3627 | 0 | 0 | 0 | 138.1626 | off_peak | 589.9174 |  |  | 18.98 | 0 | 81.02 | 602.7618 | 0
6230 | 741.91 | 818.516 | 30.7 | 129.8786 | 129.8786 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18.9814 | 612.0314 | 0 | 0.05921 | 4.6759 | 0 | 0 | 0 | 129.8786 | off_peak | 612.0314 |  |  | 17.51 | 0 | 82.49 | 607.2956 | 0
6231 | 702.25 | 476.92 | 30.6 | 75.7035 | 75.7035 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18.9814 | 626.5465 | 0 | 0.05921 | 5.2386 | 0 | 0 | 0 | 75.7035 | off_peak | 626.5465 |  |  | 10.78 | 0 | 89.22 | 396.5793 | 0
6232 | 717.11 | 350.693 | 30.4 | 55.7078 | 55.7078 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18.9814 | 661.4022 | 0 | 0.05921 | 5.8149 | 0 | 0 | 0 | 55.7078 | off_peak | 661.4022 |  |  | 7.77 | 0 | 92.23 | 323.9355 | 0
6233 | 724.78 | 240.838 | 30 | 38.3135 | 38.3135 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18.9814 | 686.4665 | 0 | 0.05921 | 6.4472 | 0 | 0 | 0 | 38.3135 | off_peak | 686.4665 |  |  | 5.29 | 0 | 94.71 | 247.0151 | 0
6234 | 664.56 | 44.65 | 29.5 | 7.1161 | 7.1161 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18.9814 | 657.4439 | 0 | 0.05921 | 6.9775 | 0 | 0 | 0 | 7.1161 | off_peak | 657.4439 |  |  | 1.07 | 0 | 98.93 | 49.6531 | 0
6235 | 639.82 | 0 | 29.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18.9814 | 639.82 | 0 | 0.05921 | 7.2691 | 0 | 0 | 0 | 0 | off_peak | 639.82 |  |  | 0 | 0 | 100 | 0 | 0
6236 | 596.3 | 0 | 28.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18.9814 | 596.3 | 0 | 0.05921 | 7.6361 | 0 | 0 | 0 | 0 | off_peak | 596.3 |  |  | 0 | 0 | 100 | 0 | 0
6237 | 620.91 | 0 | 28.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18.9814 | 620.91 | 0 | 0.05921 | 7.6773 | 0 | 0 | 0 | 0 | off_peak | 620.91 |  |  | 0 | 0 | 100 | 0 | 0
6238 | 623.05 | 0 | 28.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18.9814 | 623.05 | 0 | 0.05921 | 7.8579 | 0 | 0 | 0 | 0 | off_peak | 623.05 |  |  | 0 | 0 | 100 | 0 | 0
6239 | 639.87 | 0 | 28.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18.9814 | 639.87 | 0 | 0.05921 | 7.9091 | 0 | 0 | 0 | 0 | off_peak | 639.87 |  |  | 0 | 0 | 100 | 0 | 0
6240 | 620.11 | 0 | 28.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18.9814 | 620.11 | 0 | 0.05921 | 7.9088 | 0 | 0 | 0 | 0 | off_peak | 620.11 |  |  | 0 | 0 | 100 | 0 | 0
6241 | 629.61 | 0 | 28.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18.9814 | 629.61 | 0 | 0.05921 | 8.004 | 0 | 0 | 0 | 0 | off_peak | 629.61 |  |  | 0 | 0 | 100 | 0 | 0
6242 | 615.81 | 0 | 28.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18.9814 | 615.81 | 0 | 0.05921 | 7.6972 | 0 | 0 | 0 | 0 | off_peak | 615.81 |  |  | 0 | 0 | 100 | 0 | 0
6243 | 602.54 | 0 | 28.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18.9814 | 602.54 | 0 | 0.05921 | 7.2821 | 0 | 0 | 0 | 0 | off_peak | 602.54 |  |  | 0 | 0 | 100 | 0 | 0
6244 | 609.98 | 0 | 28.3 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 30.5453 | 622.3424 | 0 | 0.05921 | 6.644 | 0 | 0 | 0 | 0 | off_peak | 609.98 | 0 | 100 | 0 | 0 | 100 | 0 | 0
6245 | 615.66 | 0 | 28.3 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 42.1093 | 628.0224 | 0 | 0.05921 | 5.84 | 0 | 0 | 0 | 0 | off_peak | 615.66 | 0 | 100 | 0 | 0 | 100 | 0 | 0
6246 | 724.24 | 0 | 28.3 | 0 | 0 | 0 | 0 | 8.7006 | 8.7006 | 0 | 0 | 0 | 50.2479 | 732.9406 | 0 | 0.05921 | 5.2554 | 0 | 0 | 0 | 0 | off_peak | 724.24 | 0 | 100 | 0 | 0 | 100 | 0 | 0
6247 | 778.28 | 35.7786 | 28.6 | 5.721 | 5.721 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 61.8119 | 784.9214 | 0 | 0.05921 | 4.7813 | 0 | 0 | 0 | 5.721 | off_peak | 772.559 | 0 | 100 | 0.74 | 0 | 99.26 | 27.3541 | 0
6248 | 816.86 | 230.318 | 29.2 | 36.7474 | 36.7474 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 73.3758 | 792.475 | 0 | 0.05921 | 4.5092 | 0 | 0 | 0 | 36.7474 | off_peak | 780.1126 | 0 | 100 | 4.5 | 0 | 95.5 | 165.7023 | 0
6249 | 789.98 | 447.128 | 29.5 | 71.2613 | 71.2613 | 0 | 0 | 0.79843 | 0.79843 | 0 | 0 | 0 | 74.1227 | 719.5171 | 0 | 0.05921 | 4.3269 | 0 | 0 | 0 | 71.2613 | off_peak | 718.7187 | 0 | 100 | 9.02 | 0 | 90.98 | 308.3376 | 0
6250 | 856.38 | 640.065 | 29.9 | 101.8614 | 101.8614 | 0 | 0 | 0.051567 | 0.051567 | 0 | 0 | 0 | 74.1709 | 754.5701 | 0 | 0.05921 | 4.2752 | 0 | 0 | 0 | 101.8614 | off_peak | 754.5186 | 0 | 100 | 11.89 | 0 | 88.11 | 435.4812 | 0
6251 | 814.39 | 785.81 | 30.2 | 124.9181 | 124.9181 | 0 | 0 | 0.0033305 | 0.0033305 | 0 | 0 | 0 | 74.174 | 689.4752 | 0 | 0.05921 | 4.4517 | 0 | 0 | 0 | 124.9181 | off_peak | 689.4719 | 0 | 100 | 15.34 | 0 | 84.66 | 556.098 | 0
6252 | 834.32 | 871.206 | 30.4 | 138.3917 | 138.3917 | 0 | 0 | 0.0002151 | 0.0002151 | 0 | 0 | 0 | 74.1742 | 695.9285 | 0 | 0.05921 | 4.8255 | 0 | 0 | 0 | 138.3917 | off_peak | 695.9283 | 0 | 100 | 16.59 | 0 | 83.41 | 667.8102 | 0
6253 | 827.76 | 889.363 | 30.5 | 141.2241 | 141.2241 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1742 | 686.5359 | 0 | 0.088511 | 5.0279 | 0 | 0 | 0 | 141.2241 | on_peak | 686.5359 |  |  | 17.06 | 0 | 82.94 | 710.0546 | 0
6254 | 844.74 | 813.541 | 30.5 | 129.1841 | 129.1841 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1742 | 715.5559 | 0 | 0.088511 | 5.1279 | 0 | 0 | 0 | 129.1841 | on_peak | 715.5559 |  |  | 15.29 | 0 | 84.71 | 662.443 | 0
6255 | 875.7 | 718.469 | 30.4 | 114.1293 | 114.1293 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1742 | 761.5707 | 0 | 0.088511 | 5.2794 | 0 | 0 | 0 | 114.1293 | on_peak | 761.5707 |  |  | 13.03 | 0 | 86.97 | 602.5286 | 0
6256 | 838.54 | 548.353 | 30.2 | 87.1702 | 87.1702 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1742 | 751.3698 | 0 | 0.088511 | 5.7063 | 0 | 0 | 0 | 87.1702 | on_peak | 751.3698 |  |  | 10.4 | 0 | 89.6 | 497.4189 | 0
6257 | 837.88 | 340.894 | 29.8 | 54.2705 | 54.2705 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1742 | 783.6095 | 0 | 0.088511 | 6.2382 | 0 | 0 | 0 | 54.2705 | on_peak | 783.6095 |  |  | 6.48 | 0 | 93.52 | 338.5496 | 0
6258 | 828.98 | 126.407 | 29.3 | 20.1609 | 20.1609 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1742 | 808.8191 | 0 | 0.088511 | 6.7455 | 0 | 0 | 0 | 20.1609 | on_peak | 808.8191 |  |  | 2.43 | 0 | 97.57 | 135.9959 | 0
6259 | 843.34 | 0 | 29.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1742 | 843.34 | 0 | 0.088511 | 7.2523 | 0 | 0 | 0 | 0 | on_peak | 843.34 |  |  | 0 | 0 | 100 | 0 | 0
6260 | 806.08 | 0 | 28.8 | 0 | 0 | 0 | 0 | 0 | 0 | 62.4453 | 62.4453 | 0 | 7.4174 | 743.6347 | 0 | 0.088511 | 7.6687 | 0 | 0 | 0 | 0 | on_peak | 743.6347 |  |  | 0 | 7.75 | 92.25 | 0 | 0
6261 | 789.97 | 0 | 28.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 789.97 | 0 | 0.088511 | 7.9265 | 0 | 0 | 0 | 0 | on_peak | 789.97 |  |  | 0 | 0 | 100 | 0 | 0
6262 | 787.55 | 0 | 28.5 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 18.9814 | 799.9124 | 0 | 0.05921 | 8.2984 | 0 | 0 | 0 | 0 | off_peak | 787.55 | 0 | 100 | 0 | 0 | 100 | 0 | 0
6263 | 755.11 | 0 | 28.3 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 30.5453 | 767.4724 | 0 | 0.05921 | 8.229 | 0 | 0 | 0 | 0 | off_peak | 755.11 | 0 | 100 | 0 | 0 | 100 | 0 | 0
6264 | 749.68 | 0 | 28.2 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 42.1093 | 762.0424 | 0 | 0.05921 | 8.2141 | 0 | 0 | 0 | 0 | off_peak | 749.68 | 0 | 100 | 0 | 0 | 100 | 0 | 0
6265 | 682.37 | 0 | 28 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 53.6732 | 694.7324 | 0 | 0.05921 | 8.0707 | 0 | 0 | 0 | 0 | off_peak | 682.37 | 0 | 100 | 0 | 0 | 100 | 0 | 0
6266 | 613.61 | 0 | 27.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 53.6732 | 613.61 | 0 | 0.05921 | 7.6165 | 0 | 0 | 0 | 0 | off_peak | 613.61 |  |  | 0 | 0 | 100 | 0 | 0
6267 | 592.13 | 0 | 27.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 53.6732 | 592.13 | 0 | 0.05921 | 6.9729 | 0 | 0 | 0 | 0 | off_peak | 592.13 |  |  | 0 | 0 | 100 | 0 | 0
6268 | 583.69 | 0 | 27.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 53.6732 | 583.69 | 0 | 0.05921 | 6.3699 | 0 | 0 | 0 | 0 | off_peak | 583.69 |  |  | 0 | 0 | 100 | 0 | 0
6269 | 604.93 | 0 | 27.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 53.6732 | 604.93 | 0 | 0.05921 | 5.598 | 0 | 0 | 0 | 0 | off_peak | 604.93 |  |  | 0 | 0 | 100 | 0 | 0
6270 | 653.02 | 0 | 27.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 53.6732 | 653.02 | 0 | 0.05921 | 4.9918 | 0 | 0 | 0 | 0 | off_peak | 653.02 |  |  | 0 | 0 | 100 | 0 | 0
6271 | 770.37 | 36.6746 | 28 | 5.8771 | 5.8771 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 65.2371 | 776.8553 | 0 | 0.05921 | 4.6101 | 0 | 0 | 0 | 5.8771 | off_peak | 764.4929 | 0 | 100 | 0.76 | 0 | 99.24 | 27.0939 | 0
6272 | 797.27 | 230.456 | 28.6 | 36.85 | 36.85 | 0 | 0 | 8.9371 | 8.9371 | 0 | 0 | 0 | 73.597 | 769.3571 | 0 | 0.05921 | 4.3446 | 0 | 0 | 0 | 36.85 | off_peak | 760.42 | 0 | 100 | 4.62 | 0 | 95.38 | 160.1 | 0
6273 | 837.93 | 445.22 | 29.1 | 71.0611 | 71.0611 | 0 | 0 | 0.57721 | 0.57721 | 0 | 0 | 0 | 74.137 | 767.4461 | 0 | 0.05921 | 4.1907 | 0 | 0 | 0 | 71.0611 | off_peak | 766.8689 | 0 | 100 | 8.48 | 0 | 91.52 | 297.7989 | 0
6274 | 838.06 | 636.609 | 29.4 | 101.4971 | 101.4971 | 0 | 0 | 0.037279 | 0.037279 | 0 | 0 | 0 | 74.1718 | 736.6002 | 0 | 0.05921 | 4.1475 | 0 | 0 | 0 | 101.4971 | off_peak | 736.5629 | 0 | 100 | 12.11 | 0 | 87.89 | 420.9567 | 0
6275 | 808.82 | 776.418 | 29.6 | 123.6968 | 123.6968 | 0 | 0 | 0.0024077 | 0.0024077 | 0 | 0 | 0 | 74.1741 | 685.1256 | 0 | 0.05921 | 4.3381 | 0 | 0 | 0 | 123.6968 | off_peak | 685.1232 | 0 | 100 | 15.29 | 0 | 84.71 | 536.6044 | 0
6276 | 856.36 | 861.646 | 29.8 | 137.1746 | 137.1746 | 0 | 0 | 0.0001555 | 0.0001555 | 0 | 0 | 0 | 74.1742 | 719.1856 | 0 | 0.05921 | 4.7983 | 0 | 0 | 0 | 137.1746 | off_peak | 719.1854 | 0 | 100 | 16.02 | 0 | 83.98 | 658.2088 | 0
6277 | 809.6 | 879.586 | 29.8 | 140.0307 | 140.0307 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1742 | 669.5693 | 0 | 0.088511 | 5.0281 | 0 | 0 | 0 | 140.0307 | on_peak | 669.5693 |  |  | 17.3 | 0 | 82.7 | 704.0895 | 0
6278 | 840.93 | 826.885 | 29.8 | 131.6406 | 131.6406 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1742 | 709.2894 | 0 | 0.088511 | 5.104 | 0 | 0 | 0 | 131.6406 | on_peak | 709.2894 |  |  | 15.65 | 0 | 84.35 | 671.8906 | 0
6279 | 912.57 | 705.864 | 29.7 | 112.4152 | 112.4152 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1742 | 800.1548 | 0 | 0.088511 | 5.2293 | 0 | 0 | 0 | 112.4152 | on_peak | 800.1548 |  |  | 12.32 | 0 | 87.68 | 587.8531 | 0
6280 | 811.28 | 157.7 | 29.5 | 25.1335 | 25.1335 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1742 | 786.1465 | 0 | 0.088511 | 5.6721 | 0 | 0 | 0 | 25.1335 | on_peak | 786.1465 |  |  | 3.1 | 0 | 96.9 | 142.5605 | 0
6281 | 816.41 | 213.171 | 29.2 | 34.0116 | 34.0116 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1742 | 782.3984 | 0 | 0.088511 | 6.139 | 0 | 0 | 0 | 34.0116 | on_peak | 782.3984 |  |  | 4.17 | 0 | 95.83 | 208.7982 | 0
6282 | 806.52 | 59.0753 | 28.8 | 9.4393 | 9.4393 | 0 | 0 | 0 | 0 | 62.4453 | 62.4453 | 0 | 7.4174 | 734.6354 | 0 | 0.088511 | 6.58 | 0 | 0 | 0 | 9.4393 | on_peak | 734.6354 |  |  | 1.17 | 7.74 | 91.09 | 62.1102 | 0
6283 | 779.93 | 0 | 28.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 779.93 | 0 | 0.088511 | 7.0973 | 0 | 0 | 0 | 0 | on_peak | 779.93 |  |  | 0 | 0 | 100 | 0 | 0
6284 | 804.03 | 0 | 28.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 804.03 | 0 | 0.088511 | 7.2677 | 0 | 0 | 0 | 0 | on_peak | 804.03 |  |  | 0 | 0 | 100 | 0 | 0
6285 | 791.25 | 0 | 28.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 791.25 | 0 | 0.088511 | 7.3351 | 0 | 0 | 0 | 0 | on_peak | 791.25 |  |  | 0 | 0 | 100 | 0 | 0
6286 | 744.75 | 0 | 28.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 744.75 | 0 | 0.05921 | 7.5419 | 0 | 0 | 0 | 0 | off_peak | 744.75 |  |  | 0 | 0 | 100 | 0 | 0
6287 | 771.21 | 0 | 28.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 771.21 | 0 | 0.05921 | 7.5632 | 0 | 0 | 0 | 0 | off_peak | 771.21 |  |  | 0 | 0 | 100 | 0 | 0
6288 | 763.54 | 0 | 28.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 763.54 | 0 | 0.05921 | 7.5492 | 0 | 0 | 0 | 0 | off_peak | 763.54 |  |  | 0 | 0 | 100 | 0 | 0
6289 | 724.63 | 0 | 28.2 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 18.9814 | 736.9924 | 0 | 0.05921 | 7.522 | 0 | 0 | 0 | 0 | off_peak | 724.63 | 0 | 100 | 0 | 0 | 100 | 0 | 0
6290 | 632.92 | 0 | 28.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18.9814 | 632.92 | 0 | 0.05921 | 7.0974 | 0 | 0 | 0 | 0 | off_peak | 632.92 |  |  | 0 | 0 | 100 | 0 | 0
6291 | 647.07 | 0 | 28.2 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 30.5453 | 659.4324 | 0 | 0.05921 | 6.4627 | 0 | 0 | 0 | 0 | off_peak | 647.07 | 0 | 100 | 0 | 0 | 100 | 0 | 0
6292 | 626.32 | 0 | 28.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30.5453 | 626.32 | 0 | 0.05921 | 5.9478 | 0 | 0 | 0 | 0 | off_peak | 626.32 |  |  | 0 | 0 | 100 | 0 | 0
6293 | 651 | 0 | 28.3 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 42.1093 | 663.3624 | 0 | 0.05921 | 5.186 | 0 | 0 | 0 | 0 | off_peak | 651 | 0 | 100 | 0 | 0 | 100 | 0 | 0
6294 | 701.57 | 0 | 28.3 | 0 | 0 | 0 | 0 | 8.7006 | 8.7006 | 0 | 0 | 0 | 50.2479 | 710.2706 | 0 | 0.05921 | 4.6621 | 0 | 0 | 0 | 0 | off_peak | 701.57 | 0 | 100 | 0 | 0 | 100 | 0 | 0
6295 | 796.04 | 34.607 | 28.3 | 5.5397 | 5.5397 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 61.8119 | 802.8626 | 0 | 0.05921 | 4.3062 | 0 | 0 | 0 | 5.5397 | off_peak | 790.5003 | 0 | 100 | 0.7 | 0 | 99.3 | 23.855 | 0
6296 | 890.26 | 226.477 | 28.3 | 36.2534 | 36.2534 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 73.3758 | 866.369 | 0 | 0.05921 | 4.1128 | 0 | 0 | 0 | 36.2534 | off_peak | 854.0066 | 0 | 100 | 4.07 | 0 | 95.93 | 149.102 | 0
6297 | 872.26 | 439.98 | 28.3 | 70.43 | 70.43 | 0 | 0 | 0.79843 | 0.79843 | 0 | 0 | 0 | 74.1227 | 802.6284 | 0 | 0.05921 | 3.9811 | 0 | 0 | 0 | 70.43 | off_peak | 801.83 | 0 | 100 | 8.07 | 0 | 91.93 | 280.3865 | 0
6298 | 889.18 | 629.562 | 28.5 | 100.704 | 100.704 | 0 | 0 | 0.051567 | 0.051567 | 0 | 0 | 0 | 74.1709 | 788.5276 | 0 | 0.05921 | 3.9164 | 0 | 0 | 0 | 100.704 | off_peak | 788.476 | 0 | 100 | 11.33 | 0 | 88.67 | 394.3982 | 0
6299 | 824.33 | 504.199 | 28.7 | 80.5923 | 80.5923 | 0 | 0 | 0.0033305 | 0.0033305 | 0 | 0 | 0 | 74.174 | 743.7411 | 0 | 0.05921 | 3.6804 | 0 | 0 | 0 | 80.5923 | off_peak | 743.7377 | 0 | 100 | 9.78 | 0 | 90.22 | 296.6144 | 0
6300 | 857.6 | 848.18 | 28.8 | 135.5255 | 135.5252 | 0 | 0.0002151 | 0.0002151 | 0 | 0 | 0 | 0 | 74.1742 | 722.0748 | 0 | 0.05921 | 4.4638 | 0 | 0 | 0.00020121 | 135.5252 | off_peak | 722.0748 | 100 | 0 | 15.8 | 0 | 84.2 | 604.9599 | 0
6301 | 832.15 | 579.493 | 28.9 | 92.5598 | 92.5598 | 0 | 0 | 0 | 0 | 62.4451 | 62.4451 | 0 | 7.4176 | 677.1451 | 0 | 0.088511 | 4.7012 | 0 | 0 | 0.00020121 | 92.5598 | on_peak | 677.1451 |  |  | 11.12 | 7.5 | 81.37 | 435.1391 | 0
6302 | 858.77 | 504.09 | 28.9 | 80.516 | 80.516 | 0 | 0 | 0 | 0 | 0.00018821 | 0.00018821 | 0 | 7.4174 | 778.2538 | 0 | 0.088511 | 4.7882 | 0.00018821 | 0 | 0 | 80.5162 | on_peak | 778.2538 |  |  | 9.38 | 0 | 90.62 | 385.524 | 0
6303 | 887.27 | 383.709 | 28.9 | 61.2881 | 61.2881 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 825.9819 | 0 | 0.088511 | 4.9344 | 0 | 0 | 0 | 61.2881 | on_peak | 825.9819 |  |  | 6.91 | 0 | 93.09 | 302.4173 | 0
6304 | 847.46 | 517.872 | 28.9 | 82.7174 | 82.7174 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 764.7426 | 0 | 0.088511 | 5.3278 | 0 | 0 | 0 | 82.7174 | on_peak | 764.7426 |  |  | 9.76 | 0 | 90.24 | 440.705 | 0
6305 | 828.21 | 155.057 | 28.8 | 24.7756 | 24.7756 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 803.4344 | 0 | 0.088511 | 5.8306 | 0 | 0 | 0 | 24.7756 | on_peak | 803.4344 |  |  | 2.99 | 0 | 97.01 | 144.4564 | 0
6306 | 825.12 | 108.698 | 28.7 | 17.3745 | 17.3745 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 807.7455 | 0 | 0.088511 | 6.395 | 0 | 0 | 0 | 17.3745 | on_peak | 807.7455 |  |  | 2.11 | 0 | 97.89 | 111.1109 | 0
6307 | 811.28 | 0 | 28.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 811.28 | 0 | 0.088511 | 7.0465 | 0 | 0 | 0 | 0 | on_peak | 811.28 |  |  | 0 | 0 | 100 | 0 | 0
6308 | 820.9 | 0 | 28.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 820.9 | 0 | 0.088511 | 7.6023 | 0 | 0 | 0 | 0 | on_peak | 820.9 |  |  | 0 | 0 | 100 | 0 | 0
6309 | 780.46 | 0 | 28.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 780.46 | 0 | 0.088511 | 7.639 | 0 | 0 | 0 | 0 | on_peak | 780.46 |  |  | 0 | 0 | 100 | 0 | 0
6310 | 763.6 | 0 | 28.4 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 18.9814 | 775.9624 | 0 | 0.05921 | 7.708 | 0 | 0 | 0 | 0 | off_peak | 763.6 | 0 | 100 | 0 | 0 | 100 | 0 | 0
6311 | 805.1 | 0 | 28.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18.9814 | 805.1 | 0 | 0.05921 | 7.6044 | 0 | 0 | 0 | 0 | off_peak | 805.1 |  |  | 0 | 0 | 100 | 0 | 0
6312 | 768.19 | 0 | 28.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18.9814 | 768.19 | 0 | 0.05921 | 7.3403 | 0 | 0 | 0 | 0 | off_peak | 768.19 |  |  | 0 | 0 | 100 | 0 | 0
6313 | 720.29 | 0 | 28.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18.9814 | 720.29 | 0 | 0.05921 | 7.2851 | 0 | 0 | 0 | 0 | off_peak | 720.29 |  |  | 0 | 0 | 100 | 0 | 0
6314 | 660.36 | 0 | 28 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18.9814 | 660.36 | 0 | 0.05921 | 7.0619 | 0 | 0 | 0 | 0 | off_peak | 660.36 |  |  | 0 | 0 | 100 | 0 | 0
6315 | 625.04 | 0 | 27.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18.9814 | 625.04 | 0 | 0.05921 | 6.5923 | 0 | 0 | 0 | 0 | off_peak | 625.04 |  |  | 0 | 0 | 100 | 0 | 0
6316 | 658.67 | 0 | 27.8 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 30.5453 | 671.0324 | 0 | 0.05921 | 5.9521 | 0 | 0 | 0 | 0 | off_peak | 658.67 | 0 | 100 | 0 | 0 | 100 | 0 | 0
6317 | 623.85 | 0 | 27.9 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 42.1093 | 636.2124 | 0 | 0.05921 | 5.1606 | 0 | 0 | 0 | 0 | off_peak | 623.85 | 0 | 100 | 0 | 0 | 100 | 0 | 0
6318 | 720.18 | 0 | 28 | 0 | 0 | 0 | 0 | 8.7006 | 8.7006 | 0 | 0 | 0 | 50.2479 | 728.8806 | 0 | 0.05921 | 4.5627 | 0 | 0 | 0 | 0 | off_peak | 720.18 | 0 | 100 | 0 | 0 | 100 | 0 | 0
6319 | 770.76 | 31.5657 | 28.1 | 5.0566 | 5.0566 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 61.8119 | 778.0658 | 0 | 0.05921 | 4.1041 | 0 | 0 | 0 | 5.0566 | off_peak | 765.7034 | 0 | 100 | 0.66 | 0 | 99.34 | 20.7526 | 0
6320 | 828.21 | 218.867 | 28.4 | 35.0225 | 35.0225 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 73.3758 | 805.5499 | 0 | 0.05921 | 3.9092 | 0 | 0 | 0 | 35.0225 | off_peak | 793.1875 | 0 | 100 | 4.23 | 0 | 95.77 | 136.9094 | 0
6321 | 842.43 | 428.913 | 28.7 | 68.5584 | 68.5584 | 0 | 0 | 0.79843 | 0.79843 | 0 | 0 | 0 | 74.1227 | 774.6701 | 0 | 0.05921 | 3.7881 | 0 | 0 | 0 | 68.5584 | off_peak | 773.8716 | 0 | 100 | 8.14 | 0 | 91.86 | 259.7057 | 0
6322 | 825.5 | 615.223 | 28.9 | 98.2668 | 98.2668 | 0 | 0 | 0.051567 | 0.051567 | 0 | 0 | 0 | 74.1709 | 727.2848 | 0 | 0.05921 | 3.7754 | 0 | 0 | 0 | 98.2668 | off_peak | 727.2332 | 0 | 100 | 11.9 | 0 | 88.1 | 370.9947 | 0
6323 | 851.07 | 753.052 | 29.1 | 120.1938 | 120.1938 | 0 | 0 | 0.0033305 | 0.0033305 | 0 | 0 | 0 | 74.174 | 730.8795 | 0 | 0.05921 | 4.0199 | 0 | 0 | 0 | 120.1938 | off_peak | 730.8762 | 0 | 100 | 14.12 | 0 | 85.88 | 483.1654 | 0
6324 | 899.03 | 423.214 | 29.2 | 67.524 | 67.524 | 0 | 0 | 0.0002151 | 0.0002151 | 0 | 0 | 0 | 74.1742 | 831.5062 | 0 | 0.05921 | 4.4544 | 0 | 0 | 0 | 67.524 | off_peak | 831.506 | 0 | 100 | 7.51 | 0 | 92.49 | 300.7794 | 0
6325 | 806.42 | 198.55 | 29.3 | 31.6672 | 31.6672 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1742 | 774.7528 | 0 | 0.088511 | 4.6802 | 0 | 0 | 0 | 31.6672 | on_peak | 774.7528 |  |  | 3.93 | 0 | 96.07 | 148.2103 | 0
6326 | 829.28 | 105.45 | 29.3 | 16.8185 | 16.8185 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1742 | 812.4615 | 0 | 0.088511 | 4.807 | 0 | 0 | 0 | 16.8185 | on_peak | 812.4615 |  |  | 2.03 | 0 | 97.97 | 80.8458 | 0
6327 | 823.18 | 263.618 | 29.2 | 42.0604 | 42.0604 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1742 | 781.1196 | 0 | 0.088511 | 4.9221 | 0 | 0 | 0 | 42.0604 | on_peak | 781.1196 |  |  | 5.11 | 0 | 94.89 | 207.0239 | 0
6328 | 881.28 | 302.317 | 29 | 48.2701 | 48.2701 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1742 | 833.0099 | 0 | 0.088511 | 5.301 | 0 | 0 | 0 | 48.2701 | on_peak | 833.0099 |  |  | 5.48 | 0 | 94.52 | 255.8795 | 0
6329 | 892.94 | 315.868 | 28.8 | 50.4706 | 50.4706 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1742 | 842.4694 | 0 | 0.088511 | 5.7752 | 0 | 0 | 0 | 50.4706 | on_peak | 842.4694 |  |  | 5.65 | 0 | 94.35 | 291.4776 | 0
6330 | 863.15 | 110.005 | 28.6 | 17.5899 | 17.5899 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1742 | 845.5601 | 0 | 0.088511 | 6.3456 | 0 | 0 | 0 | 17.5899 | on_peak | 845.5601 |  |  | 2.04 | 0 | 97.96 | 111.6182 | 0
6331 | 821.43 | 0 | 28.4 | 0 | 0 | 0 | 0 | 0 | 0 | 62.4453 | 62.4453 | 0 | 7.4174 | 758.9847 | 0 | 0.088511 | 6.7608 | 0 | 0 | 0 | 0 | on_peak | 758.9847 |  |  | 0 | 7.6 | 92.4 | 0 | 0
6332 | 798.21 | 0 | 28.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 798.21 | 0 | 0.088511 | 7.0008 | 0 | 0 | 0 | 0 | on_peak | 798.21 |  |  | 0 | 0 | 100 | 0 | 0
6333 | 818.99 | 0 | 28.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 818.99 | 0 | 0.088511 | 7.1828 | 0 | 0 | 0 | 0 | on_peak | 818.99 |  |  | 0 | 0 | 100 | 0 | 0
6334 | 768.88 | 0 | 28.4 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 18.9814 | 781.2424 | 0 | 0.05921 | 7.3375 | 0 | 0 | 0 | 0 | off_peak | 768.88 | 0 | 100 | 0 | 0 | 100 | 0 | 0
6335 | 806.56 | 0 | 28.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18.9814 | 806.56 | 0 | 0.05921 | 7.3761 | 0 | 0 | 0 | 0 | off_peak | 806.56 |  |  | 0 | 0 | 100 | 0 | 0
6336 | 784.32 | 0 | 28.3 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 30.5453 | 796.6824 | 0 | 0.05921 | 7.1634 | 0 | 0 | 0 | 0 | off_peak | 784.32 | 0 | 100 | 0 | 0 | 100 | 0 | 0
6337 | 721.74 | 0 | 28.2 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 42.1093 | 734.1024 | 0 | 0.05921 | 7.0162 | 0 | 0 | 0 | 0 | off_peak | 721.74 | 0 | 100 | 0 | 0 | 100 | 0 | 0
6338 | 655.1 | 0 | 28.2 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 53.6732 | 667.4624 | 0 | 0.05921 | 6.6885 | 0 | 0 | 0 | 0 | off_peak | 655.1 | 0 | 100 | 0 | 0 | 100 | 0 | 0
6339 | 666.2 | 0 | 28.1 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 65.2371 | 678.5624 | 0 | 0.05921 | 6.1935 | 0 | 0 | 0 | 0 | off_peak | 666.2 | 0 | 100 | 0 | 0 | 100 | 0 | 0
6340 | 650.47 | 0 | 28 | 0 | 0 | 0 | 0 | 8.9371 | 8.9371 | 0 | 0 | 0 | 73.597 | 659.4071 | 0 | 0.05921 | 5.6515 | 0 | 0 | 0 | 0 | off_peak | 650.47 | 0 | 100 | 0 | 0 | 100 | 0 | 0
6341 | 673.23 | 0 | 28 | 0 | 0 | 0 | 0 | 0.57721 | 0.57721 | 0 | 0 | 0 | 74.137 | 673.8072 | 0 | 0.05921 | 5.0215 | 0 | 0 | 0 | 0 | off_peak | 673.23 | 0 | 100 | 0 | 0 | 100 | 0 | 0
6342 | 728.59 | 0 | 28 | 0 | 0 | 0 | 0 | 0.037279 | 0.037279 | 0 | 0 | 0 | 74.1718 | 728.6273 | 0 | 0.05921 | 4.3886 | 0 | 0 | 0 | 0 | off_peak | 728.59 | 0 | 100 | 0 | 0 | 100 | 0 | 0
6343 | 790.17 | 32.3497 | 28.1 | 5.1822 | 5.1822 | 0 | 0 | 0.0024077 | 0.0024077 | 0 | 0 | 0 | 74.1741 | 784.9902 | 0 | 0.05921 | 3.9561 | 0 | 0 | 0 | 5.1822 | off_peak | 784.9878 | 0 | 100 | 0.66 | 0 | 99.34 | 20.5009 | 0
6344 | 804.89 | 221.566 | 28.4 | 35.4544 | 35.4544 | 0 | 0 | 0.0001555 | 0.0001555 | 0 | 0 | 0 | 74.1742 | 769.4358 | 0 | 0.05921 | 3.723 | 0 | 0 | 0 | 35.4544 | off_peak | 769.4356 | 0 | 100 | 4.4 | 0 | 95.6 | 131.9963 | 0
6345 | 875.69 | 431.795 | 28.6 | 69.0442 | 69.0442 | 0 | 0 | 1.0043e-05 | 1.0043e-05 | 0 | 0 | 0 | 74.1743 | 806.6458 | 0 | 0.05921 | 3.5885 | 0 | 0 | 0 | 69.0442 | off_peak | 806.6458 | 0 | 100 | 7.88 | 0 | 92.12 | 247.7681 | 0
6346 | 886.52 | 279.55 | 28.8 | 44.6676 | 44.6676 | 0 | 0 | 6.4865e-07 | 6.4865e-07 | 0 | 0 | 0 | 74.1743 | 841.8524 | 0 | 0.05921 | 3.5507 | 0 | 0 | 0 | 44.6676 | off_peak | 841.8524 | 0 | 100 | 5.04 | 0 | 94.96 | 158.6 | 0
6347 | 915.87 | 128.069 | 28.9 | 20.4559 | 20.4559 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1743 | 895.4141 | 0 | 0.05921 | 3.7544 | 0 | 0 | 0 | 20.4559 | off_peak | 895.4141 |  |  | 2.23 | 0 | 97.77 | 76.7987 | 0
6348 | 950.81 | 288.979 | 29 | 46.1405 | 46.1405 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1743 | 904.6695 | 0 | 0.05921 | 4.1932 | 0 | 0 | 0 | 46.1405 | off_peak | 904.6695 |  |  | 4.85 | 0 | 95.15 | 193.4785 | 0
6349 | 892.98 | 45.6 | 29 | 7.2808 | 7.2808 | 0 | 0 | 0 | 0 | 32.9236 | 32.9236 | 0 | 38.9774 | 852.7755 | 0 | 0.088511 | 4.4307 | 0 | 0 | 0 | 7.2808 | on_peak | 852.7755 |  |  | 0.82 | 3.69 | 95.5 | 32.2594 | 0
6350 | 880.86 | 194.608 | 29 | 31.0725 | 31.0725 | 0 | 0 | 2.988 | 2.988 | 0 | 0 | 0 | 41.7725 | 852.7755 | 0 | 0.088511 | 4.5285 | 0 | 0 | 0 | 31.0725 | on_peak | 849.7875 | 0 | 100 | 3.53 | 0 | 96.47 | 140.7132 | 0
6351 | 898.72 | 86.45 | 28.9 | 13.8083 | 13.8083 | 0 | 0 | 0 | 0 | 32.1362 | 32.1362 | 0 | 7.4174 | 852.7755 | 0 | 0.088511 | 4.5819 | 0 | 0 | 0 | 13.8083 | on_peak | 852.7755 |  |  | 1.54 | 3.58 | 94.89 | 63.2681 | 0
6352 | 808.36 | 108.86 | 28.7 | 17.4004 | 17.4004 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 790.9596 | 0 | 0.088511 | 4.7421 | 0 | 0 | 0 | 17.4004 | on_peak | 790.9596 |  |  | 2.15 | 0 | 97.85 | 82.515 | 0
6353 | 821.1 | 84.3484 | 28.5 | 13.4923 | 13.4923 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 807.6077 | 0 | 0.088511 | 5.1328 | 0 | 0 | 0 | 13.4923 | on_peak | 807.6077 |  |  | 1.64 | 0 | 98.36 | 69.2525 | 0
6354 | 793.76 | 39.1132 | 28.3 | 6.2611 | 6.2611 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 787.4989 | 0 | 0.088511 | 5.6346 | 0 | 0 | 0 | 6.2611 | on_peak | 787.4989 |  |  | 0.79 | 0 | 99.21 | 35.2788 | 0
6355 | 790.47 | 0 | 28.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 790.47 | 0 | 0.088511 | 6.1354 | 0 | 0 | 0 | 0 | on_peak | 790.47 |  |  | 0 | 0 | 100 | 0 | 0
6356 | 819.75 | 0 | 28.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 819.75 | 0 | 0.088511 | 6.4941 | 0 | 0 | 0 | 0 | on_peak | 819.75 |  |  | 0 | 0 | 100 | 0 | 0
6357 | 778.65 | 0 | 28.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 778.65 | 0 | 0.088511 | 6.8184 | 0 | 0 | 0 | 0 | on_peak | 778.65 |  |  | 0 | 0 | 100 | 0 | 0
6358 | 781.01 | 0 | 28.1 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 18.9814 | 793.3724 | 0 | 0.05921 | 7.1965 | 0 | 0 | 0 | 0 | off_peak | 781.01 | 0 | 100 | 0 | 0 | 100 | 0 | 0
6359 | 769.88 | 0 | 28 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18.9814 | 769.88 | 0 | 0.05921 | 7.3273 | 0 | 0 | 0 | 0 | off_peak | 769.88 |  |  | 0 | 0 | 100 | 0 | 0
6360 | 753.8 | 0 | 27.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18.9814 | 753.8 | 0 | 0.05921 | 7.7786 | 0 | 0 | 0 | 0 | off_peak | 753.8 |  |  | 0 | 0 | 100 | 0 | 0
6361 | 702.98 | 0 | 27.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18.9814 | 702.98 | 0 | 0.05921 | 7.849 | 0 | 0 | 0 | 0 | off_peak | 702.98 |  |  | 0 | 0 | 100 | 0 | 0
6362 | 649.45 | 0 | 27.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18.9814 | 649.45 | 0 | 0.05921 | 7.4537 | 0 | 0 | 0 | 0 | off_peak | 649.45 |  |  | 0 | 0 | 100 | 0 | 0
6363 | 659.22 | 0 | 27.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18.9814 | 659.22 | 0 | 0.05921 | 6.8538 | 0 | 0 | 0 | 0 | off_peak | 659.22 |  |  | 0 | 0 | 100 | 0 | 0
6364 | 660.05 | 0 | 27.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18.9814 | 660.05 | 0 | 0.05921 | 6.2871 | 0 | 0 | 0 | 0 | off_peak | 660.05 |  |  | 0 | 0 | 100 | 0 | 0
6365 | 680.25 | 0 | 27.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18.9814 | 680.25 | 0 | 0.05921 | 5.5364 | 0 | 0 | 0 | 0 | off_peak | 680.25 |  |  | 0 | 0 | 100 | 0 | 0
6366 | 677.15 | 0 | 27.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18.9814 | 677.15 | 0 | 0.05921 | 5.0524 | 0 | 0 | 0 | 0 | off_peak | 677.15 |  |  | 0 | 0 | 100 | 0 | 0
6367 | 736.98 | 29.3105 | 28 | 4.697 | 0 | 0 | 4.697 | 4.697 | 0 | 0 | 0 | 0 | 23.375 | 736.98 | 0 | 0.05921 | 4.6054 | 0 | 0 | 4.3937 | 0 | off_peak | 736.98 | 100 | 0 | 0 | 0 | 100 | 0 | 0
6368 | 732.56 | 213.519 | 28.3 | 34.1791 | 34.1791 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 23.375 | 698.3809 | 0 | 0.05921 | 4.2691 | 0 | 0 | 4.3937 | 34.1791 | off_peak | 698.3809 |  |  | 4.67 | 0 | 95.33 | 145.9143 | 0
6369 | 766.53 | 421.396 | 28.6 | 67.3814 | 67.3814 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 23.375 | 699.1486 | 0 | 0.05921 | 4.0621 | 0 | 0 | 4.3937 | 67.3814 | off_peak | 699.1486 |  |  | 8.79 | 0 | 91.21 | 273.7077 | 0
6370 | 770.11 | 605.612 | 28.7 | 96.8023 | 96.8023 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 23.375 | 673.3077 | 0 | 0.05921 | 3.913 | 0 | 0 | 4.3937 | 96.8023 | off_peak | 673.3077 |  |  | 12.57 | 0 | 87.43 | 378.7898 | 0
6371 | 757.49 | 329.497 | 28.9 | 52.6291 | 52.6291 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 23.375 | 704.8609 | 0 | 0.05921 | 3.8786 | 0 | 0 | 4.3937 | 52.6291 | off_peak | 704.8609 |  |  | 6.95 | 0 | 93.05 | 204.1251 | 0
6372 | 786.25 | 699.525 | 29 | 111.6912 | 111.6912 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 23.375 | 674.5588 | 0 | 0.05921 | 3.9684 | 0 | 0 | 4.3937 | 111.6912 | off_peak | 674.5588 |  |  | 14.21 | 0 | 85.79 | 443.2379 | 0
6373 | 724.94 | 454.763 | 29.1 | 72.5842 | 72.5842 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 23.375 | 652.3558 | 0 | 0.05921 | 4.1675 | 0 | 0 | 4.3937 | 72.5842 | off_peak | 652.3558 |  |  | 10.01 | 0 | 89.99 | 302.4965 | 0
6374 | 744.79 | 714.345 | 29.1 | 114.0158 | 114.0158 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 23.375 | 630.7742 | 0 | 0.05921 | 4.2819 | 0 | 0 | 4.3937 | 114.0158 | off_peak | 630.7742 |  |  | 15.31 | 0 | 84.69 | 488.2049 | 0
6375 | 725.59 | 403.208 | 29.1 | 64.3556 | 64.3556 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 23.375 | 661.2344 | 0 | 0.05921 | 4.3047 | 0 | 0 | 4.3937 | 64.3556 | off_peak | 661.2344 |  |  | 8.87 | 0 | 91.13 | 277.0312 | 0
6376 | 724.57 | 405.515 | 28.9 | 64.7711 | 64.7711 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 23.375 | 659.7989 | 0 | 0.05921 | 4.4767 | 0 | 0 | 4.3937 | 64.7711 | off_peak | 659.7989 |  |  | 8.94 | 0 | 91.06 | 289.9633 | 0
6377 | 724.43 | 206.913 | 28.7 | 33.0734 | 33.0734 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 23.375 | 691.3566 | 0 | 0.05921 | 4.7605 | 0 | 0 | 4.3937 | 33.0734 | off_peak | 691.3566 |  |  | 4.57 | 0 | 95.43 | 157.4461 | 0
6378 | 658.68 | 69.2001 | 28.2 | 11.0813 | 11.0813 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 23.375 | 647.5987 | 0 | 0.05921 | 5.2466 | 0 | 0 | 4.3937 | 11.0813 | off_peak | 647.5987 |  |  | 1.68 | 0 | 98.32 | 58.139 | 0
6379 | 626.34 | 0 | 28 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 23.375 | 626.34 | 0 | 0.05921 | 5.7282 | 0 | 0 | 4.3937 | 0 | off_peak | 626.34 |  |  | 0 | 0 | 100 | 0 | 0
6380 | 626.63 | 0 | 27.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 23.375 | 626.63 | 0 | 0.05921 | 6.1698 | 0 | 0 | 4.3937 | 0 | off_peak | 626.63 |  |  | 0 | 0 | 100 | 0 | 0
6381 | 608.47 | 0 | 27.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 23.375 | 608.47 | 0 | 0.05921 | 6.4444 | 0 | 0 | 4.3937 | 0 | off_peak | 608.47 |  |  | 0 | 0 | 100 | 0 | 0
6382 | 615.7 | 0 | 27.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 23.375 | 615.7 | 0 | 0.05921 | 6.7023 | 0 | 0 | 4.3937 | 0 | off_peak | 615.7 |  |  | 0 | 0 | 100 | 0 | 0
6383 | 592.34 | 0 | 27.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 23.375 | 592.34 | 0 | 0.05921 | 6.8226 | 0 | 0 | 4.3937 | 0 | off_peak | 592.34 |  |  | 0 | 0 | 100 | 0 | 0
6384 | 621.64 | 0 | 27.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 23.375 | 621.64 | 0 | 0.05921 | 7.0322 | 0 | 0 | 4.3937 | 0 | off_peak | 621.64 |  |  | 0 | 0 | 100 | 0 | 0
6385 | 602.26 | 0 | 27.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 23.375 | 602.26 | 0 | 0.05921 | 7.0536 | 0 | 0 | 4.3937 | 0 | off_peak | 602.26 |  |  | 0 | 0 | 100 | 0 | 0
6386 | 598.94 | 0 | 27.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 23.375 | 598.94 | 0 | 0.05921 | 6.8208 | 0 | 0 | 4.3937 | 0 | off_peak | 598.94 |  |  | 0 | 0 | 100 | 0 | 0
6387 | 626.06 | 0 | 27.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 23.375 | 626.06 | 0 | 0.05921 | 6.3944 | 0 | 0 | 4.3937 | 0 | off_peak | 626.06 |  |  | 0 | 0 | 100 | 0 | 0
6388 | 625.53 | 0 | 27.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 23.375 | 625.53 | 0 | 0.05921 | 5.9223 | 0 | 0 | 4.3937 | 0 | off_peak | 625.53 |  |  | 0 | 0 | 100 | 0 | 0
6389 | 638.2 | 0 | 27.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 23.375 | 638.2 | 0 | 0.05921 | 5.3155 | 0 | 0 | 4.3937 | 0 | off_peak | 638.2 |  |  | 0 | 0 | 100 | 0 | 0
6390 | 690.11 | 0 | 27.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 23.375 | 690.11 | 0 | 0.05921 | 4.7991 | 0 | 0 | 4.3937 | 0 | off_peak | 690.11 |  |  | 0 | 0 | 100 | 0 | 0
6391 | 671.39 | 28.6557 | 27.5 | 4.6004 | 4.6004 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 23.375 | 666.7896 | 0 | 0.05921 | 4.328 | 0 | 0 | 4.3937 | 4.6004 | off_peak | 666.7896 |  |  | 0.69 | 0 | 99.31 | 19.9105 | 0
6392 | 733.06 | 212.73 | 28 | 34.0901 | 34.0901 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 23.375 | 698.9699 | 0 | 0.05921 | 4.0122 | 0 | 0 | 4.3937 | 34.0901 | off_peak | 698.9699 |  |  | 4.65 | 0 | 95.35 | 136.7771 | 0
6393 | 743.93 | 422.136 | 28.4 | 67.549 | 67.549 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 23.375 | 676.381 | 0 | 0.05921 | 3.7863 | 0 | 0 | 4.3937 | 67.549 | off_peak | 676.381 |  |  | 9.08 | 0 | 90.92 | 255.7629 | 0
6394 | 722.06 | 609.028 | 28.8 | 97.3128 | 97.3128 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 23.375 | 624.7472 | 0 | 0.05921 | 3.6511 | 0 | 0 | 4.3937 | 97.3128 | off_peak | 624.7472 |  |  | 13.48 | 0 | 86.52 | 355.2966 | 0
6395 | 719.04 | 755.694 | 29.1 | 120.6155 | 120.6155 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 23.375 | 598.4245 | 0 | 0.05921 | 3.5738 | 0 | 0 | 4.3937 | 120.6155 | off_peak | 598.4245 |  |  | 16.77 | 0 | 83.23 | 431.0514 | 0
6396 | 746.68 | 837.144 | 29.3 | 133.518 | 133.518 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 23.375 | 613.162 | 0 | 0.05921 | 3.6312 | 0 | 0 | 4.3937 | 133.518 | off_peak | 613.162 |  |  | 17.88 | 0 | 82.12 | 484.8296 | 0
6397 | 724.74 | 428.346 | 29.4 | 68.2929 | 68.2929 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 23.375 | 656.4471 | 0 | 0.05921 | 3.7998 | 0 | 0 | 4.3937 | 68.2929 | off_peak | 656.4471 |  |  | 9.42 | 0 | 90.58 | 259.5027 | 0
6398 | 697.96 | 548.926 | 29.4 | 87.5174 | 87.5174 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 23.375 | 610.4426 | 0 | 0.05921 | 3.9576 | 0 | 0 | 4.3937 | 87.5174 | off_peak | 610.4426 |  |  | 12.54 | 0 | 87.46 | 346.3604 | 0
6399 | 708.86 | 242.001 | 29.2 | 38.6114 | 38.6114 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 23.375 | 670.2486 | 0 | 0.05921 | 4.1992 | 0 | 0 | 4.3937 | 38.6114 | off_peak | 670.2486 |  |  | 5.45 | 0 | 94.55 | 162.1369 | 0
6400 | 704.38 | 65.55 | 29 | 10.4662 | 10.4662 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 23.375 | 693.9138 | 0 | 0.05921 | 4.5873 | 0 | 0 | 4.3937 | 10.4662 | off_peak | 693.9138 |  |  | 1.49 | 0 | 98.51 | 48.0118 | 0
6401 | 696.78 | 269.138 | 28.6 | 43.0353 | 43.0353 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 23.375 | 653.7447 | 0 | 0.05921 | 4.9715 | 0 | 0 | 4.3937 | 43.0353 | off_peak | 653.7447 |  |  | 6.18 | 0 | 93.82 | 213.9516 | 0
6402 | 664.78 | 71.8306 | 28 | 11.5109 | 11.5109 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 23.375 | 653.2691 | 0 | 0.05921 | 5.4755 | 0 | 0 | 4.3937 | 11.5109 | off_peak | 653.2691 |  |  | 1.73 | 0 | 98.27 | 63.0273 | 0
6403 | 578.58 | 0 | 27.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 23.375 | 578.58 | 0 | 0.05921 | 6.1642 | 0 | 0 | 4.3937 | 0 | off_peak | 578.58 |  |  | 0 | 0 | 100 | 0 | 0
6404 | 600.9 | 0 | 27.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 23.375 | 600.9 | 0 | 0.05921 | 6.6987 | 0 | 0 | 4.3937 | 0 | off_peak | 600.9 |  |  | 0 | 0 | 100 | 0 | 0
6405 | 585.45 | 0 | 27.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 23.375 | 585.45 | 0 | 0.05921 | 6.9964 | 0 | 0 | 4.3937 | 0 | off_peak | 585.45 |  |  | 0 | 0 | 100 | 0 | 0
6406 | 601.63 | 0 | 27.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 23.375 | 601.63 | 0 | 0.05921 | 7.2637 | 0 | 0 | 4.3937 | 0 | off_peak | 601.63 |  |  | 0 | 0 | 100 | 0 | 0
6407 | 604.71 | 0 | 27.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 23.375 | 604.71 | 0 | 0.05921 | 7.5184 | 0 | 0 | 4.3937 | 0 | off_peak | 604.71 |  |  | 0 | 0 | 100 | 0 | 0
6408 | 572.94 | 0 | 27 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 23.375 | 572.94 | 0 | 0.05921 | 7.4949 | 0 | 0 | 4.3937 | 0 | off_peak | 572.94 |  |  | 0 | 0 | 100 | 0 | 0
6409 | 619.56 | 0 | 26.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 23.375 | 619.56 | 0 | 0.05921 | 7.3741 | 0 | 0 | 4.3937 | 0 | off_peak | 619.56 |  |  | 0 | 0 | 100 | 0 | 0
6410 | 610.13 | 0 | 26.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 23.375 | 610.13 | 0 | 0.05921 | 7.1586 | 0 | 0 | 4.3937 | 0 | off_peak | 610.13 |  |  | 0 | 0 | 100 | 0 | 0
6411 | 553.13 | 0 | 26.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 23.375 | 553.13 | 0 | 0.05921 | 6.6908 | 0 | 0 | 4.3937 | 0 | off_peak | 553.13 |  |  | 0 | 0 | 100 | 0 | 0
6412 | 596.96 | 0 | 26.6 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 34.939 | 609.3224 | 0 | 0.05921 | 6.07 | 0 | 0 | 4.3937 | 0 | off_peak | 596.96 | 0 | 100 | 0 | 0 | 100 | 0 | 0
6413 | 599.94 | 0 | 26.4 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 46.5029 | 612.3024 | 0 | 0.05921 | 5.4576 | 0 | 0 | 4.3937 | 0 | off_peak | 599.94 | 0 | 100 | 0 | 0 | 100 | 0 | 0
6414 | 683.44 | 0 | 26.4 | 0 | 0 | 0 | 0 | 4.0036 | 4.0036 | 0 | 0 | 0 | 50.2479 | 687.4436 | 0 | 0.05921 | 4.8138 | 0 | 0 | 4.3937 | 0 | off_peak | 683.44 | 0 | 100 | 0 | 0 | 100 | 0 | 0
6415 | 721.35 | 28.4243 | 26.8 | 4.5749 | 4.5749 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 61.8119 | 729.1375 | 0 | 0.05921 | 4.1503 | 0 | 0 | 4.3937 | 4.5749 | off_peak | 716.7751 | 0 | 100 | 0.63 | 0 | 99.37 | 18.987 | 0
6416 | 803.02 | 212.939 | 27.4 | 34.1981 | 34.1981 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 73.3758 | 781.1843 | 0 | 0.05921 | 3.7821 | 0 | 0 | 4.3937 | 34.1981 | off_peak | 768.8219 | 0 | 100 | 4.26 | 0 | 95.74 | 129.339 | 0
6417 | 788.5 | 422.344 | 27.8 | 67.7301 | 67.7301 | 0 | 0 | 0.79843 | 0.79843 | 0 | 0 | 0 | 74.1227 | 721.5684 | 0 | 0.05921 | 3.5913 | 0 | 0 | 4.3937 | 67.7301 | off_peak | 720.7699 | 0 | 100 | 8.59 | 0 | 91.41 | 243.2377 | 0
6418 | 800.32 | 608.434 | 28.2 | 97.4308 | 97.3793 | 0 | 0.051567 | 0.051567 | 0 | 0 | 0 | 0 | 74.1709 | 702.9407 | 0 | 0.05921 | 3.5528 | 0 | 0 | 4.4419 | 97.3793 | off_peak | 702.9407 | 100 | 0 | 12.17 | 0 | 87.83 | 345.97 | 0
6419 | 809.85 | 748.334 | 28.6 | 119.659 | 119.6556 | 0 | 0.0033305 | 0.0033305 | 0 | 0 | 0 | 0 | 74.174 | 690.1944 | 0 | 0.05921 | 3.7344 | 0 | 0 | 4.445 | 119.6556 | off_peak | 690.1944 | 100 | 0 | 14.78 | 0 | 85.22 | 446.8433 | 0
6420 | 835.2 | 629.776 | 28.9 | 100.5913 | 100.5913 | 0 | 0 | 0.0002151 | 0.0002151 | 0 | 0 | 0 | 74.1742 | 734.6089 | 0 | 0.05921 | 4.0928 | 0 | 0 | 4.445 | 100.5913 | off_peak | 734.6087 | 0 | 100 | 12.04 | 0 | 87.96 | 411.7022 | 0
6421 | 819.74 | 782.907 | 29.1 | 124.9589 | 124.9589 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1742 | 694.7811 | 0 | 0.088511 | 4.3832 | 0 | 0 | 4.445 | 124.9589 | on_peak | 694.7811 |  |  | 15.24 | 0 | 84.76 | 547.7174 | 0
6422 | 847.14 | 525.027 | 29.2 | 83.7684 | 83.7684 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1742 | 763.3716 | 0 | 0.088511 | 4.5507 | 0 | 0 | 4.445 | 83.7684 | on_peak | 763.3716 |  |  | 9.89 | 0 | 90.11 | 381.2012 | 0
6423 | 831.02 | 349.603 | 29.1 | 55.7997 | 55.7997 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1742 | 775.2203 | 0 | 0.088511 | 4.7625 | 0 | 0 | 4.445 | 55.7997 | on_peak | 775.2203 |  |  | 6.71 | 0 | 93.29 | 265.7467 | 0
6424 | 857.7 | 412.489 | 28.9 | 65.885 | 65.885 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1742 | 791.815 | 0 | 0.088511 | 5.1765 | 0 | 0 | 4.445 | 65.885 | on_peak | 791.815 |  |  | 7.68 | 0 | 92.32 | 341.0551 | 0
6425 | 816.17 | 217.126 | 28.5 | 34.7312 | 34.7312 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1742 | 781.4388 | 0 | 0.088511 | 5.6337 | 0 | 0 | 4.445 | 34.7312 | on_peak | 781.4388 |  |  | 4.26 | 0 | 95.74 | 195.6649 | 0
6426 | 829.11 | 63.952 | 27.9 | 10.2521 | 10.2521 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1742 | 818.8579 | 0 | 0.088511 | 6.3077 | 0 | 0 | 4.445 | 10.2521 | on_peak | 818.8579 |  |  | 1.24 | 0 | 98.76 | 64.6666 | 0
6427 | 781.91 | 0 | 27.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1742 | 781.91 | 0 | 0.088511 | 6.9536 | 0 | 0 | 4.445 | 0 | on_peak | 781.91 |  |  | 0 | 0 | 100 | 0 | 0
6428 | 803.42 | 0 | 27.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1742 | 803.42 | 0 | 0.088511 | 7.3444 | 0 | 0 | 4.445 | 0 | on_peak | 803.42 |  |  | 0 | 0 | 100 | 0 | 0
6429 | 843.28 | 0 | 27.2 | 0 | 0 | 0 | 0 | 0 | 0 | 62.4453 | 62.4453 | 0 | 7.4174 | 780.8347 | 0 | 0.088511 | 7.8135 | 4.1579 | 0 | 0 | 4.1579 | on_peak | 780.8347 |  |  | 0 | 7.41 | 92.59 | 32.4879 | 0
6430 | 770.12 | 0 | 27.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 770.12 | 0 | 0.05921 | 7.9483 | 0 | 0 | 0 | 0 | off_peak | 770.12 |  |  | 0 | 0 | 100 | 0 | 0
6431 | 787.95 | 0 | 27 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 18.9814 | 800.3124 | 0 | 0.05921 | 7.7509 | 0 | 0 | 0 | 0 | off_peak | 787.95 | 0 | 100 | 0 | 0 | 100 | 0 | 0
6432 | 786.53 | 0 | 27 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 30.5453 | 798.8924 | 0 | 0.05921 | 7.5939 | 0 | 0 | 0 | 0 | off_peak | 786.53 | 0 | 100 | 0 | 0 | 100 | 0 | 0
6433 | 727.84 | 0 | 26.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30.5453 | 727.84 | 0 | 0.05921 | 7.5105 | 0 | 0 | 0 | 0 | off_peak | 727.84 |  |  | 0 | 0 | 100 | 0 | 0
6434 | 684.15 | 0 | 26.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30.5453 | 684.15 | 0 | 0.05921 | 7.2218 | 0 | 0 | 0 | 0 | off_peak | 684.15 |  |  | 0 | 0 | 100 | 0 | 0
6435 | 636.03 | 0 | 26.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30.5453 | 636.03 | 0 | 0.05921 | 6.7156 | 0 | 0 | 0 | 0 | off_peak | 636.03 |  |  | 0 | 0 | 100 | 0 | 0
6436 | 642.2 | 0 | 26.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30.5453 | 642.2 | 0 | 0.05921 | 6.1128 | 0 | 0 | 0 | 0 | off_peak | 642.2 |  |  | 0 | 0 | 100 | 0 | 0
6437 | 666.73 | 0 | 26.9 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 42.1093 | 679.0924 | 0 | 0.05921 | 5.4288 | 0 | 0 | 0 | 0 | off_peak | 666.73 | 0 | 100 | 0 | 0 | 100 | 0 | 0
6438 | 711.62 | 0 | 27 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 53.6732 | 723.9824 | 0 | 0.05921 | 4.9045 | 0 | 0 | 0 | 0 | off_peak | 711.62 | 0 | 100 | 0 | 0 | 100 | 0 | 0
6439 | 794.09 | 12.35 | 27.4 | 1.9834 | 1.9834 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 65.2371 | 804.469 | 0 | 0.05921 | 4.5066 | 0 | 0 | 0 | 1.9834 | off_peak | 792.1066 | 0 | 100 | 0.25 | 0 | 99.75 | 8.9385 | 0
6440 | 852.98 | 58.4982 | 28 | 9.3744 | 9.3744 | 0 | 0 | 8.9371 | 8.9371 | 0 | 0 | 0 | 73.597 | 852.5428 | 0 | 0.05921 | 4.2446 | 0 | 0 | 0 | 9.3744 | off_peak | 843.6056 | 0 | 100 | 1.1 | 0 | 98.9 | 39.7902 | 0
6441 | 906.27 | 58.9 | 28.4 | 9.425 | 9.425 | 0 | 0 | 0.57721 | 0.57721 | 0 | 0 | 0 | 74.137 | 897.4222 | 0 | 0.05921 | 4.0762 | 0 | 0 | 0 | 9.425 | off_peak | 896.845 | 0 | 100 | 1.04 | 0 | 98.96 | 38.4185 | 0
6442 | 892.3 | 611.084 | 28.8 | 97.6413 | 97.6413 | 0 | 0 | 0.037279 | 0.037279 | 0 | 0 | 0 | 74.1718 | 794.6959 | 0 | 0.05921 | 4.0456 | 0 | 0 | 0 | 97.6413 | off_peak | 794.6587 | 0 | 100 | 10.94 | 0 | 89.06 | 395.0179 | 0
6443 | 842.39 | 623.244 | 29.1 | 99.4753 | 99.4753 | 0 | 0 | 0.0024077 | 0.0024077 | 0 | 0 | 0 | 74.1741 | 742.9171 | 0 | 0.05921 | 4.3061 | 0 | 0 | 0 | 99.4753 | off_peak | 742.9147 | 0 | 100 | 11.81 | 0 | 88.19 | 428.3518 | 0
6444 | 971.02 | 725.366 | 29.3 | 115.6902 | 115.6902 | 0 | 0 | 0.0001555 | 0.0001555 | 0 | 0 | 0 | 74.1742 | 855.3299 | 0 | 0.05921 | 4.7811 | 0 | 0 | 0 | 115.6902 | off_peak | 855.3298 | 0 | 100 | 11.91 | 0 | 88.09 | 553.1323 | 0
6445 | 873.71 | 669.729 | 29.5 | 106.7385 | 106.7385 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1742 | 766.9715 | 0 | 0.088511 | 5.0421 | 0 | 0 | 0 | 106.7385 | on_peak | 766.9715 |  |  | 12.22 | 0 | 87.78 | 538.1815 | 0
6446 | 895.8 | 599.733 | 29.5 | 95.5828 | 95.5828 | 0 | 0 | 0 | 0 | 62.4453 | 62.4453 | 0 | 7.4174 | 737.7719 | 0 | 0.088511 | 5.2312 | 0 | 0 | 0 | 95.5828 | on_peak | 737.7719 |  |  | 10.67 | 6.97 | 82.36 | 500.0135 | 0
6447 | 863.35 | 636.302 | 29.5 | 101.411 | 101.411 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 761.939 | 0 | 0.088511 | 5.4895 | 0 | 0 | 0 | 101.411 | on_peak | 761.939 |  |  | 11.75 | 0 | 88.25 | 556.6991 | 0
6448 | 806.76 | 461.775 | 29.3 | 73.6495 | 73.6495 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 733.1105 | 0 | 0.088511 | 5.9823 | 0 | 0 | 0 | 73.6495 | on_peak | 733.1105 |  |  | 9.13 | 0 | 90.87 | 440.5968 | 0
6449 | 808.72 | 300.82 | 29 | 48.0311 | 48.0311 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 760.6889 | 0 | 0.088511 | 6.3898 | 0 | 0 | 0 | 48.0311 | on_peak | 760.6889 |  |  | 5.94 | 0 | 94.06 | 306.9096 | 0
6450 | 815.83 | 95.5688 | 28.5 | 15.2871 | 15.2871 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 800.5429 | 0 | 0.088511 | 6.6151 | 0 | 0 | 0 | 15.2871 | on_peak | 800.5429 |  |  | 1.87 | 0 | 98.13 | 101.1254 | 0
6451 | 828.97 | 0 | 28.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 828.97 | 0 | 0.088511 | 6.7528 | 0 | 0 | 0 | 0 | on_peak | 828.97 |  |  | 0 | 0 | 100 | 0 | 0
6452 | 811.55 | 0 | 28 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 811.55 | 0 | 0.088511 | 6.8424 | 0 | 0 | 0 | 0 | on_peak | 811.55 |  |  | 0 | 0 | 100 | 0 | 0
6453 | 791.59 | 0 | 27.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 791.59 | 0 | 0.088511 | 7.1487 | 0 | 0 | 0 | 0 | on_peak | 791.59 |  |  | 0 | 0 | 100 | 0 | 0
6454 | 777.27 | 0 | 27.8 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 18.9814 | 789.6324 | 0 | 0.05921 | 7.563 | 0 | 0 | 0 | 0 | off_peak | 777.27 | 0 | 100 | 0 | 0 | 100 | 0 | 0
6455 | 772.52 | 0 | 27.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18.9814 | 772.52 | 0 | 0.05921 | 7.6305 | 0 | 0 | 0 | 0 | off_peak | 772.52 |  |  | 0 | 0 | 100 | 0 | 0
6456 | 780.54 | 0 | 27.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18.9814 | 780.54 | 0 | 0.05921 | 7.5293 | 0 | 0 | 0 | 0 | off_peak | 780.54 |  |  | 0 | 0 | 100 | 0 | 0
6457 | 711.66 | 0 | 27.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18.9814 | 711.66 | 0 | 0.05921 | 7.5065 | 0 | 0 | 0 | 0 | off_peak | 711.66 |  |  | 0 | 0 | 100 | 0 | 0
6458 | 654.33 | 0 | 27.1 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 30.5453 | 666.6924 | 0 | 0.05921 | 7.153 | 0 | 0 | 0 | 0 | off_peak | 654.33 | 0 | 100 | 0 | 0 | 100 | 0 | 0
6459 | 633.33 | 0 | 27 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30.5453 | 633.33 | 0 | 0.05921 | 6.6863 | 0 | 0 | 0 | 0 | off_peak | 633.33 |  |  | 0 | 0 | 100 | 0 | 0
6460 | 621.8 | 0 | 26.9 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 42.1093 | 634.1624 | 0 | 0.05921 | 5.9267 | 0 | 0 | 0 | 0 | off_peak | 621.8 | 0 | 100 | 0 | 0 | 100 | 0 | 0
6461 | 675.46 | 0 | 27 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 42.1093 | 675.46 | 0 | 0.05921 | 14.316 | 0 | 0 | 0 | 0 | off_peak | 675.46 |  |  | 0 | 0 | 100 | 0 | 0
6462 | 706.27 | 0 | 27.1 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 53.6732 | 718.6324 | 0 | 0.05921 | 4.7305 | 0 | 0 | 0 | 0 | off_peak | 706.27 | 0 | 100 | 0 | 0 | 100 | 0 | 0
6463 | 796.25 | 20.7669 | 27.4 | 3.3352 | 3.3352 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 65.2371 | 805.2772 | 0 | 0.05921 | 4.382 | 0 | 0 | 0 | 3.3352 | off_peak | 792.9148 | 0 | 100 | 0.42 | 0 | 99.58 | 14.6147 | 0
6464 | 817.18 | 94.1964 | 27.9 | 15.1005 | 15.1005 | 0 | 0 | 8.9371 | 8.9371 | 0 | 0 | 0 | 73.597 | 811.0166 | 0 | 0.05921 | 4.1442 | 0 | 0 | 0 | 15.1005 | off_peak | 802.0795 | 0 | 100 | 1.85 | 0 | 98.15 | 62.5798 | 0
6465 | 798.22 | 201.263 | 28.3 | 32.2173 | 32.2173 | 0 | 0 | 0.57721 | 0.57721 | 0 | 0 | 0 | 74.137 | 766.5799 | 0 | 0.05921 | 4.0219 | 0 | 0 | 0 | 32.2173 | off_peak | 766.0027 | 0 | 100 | 4.04 | 0 | 95.96 | 129.5755 | 0
6466 | 831.18 | 457.926 | 28.6 | 73.2226 | 73.2226 | 0 | 0 | 0.037279 | 0.037279 | 0 | 0 | 0 | 74.1718 | 757.9947 | 0 | 0.05921 | 4.0332 | 0 | 0 | 0 | 73.2226 | off_peak | 757.9574 | 0 | 100 | 8.81 | 0 | 91.19 | 295.3224 | 0
6467 | 832.63 | 190.373 | 28.9 | 30.4074 | 30.4074 | 0 | 0 | 0.0024077 | 0.0024077 | 0 | 0 | 0 | 74.1741 | 802.225 | 0 | 0.05921 | 4.3183 | 0 | 0 | 0 | 30.4074 | off_peak | 802.2226 | 0 | 100 | 3.65 | 0 | 96.35 | 131.3098 | 0
6468 | 880.67 | 303.345 | 29.2 | 48.3989 | 48.3989 | 0 | 0 | 0.0001555 | 0.0001555 | 0 | 0 | 0 | 74.1742 | 832.2713 | 0 | 0.05921 | 4.763 | 0 | 0 | 0 | 48.3989 | off_peak | 832.2711 | 0 | 100 | 5.5 | 0 | 94.5 | 230.5252 | 0
6469 | 848.79 | 53.2 | 29.5 | 8.4788 | 8.4788 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1742 | 840.3112 | 0 | 0.088511 | 5.1457 | 0 | 0 | 0 | 8.4788 | on_peak | 840.3112 |  |  | 1 | 0 | 99 | 43.6293 | 0
6470 | 875.3 | 486.563 | 29.6 | 77.5179 | 77.5179 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1742 | 797.7821 | 0 | 0.088511 | 5.3121 | 0 | 0 | 0 | 77.5179 | on_peak | 797.7821 |  |  | 8.86 | 0 | 91.14 | 411.7833 | 0
6471 | 928.27 | 228.083 | 29.7 | 36.3243 | 36.3243 | 0 | 0 | 0 | 0 | 62.4453 | 62.4453 | 0 | 7.4174 | 829.5005 | 0 | 0.088511 | 5.4675 | 0 | 0 | 0 | 36.3243 | on_peak | 829.5005 |  |  | 3.91 | 6.73 | 89.36 | 198.6045 | 0
6472 | 836.62 | 413.092 | 29.6 | 65.8127 | 65.8127 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 770.8073 | 0 | 0.088511 | 5.6428 | 0 | 0 | 0 | 65.8127 | on_peak | 770.8073 |  |  | 7.87 | 0 | 92.13 | 371.3669 | 0
6473 | 840.53 | 5.7 | 29.3 | 0.90911 | 0.90911 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 839.6209 | 0 | 0.088511 | 5.8594 | 0 | 0 | 0 | 0.90911 | on_peak | 839.6209 |  |  | 0.11 | 0 | 99.89 | 5.3268 | 0
6474 | 840.13 | 45.8858 | 28.7 | 7.3345 | 7.3345 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 832.7955 | 0 | 0.088511 | 6.0921 | 0 | 0 | 0 | 7.3345 | on_peak | 832.7955 |  |  | 0.87 | 0 | 99.13 | 44.6824 | 0
6475 | 812.39 | 0 | 28.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 812.39 | 0 | 0.088511 | 6.2664 | 0 | 0 | 0 | 0 | on_peak | 812.39 |  |  | 0 | 0 | 100 | 0 | 0
6476 | 851.03 | 0 | 27.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 851.03 | 0 | 0.088511 | 6.5455 | 0 | 0 | 0 | 0 | on_peak | 851.03 |  |  | 0 | 0 | 100 | 0 | 0
6477 | 808.35 | 0 | 27.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 808.35 | 0 | 0.088511 | 6.8197 | 0 | 0 | 0 | 0 | on_peak | 808.35 |  |  | 0 | 0 | 100 | 0 | 0
6478 | 784.28 | 0 | 27.2 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 18.9814 | 796.6424 | 0 | 0.05921 | 7.0504 | 0 | 0 | 0 | 0 | off_peak | 784.28 | 0 | 100 | 0 | 0 | 100 | 0 | 0
6479 | 806.33 | 0 | 27.1 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 30.5453 | 818.6924 | 0 | 0.05921 | 7.1789 | 0 | 0 | 0 | 0 | off_peak | 806.33 | 0 | 100 | 0 | 0 | 100 | 0 | 0
6480 | 784.74 | 0 | 27.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30.5453 | 784.74 | 0 | 0.05921 | 7.2032 | 0 | 0 | 0 | 0 | off_peak | 784.74 |  |  | 0 | 0 | 100 | 0 | 0
6481 | 750.53 | 0 | 27.1 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 42.1093 | 762.8924 | 0 | 0.05921 | 7.2427 | 0 | 0 | 0 | 0 | off_peak | 750.53 | 0 | 100 | 0 | 0 | 100 | 0 | 0
6482 | 683.56 | 0 | 27.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 42.1093 | 683.56 | 0 | 0.05921 | 6.9787 | 0 | 0 | 0 | 0 | off_peak | 683.56 |  |  | 0 | 0 | 100 | 0 | 0
6483 | 655.03 | 0 | 27.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 42.1093 | 655.03 | 0 | 0.05921 | 6.4099 | 0 | 0 | 0 | 0 | off_peak | 655.03 |  |  | 0 | 0 | 100 | 0 | 0
6484 | 658.58 | 0 | 27.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 42.1093 | 658.58 | 0 | 0.05921 | 5.889 | 0 | 0 | 0 | 0 | off_peak | 658.58 |  |  | 0 | 0 | 100 | 0 | 0
6485 | 675.2 | 0 | 27.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 42.1093 | 675.2 | 0 | 0.05921 | 5.2228 | 0 | 0 | 0 | 0 | off_peak | 675.2 |  |  | 0 | 0 | 100 | 0 | 0
6486 | 722.25 | 0 | 27.3 | 0 | 0 | 0 | 0 | 8.7006 | 8.7006 | 0 | 0 | 0 | 50.2479 | 730.9506 | 0 | 0.05921 | 4.688 | 0 | 0 | 0 | 0 | off_peak | 722.25 | 0 | 100 | 0 | 0 | 100 | 0 | 0
6487 | 795.98 | 25.6724 | 27.5 | 4.1215 | 4.1215 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 61.8119 | 804.2209 | 0 | 0.05921 | 4.2898 | 0 | 0 | 0 | 4.1215 | off_peak | 791.8585 | 0 | 100 | 0.52 | 0 | 99.48 | 17.6805 | 0
6488 | 842.47 | 209.313 | 27.9 | 33.5547 | 33.5547 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 73.3758 | 821.2777 | 0 | 0.05921 | 4.0431 | 0 | 0 | 0 | 33.5547 | off_peak | 808.9153 | 0 | 100 | 3.98 | 0 | 96.02 | 135.6635 | 0
6489 | 842.16 | 417.104 | 28.2 | 66.7924 | 66.7924 | 0 | 0 | 0.79843 | 0.79843 | 0 | 0 | 0 | 74.1227 | 776.166 | 0 | 0.05921 | 3.8913 | 0 | 0 | 0 | 66.7924 | off_peak | 775.3676 | 0 | 100 | 7.93 | 0 | 92.07 | 259.9113 | 0
6490 | 878.87 | 601.653 | 28.6 | 96.2046 | 96.2046 | 0 | 0 | 0.051567 | 0.051567 | 0 | 0 | 0 | 74.1709 | 782.717 | 0 | 0.05921 | 3.8739 | 0 | 0 | 0 | 96.2046 | off_peak | 782.6654 | 0 | 100 | 10.95 | 0 | 89.05 | 372.6878 | 0
6491 | 831.83 | 732.122 | 28.8 | 116.9813 | 116.9813 | 0 | 0 | 0.0033305 | 0.0033305 | 0 | 0 | 0 | 74.174 | 714.8521 | 0 | 0.05921 | 4.1676 | 0 | 0 | 0 | 116.9813 | off_peak | 714.8487 | 0 | 100 | 14.06 | 0 | 85.94 | 487.5265 | 0
6492 | 878.3 | 167.2 | 29 | 26.6964 | 26.6964 | 0 | 0 | 0.0002151 | 0.0002151 | 0 | 0 | 0 | 74.1742 | 851.6039 | 0 | 0.05921 | 4.6323 | 0 | 0 | 0 | 26.6964 | off_peak | 851.6036 | 0 | 100 | 3.04 | 0 | 96.96 | 123.6669 | 0
6493 | 831.28 | 760.278 | 29.1 | 121.3471 | 121.3471 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1742 | 709.9329 | 0 | 0.088511 | 4.9056 | 0 | 0 | 0 | 121.3471 | on_peak | 709.9329 |  |  | 14.6 | 0 | 85.4 | 595.2761 | 0
6494 | 867.41 | 714.219 | 29.2 | 113.954 | 113.954 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1742 | 753.456 | 0 | 0.088511 | 4.9959 | 0 | 0 | 0 | 113.954 | on_peak | 753.456 |  |  | 13.14 | 0 | 86.86 | 569.3071 | 0
6495 | 842.67 | 657.909 | 29.2 | 104.9697 | 104.9697 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1742 | 737.7003 | 0 | 0.088511 | 5.1748 | 0 | 0 | 0 | 104.9697 | on_peak | 737.7003 |  |  | 12.46 | 0 | 87.54 | 543.1979 | 0
6496 | 837.19 | 490.113 | 29.1 | 78.2264 | 78.2264 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1742 | 758.9636 | 0 | 0.088511 | 5.3749 | 0 | 0 | 0 | 78.2264 | on_peak | 758.9636 |  |  | 9.34 | 0 | 90.66 | 420.4559 | 0
6497 | 828.1 | 222.374 | 28.8 | 35.5318 | 35.5318 | 0 | 0 | 0 | 0 | 62.4453 | 62.4453 | 0 | 7.4174 | 730.1229 | 0 | 0.088511 | 5.7908 | 0 | 0 | 0 | 35.5318 | on_peak | 730.1229 |  |  | 4.29 | 7.54 | 88.17 | 205.7579 | 0
6498 | 853.83 | 31.4889 | 28.3 | 5.0406 | 5.0406 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 848.7894 | 0 | 0.088511 | 6.161 | 0 | 0 | 0 | 5.0406 | on_peak | 848.7894 |  |  | 0.59 | 0 | 99.41 | 31.0549 | 0
6499 | 839.84 | 0 | 28.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 839.84 | 0 | 0.088511 | 6.5571 | 0 | 0 | 0 | 0 | on_peak | 839.84 |  |  | 0 | 0 | 100 | 0 | 0
6500 | 824.51 | 0 | 27.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 824.51 | 0 | 0.088511 | 6.9346 | 0 | 0 | 0 | 0 | on_peak | 824.51 |  |  | 0 | 0 | 100 | 0 | 0
6501 | 821.68 | 0 | 27.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 821.68 | 0 | 0.088511 | 7.2601 | 0 | 0 | 0 | 0 | on_peak | 821.68 |  |  | 0 | 0 | 100 | 0 | 0
6502 | 804.52 | 0 | 27.6 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 18.9814 | 816.8824 | 0 | 0.05921 | 7.5411 | 0 | 0 | 0 | 0 | off_peak | 804.52 | 0 | 100 | 0 | 0 | 100 | 0 | 0
6503 | 810.15 | 0 | 27.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18.9814 | 810.15 | 0 | 0.05921 | 7.6651 | 0 | 0 | 0 | 0 | off_peak | 810.15 |  |  | 0 | 0 | 100 | 0 | 0
6504 | 805.8 | 0 | 27.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18.9814 | 805.8 | 0 | 0.05921 | 7.7164 | 0 | 0 | 0 | 0 | off_peak | 805.8 |  |  | 0 | 0 | 100 | 0 | 0
6505 | 727.49 | 0 | 27.2 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 30.5453 | 739.8524 | 0 | 0.05921 | 7.73 | 0 | 0 | 0 | 0 | off_peak | 727.49 | 0 | 100 | 0 | 0 | 100 | 0 | 0
6506 | 698.04 | 0 | 27.1 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 42.1093 | 710.4024 | 0 | 0.05921 | 7.2872 | 0 | 0 | 0 | 0 | off_peak | 698.04 | 0 | 100 | 0 | 0 | 100 | 0 | 0
6507 | 679.21 | 0 | 27 | 0 | 0 | 0 | 0 | 8.7006 | 8.7006 | 0 | 0 | 0 | 50.2479 | 687.9106 | 0 | 0.05921 | 6.8351 | 0 | 0 | 0 | 0 | off_peak | 679.21 | 0 | 100 | 0 | 0 | 100 | 0 | 0
6508 | 658.14 | 0 | 27 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50.2479 | 658.14 | 0 | 0.05921 | 6.2653 | 0 | 0 | 0 | 0 | off_peak | 658.14 |  |  | 0 | 0 | 100 | 0 | 0
6509 | 707.21 | 0 | 27 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50.2479 | 707.21 | 0 | 0.05921 | 5.6284 | 0 | 0 | 0 | 0 | off_peak | 707.21 |  |  | 0 | 0 | 100 | 0 | 0
6510 | 705.45 | 0 | 27 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50.2479 | 705.45 | 0 | 0.05921 | 5.0972 | 0 | 0 | 0 | 0 | off_peak | 705.45 |  |  | 0 | 0 | 100 | 0 | 0
6511 | 814.35 | 14.25 | 27.4 | 2.2886 | 2.2886 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 61.8119 | 824.4238 | 0 | 0.05921 | 4.7392 | 0 | 0 | 0 | 2.2886 | off_peak | 812.0614 | 0 | 100 | 0.28 | 0 | 99.72 | 10.846 | 0
6512 | 842.21 | 65.138 | 27.9 | 10.4422 | 10.4422 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 73.3758 | 844.1302 | 0 | 0.05921 | 4.5199 | 0 | 0 | 0 | 10.4422 | off_peak | 831.7678 | 0 | 100 | 1.24 | 0 | 98.76 | 47.1976 | 0
6513 | 880.9 | 300.739 | 28.2 | 48.1585 | 48.1585 | 0 | 0 | 0.79843 | 0.79843 | 0 | 0 | 0 | 74.1227 | 833.54 | 0 | 0.05921 | 4.3677 | 0 | 0 | 0 | 48.1585 | off_peak | 832.7415 | 0 | 100 | 5.47 | 0 | 94.53 | 210.3394 | 0
6514 | 888.51 | 476.107 | 28.5 | 76.1575 | 76.1575 | 0 | 0 | 0.051567 | 0.051567 | 0 | 0 | 0 | 74.1709 | 812.4041 | 0 | 0.05921 | 4.357 | 0 | 0 | 0 | 76.1575 | off_peak | 812.3525 | 0 | 100 | 8.57 | 0 | 91.43 | 331.8206 | 0
6515 | 849.66 | 726.44 | 28.8 | 116.0734 | 116.0734 | 0 | 0 | 0.0033305 | 0.0033305 | 0 | 0 | 0 | 74.174 | 733.59 | 0 | 0.05921 | 4.6063 | 0 | 0 | 0 | 116.0734 | off_peak | 733.5866 | 0 | 100 | 13.66 | 0 | 86.34 | 534.6681 | 0
6516 | 872.33 | 702.785 | 29 | 112.2117 | 112.2117 | 0 | 0 | 0.0002151 | 0.0002151 | 0 | 0 | 0 | 74.1742 | 760.1185 | 0 | 0.05921 | 5.025 | 0 | 0 | 0 | 112.2117 | off_peak | 760.1183 | 0 | 100 | 12.86 | 0 | 87.14 | 563.8615 | 0
6517 | 857.97 | 346.764 | 29.1 | 55.3466 | 55.3466 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1742 | 802.6234 | 0 | 0.088511 | 5.3346 | 0 | 0 | 0 | 55.3466 | on_peak | 802.6234 |  |  | 6.45 | 0 | 93.55 | 295.2515 | 0
6518 | 855.48 | 77.9 | 29.1 | 12.4335 | 12.4335 | 0 | 0 | 0 | 0 | 62.4453 | 62.4453 | 0 | 7.4174 | 780.6012 | 0 | 0.088511 | 5.4931 | 0 | 0 | 0 | 12.4335 | on_peak | 780.6012 |  |  | 1.45 | 7.3 | 91.25 | 68.2984 | 0
6519 | 867.81 | 323.57 | 29 | 51.6635 | 51.6635 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 816.1465 | 0 | 0.088511 | 5.6973 | 0 | 0 | 0 | 51.6635 | on_peak | 816.1465 |  |  | 5.95 | 0 | 94.05 | 294.3423 | 0
6520 | 773.79 | 60.8 | 28.8 | 9.7149 | 9.7149 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 764.0751 | 0 | 0.088511 | 5.9231 | 0 | 0 | 0 | 9.7149 | on_peak | 764.0751 |  |  | 1.26 | 0 | 98.74 | 57.5416 | 0
6521 | 842.9 | 55.1 | 28.5 | 8.8137 | 8.8137 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 834.0863 | 0 | 0.088511 | 6.3358 | 0 | 0 | 0 | 8.8137 | on_peak | 834.0863 |  |  | 1.05 | 0 | 98.95 | 55.8423 | 0
6522 | 813.57 | 38.95 | 28.1 | 6.2395 | 6.2395 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 807.3305 | 0 | 0.088511 | 6.6961 | 0 | 0 | 0 | 6.2395 | on_peak | 807.3305 |  |  | 0.77 | 0 | 99.23 | 41.7801 | 0
6523 | 804.8 | 0 | 27.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 804.8 | 0 | 0.088511 | 6.9954 | 0 | 0 | 0 | 0 | on_peak | 804.8 |  |  | 0 | 0 | 100 | 0 | 0
6524 | 805.84 | 0 | 27.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 805.84 | 0 | 0.088511 | 7.2775 | 0 | 0 | 0 | 0 | on_peak | 805.84 |  |  | 0 | 0 | 100 | 0 | 0
6525 | 811.45 | 0 | 27.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 811.45 | 0 | 0.088511 | 7.3151 | 0 | 0 | 0 | 0 | on_peak | 811.45 |  |  | 0 | 0 | 100 | 0 | 0
6526 | 771.69 | 0 | 27.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 771.69 | 0 | 0.05921 | 7.3897 | 0 | 0 | 0 | 0 | off_peak | 771.69 |  |  | 0 | 0 | 100 | 0 | 0
6527 | 792.26 | 0 | 27.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 792.26 | 0 | 0.05921 | 7.4766 | 0 | 0 | 0 | 0 | off_peak | 792.26 |  |  | 0 | 0 | 100 | 0 | 0
6528 | 762.21 | 0 | 27.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 762.21 | 0 | 0.05921 | 7.5376 | 0 | 0 | 0 | 0 | off_peak | 762.21 |  |  | 0 | 0 | 100 | 0 | 0
6529 | 714.9 | 0 | 27.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 714.9 | 0 | 0.05921 | 7.4128 | 0 | 0 | 0 | 0 | off_peak | 714.9 |  |  | 0 | 0 | 100 | 0 | 0
6530 | 643.32 | 0 | 27.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 643.32 | 0 | 0.05921 | 7.1949 | 0 | 0 | 0 | 0 | off_peak | 643.32 |  |  | 0 | 0 | 100 | 0 | 0
6531 | 650.51 | 0 | 27.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 650.51 | 0 | 0.05921 | 6.7472 | 0 | 0 | 0 | 0 | off_peak | 650.51 |  |  | 0 | 0 | 100 | 0 | 0
6532 | 645.62 | 0 | 27.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 645.62 | 0 | 0.05921 | 6.2844 | 0 | 0 | 0 | 0 | off_peak | 645.62 |  |  | 0 | 0 | 100 | 0 | 0
6533 | 656.21 | 0 | 27.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 656.21 | 0 | 0.05921 | 5.6717 | 0 | 0 | 0 | 0 | off_peak | 656.21 |  |  | 0 | 0 | 100 | 0 | 0
6534 | 693.34 | 0 | 27.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 693.34 | 0 | 0.05921 | 5.2328 | 0 | 0 | 0 | 0 | off_peak | 693.34 |  |  | 0 | 0 | 100 | 0 | 0
6535 | 753.28 | 10.45 | 27.4 | 1.6783 | 1.6783 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 751.6017 | 0 | 0.05921 | 4.8806 | 0 | 0 | 0 | 1.6783 | off_peak | 751.6017 |  |  | 0.22 | 0 | 99.78 | 8.1909 | 0
6536 | 749.39 | 188.687 | 27.8 | 30.2592 | 30.2592 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 719.1308 | 0 | 0.05921 | 4.6534 | 0 | 0 | 0 | 30.2592 | off_peak | 719.1308 |  |  | 4.04 | 0 | 95.96 | 140.8075 | 0
6537 | 732.23 | 388.29 | 28 | 62.2236 | 62.2236 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 670.0064 | 0 | 0.05921 | 4.5008 | 0 | 0 | 0 | 62.2236 | off_peak | 670.0064 |  |  | 8.5 | 0 | 91.5 | 280.0547 | 0
6538 | 730.21 | 567.222 | 28.3 | 90.7983 | 90.7983 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 639.4117 | 0 | 0.05921 | 4.4423 | 0 | 0 | 0 | 90.7983 | off_peak | 639.4117 |  |  | 12.43 | 0 | 87.57 | 403.3511 | 0
6539 | 712.06 | 694.752 | 28.5 | 111.1317 | 111.1317 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 600.9283 | 0 | 0.05921 | 4.4569 | 0 | 0 | 0 | 111.1317 | off_peak | 600.9283 |  |  | 15.61 | 0 | 84.39 | 495.2993 | 0
6540 | 751.96 | 671.328 | 28.7 | 107.3065 | 107.3065 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 644.6535 | 0 | 0.05921 | 4.558 | 0 | 0 | 0 | 107.3065 | off_peak | 644.6535 |  |  | 14.27 | 0 | 85.73 | 489.1068 | 0
6541 | 764.36 | 558.31 | 28.7 | 89.2415 | 89.2415 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 675.1185 | 0 | 0.05921 | 4.7911 | 0 | 0 | 0 | 89.2415 | off_peak | 675.1185 |  |  | 11.68 | 0 | 88.32 | 427.5622 | 0
6542 | 728.6 | 736.259 | 28.6 | 117.7282 | 117.7282 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 610.8718 | 0 | 0.05921 | 5.1429 | 0 | 0 | 0 | 117.7282 | off_peak | 610.8718 |  |  | 16.16 | 0 | 83.84 | 605.4604 | 0
6543 | 744.05 | 614.9 | 28.5 | 98.3587 | 98.3587 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 645.6913 | 0 | 0.05921 | 5.5038 | 0 | 0 | 0 | 98.3587 | off_peak | 645.6913 |  |  | 13.22 | 0 | 86.78 | 541.3443 | 0
6544 | 742.86 | 125.4 | 28.3 | 20.0735 | 20.0735 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 722.7865 | 0 | 0.05921 | 6.0005 | 0 | 0 | 0 | 20.0735 | off_peak | 722.7865 |  |  | 2.7 | 0 | 97.3 | 120.4517 | 0
6545 | 701.63 | 257.42 | 28.1 | 41.2366 | 41.2366 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 660.3934 | 0 | 0.05921 | 6.4777 | 0 | 0 | 0 | 41.2366 | off_peak | 660.3934 |  |  | 5.88 | 0 | 94.12 | 267.1191 | 0
6546 | 644.59 | 59.4233 | 27.8 | 9.5295 | 9.5295 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 635.0605 | 0 | 0.05921 | 6.9232 | 0 | 0 | 0 | 9.5295 | off_peak | 635.0605 |  |  | 1.48 | 0 | 98.52 | 65.9751 | 0
6547 | 602.62 | 0 | 27.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 602.62 | 0 | 0.05921 | 7.4815 | 0 | 0 | 0 | 0 | off_peak | 602.62 |  |  | 0 | 0 | 100 | 0 | 0
6548 | 593.78 | 0 | 26.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 593.78 | 0 | 0.05921 | 7.7573 | 0 | 0 | 0 | 0 | off_peak | 593.78 |  |  | 0 | 0 | 100 | 0 | 0
6549 | 596.46 | 0 | 26 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 596.46 | 0 | 0.05921 | 7.8276 | 0 | 0 | 0 | 0 | off_peak | 596.46 |  |  | 0 | 0 | 100 | 0 | 0
6550 | 585.18 | 0 | 25.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 585.18 | 0 | 0.05921 | 7.7437 | 0 | 0 | 0 | 0 | off_peak | 585.18 |  |  | 0 | 0 | 100 | 0 | 0
6551 | 592.45 | 0 | 25.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 592.45 | 0 | 0.05921 | 7.5387 | 0 | 0 | 0 | 0 | off_peak | 592.45 |  |  | 0 | 0 | 100 | 0 | 0
6552 | 580.87 | 0 | 25.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 580.87 | 0 | 0.05921 | 7.3885 | 0 | 0 | 0 | 0 | off_peak | 580.87 |  |  | 0 | 0 | 100 | 0 | 0
6553 | 582.23 | 0 | 25.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 582.23 | 0 | 0.05921 | 7.2346 | 0 | 0 | 0 | 0 | off_peak | 582.23 |  |  | 0 | 0 | 100 | 0 | 0
6554 | 587.05 | 0 | 25.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 587.05 | 0 | 0.05921 | 6.9864 | 0 | 0 | 0 | 0 | off_peak | 587.05 |  |  | 0 | 0 | 100 | 0 | 0
6555 | 602.79 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 602.79 | 0 | 0.05921 | 6.4805 | 0 | 0 | 0 | 0 | off_peak | 602.79 |  |  | 0 | 0 | 100 | 0 | 0
6556 | 610.6 | 0 | 24.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 610.6 | 0 | 0.05921 | 6.0567 | 0 | 0 | 0 | 0 | off_peak | 610.6 |  |  | 0 | 0 | 100 | 0 | 0
6557 | 584.51 | 0 | 24.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 584.51 | 0 | 0.05921 | 5.5891 | 0 | 0 | 0 | 0 | off_peak | 584.51 |  |  | 0 | 0 | 100 | 0 | 0
6558 | 671.3 | 0 | 24.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 671.3 | 0 | 0.05921 | 5.1242 | 0 | 0 | 0 | 0 | off_peak | 671.3 |  |  | 0 | 0 | 100 | 0 | 0
6559 | 703.02 | 26.211 | 25.2 | 4.2431 | 4.2431 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 698.7769 | 0 | 0.05921 | 4.7945 | 0 | 0 | 0 | 4.2431 | off_peak | 698.7769 |  |  | 0.6 | 0 | 99.4 | 20.3436 | 0
6560 | 731.5 | 205.997 | 25.7 | 33.2874 | 33.2874 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 698.2126 | 0 | 0.05921 | 4.5467 | 0 | 0 | 0 | 33.2874 | off_peak | 698.2126 |  |  | 4.55 | 0 | 95.45 | 151.3474 | 0
6561 | 741.89 | 420.382 | 26.2 | 67.8077 | 67.8077 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 674.0823 | 0 | 0.05921 | 4.3755 | 0 | 0 | 0 | 67.8077 | off_peak | 674.0823 |  |  | 9.14 | 0 | 90.86 | 296.6933 | 0
6562 | 732.7 | 538.278 | 26.7 | 86.6674 | 86.6674 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 646.0326 | 0 | 0.05921 | 4.2672 | 0 | 0 | 0 | 86.6674 | off_peak | 646.0326 |  |  | 11.83 | 0 | 88.17 | 369.8288 | 0
6563 | 700.4 | 563.276 | 27.2 | 90.528 | 90.528 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 609.872 | 0 | 0.05921 | 4.2438 | 0 | 0 | 0 | 90.528 | off_peak | 609.872 |  |  | 12.93 | 0 | 87.07 | 384.1827 | 0
6564 | 704.13 | 262.613 | 27.6 | 42.1451 | 42.1451 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 661.9849 | 0 | 0.05921 | 4.3362 | 0 | 0 | 0 | 42.1451 | off_peak | 661.9849 |  |  | 5.99 | 0 | 94.01 | 182.7498 | 0
6565 | 726.86 | 257.904 | 28 | 41.3292 | 41.3292 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 685.5308 | 0 | 0.05921 | 4.5237 | 0 | 0 | 0 | 41.3292 | off_peak | 685.5308 |  |  | 5.69 | 0 | 94.31 | 186.9608 | 0
6566 | 720.25 | 167.2 | 28.1 | 26.7841 | 26.7841 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 693.4659 | 0 | 0.05921 | 4.7879 | 0 | 0 | 0 | 26.7841 | off_peak | 693.4659 |  |  | 3.72 | 0 | 96.28 | 128.2402 | 0
6567 | 728.14 | 216.584 | 28.1 | 34.695 | 34.695 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 18.9814 | 705.8073 | 0 | 0.05921 | 5.0157 | 0 | 0 | 0 | 34.695 | off_peak | 693.445 | 0 | 100 | 4.76 | 0 | 95.24 | 174.0205 | 0
6568 | 742.17 | 64.6 | 27.9 | 10.3559 | 10.3559 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 30.5453 | 744.1764 | 0 | 0.05921 | 5.333 | 0 | 0 | 0 | 10.3559 | off_peak | 731.8141 | 0 | 100 | 1.4 | 0 | 98.6 | 55.2287 | 0
6569 | 702.73 | 37.05 | 27.5 | 5.9481 | 5.9481 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 42.1093 | 709.1443 | 0 | 0.05921 | 5.9567 | 0 | 0 | 0 | 5.9481 | off_peak | 696.7819 | 0 | 100 | 0.85 | 0 | 99.15 | 35.4309 | 0
6570 | 649.63 | 20.9 | 27.1 | 3.3602 | 3.3602 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 53.6732 | 658.6322 | 0 | 0.05921 | 6.5631 | 0 | 0 | 0 | 3.3602 | off_peak | 646.2698 | 0 | 100 | 0.52 | 0 | 99.48 | 22.0535 | 0
6571 | 584.23 | 0 | 26.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 53.6732 | 584.23 | 0 | 0.05921 | 6.9352 | 0 | 0 | 0 | 0 | off_peak | 584.23 |  |  | 0 | 0 | 100 | 0 | 0
6572 | 589.44 | 0 | 26.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 53.6732 | 589.44 | 0 | 0.05921 | 7.2477 | 0 | 0 | 0 | 0 | off_peak | 589.44 |  |  | 0 | 0 | 100 | 0 | 0
6573 | 555.6 | 0 | 26.5 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 65.2371 | 567.9624 | 0 | 0.05921 | 7.4256 | 0 | 0 | 0 | 0 | off_peak | 555.6 | 0 | 100 | 0 | 0 | 100 | 0 | 0
6574 | 564.09 | 0 | 26.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 65.2371 | 564.09 | 0 | 0.05921 | 7.3044 | 0 | 0 | 0 | 0 | off_peak | 564.09 |  |  | 0 | 0 | 100 | 0 | 0
6575 | 593.09 | 0 | 26.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 65.2371 | 593.09 | 0 | 0.05921 | 7.335 | 0 | 0 | 0 | 0 | off_peak | 593.09 |  |  | 0 | 0 | 100 | 0 | 0
6576 | 575.13 | 0 | 26.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 65.2371 | 575.13 | 0 | 0.05921 | 7.3517 | 0 | 0 | 0 | 0 | off_peak | 575.13 |  |  | 0 | 0 | 100 | 0 | 0
6577 | 569.69 | 0 | 26.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 65.2371 | 569.69 | 0 | 0.05921 | 7.3751 | 0 | 0 | 0 | 0 | off_peak | 569.69 |  |  | 0 | 0 | 100 | 0 | 0
6578 | 591.15 | 0 | 25.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 65.2371 | 591.15 | 0 | 0.05921 | 7.1487 | 0 | 0 | 0 | 0 | off_peak | 591.15 |  |  | 0 | 0 | 100 | 0 | 0
6579 | 570.36 | 0 | 25.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 65.2371 | 570.36 | 0 | 0.05921 | 6.6151 | 0 | 0 | 0 | 0 | off_peak | 570.36 |  |  | 0 | 0 | 100 | 0 | 0
6580 | 591.13 | 0 | 25.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 65.2371 | 591.13 | 0 | 0.05921 | 6.0827 | 0 | 0 | 0 | 0 | off_peak | 591.13 |  |  | 0 | 0 | 100 | 0 | 0
6581 | 572.72 | 0 | 25.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 65.2371 | 572.72 | 0 | 0.05921 | 5.4123 | 0 | 0 | 0 | 0 | off_peak | 572.72 |  |  | 0 | 0 | 100 | 0 | 0
6582 | 676.88 | 0 | 25.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 65.2371 | 676.88 | 0 | 0.05921 | 4.9375 | 0 | 0 | 0 | 0 | off_peak | 676.88 |  |  | 0 | 0 | 100 | 0 | 0
6583 | 728.51 | 11.4 | 25.5 | 1.8435 | 1.8435 | 0 | 0 | 8.9371 | 8.9371 | 0 | 0 | 0 | 73.597 | 735.6036 | 0 | 0.05921 | 4.5492 | 0 | 0 | 0 | 1.8435 | off_peak | 726.6665 | 0 | 100 | 0.25 | 0 | 99.75 | 8.3863 | 0
6584 | 770.11 | 62.964 | 25.8 | 10.1708 | 10.1708 | 0 | 0 | 0.57721 | 0.57721 | 0 | 0 | 0 | 74.137 | 760.5164 | 0 | 0.05921 | 4.31 | 0 | 0 | 0 | 10.1708 | off_peak | 759.9392 | 0 | 100 | 1.32 | 0 | 98.68 | 43.8359 | 0
6585 | 806.45 | 90.25 | 26.2 | 14.5573 | 14.5573 | 0 | 0 | 0.037279 | 0.037279 | 0 | 0 | 0 | 74.1718 | 791.9299 | 0 | 0.05921 | 4.1512 | 0 | 0 | 0 | 14.5573 | off_peak | 791.8927 | 0 | 100 | 1.81 | 0 | 98.19 | 60.4306 | 0
6586 | 810.36 | 288.221 | 26.7 | 46.406 | 46.406 | 0 | 0 | 0.0024077 | 0.0024077 | 0 | 0 | 0 | 74.1741 | 763.9564 | 0 | 0.05921 | 4.1619 | 0 | 0 | 0 | 46.406 | off_peak | 763.954 | 0 | 100 | 5.73 | 0 | 94.27 | 193.1355 | 0
6587 | 805.27 | 553.659 | 27.2 | 88.9824 | 88.9824 | 0 | 0 | 0.0001555 | 0.0001555 | 0 | 0 | 0 | 74.1742 | 716.2878 | 0 | 0.05921 | 4.4257 | 0 | 0 | 0 | 88.9824 | off_peak | 716.2876 | 0 | 100 | 11.05 | 0 | 88.95 | 393.8137 | 0
6588 | 844.79 | 441.392 | 27.7 | 70.8105 | 70.8105 | 0 | 0 | 1.0043e-05 | 1.0043e-05 | 0 | 0 | 0 | 74.1743 | 773.9795 | 0 | 0.05921 | 4.8515 | 0 | 0 | 0 | 70.8105 | off_peak | 773.9795 | 0 | 100 | 8.38 | 0 | 91.62 | 343.5339 | 0
6589 | 804.51 | 379.484 | 28 | 60.8125 | 60.8125 | 0 | 0 | 0 | 0 | -6.0676e-07 | -6.0676e-07 | 0 | 74.1743 | 743.6975 | 0 | 0.088511 | 5.0935 | 0 | 0 | 0 | 60.8125 | on_peak | 743.6975 |  |  | 7.56 | 0 | 92.44 | 309.7468 | 0
6590 | 824.37 | 673.784 | 28.2 | 107.8956 | 107.8956 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1743 | 716.4744 | 0 | 0.088511 | 5.1237 | 0 | 0 | 0 | 107.8956 | on_peak | 716.4744 |  |  | 13.09 | 0 | 86.91 | 552.828 | 0
6591 | 819.2 | 587.388 | 28.2 | 94.0606 | 94.0606 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1743 | 725.1394 | 0 | 0.088511 | 5.1078 | 0 | 0 | 0 | 94.0606 | on_peak | 725.1394 |  |  | 11.48 | 0 | 88.52 | 480.4424 | 0
6592 | 817.94 | 286.081 | 28.2 | 45.8112 | 45.8112 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1743 | 772.1288 | 0 | 0.088511 | 5.2326 | 0 | 0 | 0 | 45.8112 | on_peak | 772.1288 |  |  | 5.6 | 0 | 94.4 | 239.7107 | 0
6593 | 827.27 | 273.155 | 28 | 43.7732 | 43.7732 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1743 | 783.4968 | 0 | 0.088511 | 5.5333 | 0 | 0 | 0 | 43.7732 | on_peak | 783.4968 |  |  | 5.29 | 0 | 94.71 | 242.2107 | 0
6594 | 800.25 | 74.8898 | 27.6 | 12.0186 | 12.0186 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1743 | 788.2314 | 0 | 0.088511 | 5.8372 | 0 | 0 | 0 | 12.0186 | on_peak | 788.2314 |  |  | 1.5 | 0 | 98.5 | 70.1547 | 0
6595 | 806.45 | 0 | 27.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1743 | 806.45 | 0 | 0.088511 | 6.0902 | 0 | 0 | 0 | 0 | on_peak | 806.45 |  |  | 0 | 0 | 100 | 0 | 0
6596 | 810.27 | 0 | 27.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1743 | 810.27 | 0 | 0.088511 | 6.3274 | 0 | 0 | 0 | 0 | on_peak | 810.27 |  |  | 0 | 0 | 100 | 0 | 0
6597 | 810.17 | 0 | 27.2 | 0 | 0 | 0 | 0 | 0 | 0 | 62.4453 | 62.4453 | 0 | 7.4174 | 747.7247 | 0 | 0.088511 | 6.6961 | 0 | 0 | 0 | 0 | on_peak | 747.7247 |  |  | 0 | 7.71 | 92.29 | 0 | 0
6598 | 785.83 | 0 | 27.1 | 0 | 0 | 0 | 0 | 8.7006 | 8.7006 | 0 | 0 | 0 | 15.5561 | 794.5306 | 0 | 0.05921 | 7.0542 | 0 | 0 | 0 | 0 | off_peak | 785.83 | 0 | 100 | 0 | 0 | 100 | 0 | 0
6599 | 769.23 | 0 | 26.9 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 27.12 | 781.5924 | 0 | 0.05921 | 7.4208 | 0 | 0 | 0 | 0 | off_peak | 769.23 | 0 | 100 | 0 | 0 | 100 | 0 | 0
6600 | 741.02 | 0 | 26.6 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 38.684 | 753.3824 | 0 | 0.05921 | 7.7275 | 0 | 0 | 0 | 0 | off_peak | 741.02 | 0 | 100 | 0 | 0 | 100 | 0 | 0
6601 | 711.37 | 0 | 26.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 38.684 | 711.37 | 0 | 0.05921 | 7.657 | 0 | 0 | 0 | 0 | off_peak | 711.37 |  |  | 0 | 0 | 100 | 0 | 0
6602 | 613.65 | 0 | 25.8 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 50.2479 | 626.0124 | 0 | 0.05921 | 7.3557 | 0 | 0 | 0 | 0 | off_peak | 613.65 | 0 | 100 | 0 | 0 | 100 | 0 | 0
6603 | 610.03 | 0 | 25.2 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 61.8119 | 622.3924 | 0 | 0.05921 | 6.8097 | 0 | 0 | 0 | 0 | off_peak | 610.03 | 0 | 100 | 0 | 0 | 100 | 0 | 0
6604 | 595.38 | 0 | 24.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 61.8119 | 595.38 | 0 | 0.05921 | 6.1801 | 0 | 0 | 0 | 0 | off_peak | 595.38 |  |  | 0 | 0 | 100 | 0 | 0
6605 | 634.86 | 0 | 24.3 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 73.3758 | 647.2224 | 0 | 0.05921 | 5.3291 | 0 | 0 | 0 | 0 | off_peak | 634.86 | 0 | 100 | 0 | 0 | 100 | 0 | 0
6606 | 702.38 | 0 | 24.1 | 0 | 0 | 0 | 0 | 0.79843 | 0.79843 | 0 | 0 | 0 | 74.1227 | 703.1784 | 0 | 0.05921 | 4.8461 | 0 | 0 | 0 | 0 | off_peak | 702.38 | 0 | 100 | 0 | 0 | 100 | 0 | 0
6607 | 784.4 | 24.5246 | 24.2 | 3.9844 | 3.9844 | 0 | 0 | 0.051567 | 0.051567 | 0 | 0 | 0 | 74.1709 | 780.4671 | 0 | 0.05921 | 4.4635 | 0 | 0 | 0 | 3.9844 | off_peak | 780.4156 | 0 | 100 | 0.51 | 0 | 99.49 | 17.7847 | 0
6608 | 845.46 | 212.398 | 24.8 | 34.4333 | 34.4333 | 0 | 0 | 0.0033305 | 0.0033305 | 0 | 0 | 0 | 74.174 | 811.0301 | 0 | 0.05921 | 4.206 | 0 | 0 | 0 | 34.4333 | off_peak | 811.0267 | 0 | 100 | 4.07 | 0 | 95.93 | 144.8275 | 0
6609 | 825.28 | 426.723 | 25.7 | 68.9549 | 68.9547 | 0 | 0.0002151 | 0.0002151 | 0 | 0 | 0 | 0 | 74.1742 | 756.3253 | 0 | 0.05921 | 4.0464 | 0 | 0 | 0.00020121 | 68.9547 | off_peak | 756.3253 | 100 | 0 | 8.36 | 0 | 91.64 | 279.0207 | 0
6610 | 809.06 | 616.625 | 26.7 | 99.2819 | 99.2819 | 0 | 1.3893e-05 | 1.3893e-05 | 0 | 0 | 0 | 0 | 74.1743 | 709.7781 | 0 | 0.05921 | 4.0311 | 0 | 0 | 0.00021421 | 99.2819 | off_peak | 709.7781 | 100 | 0 | 12.27 | 0 | 87.73 | 400.2143 | 0
6611 | 830.88 | 757.9 | 27.6 | 121.6306 | 121.6306 | 0 | 8.9726e-07 | 8.9726e-07 | 0 | 0 | 0 | 0 | 74.1743 | 709.2494 | 0 | 0.05921 | 4.3121 | 0 | 0 | 0.00021504 | 121.6306 | off_peak | 709.2494 | 100 | 0 | 14.64 | 0 | 85.36 | 524.4838 | 0
6612 | 839.91 | 835.613 | 28.2 | 133.8099 | 133.8099 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1743 | 706.1001 | 0 | 0.05921 | 4.7538 | 0 | 0 | 0.0002151 | 133.8099 | off_peak | 706.1001 |  |  | 15.93 | 0 | 84.07 | 636.103 | 0
6613 | 850.02 | 844.227 | 28.7 | 134.9431 | 134.9431 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1743 | 715.0769 | 0 | 0.088511 | 4.9643 | 0 | 0 | 0.0002151 | 134.9431 | on_peak | 715.0769 |  |  | 15.88 | 0 | 84.12 | 669.8979 | 0
6614 | 861.25 | 495.309 | 29 | 79.0846 | 79.0846 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1743 | 782.1654 | 0 | 0.088511 | 5.0114 | 0 | 0 | 0.0002151 | 79.0846 | on_peak | 782.1654 |  |  | 9.18 | 0 | 90.82 | 396.324 | 0
6615 | 816.24 | 226.356 | 29.1 | 36.1284 | 36.1284 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1743 | 780.1116 | 0 | 0.088511 | 5.0996 | 0 | 0 | 0.0002151 | 36.1284 | on_peak | 780.1116 |  |  | 4.43 | 0 | 95.57 | 184.2415 | 0
6616 | 794.37 | 165.825 | 29 | 26.4768 | 26.4768 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1743 | 767.8932 | 0 | 0.088511 | 5.2894 | 0 | 0 | 0.0002151 | 26.4768 | on_peak | 767.8932 |  |  | 3.33 | 0 | 96.67 | 140.0454 | 0
6617 | 819.29 | 170.369 | 28.8 | 27.2222 | 27.2222 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1743 | 792.0678 | 0 | 0.088511 | 5.5536 | 0 | 0 | 0.0002151 | 27.2222 | on_peak | 792.0678 |  |  | 3.32 | 0 | 96.68 | 151.182 | 0
6618 | 820.17 | 51.1267 | 28.2 | 8.1871 | 8.1871 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1743 | 811.9829 | 0 | 0.088511 | 5.8734 | 0 | 0 | 0.0002151 | 8.1871 | on_peak | 811.9829 |  |  | 1 | 0 | 99 | 48.0865 | 0
6619 | 824.45 | 0 | 27.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1743 | 824.45 | 0 | 0.088511 | 6.2833 | 0 | 0 | 0.0002151 | 0 | on_peak | 824.45 |  |  | 0 | 0 | 100 | 0 | 0
6620 | 817.45 | 0 | 27.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1743 | 817.45 | 0 | 0.088511 | 6.6361 | 0 | 0 | 0.0002151 | 0 | on_peak | 817.45 |  |  | 0 | 0 | 100 | 0 | 0
6621 | 827.8 | 0 | 26.9 | 0 | 0 | 0 | 0 | 0 | 0 | 62.4453 | 62.4453 | 0 | 7.4174 | 765.3547 | 0 | 0.088511 | 7.1727 | 0.00020121 | 0 | 0 | 0.00020121 | on_peak | 765.3547 |  |  | 0 | 7.54 | 92.46 | 0.0014432 | 0
6622 | 749.94 | 0 | 26.7 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 18.9814 | 762.3024 | 0 | 0.05921 | 7.5872 | 0 | 0 | 0 | 0 | off_peak | 749.94 | 0 | 100 | 0 | 0 | 100 | 0 | 0
6623 | 791.66 | 0 | 26.4 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 30.5453 | 804.0224 | 0 | 0.05921 | 7.846 | 0 | 0 | 0 | 0 | off_peak | 791.66 | 0 | 100 | 0 | 0 | 100 | 0 | 0
6624 | 774.79 | 0 | 26.1 | 0 | 0 | 0 | 0 | 8.7006 | 8.7006 | 0 | 0 | 0 | 38.684 | 783.4906 | 0 | 0.05921 | 8.0403 | 0 | 0 | 0 | 0 | off_peak | 774.79 | 0 | 100 | 0 | 0 | 100 | 0 | 0
6625 | 678.48 | 0 | 25.9 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 50.2479 | 690.8424 | 0 | 0.05921 | 7.9516 | 0 | 0 | 0 | 0 | off_peak | 678.48 | 0 | 100 | 0 | 0 | 100 | 0 | 0
6626 | 643.82 | 0 | 25.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50.2479 | 643.82 | 0 | 0.05921 | 7.5053 | 0 | 0 | 0 | 0 | off_peak | 643.82 |  |  | 0 | 0 | 100 | 0 | 0
6627 | 580.45 | 0 | 25.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50.2479 | 580.45 | 0 | 0.05921 | 6.9849 | 0 | 0 | 0 | 0 | off_peak | 580.45 |  |  | 0 | 0 | 100 | 0 | 0
6628 | 605.09 | 0 | 25.2 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 61.8119 | 617.4524 | 0 | 0.05921 | 6.3677 | 0 | 0 | 0 | 0 | off_peak | 605.09 | 0 | 100 | 0 | 0 | 100 | 0 | 0
6629 | 603.76 | 0 | 24.9 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 73.3758 | 616.1224 | 0 | 0.05921 | 5.5565 | 0 | 0 | 0 | 0 | off_peak | 603.76 | 0 | 100 | 0 | 0 | 100 | 0 | 0
6630 | 696.36 | 0 | 24.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 73.3758 | 696.36 | 0 | 0.05921 | 5.0097 | 0 | 0 | 0 | 0 | off_peak | 696.36 |  |  | 0 | 0 | 100 | 0 | 0
6631 | 745.27 | 22.4966 | 24.9 | 3.6458 | 3.6458 | 0 | 0 | 0.79843 | 0.79843 | 0 | 0 | 0 | 74.1227 | 742.4227 | 0 | 0.05921 | 4.5772 | 0 | 0 | 0 | 3.6458 | off_peak | 741.6242 | 0 | 100 | 0.49 | 0 | 99.51 | 16.6876 | 0
6632 | 774.16 | 206.136 | 25.4 | 33.3459 | 33.3459 | 0 | 0 | 0.051567 | 0.051567 | 0 | 0 | 0 | 74.1709 | 740.8656 | 0 | 0.05921 | 4.2795 | 0 | 0 | 0 | 33.3459 | off_peak | 740.8141 | 0 | 100 | 4.31 | 0 | 95.69 | 142.7031 | 0
6633 | 801.98 | 417.602 | 25.9 | 67.4323 | 67.4323 | 0 | 0 | 0.0033305 | 0.0033305 | 0 | 0 | 0 | 74.174 | 734.551 | 0 | 0.05921 | 4.0721 | 0 | 0 | 0 | 67.4323 | off_peak | 734.5477 | 0 | 100 | 8.41 | 0 | 91.59 | 274.5883 | 0
6634 | 801.37 | 604 | 26.5 | 97.3196 | 97.3196 | 0 | 0 | 0.0002151 | 0.0002151 | 0 | 0 | 0 | 74.1742 | 704.0506 | 0 | 0.05921 | 4.0761 | 0 | 0 | 0 | 97.3196 | off_peak | 704.0504 | 0 | 100 | 12.14 | 0 | 87.86 | 396.6851 | 0
6635 | 796.58 | 694.611 | 27.1 | 111.6763 | 111.6763 | 0 | 1.3893e-05 | 1.3893e-05 | 0 | 0 | 0 | 0 | 74.1743 | 684.9037 | 0 | 0.05921 | 4.3391 | 0 | 0 | 1.2995e-05 | 111.6763 | off_peak | 684.9037 | 100 | 0 | 14.02 | 0 | 85.98 | 484.5727 | 0
6636 | 861.49 | 655.499 | 27.6 | 105.1969 | 105.1969 | 0 | 8.9726e-07 | 8.9726e-07 | 0 | 0 | 0 | 0 | 74.1743 | 756.2931 | 0 | 0.05921 | 4.7512 | 0 | 0 | 1.3835e-05 | 105.1969 | off_peak | 756.2931 | 100 | 0 | 12.21 | 0 | 87.79 | 499.8163 | 0
6637 | 802.45 | 585.644 | 27.9 | 93.8838 | 93.8838 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1743 | 708.5662 | 0 | 0.088511 | 5.042 | 0 | 0 | 1.3893e-05 | 93.8838 | on_peak | 708.5662 |  |  | 11.7 | 0 | 88.3 | 473.3622 | 0
6638 | 886.38 | 473.313 | 28.1 | 75.821 | 75.821 | 0 | 0 | 0 | 0 | 1.2995e-05 | 1.2995e-05 | 0 | 74.1742 | 810.559 | 0 | 0.088511 | 5.1859 | 1.2995e-05 | 0 | 0 | 75.821 | on_peak | 810.559 |  |  | 8.55 | 0 | 91.45 | 393.2038 | 0
6639 | 868.33 | 606.638 | 28.1 | 97.1786 | 97.1786 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1742 | 771.1514 | 0 | 0.088511 | 5.2728 | 0 | 0 | 0 | 97.1786 | on_peak | 771.1514 |  |  | 11.19 | 0 | 88.81 | 512.4043 | 0
6640 | 828.51 | 311.548 | 27.9 | 49.9439 | 49.9439 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1742 | 778.5661 | 0 | 0.088511 | 5.5883 | 0 | 0 | 0 | 49.9439 | on_peak | 778.5661 |  |  | 6.03 | 0 | 93.97 | 279.1011 | 0
6641 | 853.38 | 221.386 | 27.6 | 35.5288 | 35.5288 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1742 | 817.8512 | 0 | 0.088511 | 6.1094 | 0 | 0 | 0 | 35.5288 | on_peak | 817.8512 |  |  | 4.16 | 0 | 95.84 | 217.0591 | 0
6642 | 843.18 | 66.3877 | 27 | 10.6774 | 10.6774 | 0 | 0 | 0 | 0 | 0.66299 | 0.66299 | 0 | 73.4655 | 831.8396 | 0 | 0.088511 | 6.5377 | 0 | 0 | 0 | 10.6774 | on_peak | 831.8396 |  |  | 1.27 | 0.08 | 98.66 | 69.8053 | 0
6643 | 831.8 | 0 | 26.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 73.4655 | 831.8 | 0 | 0.088511 | 6.8178 | 0 | 0 | 0 | 0 | on_peak | 831.8 |  |  | 0 | 0 | 100 | 0 | 0
6644 | 825.58 | 0 | 26.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 73.4655 | 825.58 | 0 | 0.088511 | 7.252 | 0 | 0 | 0 | 0 | on_peak | 825.58 |  |  | 0 | 0 | 100 | 0 | 0
6645 | 804.61 | 0 | 25.9 | 0 | 0 | 0 | 0 | 0 | 0 | 61.7823 | 61.7823 | 0 | 7.4174 | 742.8277 | 0 | 0.088511 | 7.7258 | 0 | 0 | 0 | 0 | on_peak | 742.8277 |  |  | 0 | 7.68 | 92.32 | 0 | 0
6646 | 762.47 | 0 | 25.7 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 18.9814 | 774.8324 | 0 | 0.05921 | 8.0553 | 0 | 0 | 0 | 0 | off_peak | 762.47 | 0 | 100 | 0 | 0 | 100 | 0 | 0
6647 | 795.65 | 0 | 25.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18.9814 | 795.65 | 0 | 0.05921 | 8.2865 | 0 | 0 | 0 | 0 | off_peak | 795.65 |  |  | 0 | 0 | 100 | 0 | 0
6648 | 750.34 | 0 | 25.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18.9814 | 750.34 | 0 | 0.05921 | 8.4707 | 0 | 0 | 0 | 0 | off_peak | 750.34 |  |  | 0 | 0 | 100 | 0 | 0
6649 | 689.37 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18.9814 | 689.37 | 0 | 0.05921 | 8.3023 | 0 | 0 | 0 | 0 | off_peak | 689.37 |  |  | 0 | 0 | 100 | 0 | 0
6650 | 641.84 | 0 | 24.9 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 30.5453 | 654.2024 | 0 | 0.05921 | 7.9966 | 0 | 0 | 0 | 0 | off_peak | 641.84 | 0 | 100 | 0 | 0 | 100 | 0 | 0
6651 | 638.37 | 0 | 24.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30.5453 | 638.37 | 0 | 0.05921 | 7.4083 | 0 | 0 | 0 | 0 | off_peak | 638.37 |  |  | 0 | 0 | 100 | 0 | 0
6652 | 641.09 | 0 | 24.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30.5453 | 641.09 | 0 | 0.05921 | 6.7319 | 0 | 0 | 0 | 0 | off_peak | 641.09 |  |  | 0 | 0 | 100 | 0 | 0
6653 | 649.61 | 0 | 24.7 | 0 | 0 | 0 | 0 | 8.7006 | 8.7006 | 0 | 0 | 0 | 38.684 | 658.3106 | 0 | 0.05921 | 5.8306 | 0 | 0 | 0 | 0 | off_peak | 649.61 | 0 | 100 | 0 | 0 | 100 | 0 | 0
6654 | 705.18 | 0 | 24.7 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 50.2479 | 717.5424 | 0 | 0.05921 | 5.2668 | 0 | 0 | 0 | 0 | off_peak | 705.18 | 0 | 100 | 0 | 0 | 100 | 0 | 0
6655 | 773.93 | 23.5305 | 25.1 | 3.8106 | 3.8106 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 61.8119 | 782.4818 | 0 | 0.05921 | 4.8205 | 0 | 0 | 0 | 3.8106 | off_peak | 770.1194 | 0 | 100 | 0.49 | 0 | 99.51 | 18.3689 | 0
6656 | 807.68 | 208.17 | 25.8 | 33.6264 | 33.6264 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 73.3758 | 786.416 | 0 | 0.05921 | 4.5461 | 0 | 0 | 0 | 33.6264 | off_peak | 774.0536 | 0 | 100 | 4.16 | 0 | 95.84 | 152.8687 | 0
6657 | 803.67 | 419.49 | 26.4 | 67.6149 | 67.6149 | 0 | 0 | 0.79843 | 0.79843 | 0 | 0 | 0 | 74.1227 | 736.8536 | 0 | 0.05921 | 4.3716 | 0 | 0 | 0 | 67.6149 | off_peak | 736.0551 | 0 | 100 | 8.41 | 0 | 91.59 | 295.5827 | 0
6658 | 855.86 | 604.204 | 27 | 97.1763 | 97.1763 | 0 | 0 | 0.051567 | 0.051567 | 0 | 0 | 0 | 74.1709 | 758.7353 | 0 | 0.05921 | 4.3443 | 0 | 0 | 0 | 97.1763 | off_peak | 758.6837 | 0 | 100 | 11.35 | 0 | 88.65 | 422.1608 | 0
6659 | 824.18 | 740.734 | 27.5 | 118.9189 | 118.9189 | 0 | 0 | 0.0033305 | 0.0033305 | 0 | 0 | 0 | 74.174 | 705.2644 | 0 | 0.05921 | 4.569 | 0 | 0 | 0 | 118.9189 | off_peak | 705.2611 | 0 | 100 | 14.43 | 0 | 85.57 | 543.3452 | 0
6660 | 829.84 | 597.52 | 27.8 | 95.8225 | 95.8225 | 0 | 0 | 0.0002151 | 0.0002151 | 0 | 0 | 0 | 74.1742 | 734.0177 | 0 | 0.05921 | 4.9546 | 0 | 0 | 0 | 95.8225 | off_peak | 734.0175 | 0 | 100 | 11.55 | 0 | 88.45 | 474.7613 | 0
6661 | 829.54 | 648.232 | 28 | 103.8794 | 103.8794 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1742 | 725.6606 | 0 | 0.088511 | 5.259 | 0 | 0 | 0 | 103.8794 | on_peak | 725.6606 |  |  | 12.52 | 0 | 87.48 | 546.2971 | 0
6662 | 815.05 | 379.921 | 28.1 | 60.8603 | 60.8603 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1742 | 754.1897 | 0 | 0.088511 | 5.3604 | 0 | 0 | 0 | 60.8603 | on_peak | 754.1897 |  |  | 7.47 | 0 | 92.53 | 326.2366 | 0
6663 | 812.75 | 171.956 | 28.1 | 27.546 | 27.546 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1742 | 785.204 | 0 | 0.088511 | 5.606 | 0 | 0 | 0 | 27.546 | on_peak | 785.204 |  |  | 3.39 | 0 | 96.61 | 154.4233 | 0
6664 | 801.78 | 90.3924 | 27.9 | 14.4907 | 14.4907 | 0 | 0 | 0 | 0 | 62.4453 | 62.4453 | 0 | 7.4174 | 724.844 | 0 | 0.088511 | 5.9971 | 0 | 0 | 0 | 14.4907 | on_peak | 724.844 |  |  | 1.81 | 7.79 | 90.4 | 86.9016 | 0
6665 | 829.3 | 42.769 | 27.5 | 6.8662 | 6.8662 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 822.4338 | 0 | 0.088511 | 6.5652 | 0 | 0 | 0 | 6.8662 | on_peak | 822.4338 |  |  | 0.83 | 0 | 99.17 | 45.0778 | 0
6666 | 816.12 | 38.4589 | 26.9 | 6.1877 | 6.1877 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 809.9323 | 0 | 0.088511 | 6.9353 | 0 | 0 | 0 | 6.1877 | on_peak | 809.9323 |  |  | 0.76 | 0 | 99.24 | 42.9135 | 0
6667 | 800.14 | 0 | 26.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 800.14 | 0 | 0.088511 | 7.4065 | 0 | 0 | 0 | 0 | on_peak | 800.14 |  |  | 0 | 0 | 100 | 0 | 0
6668 | 770.3 | 0 | 26.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 770.3 | 0 | 0.088511 | 7.8031 | 0 | 0 | 0 | 0 | on_peak | 770.3 |  |  | 0 | 0 | 100 | 0 | 0
6669 | 792.92 | 0 | 26.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 792.92 | 0 | 0.088511 | 7.9639 | 0 | 0 | 0 | 0 | on_peak | 792.92 |  |  | 0 | 0 | 100 | 0 | 0
6670 | 731.27 | 0 | 25.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 731.27 | 0 | 0.05921 | 8.1491 | 0 | 0 | 0 | 0 | off_peak | 731.27 |  |  | 0 | 0 | 100 | 0 | 0
6671 | 745.93 | 0 | 25.8 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 18.9814 | 758.2924 | 0 | 0.05921 | 8.4079 | 0 | 0 | 0 | 0 | off_peak | 745.93 | 0 | 100 | 0 | 0 | 100 | 0 | 0
6672 | 730.54 | 0 | 25.7 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 30.5453 | 742.9024 | 0 | 0.05921 | 8.5504 | 0 | 0 | 0 | 0 | off_peak | 730.54 | 0 | 100 | 0 | 0 | 100 | 0 | 0
6673 | 670.89 | 0 | 25.6 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 42.1093 | 683.2524 | 0 | 0.05921 | 8.4486 | 0 | 0 | 0 | 0 | off_peak | 670.89 | 0 | 100 | 0 | 0 | 100 | 0 | 0
6674 | 588.15 | 0 | 25.5 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 53.6732 | 600.5124 | 0 | 0.05921 | 8.0942 | 0 | 0 | 0 | 0 | off_peak | 588.15 | 0 | 100 | 0 | 0 | 100 | 0 | 0
6675 | 573.88 | 0 | 25.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 53.6732 | 573.88 | 0 | 0.05921 | 7.57 | 0 | 0 | 0 | 0 | off_peak | 573.88 |  |  | 0 | 0 | 100 | 0 | 0
6676 | 557.04 | 0 | 25.3 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 65.2371 | 569.4024 | 0 | 0.05921 | 6.9091 | 0 | 0 | 0 | 0 | off_peak | 557.04 | 0 | 100 | 0 | 0 | 100 | 0 | 0
6677 | 601.03 | 0 | 25.3 | 0 | 0 | 0 | 0 | 8.9371 | 8.9371 | 0 | 0 | 0 | 73.597 | 609.9671 | 0 | 0.05921 | 6.0275 | 0 | 0 | 0 | 0 | off_peak | 601.03 | 0 | 100 | 0 | 0 | 100 | 0 | 0
6678 | 673.13 | 0 | 25.2 | 0 | 0 | 0 | 0 | 0.57721 | 0.57721 | 0 | 0 | 0 | 74.137 | 673.7072 | 0 | 0.05921 | 5.3886 | 0 | 0 | 0 | 0 | off_peak | 673.13 | 0 | 100 | 0 | 0 | 100 | 0 | 0
6679 | 756.14 | 22.4185 | 25.7 | 3.6226 | 3.6226 | 0 | 0 | 0.037279 | 0.037279 | 0 | 0 | 0 | 74.1718 | 752.5546 | 0 | 0.05921 | 4.9124 | 0 | 0 | 0 | 3.6226 | off_peak | 752.5174 | 0 | 100 | 0.48 | 0 | 99.52 | 17.796 | 0
6680 | 812.23 | 205.317 | 26.3 | 33.1057 | 33.1057 | 0 | 0 | 0.0024077 | 0.0024077 | 0 | 0 | 0 | 74.1741 | 779.1267 | 0 | 0.05921 | 4.5887 | 0 | 0 | 0 | 33.1057 | off_peak | 779.1243 | 0 | 100 | 4.08 | 0 | 95.92 | 151.9129 | 0
6681 | 796.96 | 418.143 | 26.9 | 67.2758 | 67.2758 | 0 | 0 | 0.0001555 | 0.0001555 | 0 | 0 | 0 | 74.1742 | 729.6843 | 0 | 0.05921 | 4.3803 | 0 | 0 | 0 | 67.2758 | off_peak | 729.6842 | 0 | 100 | 8.44 | 0 | 91.56 | 294.6907 | 0
6682 | 820.33 | 573.12 | 27.3 | 92.0767 | 92.0767 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1742 | 728.2533 | 0 | 0.05921 | 4.3093 | 0 | 0 | 0 | 92.0767 | off_peak | 728.2533 |  |  | 11.22 | 0 | 88.78 | 396.7831 | 0
6683 | 780.46 | 432.814 | 27.7 | 69.4343 | 69.4343 | 0 | 0 | 1.0737e-05 | 1.0737e-05 | 0 | 0 | 0 | 74.1743 | 711.0257 | 0 | 0.05921 | 4.4935 | 0 | 0 | 0 | 69.4343 | off_peak | 711.0257 | 0 | 100 | 8.9 | 0 | 91.1 | 312.0042 | 0
6684 | 835.31 | 505.017 | 28 | 80.9292 | 80.9292 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1743 | 754.3808 | 0 | 0.05921 | 4.8612 | 0 | 0 | 0 | 80.9292 | off_peak | 754.3808 |  |  | 9.69 | 0 | 90.31 | 393.4122 | 0
6685 | 813.14 | 521.169 | 28.1 | 83.4871 | 83.4871 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1743 | 729.6529 | 0 | 0.088511 | 5.1896 | 0 | 0 | 0 | 83.4871 | on_peak | 729.6529 |  |  | 10.27 | 0 | 89.73 | 433.2649 | 0
6686 | 847.05 | 643.73 | 28.2 | 103.0829 | 103.0829 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1743 | 743.9671 | 0 | 0.088511 | 5.348 | 0 | 0 | 0 | 103.0829 | on_peak | 743.9671 |  |  | 12.17 | 0 | 87.83 | 551.2897 | 0
6687 | 865.45 | 477.33 | 28.1 | 76.4645 | 76.4645 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1743 | 788.9855 | 0 | 0.088511 | 5.6738 | 0 | 0 | 0 | 76.4645 | on_peak | 788.9855 |  |  | 8.84 | 0 | 91.16 | 433.8448 | 0
6688 | 814.9 | 467.784 | 27.8 | 75.0171 | 75.0171 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1743 | 739.8829 | 0 | 0.088511 | 6.1058 | 0 | 0 | 0 | 75.0171 | on_peak | 739.8829 |  |  | 9.21 | 0 | 90.79 | 458.04 | 0
6689 | 828.39 | 262.567 | 27.4 | 42.1683 | 42.1683 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1743 | 786.2217 | 0 | 0.088511 | 6.5454 | 0 | 0 | 0 | 42.1683 | on_peak | 786.2217 |  |  | 5.09 | 0 | 94.91 | 276.0103 | 0
6690 | 827.76 | 58.6273 | 26.8 | 9.4361 | 9.4361 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1743 | 818.3239 | 0 | 0.088511 | 6.9055 | 0 | 0 | 0 | 9.4361 | on_peak | 818.3239 |  |  | 1.14 | 0 | 98.86 | 65.1612 | 0
6691 | 801.04 | 0 | 26.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1743 | 801.04 | 0 | 0.088511 | 7.3186 | 0 | 0 | 0 | 0 | on_peak | 801.04 |  |  | 0 | 0 | 100 | 0 | 0
6692 | 807.89 | 0 | 26.3 | 0 | 0 | 0 | 0 | 0 | 0 | 62.4453 | 62.4453 | 0 | 7.4174 | 745.4447 | 0 | 0.088511 | 7.7322 | 0 | 0 | 0 | 0 | on_peak | 745.4447 |  |  | 0 | 7.73 | 92.27 | 0 | 0
6693 | 794.22 | 0 | 26.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 794.22 | 0 | 0.088511 | 7.9898 | 0 | 0 | 0 | 0 | on_peak | 794.22 |  |  | 0 | 0 | 100 | 0 | 0
6694 | 774.59 | 0 | 26 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 774.59 | 0 | 0.05921 | 8.1991 | 0 | 0 | 0 | 0 | off_peak | 774.59 |  |  | 0 | 0 | 100 | 0 | 0
6695 | 764.72 | 0 | 25.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 764.72 | 0 | 0.05921 | 8.317 | 0 | 0 | 0 | 0 | off_peak | 764.72 |  |  | 0 | 0 | 100 | 0 | 0
6696 | 742.9 | 0 | 25.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 742.9 | 0 | 0.05921 | 8.3296 | 0 | 0 | 0 | 0 | off_peak | 742.9 |  |  | 0 | 0 | 100 | 0 | 0
6697 | 673.73 | 0 | 25.7 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 18.9814 | 686.0924 | 0 | 0.05921 | 8.0681 | 0 | 0 | 0 | 0 | off_peak | 673.73 | 0 | 100 | 0 | 0 | 100 | 0 | 0
6698 | 617.53 | 0 | 25.6 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 30.5453 | 629.8924 | 0 | 0.05921 | 7.7562 | 0 | 0 | 0 | 0 | off_peak | 617.53 | 0 | 100 | 0 | 0 | 100 | 0 | 0
6699 | 593.83 | 0 | 25.5 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 42.1093 | 606.1924 | 0 | 0.05921 | 7.2152 | 0 | 0 | 0 | 0 | off_peak | 593.83 | 0 | 100 | 0 | 0 | 100 | 0 | 0
6700 | 604.95 | 0 | 25.4 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 53.6732 | 617.3124 | 0 | 0.05921 | 6.6788 | 0 | 0 | 0 | 0 | off_peak | 604.95 | 0 | 100 | 0 | 0 | 100 | 0 | 0
6701 | 613.6 | 0 | 25.3 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 65.2371 | 625.9624 | 0 | 0.05921 | 5.9842 | 0 | 0 | 0 | 0 | off_peak | 613.6 | 0 | 100 | 0 | 0 | 100 | 0 | 0
6702 | 704.29 | 0 | 25.2 | 0 | 0 | 0 | 0 | 8.9371 | 8.9371 | 0 | 0 | 0 | 73.597 | 713.2271 | 0 | 0.05921 | 5.4123 | 0 | 0 | 0 | 0 | off_peak | 704.29 | 0 | 100 | 0 | 0 | 100 | 0 | 0
6703 | 789.7 | 21.7429 | 25.5 | 3.516 | 3.516 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 73.597 | 786.184 | 0 | 0.05921 | 5.0368 | 0 | 0 | 0 | 3.516 | off_peak | 786.184 |  |  | 0.45 | 0 | 99.55 | 17.7094 | 0
6704 | 755.99 | 203.496 | 26.1 | 32.8358 | 32.8358 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 73.597 | 723.1542 | 0 | 0.05921 | 4.7089 | 0 | 0 | 0 | 32.8358 | off_peak | 723.1542 |  |  | 4.34 | 0 | 95.66 | 154.6215 | 0
6705 | 723.77 | 414.956 | 26.5 | 66.8599 | 66.8599 | 0 | 0 | 0.57721 | 0.57721 | 0 | 0 | 0 | 74.137 | 657.4873 | 0 | 0.05921 | 4.4665 | 0 | 0 | 0 | 66.8599 | off_peak | 656.9101 | 0 | 100 | 9.24 | 0 | 90.76 | 298.63 | 0
6706 | 783.42 | 603.384 | 27 | 97.0444 | 97.0444 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.137 | 686.3756 | 0 | 0.05921 | 4.3171 | 0 | 0 | 0 | 97.0444 | off_peak | 686.3756 |  |  | 12.39 | 0 | 87.61 | 418.9489 | 0
6707 | 737.38 | 744.262 | 27.4 | 119.5287 | 119.5287 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.137 | 617.8513 | 0 | 0.05921 | 4.3179 | 0 | 0 | 0 | 119.5287 | off_peak | 617.8513 |  |  | 16.21 | 0 | 83.79 | 516.1171 | 0
6708 | 763.02 | 823.934 | 27.7 | 132.1799 | 132.1799 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.137 | 630.8401 | 0 | 0.05921 | 4.4002 | 0 | 0 | 0 | 132.1799 | off_peak | 630.8401 |  |  | 17.32 | 0 | 82.68 | 581.6174 | 0
6709 | 758.61 | 700.302 | 27.9 | 112.2645 | 112.2645 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.137 | 646.3455 | 0 | 0.05921 | 4.5597 | 0 | 0 | 0 | 112.2645 | off_peak | 646.3455 |  |  | 14.8 | 0 | 85.2 | 511.8972 | 0
6710 | 734.26 | 763.558 | 28 | 122.3605 | 122.3605 | 0 | 0 | 0.037279 | 0.037279 | 0 | 0 | 0 | 74.1718 | 611.9368 | 0 | 0.05921 | 4.8664 | 0 | 0 | 0 | 122.3605 | off_peak | 611.8995 | 0 | 100 | 16.66 | 0 | 83.34 | 595.4504 | 0
6711 | 737.12 | 650.847 | 28 | 104.2985 | 104.2985 | 0 | 0 | 0.0024077 | 0.0024077 | 0 | 0 | 0 | 74.1741 | 632.8239 | 0 | 0.05921 | 5.2115 | 0 | 0 | 0 | 104.2985 | off_peak | 632.8215 | 0 | 100 | 14.15 | 0 | 85.85 | 543.5557 | 0
6712 | 745.06 | 439.556 | 27.8 | 70.4903 | 70.4903 | 0 | 0 | 0.0001555 | 0.0001555 | 0 | 0 | 0 | 74.1742 | 674.5699 | 0 | 0.05921 | 5.5576 | 0 | 0 | 0 | 70.4903 | off_peak | 674.5697 | 0 | 100 | 9.46 | 0 | 90.54 | 391.7543 | 0
6713 | 739.05 | 268.823 | 27.3 | 43.1887 | 43.1887 | 0 | 0 | 1.0737e-05 | 1.0737e-05 | 0 | 0 | 0 | 74.1743 | 695.8613 | 0 | 0.05921 | 6.0465 | 0 | 0 | 0 | 43.1887 | off_peak | 695.8613 | 0 | 100 | 5.84 | 0 | 94.16 | 261.14 | 0
6714 | 672.69 | 67.9294 | 26.6 | 10.9412 | 10.9412 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1743 | 661.7488 | 0 | 0.05921 | 6.6525 | 0 | 0 | 0 | 10.9412 | off_peak | 661.7488 |  |  | 1.63 | 0 | 98.37 | 72.7858 | 0
6715 | 644.79 | 0 | 26.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1743 | 644.79 | 0 | 0.05921 | 7.2651 | 0 | 0 | 0 | 0 | off_peak | 644.79 |  |  | 0 | 0 | 100 | 0 | 0
6716 | 646.07 | 0 | 25.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1743 | 646.07 | 0 | 0.05921 | 7.6726 | 0 | 0 | 0 | 0 | off_peak | 646.07 |  |  | 0 | 0 | 100 | 0 | 0
6717 | 593.07 | 0 | 25.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1743 | 593.07 | 0 | 0.05921 | 7.9281 | 0 | 0 | 0 | 0 | off_peak | 593.07 |  |  | 0 | 0 | 100 | 0 | 0
6718 | 622.69 | 0 | 25.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1743 | 622.69 | 0 | 0.05921 | 8.1634 | 0 | 0 | 0 | 0 | off_peak | 622.69 |  |  | 0 | 0 | 100 | 0 | 0
6719 | 605.98 | 0 | 25.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1743 | 605.98 | 0 | 0.05921 | 8.2269 | 0 | 0 | 0 | 0 | off_peak | 605.98 |  |  | 0 | 0 | 100 | 0 | 0
6720 | 620.6 | 0 | 25.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1743 | 620.6 | 0 | 0.05921 | 8.0435 | 0 | 0 | 0 | 0 | off_peak | 620.6 |  |  | 0 | 0 | 100 | 0 | 0
6721 | 601.83 | 0 | 25.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1743 | 601.83 | 0 | 0.05921 | 7.7637 | 0 | 0 | 0 | 0 | off_peak | 601.83 |  |  | 0 | 0 | 100 | 0 | 0
6722 | 591.87 | 0 | 25.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1743 | 591.87 | 0 | 0.05921 | 7.2691 | 0 | 0 | 0 | 0 | off_peak | 591.87 |  |  | 0 | 0 | 100 | 0 | 0
6723 | 618.99 | 0 | 25.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1743 | 618.99 | 0 | 0.05921 | 6.7729 | 0 | 0 | 0 | 0 | off_peak | 618.99 |  |  | 0 | 0 | 100 | 0 | 0
6724 | 630.14 | 0 | 25.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1743 | 630.14 | 0 | 0.05921 | 6.2367 | 0 | 0 | 0 | 0 | off_peak | 630.14 |  |  | 0 | 0 | 100 | 0 | 0
6725 | 620.78 | 0 | 25.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1743 | 620.78 | 0 | 0.05921 | 5.6819 | 0 | 0 | 0 | 0 | off_peak | 620.78 |  |  | 0 | 0 | 100 | 0 | 0
6726 | 687.8 | 0 | 25.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1743 | 687.8 | 0 | 0.05921 | 5.0726 | 0 | 0 | 0 | 0 | off_peak | 687.8 |  |  | 0 | 0 | 100 | 0 | 0
6727 | 710.49 | 21.9065 | 25.9 | 3.5374 | 3.5374 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1743 | 706.9526 | 0 | 0.05921 | 4.6405 | 0 | 0 | 0 | 3.5374 | off_peak | 706.9526 |  |  | 0.5 | 0 | 99.5 | 16.4151 | 0
6728 | 719.99 | 175.519 | 26.4 | 28.2908 | 28.2908 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1743 | 691.6992 | 0 | 0.05921 | 4.3224 | 0 | 0 | 0 | 28.2908 | off_peak | 691.6992 |  |  | 3.93 | 0 | 96.07 | 122.2844 | 0
6729 | 726.98 | 92.9666 | 26.9 | 14.9576 | 14.9576 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1743 | 712.0224 | 0 | 0.05921 | 4.0911 | 0 | 0 | 0 | 14.9576 | off_peak | 712.0224 |  |  | 2.06 | 0 | 97.94 | 61.1932 | 0
6730 | 733.34 | 526.793 | 27.5 | 84.5724 | 84.5724 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1743 | 648.7676 | 0 | 0.05921 | 3.9286 | 0 | 0 | 0 | 84.5724 | off_peak | 648.7676 |  |  | 11.53 | 0 | 88.47 | 332.2518 | 0
6731 | 706.55 | 406.249 | 28 | 65.1016 | 65.1016 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1743 | 641.4484 | 0 | 0.05921 | 3.8773 | 0 | 0 | 0 | 65.1016 | off_peak | 641.4484 |  |  | 9.21 | 0 | 90.79 | 252.4154 | 0
6732 | 738.75 | 401.063 | 28.4 | 64.1769 | 64.1769 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1743 | 674.5731 | 0 | 0.05921 | 3.9185 | 0 | 0 | 0 | 64.1769 | off_peak | 674.5731 |  |  | 8.69 | 0 | 91.31 | 251.4776 | 0
6733 | 736.84 | 344.579 | 28.7 | 55.0783 | 55.0783 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1743 | 681.7617 | 0 | 0.05921 | 4.0261 | 0 | 0 | 0 | 55.0783 | off_peak | 681.7617 |  |  | 7.47 | 0 | 92.53 | 221.7512 | 0
6734 | 753.04 | 342.844 | 28.7 | 54.8009 | 54.8009 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1743 | 698.2391 | 0 | 0.05921 | 4.3417 | 0 | 0 | 0 | 54.8009 | off_peak | 698.2391 |  |  | 7.28 | 0 | 92.72 | 237.928 | 0
6735 | 749.31 | 569.851 | 28.6 | 91.1194 | 91.1194 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1743 | 658.1906 | 0 | 0.05921 | 4.6486 | 0 | 0 | 0 | 91.1194 | off_peak | 658.1906 |  |  | 12.16 | 0 | 87.84 | 423.5785 | 0
6736 | 736.32 | 368.407 | 28.4 | 58.9514 | 58.9514 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1743 | 677.3686 | 0 | 0.05921 | 5.0153 | 0 | 0 | 0 | 58.9514 | off_peak | 677.3686 |  |  | 8.01 | 0 | 91.99 | 295.6589 | 0
6737 | 722.57 | 172.525 | 28.1 | 27.6371 | 27.6371 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1743 | 694.9329 | 0 | 0.05921 | 5.3292 | 0 | 0 | 0 | 27.6371 | off_peak | 694.9329 |  |  | 3.82 | 0 | 96.18 | 147.2839 | 0
6738 | 648.97 | 44.1011 | 27.6 | 7.0775 | 7.0775 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1743 | 641.8925 | 0 | 0.05921 | 5.758 | 0 | 0 | 0 | 7.0775 | off_peak | 641.8925 |  |  | 1.09 | 0 | 98.91 | 40.7526 | 0
6739 | 617.03 | 0 | 27.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1743 | 617.03 | 0 | 0.05921 | 6.2196 | 0 | 0 | 0 | 0 | off_peak | 617.03 |  |  | 0 | 0 | 100 | 0 | 0
6740 | 620.46 | 0 | 27.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1743 | 620.46 | 0 | 0.05921 | 6.4317 | 0 | 0 | 0 | 0 | off_peak | 620.46 |  |  | 0 | 0 | 100 | 0 | 0
6741 | 613.25 | 0 | 27 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1743 | 613.25 | 0 | 0.05921 | 6.5074 | 0 | 0 | 0 | 0 | off_peak | 613.25 |  |  | 0 | 0 | 100 | 0 | 0
6742 | 599.76 | 0 | 27 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1743 | 599.76 | 0 | 0.05921 | 6.5817 | 0 | 0 | 0 | 0 | off_peak | 599.76 |  |  | 0 | 0 | 100 | 0 | 0
6743 | 612.72 | 0 | 26.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1743 | 612.72 | 0 | 0.05921 | 6.6769 | 0 | 0 | 0 | 0 | off_peak | 612.72 |  |  | 0 | 0 | 100 | 0 | 0
6744 | 610.91 | 0 | 26.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1743 | 610.91 | 0 | 0.05921 | 6.8442 | 0 | 0 | 0 | 0 | off_peak | 610.91 |  |  | 0 | 0 | 100 | 0 | 0
6745 | 582.95 | 0 | 26.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1743 | 582.95 | 0 | 0.05921 | 6.9482 | 0 | 0 | 0 | 0 | off_peak | 582.95 |  |  | 0 | 0 | 100 | 0 | 0
6746 | 602.19 | 0 | 26.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1743 | 602.19 | 0 | 0.05921 | 6.6225 | 0 | 0 | 0 | 0 | off_peak | 602.19 |  |  | 0 | 0 | 100 | 0 | 0
6747 | 588.63 | 0 | 26.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1743 | 588.63 | 0 | 0.05921 | 6.1179 | 0 | 0 | 0 | 0 | off_peak | 588.63 |  |  | 0 | 0 | 100 | 0 | 0
6748 | 597.37 | 0 | 26.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1743 | 597.37 | 0 | 0.05921 | 5.5232 | 0 | 0 | 0 | 0 | off_peak | 597.37 |  |  | 0 | 0 | 100 | 0 | 0
6749 | 624.27 | 0 | 26.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1743 | 624.27 | 0 | 0.05921 | 4.9292 | 0 | 0 | 0 | 0 | off_peak | 624.27 |  |  | 0 | 0 | 100 | 0 | 0
6750 | 674.35 | 0 | 26.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1743 | 674.35 | 0 | 0.05921 | 4.431 | 0 | 0 | 0 | 0 | off_peak | 674.35 |  |  | 0 | 0 | 100 | 0 | 0
6751 | 798.56 | 20.9108 | 26.9 | 3.3644 | 3.3644 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1743 | 795.1956 | 0 | 0.05921 | 4.0509 | 0 | 0 | 0 | 3.3644 | off_peak | 795.1956 |  |  | 0.42 | 0 | 99.58 | 13.6288 | 0
6752 | 788.15 | 189.989 | 27.3 | 30.5234 | 30.5234 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1743 | 757.6266 | 0 | 0.05921 | 3.7925 | 0 | 0 | 0 | 30.5234 | off_peak | 757.6266 |  |  | 3.87 | 0 | 96.13 | 115.7613 | 0
6753 | 841.21 | 172.823 | 27.7 | 27.7252 | 27.7252 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1743 | 813.4848 | 0 | 0.05921 | 3.6344 | 0 | 0 | 0 | 27.7252 | off_peak | 813.4848 |  |  | 3.3 | 0 | 96.7 | 100.7637 | 0
6754 | 843.57 | 542.433 | 28.1 | 86.8935 | 86.8935 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1743 | 756.6765 | 0 | 0.05921 | 3.6323 | 0 | 0 | 0 | 86.8935 | off_peak | 756.6765 |  |  | 10.3 | 0 | 89.7 | 315.624 | 0
6755 | 837.41 | 448.914 | 28.4 | 71.8339 | 71.8339 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1743 | 765.5761 | 0 | 0.05921 | 3.8622 | 0 | 0 | 0 | 71.8339 | off_peak | 765.5761 |  |  | 8.58 | 0 | 91.42 | 277.4349 | 0
6756 | 867.69 | 119.539 | 28.5 | 19.1213 | 19.1213 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1743 | 848.5687 | 0 | 0.05921 | 4.2868 | 0 | 0 | 0 | 19.1213 | off_peak | 848.5687 |  |  | 2.2 | 0 | 97.8 | 81.9701 | 0
6757 | 774.11 | 33.25 | 28.5 | 5.3186 | 5.3186 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1743 | 768.7914 | 0 | 0.088511 | 4.6556 | 0 | 0 | 0 | 5.3186 | on_peak | 768.7914 |  |  | 0.69 | 0 | 99.31 | 24.7613 | 0
6758 | 859.37 | 43.7 | 28.5 | 6.9902 | 6.9902 | 0 | 0 | 0 | 0 | 20.5402 | 20.5402 | 0 | 52.2159 | 831.8396 | 0 | 0.088511 | 4.5038 | 0 | 0 | 0 | 6.9902 | on_peak | 831.8396 |  |  | 0.81 | 2.39 | 96.8 | 31.4822 | 0
6759 | 850.39 | 60.8 | 28.3 | 9.7326 | 9.7326 | 0 | 0 | 0 | 0 | 8.8178 | 8.8178 | 0 | 42.7893 | 831.8396 | 0 | 0.088511 | 4.4526 | 0 | 0 | 0 | 9.7326 | on_peak | 831.8396 |  |  | 1.14 | 1.04 | 97.82 | 43.3349 | 0
6760 | 796.79 | 302.461 | 28.1 | 48.4519 | 48.4519 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 42.7893 | 748.3381 | 0 | 0.088511 | 4.7647 | 0 | 0 | 0 | 48.4519 | on_peak | 748.3381 |  |  | 6.08 | 0 | 93.92 | 230.8606 | 0
6761 | 828.73 | 155.628 | 27.8 | 24.9576 | 24.9576 | 0 | 0 | 0 | 0 | 33.0873 | 33.0873 | 0 | 7.4174 | 770.685 | 0 | 0.088511 | 5.0289 | 0 | 0 | 0 | 24.9576 | on_peak | 770.685 |  |  | 3.01 | 3.99 | 93 | 125.5094 | 0
6762 | 807.3 | 27.6467 | 27.4 | 4.4401 | 4.4401 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 802.8599 | 0 | 0.088511 | 5.2603 | 0 | 0 | 0 | 4.4401 | on_peak | 802.8599 |  |  | 0.55 | 0 | 99.45 | 23.3561 | 0
6763 | 772.79 | 0 | 27.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 772.79 | 0 | 0.088511 | 5.4639 | 0 | 0 | 0 | 0 | on_peak | 772.79 |  |  | 0 | 0 | 100 | 0 | 0
6764 | 800.02 | 0 | 27 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 800.02 | 0 | 0.088511 | 5.5595 | 0 | 0 | 0 | 0 | on_peak | 800.02 |  |  | 0 | 0 | 100 | 0 | 0
6765 | 762.71 | 0 | 27 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 762.71 | 0 | 0.088511 | 5.6242 | 0 | 0 | 0 | 0 | on_peak | 762.71 |  |  | 0 | 0 | 100 | 0 | 0
6766 | 777.89 | 0 | 26.9 | 0 | 0 | 0 | 0 | 6.0298 | 6.0298 | 0 | 0 | 0 | 13.0578 | 783.9198 | 0 | 0.05921 | 5.7884 | 0 | 0 | 0 | 0 | off_peak | 777.89 | 0 | 100 | 0 | 0 | 100 | 0 | 0
6767 | 768.61 | 0 | 26.9 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 24.6217 | 780.9724 | 0 | 0.05921 | 6.111 | 0 | 0 | 0 | 0 | off_peak | 768.61 | 0 | 100 | 0 | 0 | 100 | 0 | 0
6768 | 696.77 | 0 | 26.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 24.6217 | 696.77 | 0 | 0.05921 | 6.4245 | 0 | 0 | 0 | 0 | off_peak | 696.77 |  |  | 0 | 0 | 100 | 0 | 0
6769 | 660.18 | 0 | 26.9 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 36.1857 | 672.5424 | 0 | 0.05921 | 6.6319 | 0 | 0 | 0 | 0 | off_peak | 660.18 | 0 | 100 | 0 | 0 | 100 | 0 | 0
6770 | 595.52 | 0 | 26.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 36.1857 | 595.52 | 0 | 0.05921 | 6.3665 | 0 | 0 | 0 | 0 | off_peak | 595.52 |  |  | 0 | 0 | 100 | 0 | 0
6771 | 601.43 | 0 | 27 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 36.1857 | 601.43 | 0 | 0.05921 | 5.9109 | 0 | 0 | 0 | 0 | off_peak | 601.43 |  |  | 0 | 0 | 100 | 0 | 0
6772 | 612.06 | 0 | 27 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 47.7496 | 624.4224 | 0 | 0.05921 | 5.3245 | 0 | 0 | 0 | 0 | off_peak | 612.06 | 0 | 100 | 0 | 0 | 100 | 0 | 0
6773 | 589.52 | 0 | 27.1 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 59.3135 | 601.8824 | 0 | 0.05921 | 4.6979 | 0 | 0 | 0 | 0 | off_peak | 589.52 | 0 | 100 | 0 | 0 | 100 | 0 | 0
6774 | 673.84 | 0 | 27.2 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 70.8775 | 686.2024 | 0 | 0.05921 | 4.2281 | 0 | 0 | 0 | 0 | off_peak | 673.84 | 0 | 100 | 0 | 0 | 100 | 0 | 0
6775 | 740.11 | 20.5278 | 27.4 | 3.2968 | 0 | 0 | 3.2968 | 3.2968 | 0 | 0 | 0 | 0 | 73.9613 | 740.11 | 0 | 0.05921 | 3.8723 | 0 | 0 | 3.0838 | 0 | off_peak | 740.11 | 100 | 0 | 0 | 0 | 100 | 0 | 0
6776 | 762.13 | 192.262 | 27.9 | 30.8213 | 30.8213 | 0 | 0 | 0.21292 | 0.21292 | 0 | 0 | 0 | 74.1605 | 731.5216 | 0 | 0.05921 | 3.6465 | 0 | 0 | 3.0838 | 30.8213 | off_peak | 731.3087 | 0 | 100 | 4.04 | 0 | 95.96 | 112.3883 | 0
6777 | 783.53 | 340.794 | 28.3 | 54.5527 | 54.5527 | 0 | 0 | 0.013752 | 0.013752 | 0 | 0 | 0 | 74.1734 | 728.991 | 0 | 0.05921 | 3.5388 | 0 | 0 | 3.0838 | 54.5527 | off_peak | 728.9773 | 0 | 100 | 6.96 | 0 | 93.04 | 193.0534 | 0
6778 | 804.18 | 569.441 | 28.7 | 91.0207 | 91.0207 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1734 | 713.1593 | 0 | 0.05921 | 3.5365 | 0 | 0 | 3.0838 | 91.0207 | off_peak | 713.1593 |  |  | 11.32 | 0 | 88.68 | 321.8935 | 0
6779 | 810.67 | 720.957 | 29.1 | 115.0711 | 115.0711 | 0 | 0 | 0.00088817 | 0.00088817 | 0 | 0 | 0 | 74.1742 | 695.5997 | 0 | 0.05921 | 3.7987 | 0 | 0 | 3.0838 | 115.0711 | off_peak | 695.5989 | 0 | 100 | 14.19 | 0 | 85.81 | 437.1245 | 0
6780 | 868.78 | 713.043 | 29.5 | 113.6417 | 113.6416 | 0 | 6.1324e-05 | 6.1324e-05 | 0 | 0 | 0 | 0 | 74.1743 | 755.1384 | 0 | 0.05921 | 4.2763 | 0 | 0 | 3.0839 | 113.6416 | off_peak | 755.1384 | 100 | 0 | 13.08 | 0 | 86.92 | 485.9626 | 0
6781 | 816.76 | 787.527 | 29.6 | 125.4667 | 125.4667 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1743 | 691.2933 | 0 | 0.088511 | 4.4577 | 0 | 0 | 3.0839 | 125.4667 | on_peak | 691.2933 |  |  | 15.36 | 0 | 84.64 | 559.2895 | 0
6782 | 867.36 | 687.253 | 29.7 | 109.4512 | 109.4512 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1743 | 757.9088 | 0 | 0.088511 | 4.4858 | 0 | 0 | 3.0839 | 109.4512 | on_peak | 757.9088 |  |  | 12.62 | 0 | 87.38 | 490.9746 | 0
6783 | 838.85 | 628.162 | 29.7 | 100.0404 | 100.0404 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1743 | 738.8096 | 0 | 0.088511 | 4.5179 | 0 | 0 | 3.0839 | 100.0404 | on_peak | 738.8096 |  |  | 11.93 | 0 | 88.07 | 451.9708 | 0
6784 | 804.62 | 455.64 | 29.6 | 72.5913 | 72.5913 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1743 | 732.0287 | 0 | 0.088511 | 4.8728 | 0 | 0 | 3.0839 | 72.5913 | on_peak | 732.0287 |  |  | 9.02 | 0 | 90.98 | 353.7203 | 0
6785 | 868.76 | 250.812 | 29.2 | 40.0172 | 40.0172 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1743 | 828.7428 | 0 | 0.088511 | 5.2121 | 0 | 0 | 3.0839 | 40.0172 | on_peak | 828.7428 |  |  | 4.61 | 0 | 95.39 | 208.5729 | 0
6786 | 839.51 | 55.658 | 28.7 | 8.8965 | 8.8965 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1743 | 830.6135 | 0 | 0.088511 | 5.5121 | 0 | 0 | 3.0839 | 8.8965 | on_peak | 830.6135 |  |  | 1.06 | 0 | 98.94 | 49.0383 | 0
6787 | 839.7 | 0 | 28.2 | 0 | 0 | 0 | 0 | 0 | 0 | 7.8604 | 7.8604 | 0 | 65.7712 | 831.8396 | 0 | 0.088511 | 6.0333 | 0 | 0 | 3.0839 | 0 | on_peak | 831.8396 |  |  | 0 | 0.94 | 99.06 | 0 | 0
6788 | 842.95 | 0 | 28 | 0 | 0 | 0 | 0 | 0 | 0 | 51.7002 | 51.7002 | 0 | 10.5013 | 791.2498 | 0 | 0.088511 | 6.4557 | 0 | 0 | 3.0839 | 0 | on_peak | 791.2498 |  |  | 0 | 6.13 | 93.87 | 0 | 0
6789 | 825.9 | 0 | 27.8 | 0 | 0 | 0 | 0 | 0 | 0 | 2.8847 | 2.8847 | 0 | 7.4174 | 823.0153 | 0 | 0.088511 | 6.8415 | 2.8847 | 0 | 0 | 2.8847 | on_peak | 823.0153 |  |  | 0 | 0.35 | 99.65 | 19.7359 | 0
6790 | 778.66 | 0 | 27.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 778.66 | 0 | 0.05921 | 7.2547 | 0 | 0 | 0 | 0 | off_peak | 778.66 |  |  | 0 | 0 | 100 | 0 | 0
6791 | 792.66 | 0 | 27.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 792.66 | 0 | 0.05921 | 7.6124 | 0 | 0 | 0 | 0 | off_peak | 792.66 |  |  | 0 | 0 | 100 | 0 | 0
6792 | 751.3 | 0 | 27.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 751.3 | 0 | 0.05921 | 7.7636 | 0 | 0 | 0 | 0 | off_peak | 751.3 |  |  | 0 | 0 | 100 | 0 | 0
6793 | 666.08 | 0 | 27.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 666.08 | 0 | 0.05921 | 7.8072 | 0 | 0 | 0 | 0 | off_peak | 666.08 |  |  | 0 | 0 | 100 | 0 | 0
6794 | 620.27 | 0 | 27.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 620.27 | 0 | 0.05921 | 7.3915 | 0 | 0 | 0 | 0 | off_peak | 620.27 |  |  | 0 | 0 | 100 | 0 | 0
6795 | 616.58 | 0 | 27.3 | 0 | 0 | 0 | 0 | 8.7006 | 8.7006 | 0 | 0 | 0 | 15.5561 | 625.2806 | 0 | 0.05921 | 6.9186 | 0 | 0 | 0 | 0 | off_peak | 616.58 | 0 | 100 | 0 | 0 | 100 | 0 | 0
6796 | 612.55 | 0 | 27.4 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 27.12 | 624.9124 | 0 | 0.05921 | 6.3172 | 0 | 0 | 0 | 0 | off_peak | 612.55 | 0 | 100 | 0 | 0 | 100 | 0 | 0
6797 | 628.55 | 0 | 27.4 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 38.684 | 640.9124 | 0 | 0.05921 | 5.6306 | 0 | 0 | 0 | 0 | off_peak | 628.55 | 0 | 100 | 0 | 0 | 100 | 0 | 0
6798 | 697.56 | 0 | 27.4 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 50.2479 | 709.9224 | 0 | 0.05921 | 5.0871 | 0 | 0 | 0 | 0 | off_peak | 697.56 | 0 | 100 | 0 | 0 | 100 | 0 | 0
6799 | 715.45 | 19.8476 | 27.7 | 3.1841 | 3.1841 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 61.8119 | 724.6283 | 0 | 0.05921 | 4.6804 | 0 | 0 | 0 | 3.1841 | off_peak | 712.2659 | 0 | 100 | 0.45 | 0 | 99.55 | 14.9028 | 0
6800 | 794.29 | 190.669 | 28.3 | 30.5214 | 30.5214 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 73.3758 | 776.131 | 0 | 0.05921 | 4.3996 | 0 | 0 | 0 | 30.5214 | off_peak | 763.7686 | 0 | 100 | 3.84 | 0 | 96.16 | 134.2814 | 0
6801 | 748.11 | 399.053 | 28.7 | 63.7855 | 63.7855 | 0 | 0 | 0.79843 | 0.79843 | 0 | 0 | 0 | 74.1227 | 685.1229 | 0 | 0.05921 | 4.2424 | 0 | 0 | 0 | 63.7855 | off_peak | 684.3245 | 0 | 100 | 8.53 | 0 | 91.47 | 270.6056 | 0
6802 | 793.25 | 517.76 | 29.1 | 82.6391 | 82.6391 | 0 | 0 | 0.051567 | 0.051567 | 0 | 0 | 0 | 74.1709 | 710.6625 | 0 | 0.05921 | 4.2261 | 0 | 0 | 0 | 82.6391 | off_peak | 710.6109 | 0 | 100 | 10.42 | 0 | 89.58 | 349.2438 | 0
6803 | 774.9 | 613.731 | 29.4 | 97.8495 | 97.8495 | 0 | 0 | 0.0033305 | 0.0033305 | 0 | 0 | 0 | 74.174 | 677.0538 | 0 | 0.05921 | 4.4451 | 0 | 0 | 0 | 97.8495 | off_peak | 677.0505 | 0 | 100 | 12.63 | 0 | 87.37 | 434.9503 | 0
6804 | 826.74 | 728.682 | 29.6 | 116.0916 | 116.0916 | 0 | 0 | 0.0002151 | 0.0002151 | 0 | 0 | 0 | 74.1742 | 710.6486 | 0 | 0.05921 | 4.8841 | 0 | 0 | 0 | 116.0916 | off_peak | 710.6484 | 0 | 100 | 14.04 | 0 | 85.96 | 567.0039 | 0
6805 | 792.39 | 747.408 | 29.6 | 119.075 | 119.075 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1742 | 673.315 | 0 | 0.088511 | 5.0767 | 0 | 0 | 0 | 119.075 | on_peak | 673.315 |  |  | 15.03 | 0 | 84.97 | 604.5103 | 0
6806 | 802.13 | 644.165 | 29.6 | 102.6266 | 102.6266 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1742 | 699.5034 | 0 | 0.088511 | 5.3015 | 0 | 0 | 0 | 102.6266 | on_peak | 699.5034 |  |  | 12.79 | 0 | 87.21 | 544.0714 | 0
6807 | 806.22 | 616.677 | 29.5 | 98.2833 | 98.2833 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1742 | 707.9367 | 0 | 0.088511 | 5.6372 | 0 | 0 | 0 | 98.2833 | on_peak | 707.9367 |  |  | 12.19 | 0 | 87.81 | 554.0441 | 0
6808 | 748.29 | 441.536 | 29.2 | 70.4473 | 70.4473 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1742 | 677.8427 | 0 | 0.088511 | 5.9807 | 0 | 0 | 0 | 70.4473 | on_peak | 677.8427 |  |  | 9.41 | 0 | 90.59 | 421.3249 | 0
6809 | 778.02 | 244.132 | 28.8 | 39.0083 | 39.0083 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1742 | 739.0117 | 0 | 0.088511 | 6.1936 | 0 | 0 | 0 | 39.0083 | on_peak | 739.0117 |  |  | 5.01 | 0 | 94.99 | 241.6039 | 0
6810 | 793.82 | 50.0312 | 28.3 | 8.0088 | 8.0088 | 0 | 0 | 0 | 0 | 62.4453 | 62.4453 | 0 | 7.4174 | 723.366 | 0 | 0.088511 | 6.5253 | 0 | 0 | 0 | 8.0088 | on_peak | 723.366 |  |  | 1.01 | 7.87 | 91.12 | 52.2592 | 0
6811 | 773.99 | 0 | 28 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 773.99 | 0 | 0.088511 | 7.0167 | 0 | 0 | 0 | 0 | on_peak | 773.99 |  |  | 0 | 0 | 100 | 0 | 0
6812 | 783.46 | 0 | 27.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 783.46 | 0 | 0.088511 | 7.2446 | 0 | 0 | 0 | 0 | on_peak | 783.46 |  |  | 0 | 0 | 100 | 0 | 0
6813 | 781.1 | 0 | 27.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 781.1 | 0 | 0.088511 | 7.5018 | 0 | 0 | 0 | 0 | on_peak | 781.1 |  |  | 0 | 0 | 100 | 0 | 0
6814 | 725.72 | 0 | 27.7 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 18.9814 | 738.0824 | 0 | 0.05921 | 7.6857 | 0 | 0 | 0 | 0 | off_peak | 725.72 | 0 | 100 | 0 | 0 | 100 | 0 | 0
6815 | 769.93 | 0 | 27.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18.9814 | 769.93 | 0 | 0.05921 | 7.5865 | 0 | 0 | 0 | 0 | off_peak | 769.93 |  |  | 0 | 0 | 100 | 0 | 0
6816 | 718.73 | 0 | 27.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18.9814 | 718.73 | 0 | 0.05921 | 7.5395 | 0 | 0 | 0 | 0 | off_peak | 718.73 |  |  | 0 | 0 | 100 | 0 | 0
6817 | 697.41 | 0 | 27.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18.9814 | 697.41 | 0 | 0.05921 | 7.6042 | 0 | 0 | 0 | 0 | off_peak | 697.41 |  |  | 0 | 0 | 100 | 0 | 0
6818 | 597.59 | 0 | 27.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18.9814 | 597.59 | 0 | 0.05921 | 7.2627 | 0 | 0 | 0 | 0 | off_peak | 597.59 |  |  | 0 | 0 | 100 | 0 | 0
6819 | 615.41 | 0 | 27.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18.9814 | 615.41 | 0 | 0.05921 | 6.9649 | 0 | 0 | 0 | 0 | off_peak | 615.41 |  |  | 0 | 0 | 100 | 0 | 0
6820 | 599.27 | 0 | 27.4 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 30.5453 | 611.6324 | 0 | 0.05921 | 6.5033 | 0 | 0 | 0 | 0 | off_peak | 599.27 | 0 | 100 | 0 | 0 | 100 | 0 | 0
6821 | 605.35 | 0 | 27.4 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 42.1093 | 617.7124 | 0 | 0.05921 | 5.9497 | 0 | 0 | 0 | 0 | off_peak | 605.35 | 0 | 100 | 0 | 0 | 100 | 0 | 0
6822 | 656.42 | 0 | 27.4 | 0 | 0 | 0 | 0 | 8.7006 | 8.7006 | 0 | 0 | 0 | 50.2479 | 665.1206 | 0 | 0.05921 | 5.5123 | 0 | 0 | 0 | 0 | off_peak | 656.42 | 0 | 100 | 0 | 0 | 100 | 0 | 0
6823 | 677.65 | 12.3831 | 27.7 | 1.9866 | 1.9866 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 61.8119 | 688.0258 | 0 | 0.05921 | 5.2042 | 0 | 0 | 0 | 1.9866 | off_peak | 675.6634 | 0 | 100 | 0.29 | 0 | 99.71 | 10.3384 | 0
6824 | 808.29 | 134.428 | 28.2 | 21.5265 | 21.5265 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 73.3758 | 799.1259 | 0 | 0.05921 | 5.0447 | 0 | 0 | 0 | 21.5265 | off_peak | 786.7635 | 0 | 100 | 2.66 | 0 | 97.34 | 108.595 | 0
6825 | 800.8 | 283.67 | 28.5 | 45.3755 | 45.3755 | 0 | 0 | 0.79843 | 0.79843 | 0 | 0 | 0 | 74.1227 | 756.2229 | 0 | 0.05921 | 4.9947 | 0 | 0 | 0 | 45.3755 | off_peak | 755.4245 | 0 | 100 | 5.67 | 0 | 94.33 | 226.6374 | 0
6826 | 792.57 | 504.087 | 28.8 | 80.545 | 80.545 | 0 | 0 | 0.051567 | 0.051567 | 0 | 0 | 0 | 74.1709 | 712.0766 | 0 | 0.05921 | 5.0597 | 0 | 0 | 0 | 80.545 | off_peak | 712.025 | 0 | 100 | 10.16 | 0 | 89.84 | 407.5351 | 0
6827 | 823.4 | 571.211 | 29 | 91.2037 | 91.2037 | 0 | 0 | 0.0033305 | 0.0033305 | 0 | 0 | 0 | 74.174 | 732.1997 | 0 | 0.05921 | 5.3681 | 0 | 0 | 0 | 91.2037 | off_peak | 732.1963 | 0 | 100 | 11.08 | 0 | 88.92 | 489.5895 | 0
6828 | 829.86 | 790.278 | 29.2 | 126.0893 | 126.0893 | 0 | 0 | 0.0002151 | 0.0002151 | 0 | 0 | 0 | 74.1742 | 703.7709 | 0 | 0.05921 | 5.8516 | 0 | 0 | 0 | 126.0893 | off_peak | 703.7707 | 0 | 100 | 15.19 | 0 | 84.81 | 737.8209 | 0
6829 | 847.19 | 780.256 | 29.3 | 124.4448 | 124.4448 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1742 | 722.7452 | 0 | 0.088511 | 6.0286 | 0 | 0 | 0 | 124.4448 | on_peak | 722.7452 |  |  | 14.69 | 0 | 85.31 | 750.2268 | 0
6830 | 898.99 | 668.439 | 29.4 | 106.5719 | 106.5719 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1742 | 792.4181 | 0 | 0.088511 | 6.1546 | 0 | 0 | 0 | 106.5719 | on_peak | 792.4181 |  |  | 11.85 | 0 | 88.15 | 655.9033 | 0
6831 | 868.84 | 389.4 | 29.3 | 62.1063 | 62.1063 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1742 | 806.7337 | 0 | 0.088511 | 6.5222 | 0 | 0 | 0 | 62.1063 | on_peak | 806.7337 |  |  | 7.15 | 0 | 92.85 | 405.0679 | 0
6832 | 821.47 | 391.979 | 29.1 | 62.5633 | 62.5633 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1742 | 758.9067 | 0 | 0.088511 | 6.9809 | 0 | 0 | 0 | 62.5633 | on_peak | 758.9067 |  |  | 7.62 | 0 | 92.38 | 436.7501 | 0
6833 | 837.35 | 209.337 | 28.8 | 33.4487 | 33.4487 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1742 | 803.9013 | 0 | 0.088511 | 7.3223 | 0 | 0 | 0 | 33.4487 | on_peak | 803.9013 |  |  | 3.99 | 0 | 96.01 | 244.9213 | 0
6834 | 860.67 | 21.85 | 28.3 | 3.4976 | 3.4976 | 0 | 0 | 0 | 0 | 62.3949 | 62.3949 | 0 | 7.4713 | 794.7774 | 0 | 0.088511 | 7.4873 | 0 | 0 | 0 | 3.4976 | on_peak | 794.7774 |  |  | 0.41 | 7.25 | 92.34 | 26.1878 | 0
6835 | 812.46 | 0 | 28 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4713 | 812.46 | 0 | 0.088511 | 7.6433 | 0 | 0 | 0 | 0 | on_peak | 812.46 |  |  | 0 | 0 | 100 | 0 | 0
6836 | 827.9 | 0 | 27.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4713 | 827.9 | 0 | 0.088511 | 7.9658 | 0 | 0 | 0 | 0 | on_peak | 827.9 |  |  | 0 | 0 | 100 | 0 | 0
6837 | 831.89 | 0 | 27.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0.050365 | 0.050365 | 0 | 7.4174 | 831.8396 | 0 | 0.088511 | 8.1389 | 0 | 0 | 0 | 0 | on_peak | 831.8396 |  |  | 0 | 0.01 | 99.99 | 0 | 0
6838 | 787.58 | 0 | 27.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 787.58 | 0 | 0.05921 | 8.3388 | 0 | 0 | 0 | 0 | off_peak | 787.58 |  |  | 0 | 0 | 100 | 0 | 0
6839 | 824.6 | 0 | 27.7 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 18.9814 | 836.9624 | 0 | 0.05921 | 8.4149 | 0 | 0 | 0 | 0 | off_peak | 824.6 | 0 | 100 | 0 | 0 | 100 | 0 | 0
6840 | 777.62 | 0 | 27.6 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 30.5453 | 789.9824 | 0 | 0.05921 | 8.2733 | 0 | 0 | 0 | 0 | off_peak | 777.62 | 0 | 100 | 0 | 0 | 100 | 0 | 0
6841 | 698.89 | 0 | 27.5 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 42.1093 | 711.2524 | 0 | 0.05921 | 8.2347 | 0 | 0 | 0 | 0 | off_peak | 698.89 | 0 | 100 | 0 | 0 | 100 | 0 | 0
6842 | 636.34 | 0 | 27.5 | 0 | 0 | 0 | 0 | 8.7006 | 8.7006 | 0 | 0 | 0 | 50.2479 | 645.0406 | 0 | 0.05921 | 7.9874 | 0 | 0 | 0 | 0 | off_peak | 636.34 | 0 | 100 | 0 | 0 | 100 | 0 | 0
6843 | 609.58 | 0 | 27.5 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 61.8119 | 621.9424 | 0 | 0.05921 | 7.5787 | 0 | 0 | 0 | 0 | off_peak | 609.58 | 0 | 100 | 0 | 0 | 100 | 0 | 0
6844 | 663.46 | 0 | 27.4 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 73.3758 | 675.8224 | 0 | 0.05921 | 7.0214 | 0 | 0 | 0 | 0 | off_peak | 663.46 | 0 | 100 | 0 | 0 | 100 | 0 | 0
6845 | 618.89 | 0 | 27.5 | 0 | 0 | 0 | 0 | 0.79843 | 0.79843 | 0 | 0 | 0 | 74.1227 | 619.6884 | 0 | 0.05921 | 6.3716 | 0 | 0 | 0 | 0 | off_peak | 618.89 | 0 | 100 | 0 | 0 | 100 | 0 | 0
6846 | 666.06 | 0 | 27.5 | 0 | 0 | 0 | 0 | 0.051567 | 0.051567 | 0 | 0 | 0 | 74.1709 | 666.1116 | 0 | 0.05921 | 5.9058 | 0 | 0 | 0 | 0 | off_peak | 666.06 | 0 | 100 | 0 | 0 | 100 | 0 | 0
6847 | 710.96 | 15.9109 | 27.7 | 2.5525 | 2.5525 | 0 | 0 | 0.0033305 | 0.0033305 | 0 | 0 | 0 | 74.174 | 708.4108 | 0 | 0.05921 | 5.5402 | 0 | 0 | 0 | 2.5525 | off_peak | 708.4075 | 0 | 100 | 0.36 | 0 | 99.64 | 14.1414 | 0
6848 | 866.72 | 188.935 | 28.1 | 30.2659 | 30.2659 | 0 | 0 | 0.0002151 | 0.0002151 | 0 | 0 | 0 | 74.1742 | 836.4543 | 0 | 0.05921 | 5.275 | 0 | 0 | 0 | 30.2659 | off_peak | 836.4541 | 0 | 100 | 3.49 | 0 | 96.51 | 159.6523 | 0
6849 | 899.1 | 392.408 | 28.4 | 62.792 | 62.792 | 0 | 0 | 1.3893e-05 | 1.3893e-05 | 0 | 0 | 0 | 74.1743 | 836.308 | 0 | 0.05921 | 5.1205 | 0 | 0 | 0 | 62.792 | off_peak | 836.308 | 0 | 100 | 6.98 | 0 | 93.02 | 321.5267 | 0
6850 | 870.22 | 520.935 | 28.6 | 83.2978 | 83.2978 | 0 | 0 | 8.9726e-07 | 8.9726e-07 | 0 | 0 | 0 | 74.1743 | 786.9222 | 0 | 0.05921 | 5.1247 | 0 | 0 | 0 | 83.2978 | off_peak | 786.9222 | 0 | 100 | 9.57 | 0 | 90.43 | 426.8756 | 0
6851 | 853.34 | 407.549 | 28.5 | 65.191 | 65.191 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1743 | 788.149 | 0 | 0.05921 | 5.3918 | 0 | 0 | 0 | 65.191 | off_peak | 788.149 |  |  | 7.64 | 0 | 92.36 | 351.4948 | 0
6852 | 923.72 | 270.18 | 28.4 | 43.2334 | 43.2334 | 0 | 0 | 0 | 0 | 18.6218 | 18.6218 | 0 | 54.2667 | 861.8648 | 0 | 0.05921 | 5.7229 | 0 | 0 | 0 | 43.2334 | off_peak | 861.8648 |  |  | 4.68 | 2.02 | 93.3 | 247.4214 | 0
6853 | 825.01 | 83.6 | 28.2 | 13.3872 | 1.0248 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 0 | 65.8306 | 823.9852 | 0 | 0.088511 | 5.8573 | 0 | 0 | 11.5639 | 1.0248 | on_peak | 823.9852 | 100 | 0 | 0.12 | 0 | 99.88 | 6.0026 | 0
6854 | 874.06 | 81.7 | 28 | 13.0925 | 13.0925 | 0 | 0 | 0 | 0 | 29.1279 | 29.1279 | 0 | 34.6916 | 831.8396 | 0 | 0.088511 | 6.1461 | 10.8171 | 0 | 0 | 23.9095 | on_peak | 831.8396 |  |  | 1.5 | 3.33 | 95.17 | 146.9509 | 0
6855 | 880.72 | 145.661 | 27.7 | 23.3677 | 23.3677 | 0 | 0 | 0 | 0 | 25.5126 | 25.5126 | 0 | 7.4174 | 831.8396 | 0 | 0.088511 | 6.4637 | 0 | 0 | 0 | 23.3677 | on_peak | 831.8396 |  |  | 2.65 | 2.9 | 94.45 | 151.0422 | 0
6856 | 815.98 | 160.603 | 27.3 | 25.8023 | 25.8023 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 790.1777 | 0 | 0.088511 | 6.7994 | 0 | 0 | 0 | 25.8023 | on_peak | 790.1777 |  |  | 3.16 | 0 | 96.84 | 175.4389 | 0
6857 | 807.77 | 26.6 | 26.9 | 4.2797 | 4.2797 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 803.4903 | 0 | 0.088511 | 7.1329 | 0 | 0 | 0 | 4.2797 | on_peak | 803.4903 |  |  | 0.53 | 0 | 99.47 | 30.527 | 0
6858 | 800.58 | 11.4 | 26.5 | 1.8368 | 1.8368 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 798.7432 | 0 | 0.088511 | 7.5116 | 0 | 0 | 0 | 1.8368 | on_peak | 798.7432 |  |  | 0.23 | 0 | 99.77 | 13.7974 | 0
6859 | 787.61 | 0 | 26.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 787.61 | 0 | 0.088511 | 7.6897 | 0 | 0 | 0 | 0 | on_peak | 787.61 |  |  | 0 | 0 | 100 | 0 | 0
6860 | 761.18 | 0 | 26.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 761.18 | 0 | 0.088511 | 7.779 | 0 | 0 | 0 | 0 | on_peak | 761.18 |  |  | 0 | 0 | 100 | 0 | 0
6861 | 821.36 | 0 | 26 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 821.36 | 0 | 0.088511 | 7.7892 | 0 | 0 | 0 | 0 | on_peak | 821.36 |  |  | 0 | 0 | 100 | 0 | 0
6862 | 742.81 | 0 | 25.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 742.81 | 0 | 0.05921 | 7.8725 | 0 | 0 | 0 | 0 | off_peak | 742.81 |  |  | 0 | 0 | 100 | 0 | 0
6863 | 762.79 | 0 | 25.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 762.79 | 0 | 0.05921 | 7.941 | 0 | 0 | 0 | 0 | off_peak | 762.79 |  |  | 0 | 0 | 100 | 0 | 0
6864 | 745.54 | 0 | 26 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 745.54 | 0 | 0.05921 | 7.9433 | 0 | 0 | 0 | 0 | off_peak | 745.54 |  |  | 0 | 0 | 100 | 0 | 0
6865 | 647.51 | 0 | 26 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 647.51 | 0 | 0.05921 | 7.8703 | 0 | 0 | 0 | 0 | off_peak | 647.51 |  |  | 0 | 0 | 100 | 0 | 0
6866 | 585.55 | 0 | 26 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 585.55 | 0 | 0.05921 | 7.5808 | 0 | 0 | 0 | 0 | off_peak | 585.55 |  |  | 0 | 0 | 100 | 0 | 0
6867 | 589.79 | 0 | 25.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 589.79 | 0 | 0.05921 | 7.1767 | 0 | 0 | 0 | 0 | off_peak | 589.79 |  |  | 0 | 0 | 100 | 0 | 0
6868 | 568.1 | 0 | 25.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 568.1 | 0 | 0.05921 | 6.7207 | 0 | 0 | 0 | 0 | off_peak | 568.1 |  |  | 0 | 0 | 100 | 0 | 0
6869 | 629.13 | 0 | 25.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 629.13 | 0 | 0.05921 | 6.2085 | 0 | 0 | 0 | 0 | off_peak | 629.13 |  |  | 0 | 0 | 100 | 0 | 0
6870 | 635.55 | 0 | 25.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 635.55 | 0 | 0.05921 | 5.6647 | 0 | 0 | 0 | 0 | off_peak | 635.55 |  |  | 0 | 0 | 100 | 0 | 0
6871 | 663.55 | 11.4296 | 26 | 1.8449 | 1.8449 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 661.7051 | 0 | 0.05921 | 5.1915 | 0 | 0 | 0 | 1.8449 | off_peak | 661.7051 |  |  | 0.28 | 0 | 99.72 | 9.578 | 0
6872 | 705.18 | 112.739 | 26.3 | 18.1782 | 18.1782 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 687.0018 | 0 | 0.05921 | 4.924 | 0 | 0 | 0 | 18.1782 | off_peak | 687.0018 |  |  | 2.58 | 0 | 97.42 | 89.5092 | 0
6873 | 702.59 | 218.583 | 26.6 | 35.2065 | 35.2065 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 667.3835 | 0 | 0.05921 | 4.7256 | 0 | 0 | 0 | 35.2065 | off_peak | 667.3835 |  |  | 5.01 | 0 | 94.99 | 166.3704 | 0
6874 | 711.8 | 428.235 | 27.1 | 68.8496 | 68.8496 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 642.9504 | 0 | 0.05921 | 4.6336 | 0 | 0 | 0 | 68.8496 | off_peak | 642.9504 |  |  | 9.67 | 0 | 90.33 | 319.0228 | 0
6875 | 714.18 | 313.918 | 27.6 | 50.3787 | 50.3787 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 663.8013 | 0 | 0.05921 | 4.6592 | 0 | 0 | 0 | 50.3787 | off_peak | 663.8013 |  |  | 7.05 | 0 | 92.95 | 234.7262 | 0
6876 | 694.76 | 418.908 | 28 | 67.1302 | 67.1302 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 627.6298 | 0 | 0.05921 | 4.7845 | 0 | 0 | 0 | 67.1302 | off_peak | 627.6298 |  |  | 9.66 | 0 | 90.34 | 321.1856 | 0
6877 | 731.27 | 541.58 | 28.4 | 86.6621 | 86.6621 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 644.6079 | 0 | 0.05921 | 4.9909 | 0 | 0 | 0 | 86.6621 | off_peak | 644.6079 |  |  | 11.85 | 0 | 88.15 | 432.5197 | 0
6878 | 686.39 | 310.389 | 28.5 | 49.6495 | 49.6495 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 636.7405 | 0 | 0.05921 | 5.2542 | 0 | 0 | 0 | 49.6495 | off_peak | 636.7405 |  |  | 7.23 | 0 | 92.77 | 260.8673 | 0
6879 | 701.64 | 40.85 | 28.7 | 6.5296 | 6.5296 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 695.1104 | 0 | 0.05921 | 5.428 | 0 | 0 | 0 | 6.5296 | off_peak | 695.1104 |  |  | 0.93 | 0 | 99.07 | 35.4426 | 0
6880 | 705.45 | 308.905 | 28.6 | 49.3941 | 49.3941 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 656.0559 | 0 | 0.05921 | 5.619 | 0 | 0 | 0 | 49.3941 | off_peak | 656.0559 |  |  | 7 | 0 | 93 | 277.5445 | 0
6881 | 716.98 | 209.264 | 28.4 | 33.4858 | 33.4858 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 683.4942 | 0 | 0.05921 | 5.7965 | 0 | 0 | 0 | 33.4858 | off_peak | 683.4942 |  |  | 4.67 | 0 | 95.33 | 194.1014 | 0
6882 | 628.15 | 30.4404 | 28 | 4.8781 | 4.8781 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 623.2719 | 0 | 0.05921 | 6.3275 | 0 | 0 | 0 | 4.8781 | off_peak | 623.2719 |  |  | 0.78 | 0 | 99.22 | 30.8663 | 0
6883 | 579.75 | 0 | 27.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 579.75 | 0 | 0.05921 | 6.7215 | 0 | 0 | 0 | 0 | off_peak | 579.75 |  |  | 0 | 0 | 100 | 0 | 0
6884 | 606.35 | 0 | 27.4 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 18.9814 | 618.7124 | 0 | 0.05921 | 6.2198 | 0 | 0 | 0 | 0 | off_peak | 606.35 | 0 | 100 | 0 | 0 | 100 | 0 | 0
6885 | 571.09 | 0 | 27.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18.9814 | 571.09 | 0 | 0.05921 | 6.4708 | 0 | 0 | 0 | 0 | off_peak | 571.09 |  |  | 0 | 0 | 100 | 0 | 0
6886 | 569.71 | 0 | 27.1 | 0 | 0 | 0 | 0 | 7.0913 | 7.0913 | 0 | 0 | 0 | 25.6147 | 576.8013 | 0 | 0.05921 | 6.8429 | 0 | 0 | 0 | 0 | off_peak | 569.71 | 0 | 100 | 0 | 0 | 100 | 0 | 0
6887 | 586.19 | 0 | 27 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 37.1786 | 598.5524 | 0 | 0.05921 | 7.2255 | 0 | 0 | 0 | 0 | off_peak | 586.19 | 0 | 100 | 0 | 0 | 100 | 0 | 0
6888 | 583.58 | 0 | 26.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 37.1786 | 583.58 | 0 | 0.05921 | 7.5498 | 0 | 0 | 0 | 0 | off_peak | 583.58 |  |  | 0 | 0 | 100 | 0 | 0
6889 | 543.58 | 0 | 26.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 37.1786 | 543.58 | 0 | 0.05921 | 7.3862 | 0 | 0 | 0 | 0 | off_peak | 543.58 |  |  | 0 | 0 | 100 | 0 | 0
6890 | 589.28 | 0 | 26.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 37.1786 | 589.28 | 0 | 0.05921 | 7.0046 | 0 | 0 | 0 | 0 | off_peak | 589.28 |  |  | 0 | 0 | 100 | 0 | 0
6891 | 576.58 | 0 | 26.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 37.1786 | 576.58 | 0 | 0.05921 | 6.5898 | 0 | 0 | 0 | 0 | off_peak | 576.58 |  |  | 0 | 0 | 100 | 0 | 0
6892 | 605.84 | 0 | 26.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 37.1786 | 605.84 | 0 | 0.05921 | 6.0771 | 0 | 0 | 0 | 0 | off_peak | 605.84 |  |  | 0 | 0 | 100 | 0 | 0
6893 | 614.39 | 0 | 26.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 37.1786 | 614.39 | 0 | 0.05921 | 5.5028 | 0 | 0 | 0 | 0 | off_peak | 614.39 |  |  | 0 | 0 | 100 | 0 | 0
6894 | 631.86 | 0 | 26.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 37.1786 | 631.86 | 0 | 0.05921 | 4.9202 | 0 | 0 | 0 | 0 | off_peak | 631.86 |  |  | 0 | 0 | 100 | 0 | 0
6895 | 678.38 | 16.3135 | 26.9 | 2.6247 | 2.6247 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 48.7425 | 688.1177 | 0 | 0.05921 | 4.4625 | 0 | 0 | 0 | 2.6247 | off_peak | 675.7553 | 0 | 100 | 0.39 | 0 | 99.61 | 11.7129 | 0
6896 | 696.93 | 181.658 | 27.5 | 29.1637 | 29.1637 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 48.7425 | 667.7663 | 0 | 0.05921 | 4.0994 | 0 | 0 | 0 | 29.1637 | off_peak | 667.7663 |  |  | 4.18 | 0 | 95.82 | 119.5539 | 0
6897 | 664.21 | 377.98 | 27.9 | 60.5935 | 60.5935 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 48.7425 | 603.6165 | 0 | 0.05921 | 3.8677 | 0 | 0 | 0 | 60.5935 | off_peak | 603.6165 |  |  | 9.12 | 0 | 90.88 | 234.3583 | 0
6898 | 698.98 | 550.607 | 28.2 | 88.1708 | 88.1708 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 60.3065 | 623.1716 | 0 | 0.05921 | 3.7207 | 0 | 0 | 0 | 88.1708 | off_peak | 610.8092 | 0 | 100 | 12.61 | 0 | 87.39 | 328.0545 | 0
6899 | 663.73 | 696.116 | 28.5 | 111.3499 | 111.3499 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60.3065 | 552.3801 | 0 | 0.05921 | 3.6866 | 0 | 0 | 0 | 111.3499 | off_peak | 552.3801 |  |  | 16.78 | 0 | 83.22 | 410.501 | 0
6900 | 719.19 | 608.535 | 28.7 | 97.2695 | 97.2695 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60.3065 | 621.9205 | 0 | 0.05921 | 3.7404 | 0 | 0 | 0 | 97.2695 | off_peak | 621.9205 |  |  | 13.52 | 0 | 86.48 | 363.8276 | 0
6901 | 683.56 | 740.619 | 28.8 | 118.3389 | 118.3389 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60.3065 | 565.2211 | 0 | 0.05921 | 3.8722 | 0 | 0 | 0 | 118.3389 | off_peak | 565.2211 |  |  | 17.31 | 0 | 82.69 | 458.2264 | 0
6902 | 687.64 | 692.502 | 28.7 | 110.691 | 110.691 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 71.8704 | 589.3114 | 0 | 0.05921 | 4.1005 | 0 | 0 | 0 | 110.691 | off_peak | 576.949 | 0 | 100 | 16.1 | 0 | 83.9 | 453.8927 | 0
6903 | 679.57 | 601.285 | 28.5 | 96.1808 | 96.1808 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 71.8704 | 583.3892 | 0 | 0.05921 | 4.2684 | 0 | 0 | 0 | 96.1808 | off_peak | 583.3892 |  |  | 14.15 | 0 | 85.85 | 410.5365 | 0
6904 | 701.17 | 196.346 | 28.2 | 31.4416 | 31.4416 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 71.8704 | 669.7284 | 0 | 0.05921 | 4.6353 | 0 | 0 | 0 | 31.4416 | off_peak | 669.7284 |  |  | 4.48 | 0 | 95.52 | 145.7426 | 0
6905 | 676.78 | 55.0033 | 27.9 | 8.8175 | 8.8175 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 71.8704 | 667.9625 | 0 | 0.05921 | 5.088 | 0 | 0 | 0 | 8.8175 | off_peak | 667.9625 |  |  | 1.3 | 0 | 98.7 | 44.8636 | 0
6906 | 640.43 | 31.5553 | 27.4 | 5.0678 | 5.0678 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 71.8704 | 635.3622 | 0 | 0.05921 | 5.4952 | 0 | 0 | 0 | 5.0678 | off_peak | 635.3622 |  |  | 0.79 | 0 | 99.21 | 27.8485 | 0
6907 | 561.13 | 0 | 27.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 71.8704 | 561.13 | 0 | 0.05921 | 5.8078 | 0 | 0 | 0 | 0 | off_peak | 561.13 |  |  | 0 | 0 | 100 | 0 | 0
6908 | 587.87 | 0 | 27.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 71.8704 | 587.87 | 0 | 0.05921 | 6.1449 | 0 | 0 | 0 | 0 | off_peak | 587.87 |  |  | 0 | 0 | 100 | 0 | 0
6909 | 574.78 | 0 | 27.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 71.8704 | 574.78 | 0 | 0.05921 | 6.3938 | 0 | 0 | 0 | 0 | off_peak | 574.78 |  |  | 0 | 0 | 100 | 0 | 0
6910 | 580.56 | 0 | 27.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 71.8704 | 580.56 | 0 | 0.05921 | 6.6723 | 0 | 0 | 0 | 0 | off_peak | 580.56 |  |  | 0 | 0 | 100 | 0 | 0
6911 | 558.5 | 0 | 27.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 71.8704 | 558.5 | 0 | 0.05921 | 6.9657 | 0 | 0 | 0 | 0 | off_peak | 558.5 |  |  | 0 | 0 | 100 | 0 | 0
6912 | 558.94 | 0 | 27.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 71.8704 | 558.94 | 0 | 0.05921 | 7.1832 | 0 | 0 | 0 | 0 | off_peak | 558.94 |  |  | 0 | 0 | 100 | 0 | 0
6913 | 574.27 | 0 | 27 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 71.8704 | 574.27 | 0 | 0.05921 | 7.0764 | 0 | 0 | 0 | 0 | off_peak | 574.27 |  |  | 0 | 0 | 100 | 0 | 0
6914 | 552.79 | 0 | 27 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 71.8704 | 552.79 | 0 | 0.05921 | 6.6979 | 0 | 0 | 0 | 0 | off_peak | 552.79 |  |  | 0 | 0 | 100 | 0 | 0
6915 | 545.46 | 0 | 26.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 71.8704 | 545.46 | 0 | 0.05921 | 6.1266 | 0 | 0 | 0 | 0 | off_peak | 545.46 |  |  | 0 | 0 | 100 | 0 | 0
6916 | 546.18 | 0 | 26.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 71.8704 | 546.18 | 0 | 0.05921 | 5.4411 | 0 | 0 | 0 | 0 | off_peak | 546.18 |  |  | 0 | 0 | 100 | 0 | 0
6917 | 545.34 | 0 | 26.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 71.8704 | 545.34 | 0 | 0.05921 | 4.755 | 0 | 0 | 0 | 0 | off_peak | 545.34 |  |  | 0 | 0 | 100 | 0 | 0
6918 | 596.73 | 0 | 26.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 71.8704 | 596.73 | 0 | 0.05921 | 4.1146 | 0 | 0 | 0 | 0 | off_peak | 596.73 |  |  | 0 | 0 | 100 | 0 | 0
6919 | 620.79 | 14.3191 | 26.9 | 2.3038 | 0 | 0 | 2.3038 | 2.3038 | 0 | 0 | 0 | 0 | 74.0255 | 620.79 | 0 | 0.05921 | 3.6501 | 0 | 0 | 2.155 | 0 | off_peak | 620.79 | 100 | 0 | 0 | 0 | 100 | 0 | 0
6920 | 739.27 | 174.264 | 27.4 | 27.9869 | 27.9869 | 0 | 0 | 0.14879 | 0.14879 | 0 | 0 | 0 | 74.1646 | 711.4319 | 0 | 0.05921 | 3.3679 | 0 | 0 | 2.155 | 27.9869 | off_peak | 711.2831 | 0 | 100 | 3.79 | 0 | 96.21 | 94.2555 | 0
6921 | 764.64 | 375.478 | 27.8 | 60.2143 | 60.2143 | 0 | 0 | 0.00961 | 0.00961 | 0 | 0 | 0 | 74.1736 | 704.4353 | 0 | 0.05921 | 3.2095 | 0 | 0 | 2.155 | 60.2143 | off_peak | 704.4257 | 0 | 100 | 7.87 | 0 | 92.13 | 193.2588 | 0
6922 | 780.25 | 553.708 | 28.1 | 88.6996 | 88.6996 | 0 | 0 | 0.00062067 | 0.00062067 | 0 | 0 | 0 | 74.1742 | 691.551 | 0 | 0.05921 | 3.1842 | 0 | 0 | 2.155 | 88.6996 | off_peak | 691.5504 | 0 | 100 | 11.37 | 0 | 88.63 | 282.4378 | 0
6923 | 761.21 | 653.579 | 28.4 | 104.5838 | 104.5838 | 0 | 4.0086e-05 | 4.0086e-05 | 0 | 0 | 0 | 0 | 74.1742 | 656.6262 | 0 | 0.05921 | 3.4168 | 0 | 0 | 2.1551 | 104.5838 | off_peak | 656.6262 | 100 | 0 | 13.74 | 0 | 86.26 | 357.3399 | 0
6924 | 836.24 | 739.001 | 28.5 | 118.2097 | 118.2097 | 0 | 2.589e-06 | 2.589e-06 | 0 | 0 | 0 | 0 | 74.1743 | 718.0303 | 0 | 0.05921 | 3.8942 | 0 | 0 | 2.1551 | 118.2097 | off_peak | 718.0303 | 100 | 0 | 14.14 | 0 | 85.86 | 460.3282 | 0
6925 | 807.52 | 621.846 | 28.6 | 99.4335 | 99.4335 | 0 | 0 | 0 | 0 | 62.4453 | 62.4453 | 0 | 7.4174 | 645.6412 | 0 | 0.088511 | 4.0691 | 2.0159 | 0 | 0 | 101.4494 | on_peak | 645.6412 |  |  | 12.31 | 7.73 | 79.95 | 412.8065 | 0
6926 | 848.5 | 718.389 | 28.5 | 114.9126 | 114.9126 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 733.5874 | 0 | 0.088511 | 4.0599 | 0 | 0 | 0 | 114.9126 | on_peak | 733.5874 |  |  | 13.54 | 0 | 86.46 | 466.5378 | 0
6927 | 849.58 | 597.754 | 28.4 | 95.6509 | 95.6509 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 753.9291 | 0 | 0.088511 | 3.8898 | 0 | 0 | 0 | 95.6509 | on_peak | 753.9291 |  |  | 11.26 | 0 | 88.74 | 372.0598 | 0
6928 | 819.75 | 427.255 | 28.2 | 68.4179 | 68.4179 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 751.3321 | 0 | 0.088511 | 3.7104 | 0 | 0 | 0 | 68.4179 | on_peak | 751.3321 |  |  | 8.35 | 0 | 91.65 | 253.8555 | 0
6929 | 752.42 | 227.701 | 27.8 | 36.5157 | 36.5157 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 715.9043 | 0 | 0.088511 | 3.6622 | 0 | 0 | 0 | 36.5157 | on_peak | 715.9043 |  |  | 4.85 | 0 | 95.15 | 133.7281 | 0
6930 | 801.09 | 40.7805 | 27.4 | 6.5494 | 6.5494 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 794.5406 | 0 | 0.088511 | 3.792 | 0 | 0 | 0 | 6.5494 | on_peak | 794.5406 |  |  | 0.82 | 0 | 99.18 | 24.8352 | 0
6931 | 727.31 | 0 | 27.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 727.31 | 0 | 0.088511 | 4.0732 | 0 | 0 | 0 | 0 | on_peak | 727.31 |  |  | 0 | 0 | 100 | 0 | 0
6932 | 794.67 | 0 | 27 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 794.67 | 0 | 0.088511 | 4.3386 | 0 | 0 | 0 | 0 | on_peak | 794.67 |  |  | 0 | 0 | 100 | 0 | 0
6933 | 796.34 | 0 | 27 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 796.34 | 0 | 0.088511 | 4.5765 | 0 | 0 | 0 | 0 | on_peak | 796.34 |  |  | 0 | 0 | 100 | 0 | 0
6934 | 741.48 | 0 | 26.9 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 18.9814 | 753.8424 | 0 | 0.05921 | 4.7772 | 0 | 0 | 0 | 0 | off_peak | 741.48 | 0 | 100 | 0 | 0 | 100 | 0 | 0
6935 | 775.41 | 0 | 26.9 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 30.5453 | 787.7724 | 0 | 0.05921 | 5.1636 | 0 | 0 | 0 | 0 | off_peak | 775.41 | 0 | 100 | 0 | 0 | 100 | 0 | 0
6936 | 720.09 | 0 | 26.8 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 42.1093 | 732.4524 | 0 | 0.05921 | 5.548 | 0 | 0 | 0 | 0 | off_peak | 720.09 | 0 | 100 | 0 | 0 | 100 | 0 | 0
6937 | 665.45 | 0 | 26.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 42.1093 | 665.45 | 0 | 0.05921 | 5.7145 | 0 | 0 | 0 | 0 | off_peak | 665.45 |  |  | 0 | 0 | 100 | 0 | 0
6938 | 611.07 | 0 | 26.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 42.1093 | 611.07 | 0 | 0.05921 | 5.4736 | 0 | 0 | 0 | 0 | off_peak | 611.07 |  |  | 0 | 0 | 100 | 0 | 0
6939 | 563.52 | 0 | 26.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 42.1093 | 563.52 | 0 | 0.05921 | 5.0175 | 0 | 0 | 0 | 0 | off_peak | 563.52 |  |  | 0 | 0 | 100 | 0 | 0
6940 | 569.86 | 0 | 26.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 42.1093 | 569.86 | 0 | 0.05921 | 4.4072 | 0 | 0 | 0 | 0 | off_peak | 569.86 |  |  | 0 | 0 | 100 | 0 | 0
6941 | 555.44 | 0 | 26.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 42.1093 | 555.44 | 0 | 0.05921 | 3.7386 | 0 | 0 | 0 | 0 | off_peak | 555.44 |  |  | 0 | 0 | 100 | 0 | 0
6942 | 588.79 | 0 | 26.7 | 0 | 0 | 0 | 0 | 8.7006 | 8.7006 | 0 | 0 | 0 | 50.2479 | 597.4906 | 0 | 0.05921 | 3.2231 | 0 | 0 | 0 | 0 | off_peak | 588.79 | 0 | 100 | 0 | 0 | 100 | 0 | 0
6943 | 665.89 | 8.55 | 27 | 1.3751 | 1.3751 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 61.8119 | 676.8772 | 0 | 0.05921 | 2.8974 | 0 | 0 | 0 | 1.3751 | off_peak | 664.5149 | 0 | 100 | 0.21 | 0 | 99.79 | 3.9842 | 0
6944 | 720.33 | 157.897 | 27.6 | 25.3399 | 25.3399 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 73.3758 | 707.3525 | 0 | 0.05921 | 2.6992 | 0 | 0 | 0 | 25.3399 | off_peak | 694.9901 | 0 | 100 | 3.52 | 0 | 96.48 | 68.3987 | 0
6945 | 740.8 | 375.193 | 27.9 | 60.1467 | 60.1467 | 0 | 0 | 0.79843 | 0.79843 | 0 | 0 | 0 | 74.1227 | 681.4517 | 0 | 0.05921 | 2.5759 | 0 | 0 | 0 | 60.1467 | off_peak | 680.6533 | 0 | 100 | 8.12 | 0 | 91.88 | 154.9314 | 0
6946 | 763.52 | 552.83 | 28.2 | 88.5267 | 88.5267 | 0 | 0 | 0.051567 | 0.051567 | 0 | 0 | 0 | 74.1709 | 675.0448 | 0 | 0.05921 | 2.6168 | 0 | 0 | 0 | 88.5267 | off_peak | 674.9933 | 0 | 100 | 11.59 | 0 | 88.41 | 231.6606 | 0
6947 | 734.42 | 685.085 | 28.4 | 109.6253 | 109.6253 | 0 | 0 | 0.0033305 | 0.0033305 | 0 | 0 | 0 | 74.174 | 624.798 | 0 | 0.05921 | 2.9453 | 0 | 0 | 0 | 109.6253 | off_peak | 624.7947 | 0 | 100 | 14.93 | 0 | 85.07 | 322.8789 | 0
6948 | 761.35 | 757.705 | 28.5 | 121.2016 | 121.2016 | 0 | 0 | 0.0002151 | 0.0002151 | 0 | 0 | 0 | 74.1742 | 640.1486 | 0 | 0.05921 | 3.4397 | 0 | 0 | 0 | 121.2016 | off_peak | 640.1484 | 0 | 100 | 15.92 | 0 | 84.08 | 416.899 | 0
6949 | 749.65 | 517.792 | 28.5 | 82.8254 | 82.8254 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1742 | 666.8246 | 0 | 0.088511 | 3.7073 | 0 | 0 | 0 | 82.8254 | on_peak | 666.8246 |  |  | 11.05 | 0 | 88.95 | 307.0583 | 0
6950 | 769.25 | 368.249 | 28.5 | 58.9047 | 58.9047 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1742 | 710.3453 | 0 | 0.088511 | 3.5354 | 0 | 0 | 0 | 58.9047 | on_peak | 710.3453 |  |  | 7.66 | 0 | 92.34 | 208.2521 | 0
6951 | 786.9 | 549.809 | 28.4 | 87.9789 | 87.9789 | 0 | 0 | 0 | 0 | 62.4453 | 62.4453 | 0 | 7.4174 | 636.4759 | 0 | 0.088511 | 3.0994 | 0 | 0 | 0 | 87.9789 | on_peak | 636.4759 |  |  | 11.18 | 7.94 | 80.88 | 272.6803 | 0
6952 | 673.39 | 192.662 | 28.2 | 30.8517 | 30.8517 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 642.5383 | 0 | 0.088511 | 2.8659 | 0 | 0 | 0 | 30.8517 | on_peak | 642.5383 |  |  | 4.58 | 0 | 95.42 | 88.4164 | 0
6953 | 744.94 | 55.6542 | 28 | 8.9186 | 8.9186 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 736.0214 | 0 | 0.088511 | 2.8308 | 0 | 0 | 0 | 8.9186 | on_peak | 736.0214 |  |  | 1.2 | 0 | 98.8 | 25.2472 | 0
6954 | 753.69 | 31.2771 | 27.7 | 5.0176 | 5.0176 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 748.6724 | 0 | 0.088511 | 2.8265 | 0 | 0 | 0 | 5.0176 | on_peak | 748.6724 |  |  | 0.67 | 0 | 99.33 | 14.1821 | 0
6955 | 750.21 | 0 | 27.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 750.21 | 0 | 0.088511 | 2.9341 | 0 | 0 | 0 | 0 | on_peak | 750.21 |  |  | 0 | 0 | 100 | 0 | 0
6956 | 779.36 | 0 | 27.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 779.36 | 0 | 0.088511 | 3.1257 | 0 | 0 | 0 | 0 | on_peak | 779.36 |  |  | 0 | 0 | 100 | 0 | 0
6957 | 731.07 | 0 | 27.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 731.07 | 0 | 0.088511 | 3.4623 | 0 | 0 | 0 | 0 | on_peak | 731.07 |  |  | 0 | 0 | 100 | 0 | 0
6958 | 713.22 | 0 | 27.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 713.22 | 0 | 0.05921 | 3.9418 | 0 | 0 | 0 | 0 | off_peak | 713.22 |  |  | 0 | 0 | 100 | 0 | 0
6959 | 728.04 | 0 | 27 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 18.9814 | 740.4024 | 0 | 0.05921 | 4.5496 | 0 | 0 | 0 | 0 | off_peak | 728.04 | 0 | 100 | 0 | 0 | 100 | 0 | 0
6960 | 696.54 | 0 | 26.8 | 0 | 0 | 0 | 0 | 8.7006 | 8.7006 | 0 | 0 | 0 | 27.12 | 705.2406 | 0 | 0.05921 | 5.2024 | 0 | 0 | 0 | 0 | off_peak | 696.54 | 0 | 100 | 0 | 0 | 100 | 0 | 0
6961 | 658.97 | 0 | 26.7 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 38.684 | 671.3324 | 0 | 0.05921 | 5.3736 | 0 | 0 | 0 | 0 | off_peak | 658.97 | 0 | 100 | 0 | 0 | 100 | 0 | 0
6962 | 575.11 | 0 | 26.6 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 50.2479 | 587.4724 | 0 | 0.05921 | 5.1004 | 0 | 0 | 0 | 0 | off_peak | 575.11 | 0 | 100 | 0 | 0 | 100 | 0 | 0
6963 | 549.86 | 0 | 26.5 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 61.8119 | 562.2224 | 0 | 0.05921 | 4.6147 | 0 | 0 | 0 | 0 | off_peak | 549.86 | 0 | 100 | 0 | 0 | 100 | 0 | 0
6964 | 574.58 | 0 | 26.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 61.8119 | 574.58 | 0 | 0.05921 | 4.1035 | 0 | 0 | 0 | 0 | off_peak | 574.58 |  |  | 0 | 0 | 100 | 0 | 0
6965 | 564.13 | 0 | 26.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 61.8119 | 564.13 | 0 | 0.05921 | 3.4668 | 0 | 0 | 0 | 0 | off_peak | 564.13 |  |  | 0 | 0 | 100 | 0 | 0
6966 | 593.97 | 0 | 26.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 61.8119 | 593.97 | 0 | 0.05921 | 3.0803 | 0 | 0 | 0 | 0 | off_peak | 593.97 |  |  | 0 | 0 | 100 | 0 | 0
6967 | 628.32 | 15.217 | 26.3 | 2.4536 | 2.4536 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 73.3758 | 638.2288 | 0 | 0.05921 | 2.7972 | 0 | 0 | 0 | 2.4536 | off_peak | 625.8664 | 0 | 100 | 0.39 | 0 | 99.61 | 6.8633 | 0
6968 | 651.6 | 179.898 | 26.7 | 28.9651 | 28.9651 | 0 | 0 | 0.79843 | 0.79843 | 0 | 0 | 0 | 74.1227 | 623.4333 | 0 | 0.05921 | 2.6588 | 0 | 0 | 0 | 28.9651 | off_peak | 622.6349 | 0 | 100 | 4.45 | 0 | 95.55 | 77.0124 | 0
6969 | 773.27 | 386.326 | 26.9 | 62.1567 | 62.1567 | 0 | 0 | 0.051567 | 0.051567 | 0 | 0 | 0 | 74.1709 | 711.1648 | 0 | 0.05921 | 2.5907 | 0 | 0 | 0 | 62.1567 | off_peak | 711.1133 | 0 | 100 | 8.04 | 0 | 91.96 | 161.0297 | 0
6970 | 754.71 | 566.026 | 27.2 | 90.97 | 90.97 | 0 | 0 | 0.0033305 | 0.0033305 | 0 | 0 | 0 | 74.174 | 663.7434 | 0 | 0.05921 | 2.6386 | 0 | 0 | 0 | 90.97 | off_peak | 663.74 | 0 | 100 | 12.05 | 0 | 87.95 | 240.032 | 0
6971 | 767.09 | 522.631 | 27.5 | 83.9042 | 83.9042 | 0 | 0 | 0.0002151 | 0.0002151 | 0 | 0 | 0 | 74.1742 | 683.186 | 0 | 0.05921 | 2.9617 | 0 | 0 | 0 | 83.9042 | off_peak | 683.1858 | 0 | 100 | 10.94 | 0 | 89.06 | 248.4968 | 0
6972 | 785.82 | 597.304 | 27.9 | 95.753 | 95.753 | 0 | 0 | 1.3893e-05 | 1.3893e-05 | 0 | 0 | 0 | 74.1743 | 690.067 | 0 | 0.05921 | 3.5254 | 0 | 0 | 0 | 95.753 | off_peak | 690.067 | 0 | 100 | 12.19 | 0 | 87.81 | 337.5714 | 0
6973 | 749.26 | 313.729 | 28.2 | 50.2386 | 50.2386 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1743 | 699.0214 | 0 | 0.088511 | 3.7698 | 0 | 0 | 0 | 50.2386 | on_peak | 699.0214 |  |  | 6.71 | 0 | 93.29 | 189.3914 | 0
6974 | 845.24 | 413.776 | 28.4 | 66.2112 | 66.2112 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1743 | 779.0288 | 0 | 0.088511 | 3.6202 | 0 | 0 | 0 | 66.2112 | on_peak | 779.0288 |  |  | 7.83 | 0 | 92.17 | 239.697 | 0
6975 | 812.17 | 266.576 | 28.5 | 42.6412 | 42.6412 | 0 | 0 | 0 | 0 | 62.4453 | 62.4453 | 0 | 7.4174 | 707.0835 | 0 | 0.088511 | 3.2141 | 0 | 0 | 0 | 42.6412 | on_peak | 707.0835 |  |  | 5.25 | 7.69 | 87.06 | 137.0538 | 0
6976 | 780.41 | 163.17 | 28.5 | 26.1005 | 26.1005 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 754.3095 | 0 | 0.088511 | 3.0576 | 0 | 0 | 0 | 26.1005 | on_peak | 754.3095 |  |  | 3.34 | 0 | 96.66 | 79.8041 | 0
6977 | 794.47 | 69.4941 | 28.1 | 11.1324 | 11.1324 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 783.3376 | 0 | 0.088511 | 3.1342 | 0 | 0 | 0 | 11.1324 | on_peak | 783.3376 |  |  | 1.4 | 0 | 98.6 | 34.891 | 0
6978 | 769.36 | 17.1 | 27.6 | 2.7443 | 2.7443 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 766.6157 | 0 | 0.088511 | 3.3536 | 0 | 0 | 0 | 2.7443 | on_peak | 766.6157 |  |  | 0.36 | 0 | 99.64 | 9.2032 | 0
6979 | 781.66 | 0 | 27.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 781.66 | 0 | 0.088511 | 3.6594 | 0 | 0 | 0 | 0 | on_peak | 781.66 |  |  | 0 | 0 | 100 | 0 | 0
6980 | 777.46 | 0 | 27 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 777.46 | 0 | 0.088511 | 4.0225 | 0 | 0 | 0 | 0 | on_peak | 777.46 |  |  | 0 | 0 | 100 | 0 | 0
6981 | 773.12 | 0 | 26.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 773.12 | 0 | 0.088511 | 4.4819 | 0 | 0 | 0 | 0 | on_peak | 773.12 |  |  | 0 | 0 | 100 | 0 | 0
6982 | 761.4 | 0 | 26.5 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 18.9814 | 773.7624 | 0 | 0.05921 | 4.9689 | 0 | 0 | 0 | 0 | off_peak | 761.4 | 0 | 100 | 0 | 0 | 100 | 0 | 0
6983 | 742.24 | 0 | 26.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18.9814 | 742.24 | 0 | 0.05921 | 5.5079 | 0 | 0 | 0 | 0 | off_peak | 742.24 |  |  | 0 | 0 | 100 | 0 | 0
6984 | 740.86 | 0 | 26.2 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 30.5453 | 753.2224 | 0 | 0.05921 | 5.9962 | 0 | 0 | 0 | 0 | off_peak | 740.86 | 0 | 100 | 0 | 0 | 100 | 0 | 0
6985 | 707.33 | 0 | 25.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30.5453 | 707.33 | 0 | 0.05921 | 6.0709 | 0 | 0 | 0 | 0 | off_peak | 707.33 |  |  | 0 | 0 | 100 | 0 | 0
6986 | 632.3 | 0 | 24.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30.5453 | 632.3 | 0 | 0.05921 | 5.7511 | 0 | 0 | 0 | 0 | off_peak | 632.3 |  |  | 0 | 0 | 100 | 0 | 0
6987 | 609.54 | 0 | 23.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30.5453 | 609.54 | 0 | 0.05921 | 5.2769 | 0 | 0 | 0 | 0 | off_peak | 609.54 |  |  | 0 | 0 | 100 | 0 | 0
6988 | 612.89 | 0 | 22.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30.5453 | 612.89 | 0 | 0.05921 | 4.7539 | 0 | 0 | 0 | 0 | off_peak | 612.89 |  |  | 0 | 0 | 100 | 0 | 0
6989 | 603.59 | 0 | 21.7 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 42.1093 | 615.9524 | 0 | 0.05921 | 4.1115 | 0 | 0 | 0 | 0 | off_peak | 603.59 | 0 | 100 | 0 | 0 | 100 | 0 | 0
6990 | 638.59 | 0 | 21.1 | 0 | 0 | 0 | 0 | 8.7006 | 8.7006 | 0 | 0 | 0 | 50.2479 | 647.2906 | 0 | 0.05921 | 3.593 | 0 | 0 | 0 | 0 | off_peak | 638.59 | 0 | 100 | 0 | 0 | 100 | 0 | 0
6991 | 638.18 | 3.8 | 20.6 | 0.62535 | 0.62535 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 61.8119 | 649.917 | 0 | 0.05921 | 3.1956 | 0 | 0 | 0 | 0.62535 | off_peak | 637.5546 | 0 | 100 | 0.1 | 0 | 99.9 | 1.9984 | 0
6992 | 749.1 | 67.157 | 20.2 | 11.0674 | 11.0674 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 73.3758 | 750.3949 | 0 | 0.05921 | 2.9952 | 0 | 0 | 0 | 11.0674 | off_peak | 738.0326 | 0 | 100 | 1.48 | 0 | 98.52 | 33.1497 | 0
6993 | 710.28 | 253.314 | 20.2 | 41.746 | 41.746 | 0 | 0 | 0.79843 | 0.79843 | 0 | 0 | 0 | 74.1227 | 669.3324 | 0 | 0.05921 | 2.8805 | 0 | 0 | 0 | 41.746 | off_peak | 668.534 | 0 | 100 | 5.88 | 0 | 94.12 | 120.249 | 0
6994 | 758.85 | 220.682 | 20.4 | 36.3425 | 36.3425 | 0 | 0 | 0.051567 | 0.051567 | 0 | 0 | 0 | 74.1709 | 722.5591 | 0 | 0.05921 | 2.881 | 0 | 0 | 0 | 36.3425 | off_peak | 722.5075 | 0 | 100 | 4.79 | 0 | 95.21 | 104.7022 | 0
6995 | 820.26 | 253.066 | 20.4 | 41.6756 | 41.6756 | 0 | 0 | 0.0033305 | 0.0033305 | 0 | 0 | 0 | 74.174 | 778.5877 | 0 | 0.05921 | 3.1473 | 0 | 0 | 0 | 41.6756 | off_peak | 778.5844 | 0 | 100 | 5.08 | 0 | 94.92 | 131.165 | 0
6996 | 836.54 | 190.375 | 20.4 | 31.3515 | 31.3515 | 0 | 0 | 0.0002151 | 0.0002151 | 0 | 0 | 0 | 74.1742 | 805.1887 | 0 | 0.05921 | 3.6656 | 0 | 0 | 0 | 31.3515 | off_peak | 805.1885 | 0 | 100 | 3.75 | 0 | 96.25 | 114.9223 | 0
6997 | 818.7 | 211.106 | 20.2 | 34.7901 | 34.7901 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1742 | 783.9099 | 0 | 0.088511 | 3.9888 | 0 | 0 | 0 | 34.7901 | on_peak | 783.9099 |  |  | 4.25 | 0 | 95.75 | 138.7707 | 0
6998 | 830.86 | 100.7 | 19.8 | 16.6188 | 16.6188 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1742 | 814.2412 | 0 | 0.088511 | 3.9068 | 0 | 0 | 0 | 16.6188 | on_peak | 814.2412 |  |  | 2 | 0 | 98 | 64.9259 | 0
6999 | 893.32 | 54.15 | 19.2 | 8.9555 | 8.9555 | 0 | 0 | 0 | 0 | 52.5249 | 52.5249 | 0 | 18.0228 | 831.8396 | 0 | 0.088511 | 3.7999 | 0 | 0 | 0 | 8.9555 | on_peak | 831.8396 |  |  | 1 | 5.88 | 93.12 | 34.0297 | 0
7000 | 823.6 | 37.05 | 18.7 | 6.1382 | 6.1382 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18.0228 | 817.4618 | 0 | 0.088511 | 3.8461 | 0 | 0 | 0 | 6.1382 | on_peak | 817.4618 |  |  | 0.75 | 0 | 99.25 | 23.6082 | 0
7001 | 793.3 | 30.67 | 18.5 | 5.0848 | 5.0848 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18.0228 | 788.2152 | 0 | 0.088511 | 4.1009 | 0 | 0 | 0 | 5.0848 | on_peak | 788.2152 |  |  | 0.64 | 0 | 99.36 | 20.8525 | 0
7002 | 815.73 | 8.55 | 18.6 | 1.417 | 1.417 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18.0228 | 814.313 | 0 | 0.088511 | 4.5003 | 0 | 0 | 0 | 1.417 | on_peak | 814.313 |  |  | 0.17 | 0 | 99.83 | 6.3769 | 0
7003 | 818.7 | 0 | 18.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18.0228 | 818.7 | 0 | 0.088511 | 4.8364 | 0 | 0 | 0 | 0 | on_peak | 818.7 |  |  | 0 | 0 | 100 | 0 | 0
7004 | 837.66 | 0 | 19.2 | 0 | 0 | 0 | 0 | 0 | 0 | 9.9204 | 9.9204 | 0 | 7.4174 | 827.7396 | 0 | 0.088511 | 5.2787 | 0 | 0 | 0 | 0 | on_peak | 827.7396 |  |  | 0 | 1.18 | 98.82 | 0 | 0
7005 | 796 | 0 | 19.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 796 | 0 | 0.088511 | 5.6413 | 0 | 0 | 0 | 0 | on_peak | 796 |  |  | 0 | 0 | 100 | 0 | 0
7006 | 775.89 | 0 | 19.8 | 0 | 0 | 0 | 0 | 8.7006 | 8.7006 | 0 | 0 | 0 | 15.5561 | 784.5906 | 0 | 0.05921 | 6.0297 | 0 | 0 | 0 | 0 | off_peak | 775.89 | 0 | 100 | 0 | 0 | 100 | 0 | 0
7007 | 794.9 | 0 | 20 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 27.12 | 807.2624 | 0 | 0.05921 | 6.2571 | 0 | 0 | 0 | 0 | off_peak | 794.9 | 0 | 100 | 0 | 0 | 100 | 0 | 0
7008 | 783.94 | 0 | 20.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27.12 | 783.94 | 0 | 0.05921 | 6.4169 | 0 | 0 | 0 | 0 | off_peak | 783.94 |  |  | 0 | 0 | 100 | 0 | 0
7009 | 680.26 | 0 | 20.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27.12 | 680.26 | 0 | 0.05921 | 6.4725 | 0 | 0 | 0 | 0 | off_peak | 680.26 |  |  | 0 | 0 | 100 | 0 | 0
7010 | 611.53 | 0 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27.12 | 611.53 | 0 | 0.05921 | 6.1492 | 0 | 0 | 0 | 0 | off_peak | 611.53 |  |  | 0 | 0 | 100 | 0 | 0
7011 | 605.43 | 0 | 19.8 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 38.684 | 617.7924 | 0 | 0.05921 | 5.7279 | 0 | 0 | 0 | 0 | off_peak | 605.43 | 0 | 100 | 0 | 0 | 100 | 0 | 0
7012 | 611.51 | 0 | 19.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 38.684 | 611.51 | 0 | 0.05921 | 5.1982 | 0 | 0 | 0 | 0 | off_peak | 611.51 |  |  | 0 | 0 | 100 | 0 | 0
7013 | 620.09 | 0 | 19.6 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 50.2479 | 632.4524 | 0 | 0.05921 | 4.5234 | 0 | 0 | 0 | 0 | off_peak | 620.09 | 0 | 100 | 0 | 0 | 100 | 0 | 0
7014 | 645.8 | 0 | 19.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50.2479 | 645.8 | 0 | 0.05921 | 3.9923 | 0 | 0 | 0 | 0 | off_peak | 645.8 |  |  | 0 | 0 | 100 | 0 | 0
7015 | 686.75 | 11.8011 | 20 | 1.9462 | 1.9462 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 61.8119 | 697.1662 | 0 | 0.05921 | 3.632 | 0 | 0 | 0 | 1.9462 | off_peak | 684.8038 | 0 | 100 | 0.28 | 0 | 99.72 | 7.0686 | 0
7016 | 765.36 | 162.136 | 20.6 | 26.6821 | 26.6821 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 73.3758 | 751.0403 | 0 | 0.05921 | 3.4007 | 0 | 0 | 0 | 26.6821 | off_peak | 738.6779 | 0 | 100 | 3.49 | 0 | 96.51 | 90.7381 | 0
7017 | 821.37 | 359.937 | 21.3 | 59.0865 | 59.0865 | 0 | 0 | 0.79843 | 0.79843 | 0 | 0 | 0 | 74.1227 | 763.082 | 0 | 0.05921 | 3.2651 | 0 | 0 | 0 | 59.0865 | off_peak | 762.2835 | 0 | 100 | 7.19 | 0 | 92.81 | 192.924 | 0
7018 | 855.73 | 539.936 | 22.1 | 88.3828 | 88.3828 | 0 | 0 | 0.051567 | 0.051567 | 0 | 0 | 0 | 74.1709 | 767.3988 | 0 | 0.05921 | 3.2566 | 0 | 0 | 0 | 88.3828 | off_peak | 767.3472 | 0 | 100 | 10.33 | 0 | 89.67 | 287.8237 | 0
7019 | 836.79 | 657.693 | 23.1 | 107.275 | 107.275 | 0 | 0 | 0.0033305 | 0.0033305 | 0 | 0 | 0 | 74.174 | 729.5183 | 0 | 0.05921 | 3.4681 | 0 | 0 | 0 | 107.275 | off_peak | 729.515 | 0 | 100 | 12.82 | 0 | 87.18 | 372.0363 | 0
7020 | 882.73 | 422.464 | 24 | 68.6855 | 68.6855 | 0 | 0 | 0.0002151 | 0.0002151 | 0 | 0 | 0 | 74.1742 | 814.0447 | 0 | 0.05921 | 3.9406 | 0 | 0 | 0 | 68.6855 | off_peak | 814.0445 | 0 | 100 | 7.78 | 0 | 92.22 | 270.6618 | 0
7021 | 839.95 | 475.493 | 24.7 | 77.1131 | 77.1131 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1742 | 762.8369 | 0 | 0.088511 | 4.2243 | 0 | 0 | 0 | 77.1131 | on_peak | 762.8369 |  |  | 9.18 | 0 | 90.82 | 325.7505 | 0
7022 | 867.01 | 619.977 | 25.2 | 100.364 | 100.364 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1742 | 766.646 | 0 | 0.088511 | 4.1804 | 0 | 0 | 0 | 100.364 | on_peak | 766.646 |  |  | 11.58 | 0 | 88.42 | 419.5645 | 0
7023 | 879.03 | 578.569 | 25.5 | 93.5595 | 93.5595 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1742 | 785.4705 | 0 | 0.088511 | 3.8631 | 0 | 0 | 0 | 93.5595 | on_peak | 785.4705 |  |  | 10.64 | 0 | 89.36 | 361.4303 | 0
7024 | 839.95 | 405.967 | 25.5 | 65.6483 | 65.6483 | 0 | 0 | 0 | 0 | 24.0978 | 24.0978 | 0 | 48.4127 | 750.204 | 0 | 0.088511 | 3.7747 | 0 | 0 | 0 | 65.6483 | on_peak | 750.204 |  |  | 7.82 | 2.87 | 89.32 | 247.8036 | 0
7025 | 821.88 | 204.002 | 25.2 | 33.0245 | 33.0245 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 48.4127 | 788.8555 | 0 | 0.088511 | 4.0019 | 0 | 0 | 0 | 33.0245 | on_peak | 788.8555 |  |  | 4.02 | 0 | 95.98 | 132.1601 | 0
7026 | 842.7 | 26.0933 | 24.6 | 4.2332 | 4.2332 | 0 | 0 | 0 | 0 | 6.6272 | 6.6272 | 0 | 41.3279 | 831.8396 | 0 | 0.088511 | 4.5263 | 0 | 0 | 0 | 4.2332 | on_peak | 831.8396 |  |  | 0.5 | 0.79 | 98.71 | 19.1609 | 0
7027 | 786.6 | 0 | 24.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 41.3279 | 786.6 | 0 | 0.088511 | 5.1024 | 0 | 0 | 0 | 0 | on_peak | 786.6 |  |  | 0 | 0 | 100 | 0 | 0
7028 | 863.56 | 0 | 23.7 | 0 | 0 | 0 | 0 | 0 | 0 | 31.7204 | 31.7204 | 0 | 7.4174 | 831.8396 | 0 | 0.088511 | 5.3543 | 0 | 0 | 0 | 0 | on_peak | 831.8396 |  |  | 0 | 3.67 | 96.33 | 0 | 0
7029 | 770.81 | 0 | 23.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 770.81 | 0 | 0.088511 | 5.6922 | 0 | 0 | 0 | 0 | on_peak | 770.81 |  |  | 0 | 0 | 100 | 0 | 0
7030 | 777.63 | 0 | 23.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 777.63 | 0 | 0.05921 | 5.8952 | 0 | 0 | 0 | 0 | off_peak | 777.63 |  |  | 0 | 0 | 100 | 0 | 0
7031 | 809.19 | 0 | 23 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 18.9814 | 821.5524 | 0 | 0.05921 | 6.2454 | 0 | 0 | 0 | 0 | off_peak | 809.19 | 0 | 100 | 0 | 0 | 100 | 0 | 0
7032 | 780.78 | 0 | 22.7 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 30.5453 | 793.1424 | 0 | 0.05921 | 6.6286 | 0 | 0 | 0 | 0 | off_peak | 780.78 | 0 | 100 | 0 | 0 | 100 | 0 | 0
7033 | 698.6 | 0 | 22.4 | 0 | 0 | 0 | 0 | 8.7006 | 8.7006 | 0 | 0 | 0 | 38.684 | 707.3006 | 0 | 0.05921 | 6.4382 | 0 | 0 | 0 | 0 | off_peak | 698.6 | 0 | 100 | 0 | 0 | 100 | 0 | 0
7034 | 668.7 | 0 | 22.1 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 50.2479 | 681.0624 | 0 | 0.05921 | 6.093 | 0 | 0 | 0 | 0 | off_peak | 668.7 | 0 | 100 | 0 | 0 | 100 | 0 | 0
7035 | 647.87 | 0 | 21.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50.2479 | 647.87 | 0 | 0.05921 | 5.7171 | 0 | 0 | 0 | 0 | off_peak | 647.87 |  |  | 0 | 0 | 100 | 0 | 0
7036 | 621.1 | 0 | 21.4 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 61.8119 | 633.4624 | 0 | 0.05921 | 5.1802 | 0 | 0 | 0 | 0 | off_peak | 621.1 | 0 | 100 | 0 | 0 | 100 | 0 | 0
7037 | 634.62 | 0 | 21.2 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 73.3758 | 646.9824 | 0 | 0.05921 | 4.6249 | 0 | 0 | 0 | 0 | off_peak | 634.62 | 0 | 100 | 0 | 0 | 100 | 0 | 0
7038 | 707.27 | 0 | 21.1 | 0 | 0 | 0 | 0 | 0.79843 | 0.79843 | 0 | 0 | 0 | 74.1227 | 708.0684 | 0 | 0.05921 | 4.0982 | 0 | 0 | 0 | 0 | off_peak | 707.27 | 0 | 100 | 0 | 0 | 100 | 0 | 0
7039 | 667.91 | 12.8156 | 21.2 | 2.1045 | 2.1045 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1227 | 665.8055 | 0 | 0.05921 | 3.6343 | 0 | 0 | 0 | 2.1045 | off_peak | 665.8055 |  |  | 0.32 | 0 | 99.68 | 7.6485 | 0
7040 | 694.08 | 167.613 | 21.7 | 27.4759 | 27.4759 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1227 | 666.6041 | 0 | 0.05921 | 3.3611 | 0 | 0 | 0 | 27.4759 | off_peak | 666.6041 |  |  | 3.96 | 0 | 96.04 | 92.3484 | 0
7041 | 756.48 | 370.531 | 22.5 | 60.5663 | 60.5663 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1227 | 695.9137 | 0 | 0.05921 | 3.1669 | 0 | 0 | 0 | 60.5663 | off_peak | 695.9137 |  |  | 8.01 | 0 | 91.99 | 191.807 | 0
7042 | 700.46 | 516.906 | 23.5 | 84.191 | 84.191 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1227 | 616.269 | 0 | 0.05921 | 3.0736 | 0 | 0 | 0 | 84.191 | off_peak | 616.269 |  |  | 12.02 | 0 | 87.98 | 258.7727 | 0
7043 | 745.13 | 292.375 | 24.6 | 47.433 | 47.433 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1227 | 697.697 | 0 | 0.05921 | 3.0954 | 0 | 0 | 0 | 47.433 | off_peak | 697.697 |  |  | 6.37 | 0 | 93.63 | 146.8217 | 0
7044 | 728.11 | 678.067 | 25.4 | 109.6887 | 109.6887 | 0 | 0 | 0.051567 | 0.051567 | 0 | 0 | 0 | 74.1709 | 618.4729 | 0 | 0.05921 | 3.2349 | 0 | 0 | 0 | 109.6887 | off_peak | 618.4213 | 0 | 100 | 15.06 | 0 | 84.94 | 354.8298 | 0
7045 | 706.2 | 573.748 | 25.8 | 92.6795 | 92.6795 | 0 | 0 | 0.0033305 | 0.0033305 | 0 | 0 | 0 | 74.174 | 613.5238 | 0 | 0.05921 | 3.501 | 0 | 0 | 0 | 92.6795 | off_peak | 613.5205 | 0 | 100 | 13.12 | 0 | 86.88 | 324.4692 | 0
7046 | 693.22 | 440.457 | 26 | 71.0972 | 71.0972 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.174 | 622.1228 | 0 | 0.05921 | 3.7506 | 0 | 0 | 0 | 71.0972 | off_peak | 622.1228 |  |  | 10.26 | 0 | 89.74 | 266.6567 | 0
7047 | 711.17 | 337.219 | 25.9 | 54.4525 | 54.4525 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.174 | 656.7175 | 0 | 0.05921 | 3.7774 | 0 | 0 | 0 | 54.4525 | off_peak | 656.7175 |  |  | 7.66 | 0 | 92.34 | 205.691 | 0
7048 | 690.19 | 165.277 | 25.6 | 26.717 | 26.717 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.174 | 663.473 | 0 | 0.05921 | 4.0014 | 0 | 0 | 0 | 26.717 | off_peak | 663.473 |  |  | 3.87 | 0 | 96.13 | 106.9064 | 0
7049 | 695.05 | 52.6119 | 25.1 | 8.5201 | 8.5201 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.174 | 686.5299 | 0 | 0.05921 | 4.3495 | 0 | 0 | 0 | 8.5201 | off_peak | 686.5299 |  |  | 1.23 | 0 | 98.77 | 37.0579 | 0
7050 | 655.66 | 25.6207 | 24.5 | 4.158 | 4.158 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.174 | 651.502 | 0 | 0.05921 | 4.7504 | 0 | 0 | 0 | 4.158 | off_peak | 651.502 |  |  | 0.63 | 0 | 99.37 | 19.7524 | 0
7051 | 598.7 | 0 | 24.1 | 0 | 0 | 0 | 0 | 0.0002151 | 0.0002151 | 0 | 0 | 0 | 74.1742 | 598.7002 | 0 | 0.05921 | 5.2064 | 0 | 0 | 0 | 0 | off_peak | 598.7 | 0 | 100 | 0 | 0 | 100 | 0 | 0
7052 | 589.08 | 0 | 23.9 | 0 | 0 | 0 | 0 | 1.4852e-05 | 1.4852e-05 | 0 | 0 | 0 | 74.1743 | 589.08 | 0 | 0.05921 | 5.6379 | 0 | 0 | 0 | 0 | off_peak | 589.08 | 0 | 100 | 0 | 0 | 100 | 0 | 0
7053 | 578.6 | 0 | 23.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1743 | 578.6 | 0 | 0.05921 | 6.0591 | 0 | 0 | 0 | 0 | off_peak | 578.6 |  |  | 0 | 0 | 100 | 0 | 0
7054 | 582.04 | 0 | 23.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1743 | 582.04 | 0 | 0.05921 | 6.4835 | 0 | 0 | 0 | 0 | off_peak | 582.04 |  |  | 0 | 0 | 100 | 0 | 0
7055 | 577.68 | 0 | 23.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1743 | 577.68 | 0 | 0.05921 | 6.8953 | 0 | 0 | 0 | 0 | off_peak | 577.68 |  |  | 0 | 0 | 100 | 0 | 0
7056 | 577.77 | 0 | 23.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1743 | 577.77 | 0 | 0.05921 | 6.9404 | 0 | 0 | 0 | 0 | off_peak | 577.77 |  |  | 0 | 0 | 100 | 0 | 0
7057 | 580.27 | 0 | 22.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1743 | 580.27 | 0 | 0.05921 | 6.7314 | 0 | 0 | 0 | 0 | off_peak | 580.27 |  |  | 0 | 0 | 100 | 0 | 0
7058 | 604.33 | 0 | 22.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1743 | 604.33 | 0 | 0.05921 | 6.2768 | 0 | 0 | 0 | 0 | off_peak | 604.33 |  |  | 0 | 0 | 100 | 0 | 0
7059 | 606.87 | 0 | 22.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1743 | 606.87 | 0 | 0.05921 | 5.8426 | 0 | 0 | 0 | 0 | off_peak | 606.87 |  |  | 0 | 0 | 100 | 0 | 0
7060 | 589.79 | 0 | 22.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1743 | 589.79 | 0 | 0.05921 | 5.2933 | 0 | 0 | 0 | 0 | off_peak | 589.79 |  |  | 0 | 0 | 100 | 0 | 0
7061 | 602.44 | 0 | 22.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1743 | 602.44 | 0 | 0.05921 | 4.7187 | 0 | 0 | 0 | 0 | off_peak | 602.44 |  |  | 0 | 0 | 100 | 0 | 0
7062 | 618.93 | 0 | 22.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1743 | 618.93 | 0 | 0.05921 | 4.233 | 0 | 0 | 0 | 0 | off_peak | 618.93 |  |  | 0 | 0 | 100 | 0 | 0
7063 | 653.76 | 11.2661 | 22.7 | 1.8402 | 1.8402 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1743 | 651.9198 | 0 | 0.05921 | 3.8582 | 0 | 0 | 0 | 1.8402 | off_peak | 651.9198 |  |  | 0.28 | 0 | 99.72 | 7.1 | 0
7064 | 681.57 | 175.677 | 23.3 | 28.6338 | 28.6338 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1743 | 652.9362 | 0 | 0.05921 | 3.5609 | 0 | 0 | 0 | 28.6338 | off_peak | 652.9362 |  |  | 4.2 | 0 | 95.8 | 101.9626 | 0
7065 | 666.41 | 382.862 | 24.1 | 62.2246 | 62.2246 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1743 | 604.1854 | 0 | 0.05921 | 3.3558 | 0 | 0 | 0 | 62.2246 | off_peak | 604.1854 |  |  | 9.34 | 0 | 90.66 | 208.8118 | 0
7066 | 678.66 | 567.341 | 25.1 | 91.8762 | 91.8762 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1743 | 586.7838 | 0 | 0.05921 | 3.239 | 0 | 0 | 0 | 91.8762 | off_peak | 586.7838 |  |  | 13.54 | 0 | 86.46 | 297.5899 | 0
7067 | 689.22 | 701.589 | 26.1 | 113.2073 | 113.2073 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1743 | 576.0127 | 0 | 0.05921 | 3.2163 | 0 | 0 | 0 | 113.2073 | off_peak | 576.0127 |  |  | 16.43 | 0 | 83.57 | 364.1121 | 0
7068 | 696.34 | 607.554 | 26.6 | 97.8568 | 97.8568 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1743 | 598.4832 | 0 | 0.05921 | 3.2933 | 0 | 0 | 0 | 97.8568 | off_peak | 598.4832 |  |  | 14.05 | 0 | 85.95 | 322.2693 | 0
7069 | 685.33 | 483.524 | 27 | 77.7669 | 77.7669 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1743 | 607.5631 | 0 | 0.05921 | 3.46 | 0 | 0 | 0 | 77.7669 | off_peak | 607.5631 |  |  | 11.35 | 0 | 88.65 | 269.0715 | 0
7070 | 704.89 | 422.911 | 27.1 | 67.9936 | 67.9936 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1743 | 636.8964 | 0 | 0.05921 | 3.7301 | 0 | 0 | 0 | 67.9936 | off_peak | 636.8964 |  |  | 9.65 | 0 | 90.35 | 253.6237 | 0
7071 | 657.55 | 521.451 | 27.1 | 83.8364 | 83.8364 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1743 | 573.7136 | 0 | 0.05921 | 3.9404 | 0 | 0 | 0 | 83.8364 | off_peak | 573.7136 |  |  | 12.75 | 0 | 87.25 | 330.3468 | 0
7072 | 666.59 | 418.702 | 26.9 | 67.3658 | 67.3658 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1743 | 599.2242 | 0 | 0.05921 | 4.0194 | 0 | 0 | 0 | 67.3658 | off_peak | 599.2242 |  |  | 10.11 | 0 | 89.89 | 270.7722 | 0
7073 | 657.51 | 215.004 | 26.5 | 34.6426 | 34.6426 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1743 | 622.8674 | 0 | 0.05921 | 4.2152 | 0 | 0 | 0 | 34.6426 | off_peak | 622.8674 |  |  | 5.27 | 0 | 94.73 | 146.0254 | 0
7074 | 602.84 | 29.3058 | 25.8 | 4.7339 | 4.7339 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1743 | 598.1061 | 0 | 0.05921 | 4.5498 | 0 | 0 | 0 | 4.7339 | off_peak | 598.1061 |  |  | 0.79 | 0 | 99.21 | 21.538 | 0
7075 | 562.98 | 0 | 25.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1743 | 562.98 | 0 | 0.05921 | 4.9589 | 0 | 0 | 0 | 0 | off_peak | 562.98 |  |  | 0 | 0 | 100 | 0 | 0
7076 | 562.28 | 0 | 25.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1743 | 562.28 | 0 | 0.05921 | 5.4154 | 0 | 0 | 0 | 0 | off_peak | 562.28 |  |  | 0 | 0 | 100 | 0 | 0
7077 | 560.68 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1743 | 560.68 | 0 | 0.05921 | 5.86 | 0 | 0 | 0 | 0 | off_peak | 560.68 |  |  | 0 | 0 | 100 | 0 | 0
7078 | 541.8 | 0 | 24.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1743 | 541.8 | 0 | 0.05921 | 6.3953 | 0 | 0 | 0 | 0 | off_peak | 541.8 |  |  | 0 | 0 | 100 | 0 | 0
7079 | 566.68 | 0 | 24.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1743 | 566.68 | 0 | 0.05921 | 6.7241 | 0 | 0 | 0 | 0 | off_peak | 566.68 |  |  | 0 | 0 | 100 | 0 | 0
7080 | 550.03 | 0 | 24.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1743 | 550.03 | 0 | 0.05921 | 6.7553 | 0 | 0 | 0 | 0 | off_peak | 550.03 |  |  | 0 | 0 | 100 | 0 | 0
7081 | 555.53 | 0 | 24.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1743 | 555.53 | 0 | 0.05921 | 6.7105 | 0 | 0 | 0 | 0 | off_peak | 555.53 |  |  | 0 | 0 | 100 | 0 | 0
7082 | 537.9 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1743 | 537.9 | 0 | 0.05921 | 6.3072 | 0 | 0 | 0 | 0 | off_peak | 537.9 |  |  | 0 | 0 | 100 | 0 | 0
7083 | 529.02 | 0 | 23.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1743 | 529.02 | 0 | 0.05921 | 5.7613 | 0 | 0 | 0 | 0 | off_peak | 529.02 |  |  | 0 | 0 | 100 | 0 | 0
7084 | 554.49 | 0 | 23.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1743 | 554.49 | 0 | 0.05921 | 5.0799 | 0 | 0 | 0 | 0 | off_peak | 554.49 |  |  | 0 | 0 | 100 | 0 | 0
7085 | 543.57 | 0 | 23.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1743 | 543.57 | 0 | 0.05921 | 4.375 | 0 | 0 | 0 | 0 | off_peak | 543.57 |  |  | 0 | 0 | 100 | 0 | 0
7086 | 572.18 | 0 | 23.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1743 | 572.18 | 0 | 0.05921 | 3.7928 | 0 | 0 | 0 | 0 | off_peak | 572.18 |  |  | 0 | 0 | 100 | 0 | 0
7087 | 643.38 | 11.3978 | 23.9 | 1.8538 | 1.8538 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1743 | 641.5262 | 0 | 0.05921 | 3.4058 | 0 | 0 | 0 | 1.8538 | off_peak | 641.5262 |  |  | 0.29 | 0 | 99.71 | 6.3135 | 0
7088 | 739.44 | 179.618 | 24.7 | 29.1295 | 29.1295 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1743 | 710.3105 | 0 | 0.05921 | 3.1755 | 0 | 0 | 0 | 29.1295 | off_peak | 710.3105 |  |  | 3.94 | 0 | 96.06 | 92.5016 | 0
7089 | 765.24 | 388.801 | 25.5 | 62.8724 | 62.8724 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1743 | 702.3676 | 0 | 0.05921 | 3.0438 | 0 | 0 | 0 | 62.8724 | off_peak | 702.3676 |  |  | 8.22 | 0 | 91.78 | 191.3735 | 0
7090 | 827.56 | 571.916 | 26.2 | 92.2501 | 92.2501 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1743 | 735.3099 | 0 | 0.05921 | 3.0536 | 0 | 0 | 0 | 92.2501 | off_peak | 735.3099 |  |  | 11.15 | 0 | 88.85 | 281.6936 | 0
7091 | 761.29 | 643.006 | 26.8 | 103.492 | 103.492 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1743 | 657.798 | 0 | 0.05921 | 3.2996 | 0 | 0 | 0 | 103.492 | off_peak | 657.798 |  |  | 13.59 | 0 | 86.41 | 341.4825 | 0
7092 | 876.96 | 762.677 | 27.1 | 122.6196 | 122.6196 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1743 | 754.3404 | 0 | 0.05921 | 3.791 | 0 | 0 | 0 | 122.6196 | off_peak | 754.3404 |  |  | 13.98 | 0 | 86.02 | 464.8457 | 0
7093 | 811.72 | 742.546 | 27.4 | 119.2531 | 119.2531 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1743 | 692.4669 | 0 | 0.088511 | 4.091 | 0 | 0 | 0 | 119.2531 | on_peak | 692.4669 |  |  | 14.69 | 0 | 85.31 | 487.8618 | 0
7094 | 842.82 | 717.907 | 27.5 | 115.2542 | 115.2542 | 0 | 0 | 0 | 0 | 53.9396 | 53.9396 | 0 | 16.5104 | 673.6262 | 0 | 0.088511 | 4.0512 | 0 | 0 | 0 | 115.2542 | on_peak | 673.6262 |  |  | 13.67 | 6.4 | 79.93 | 466.9155 | 0
7095 | 895.93 | 582.308 | 27.4 | 93.5189 | 93.5189 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16.5104 | 802.4111 | 0 | 0.088511 | 3.8971 | 0 | 0 | 0 | 93.5189 | on_peak | 802.4111 |  |  | 10.44 | 0 | 89.56 | 364.452 | 0
7096 | 803.23 | 416.313 | 27.2 | 66.9086 | 66.9086 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16.5104 | 736.3214 | 0 | 0.088511 | 4.0302 | 0 | 0 | 0 | 66.9086 | on_peak | 736.3214 |  |  | 8.33 | 0 | 91.67 | 269.6569 | 0
7097 | 822.73 | 212.439 | 26.7 | 34.2045 | 34.2045 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16.5104 | 788.5255 | 0 | 0.088511 | 4.4235 | 0 | 0 | 0 | 34.2045 | on_peak | 788.5255 |  |  | 4.16 | 0 | 95.84 | 151.3052 | 0
7098 | 839.46 | 26.4223 | 26 | 4.265 | 4.265 | 0 | 0 | 0 | 0 | 3.3554 | 3.3554 | 0 | 12.9234 | 831.8396 | 0 | 0.088511 | 4.8317 | 0 | 0 | 0 | 4.265 | on_peak | 831.8396 |  |  | 0.51 | 0.4 | 99.09 | 20.6073 | 0
7099 | 795.12 | 0 | 25.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12.9234 | 795.12 | 0 | 0.088511 | 5.3963 | 0 | 0 | 0 | 0 | on_peak | 795.12 |  |  | 0 | 0 | 100 | 0 | 0
7100 | 836.99 | 0 | 25.3 | 0 | 0 | 0 | 0 | 0 | 0 | 5.1504 | 5.1504 | 0 | 7.4174 | 831.8396 | 0 | 0.088511 | 5.8339 | 0 | 0 | 0 | 0 | on_peak | 831.8396 |  |  | 0 | 0.62 | 99.38 | 0 | 0
7101 | 819.8 | 0 | 25.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 819.8 | 0 | 0.088511 | 6.3854 | 0 | 0 | 0 | 0 | on_peak | 819.8 |  |  | 0 | 0 | 100 | 0 | 0
7102 | 777.49 | 0 | 24.9 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 18.9814 | 789.8524 | 0 | 0.05921 | 6.9066 | 0 | 0 | 0 | 0 | off_peak | 777.49 | 0 | 100 | 0 | 0 | 100 | 0 | 0
7103 | 793.43 | 0 | 24.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18.9814 | 793.43 | 0 | 0.05921 | 7.1231 | 0 | 0 | 0 | 0 | off_peak | 793.43 |  |  | 0 | 0 | 100 | 0 | 0
7104 | 755.14 | 0 | 24.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18.9814 | 755.14 | 0 | 0.05921 | 7.4132 | 0 | 0 | 0 | 0 | off_peak | 755.14 |  |  | 0 | 0 | 100 | 0 | 0
7105 | 720.4 | 0 | 24.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18.9814 | 720.4 | 0 | 0.05921 | 7.2752 | 0 | 0 | 0 | 0 | off_peak | 720.4 |  |  | 0 | 0 | 100 | 0 | 0
7106 | 616.28 | 0 | 24.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18.9814 | 616.28 | 0 | 0.05921 | 6.7232 | 0 | 0 | 0 | 0 | off_peak | 616.28 |  |  | 0 | 0 | 100 | 0 | 0
7107 | 622.82 | 0 | 24.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18.9814 | 622.82 | 0 | 0.05921 | 6.2747 | 0 | 0 | 0 | 0 | off_peak | 622.82 |  |  | 0 | 0 | 100 | 0 | 0
7108 | 622.45 | 0 | 24.4 | 0 | 0 | 0 | 0 | 8.7006 | 8.7006 | 0 | 0 | 0 | 27.12 | 631.1506 | 0 | 0.05921 | 5.6266 | 0 | 0 | 0 | 0 | off_peak | 622.45 | 0 | 100 | 0 | 0 | 100 | 0 | 0
7109 | 591.14 | 0 | 24.4 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 38.684 | 603.5024 | 0 | 0.05921 | 4.9748 | 0 | 0 | 0 | 0 | off_peak | 591.14 | 0 | 100 | 0 | 0 | 100 | 0 | 0
7110 | 629.68 | 0 | 24.4 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 50.2479 | 642.0424 | 0 | 0.05921 | 4.3522 | 0 | 0 | 0 | 0 | off_peak | 629.68 | 0 | 100 | 0 | 0 | 100 | 0 | 0
7111 | 688.69 | 11.4196 | 24.7 | 1.852 | 0 | 0 | 1.852 | 12.3624 | 10.5104 | 0 | 0 | 0 | 61.8119 | 699.2004 | 0 | 0.05921 | 3.9423 | 0 | 0 | 1.7324 | 0 | off_peak | 688.69 | 14.98 | 85.02 | 0 | 0 | 100 | 0 | 0
7112 | 750.09 | 176.419 | 25.5 | 28.5284 | 28.5284 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 73.3758 | 733.9239 | 0 | 0.05921 | 3.7348 | 0 | 0 | 1.7324 | 28.5284 | off_peak | 721.5616 | 0 | 100 | 3.8 | 0 | 96.2 | 106.5471 | 0
7113 | 784.3 | 366.69 | 26.2 | 59.1472 | 59.1472 | 0 | 0 | 0.79843 | 0.79843 | 0 | 0 | 0 | 74.1227 | 725.9513 | 0 | 0.05921 | 3.5881 | 0 | 0 | 1.7324 | 59.1472 | off_peak | 725.1528 | 0 | 100 | 7.54 | 0 | 92.46 | 212.2267 | 0
7114 | 806.28 | 487.952 | 26.7 | 78.5644 | 78.5644 | 0 | 0 | 0.051567 | 0.051567 | 0 | 0 | 0 | 74.1709 | 727.7671 | 0 | 0.05921 | 3.5696 | 0 | 0 | 1.7324 | 78.5644 | off_peak | 727.7156 | 0 | 100 | 9.74 | 0 | 90.26 | 280.4448 | 0
7115 | 791.36 | 274.368 | 27.1 | 44.1116 | 44.1116 | 0 | 0 | 0.0033305 | 0.0033305 | 0 | 0 | 0 | 74.174 | 747.2517 | 0 | 0.05921 | 3.8097 | 0 | 0 | 1.7324 | 44.1116 | off_peak | 747.2484 | 0 | 100 | 5.57 | 0 | 94.43 | 168.0528 | 0
7116 | 895.2 | 294.01 | 27.3 | 47.2352 | 47.2352 | 0 | 0 | 0.0002151 | 0.0002151 | 0 | 0 | 0 | 74.1742 | 847.965 | 0 | 0.05921 | 4.3091 | 0 | 0 | 1.7324 | 47.2352 | off_peak | 847.9648 | 0 | 100 | 5.28 | 0 | 94.72 | 203.5425 | 0
7117 | 826.58 | 515.256 | 27.5 | 82.7202 | 82.7202 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1742 | 743.8598 | 0 | 0.088511 | 4.5587 | 0 | 0 | 1.7324 | 82.7202 | on_peak | 743.8598 |  |  | 10.01 | 0 | 89.99 | 377.094 | 0
7118 | 869.34 | 705.685 | 27.5 | 113.2921 | 113.2921 | 0 | 0 | 0 | 0 | 1.6205 | 1.6205 | 0 | 72.4419 | 754.4274 | 0 | 0.088511 | 4.6194 | 1.6205 | 0 | 0 | 114.9126 | on_peak | 754.4274 |  |  | 13.03 | 0.19 | 86.78 | 530.8295 | 0
7119 | 926.22 | 581.472 | 27.3 | 93.4185 | 93.4185 | 0 | 0 | 0 | 0 | 0.96186 | 0.96186 | 0 | 71.4136 | 831.8396 | 0 | 0.088511 | 4.5639 | 0 | 0 | 0 | 93.4185 | on_peak | 831.8396 |  |  | 10.09 | 0.1 | 89.81 | 426.349 | 0
7120 | 833.91 | 409.149 | 27.1 | 65.781 | 65.781 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 71.4136 | 768.129 | 0 | 0.088511 | 4.7006 | 0 | 0 | 0 | 65.781 | on_peak | 768.129 |  |  | 7.89 | 0 | 92.11 | 309.213 | 0
7121 | 846.86 | 208.157 | 26.6 | 33.5272 | 33.5272 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 71.4136 | 813.3328 | 0 | 0.088511 | 4.9615 | 0 | 0 | 0 | 33.5272 | on_peak | 813.3328 |  |  | 3.96 | 0 | 96.04 | 166.3463 | 0
7122 | 819.46 | 25.1946 | 26 | 4.0668 | 4.0668 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 71.4136 | 815.3932 | 0 | 0.088511 | 5.3417 | 0 | 0 | 0 | 4.0668 | on_peak | 815.3932 |  |  | 0.5 | 0 | 99.5 | 21.724 | 0
7123 | 859.3 | 0 | 25.6 | 0 | 0 | 0 | 0 | 0 | 0 | 27.4604 | 27.4604 | 0 | 42.0572 | 831.8396 | 0 | 0.088511 | 5.6009 | 0 | 0 | 0 | 0 | on_peak | 831.8396 |  |  | 0 | 3.2 | 96.8 | 0 | 0
7124 | 846.83 | 0 | 25.4 | 0 | 0 | 0 | 0 | 0 | 0 | 32.4026 | 32.4026 | 0 | 7.4174 | 814.4274 | 0 | 0.088511 | 5.7898 | 0 | 0 | 0 | 0 | on_peak | 814.4274 |  |  | 0 | 3.83 | 96.17 | 0 | 0
7125 | 826.81 | 0 | 25.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 826.81 | 0 | 0.088511 | 6.0158 | 0 | 0 | 0 | 0 | on_peak | 826.81 |  |  | 0 | 0 | 100 | 0 | 0
7126 | 817.32 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 817.32 | 0 | 0.05921 | 6.3219 | 0 | 0 | 0 | 0 | off_peak | 817.32 |  |  | 0 | 0 | 100 | 0 | 0
7127 | 807.6 | 0 | 24.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 807.6 | 0 | 0.05921 | 6.6944 | 0 | 0 | 0 | 0 | off_peak | 807.6 |  |  | 0 | 0 | 100 | 0 | 0
7128 | 806.63 | 0 | 24.7 | 0 | 0 | 0 | 0 | 8.7006 | 8.7006 | 0 | 0 | 0 | 15.5561 | 815.3306 | 0 | 0.05921 | 7.0073 | 0 | 0 | 0 | 0 | off_peak | 806.63 | 0 | 100 | 0 | 0 | 100 | 0 | 0
7129 | 746.22 | 0 | 24.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15.5561 | 746.22 | 0 | 0.05921 | 7.0681 | 0 | 0 | 0 | 0 | off_peak | 746.22 |  |  | 0 | 0 | 100 | 0 | 0
7130 | 637.35 | 0 | 24.4 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 27.12 | 649.7124 | 0 | 0.05921 | 6.7347 | 0 | 0 | 0 | 0 | off_peak | 637.35 | 0 | 100 | 0 | 0 | 100 | 0 | 0
7131 | 656.72 | 0 | 24.3 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 38.684 | 669.0824 | 0 | 0.05921 | 6.2591 | 0 | 0 | 0 | 0 | off_peak | 656.72 | 0 | 100 | 0 | 0 | 100 | 0 | 0
7132 | 600.02 | 0 | 24.2 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 50.2479 | 612.3824 | 0 | 0.05921 | 6.0266 | 0 | 0 | 0 | 0 | off_peak | 600.02 | 0 | 100 | 0 | 0 | 100 | 0 | 0
7133 | 627.08 | 0 | 24.1 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 61.8119 | 639.4424 | 0 | 0.05921 | 5.3331 | 0 | 0 | 0 | 0 | off_peak | 627.08 | 0 | 100 | 0 | 0 | 100 | 0 | 0
7134 | 650.92 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 61.8119 | 650.92 | 0 | 0.05921 | 4.8169 | 0 | 0 | 0 | 0 | off_peak | 650.92 |  |  | 0 | 0 | 100 | 0 | 0
7135 | 701.7 | 10.119 | 24.3 | 1.6434 | 1.6434 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 73.3758 | 712.419 | 0 | 0.05921 | 4.3543 | 0 | 0 | 0 | 1.6434 | off_peak | 700.0566 | 0 | 100 | 0.23 | 0 | 99.77 | 7.1558 | 0
7136 | 795.41 | 171.674 | 25 | 27.8112 | 27.8112 | 0 | 0 | 0.79843 | 0.79843 | 0 | 0 | 0 | 74.1227 | 768.3972 | 0 | 0.05921 | 4.1221 | 0 | 0 | 0 | 27.8112 | off_peak | 767.5988 | 0 | 100 | 3.5 | 0 | 96.5 | 114.6416 | 0
7137 | 818.59 | 383.594 | 25.7 | 61.9856 | 61.9856 | 0 | 0 | 0.051567 | 0.051567 | 0 | 0 | 0 | 74.1709 | 756.6559 | 0 | 0.05921 | 3.973 | 0 | 0 | 0 | 61.9856 | off_peak | 756.6044 | 0 | 100 | 7.57 | 0 | 92.43 | 246.2661 | 0
7138 | 832.7 | 570.357 | 26.2 | 91.9987 | 91.9987 | 0 | 0 | 0.0033305 | 0.0033305 | 0 | 0 | 0 | 74.174 | 740.7047 | 0 | 0.05921 | 4.0012 | 0 | 0 | 0 | 91.9987 | off_peak | 740.7013 | 0 | 100 | 11.05 | 0 | 88.95 | 368.1035 | 0
7139 | 833.16 | 706.749 | 26.7 | 113.7926 | 113.7926 | 0 | 0 | 0.0002151 | 0.0002151 | 0 | 0 | 0 | 74.1742 | 719.3676 | 0 | 0.05921 | 4.2879 | 0 | 0 | 0 | 113.7926 | off_peak | 719.3674 | 0 | 100 | 13.66 | 0 | 86.34 | 487.9366 | 0
7140 | 884.09 | 781.279 | 27.1 | 125.6103 | 125.6103 | 0 | 0 | 1.3893e-05 | 1.3893e-05 | 0 | 0 | 0 | 74.1743 | 758.4797 | 0 | 0.05921 | 4.7112 | 0 | 0 | 0 | 125.6103 | off_peak | 758.4797 | 0 | 100 | 14.21 | 0 | 85.79 | 591.7701 | 0
7141 | 832.78 | 686.859 | 27.4 | 110.3098 | 110.3098 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1743 | 722.4702 | 0 | 0.088511 | 5.0108 | 0 | 0 | 0 | 110.3098 | on_peak | 722.4702 |  |  | 13.25 | 0 | 86.75 | 552.7392 | 0
7142 | 871.89 | 538.255 | 27.5 | 86.4125 | 86.4125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1743 | 785.4775 | 0 | 0.088511 | 5.0999 | 0 | 0 | 0 | 86.4125 | on_peak | 785.4775 |  |  | 9.91 | 0 | 90.09 | 440.6953 | 0
7143 | 857.58 | 582.472 | 27.6 | 93.4773 | 93.4773 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1743 | 764.1027 | 0 | 0.088511 | 5.1435 | 0 | 0 | 0 | 93.4773 | on_peak | 764.1027 |  |  | 10.9 | 0 | 89.1 | 480.7993 | 0
7144 | 762.5 | 417.231 | 27.4 | 67.0074 | 67.0074 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1743 | 695.4926 | 0 | 0.088511 | 5.2587 | 0 | 0 | 0 | 67.0074 | on_peak | 695.4926 |  |  | 8.79 | 0 | 91.21 | 352.3727 | 0
7145 | 755.89 | 209.742 | 26.9 | 33.7458 | 33.7458 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1743 | 722.1442 | 0 | 0.088511 | 5.4778 | 0 | 0 | 0 | 33.7458 | on_peak | 722.1442 |  |  | 4.46 | 0 | 95.54 | 184.8528 | 0
7146 | 751.17 | 24.5542 | 26.1 | 3.962 | 3.962 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1743 | 747.208 | 0 | 0.088511 | 5.8876 | 0 | 0 | 0 | 3.962 | on_peak | 747.208 |  |  | 0.53 | 0 | 99.47 | 23.3269 | 0
7147 | 776.09 | 0 | 25.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1743 | 776.09 | 0 | 0.088511 | 6.2051 | 0 | 0 | 0 | 0 | on_peak | 776.09 |  |  | 0 | 0 | 100 | 0 | 0
7148 | 772.35 | 0 | 25.1 | 0 | 0 | 0 | 0 | 0 | 0 | 62.4453 | 62.4453 | 0 | 7.4174 | 709.9047 | 0 | 0.088511 | 6.3825 | 0 | 0 | 0 | 0 | on_peak | 709.9047 |  |  | 0 | 8.09 | 91.91 | 0 | 0
7149 | 768.39 | 0 | 24.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 768.39 | 0 | 0.088511 | 6.6792 | 0 | 0 | 0 | 0 | on_peak | 768.39 |  |  | 0 | 0 | 100 | 0 | 0
7150 | 743.98 | 0 | 24.7 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 18.9814 | 756.3424 | 0 | 0.05921 | 7.0146 | 0 | 0 | 0 | 0 | off_peak | 743.98 | 0 | 100 | 0 | 0 | 100 | 0 | 0
7151 | 749.63 | 0 | 24.7 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 30.5453 | 761.9924 | 0 | 0.05921 | 7.2794 | 0 | 0 | 0 | 0 | off_peak | 749.63 | 0 | 100 | 0 | 0 | 100 | 0 | 0
7152 | 741.78 | 0 | 24.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30.5453 | 741.78 | 0 | 0.05921 | 7.3908 | 0 | 0 | 0 | 0 | off_peak | 741.78 |  |  | 0 | 0 | 100 | 0 | 0
7153 | 696.37 | 0 | 24.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30.5453 | 696.37 | 0 | 0.05921 | 7.3987 | 0 | 0 | 0 | 0 | off_peak | 696.37 |  |  | 0 | 0 | 100 | 0 | 0
7154 | 636.35 | 0 | 24.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30.5453 | 636.35 | 0 | 0.05921 | 7.1098 | 0 | 0 | 0 | 0 | off_peak | 636.35 |  |  | 0 | 0 | 100 | 0 | 0
7155 | 653.68 | 0 | 24.6 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 42.1093 | 666.0424 | 0 | 0.05921 | 6.7026 | 0 | 0 | 0 | 0 | off_peak | 653.68 | 0 | 100 | 0 | 0 | 100 | 0 | 0
7156 | 598.57 | 0 | 24.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 42.1093 | 598.57 | 0 | 0.05921 | 6.1779 | 0 | 0 | 0 | 0 | off_peak | 598.57 |  |  | 0 | 0 | 100 | 0 | 0
7157 | 604.61 | 0 | 24.4 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 53.6732 | 616.9724 | 0 | 0.05921 | 5.4949 | 0 | 0 | 0 | 0 | off_peak | 604.61 | 0 | 100 | 0 | 0 | 100 | 0 | 0
7158 | 644.55 | 0 | 24.3 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 65.2371 | 656.9124 | 0 | 0.05921 | 4.8439 | 0 | 0 | 0 | 0 | off_peak | 644.55 | 0 | 100 | 0 | 0 | 100 | 0 | 0
7159 | 689.9 | 10.0883 | 24.4 | 1.6378 | 1.6378 | 0 | 0 | 8.9371 | 8.9371 | 0 | 0 | 0 | 73.597 | 697.1993 | 0 | 0.05921 | 4.4321 | 0 | 0 | 0 | 1.6378 | off_peak | 688.2622 | 0 | 100 | 0.24 | 0 | 99.76 | 7.2591 | 0
7160 | 743.92 | 173.885 | 25 | 28.1694 | 28.1694 | 0 | 0 | 0.57721 | 0.57721 | 0 | 0 | 0 | 74.137 | 716.3278 | 0 | 0.05921 | 4.1582 | 0 | 0 | 0 | 28.1694 | off_peak | 715.7506 | 0 | 100 | 3.79 | 0 | 96.21 | 117.1349 | 0
7161 | 787.7 | 381.619 | 25.7 | 61.6665 | 61.6665 | 0 | 0 | 0.037279 | 0.037279 | 0 | 0 | 0 | 74.1718 | 726.0708 | 0 | 0.05921 | 4.0473 | 0 | 0 | 0 | 61.6665 | off_peak | 726.0335 | 0 | 100 | 7.83 | 0 | 92.17 | 249.5819 | 0
7162 | 830.14 | 564.948 | 26.3 | 91.0933 | 91.0933 | 0 | 0 | 0.0024077 | 0.0024077 | 0 | 0 | 0 | 74.1741 | 739.0492 | 0 | 0.05921 | 4.0562 | 0 | 0 | 0 | 91.0933 | off_peak | 739.0467 | 0 | 100 | 10.97 | 0 | 89.03 | 369.4957 | 0
7163 | 796.64 | 700.568 | 26.8 | 112.7566 | 112.7566 | 0 | 0 | 0.0001555 | 0.0001555 | 0 | 0 | 0 | 74.1742 | 683.8836 | 0 | 0.05921 | 4.2697 | 0 | 0 | 0 | 112.7566 | off_peak | 683.8834 | 0 | 100 | 14.15 | 0 | 85.85 | 481.4327 | 0
7164 | 848.14 | 772.538 | 27.2 | 124.16 | 124.16 | 0 | 0 | 1.0043e-05 | 1.0043e-05 | 0 | 0 | 0 | 74.1743 | 723.9801 | 0 | 0.05921 | 4.6907 | 0 | 0 | 0 | 124.16 | off_peak | 723.98 | 0 | 100 | 14.64 | 0 | 85.36 | 582.3992 | 0
7165 | 789.49 | 776.284 | 27.5 | 124.6262 | 124.6262 | 0 | 0 | 0 | 0 | 62.4453 | 62.4453 | 0 | 7.4174 | 602.4185 | 0 | 0.088511 | 4.8704 | 0 | 0 | 0 | 124.6262 | on_peak | 602.4185 |  |  | 15.79 | 7.91 | 76.3 | 606.976 | 0
7166 | 835.27 | 710.709 | 27.7 | 114.0157 | 114.0157 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 721.2543 | 0 | 0.088511 | 4.8427 | 0 | 0 | 0 | 114.0157 | on_peak | 721.2543 |  |  | 13.65 | 0 | 86.35 | 552.1393 | 0
7167 | 855.02 | 584.082 | 27.8 | 93.6675 | 93.6675 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 761.3525 | 0 | 0.088511 | 4.6778 | 0 | 0 | 0 | 93.6675 | on_peak | 761.3525 |  |  | 10.96 | 0 | 89.04 | 438.1551 | 0
7168 | 794.95 | 388.797 | 27.8 | 62.3502 | 62.3502 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 732.5998 | 0 | 0.088511 | 4.7091 | 0 | 0 | 0 | 62.3502 | on_peak | 732.5998 |  |  | 7.84 | 0 | 92.16 | 293.6127 | 0
7169 | 793.47 | 200.626 | 27.5 | 32.2089 | 32.2089 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 761.2611 | 0 | 0.088511 | 4.9784 | 0 | 0 | 0 | 32.2089 | on_peak | 761.2611 |  |  | 4.06 | 0 | 95.94 | 160.3483 | 0
7170 | 820.31 | 23.4368 | 27.2 | 3.7667 | 3.7667 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 816.5433 | 0 | 0.088511 | 5.2603 | 0 | 0 | 0 | 3.7667 | on_peak | 816.5433 |  |  | 0.46 | 0 | 99.54 | 19.8141 | 0
7171 | 778.38 | 0 | 26.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 778.38 | 0 | 0.088511 | 5.7328 | 0 | 0 | 0 | 0 | on_peak | 778.38 |  |  | 0 | 0 | 100 | 0 | 0
7172 | 814.62 | 0 | 26.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 814.62 | 0 | 0.088511 | 6.0912 | 0 | 0 | 0 | 0 | on_peak | 814.62 |  |  | 0 | 0 | 100 | 0 | 0
7173 | 795.17 | 0 | 26.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 795.17 | 0 | 0.088511 | 6.4341 | 0 | 0 | 0 | 0 | on_peak | 795.17 |  |  | 0 | 0 | 100 | 0 | 0
7174 | 740.44 | 0 | 25.8 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 18.9814 | 752.8024 | 0 | 0.05921 | 6.7264 | 0 | 0 | 0 | 0 | off_peak | 740.44 | 0 | 100 | 0 | 0 | 100 | 0 | 0
7175 | 775.84 | 0 | 25.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18.9814 | 775.84 | 0 | 0.05921 | 6.9351 | 0 | 0 | 0 | 0 | off_peak | 775.84 |  |  | 0 | 0 | 100 | 0 | 0
7176 | 755.83 | 0 | 25.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18.9814 | 755.83 | 0 | 0.05921 | 7.1101 | 0 | 0 | 0 | 0 | off_peak | 755.83 |  |  | 0 | 0 | 100 | 0 | 0
7177 | 688.17 | 0 | 25.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18.9814 | 688.17 | 0 | 0.05921 | 7.0462 | 0 | 0 | 0 | 0 | off_peak | 688.17 |  |  | 0 | 0 | 100 | 0 | 0
7178 | 684.84 | 0 | 24.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18.9814 | 684.84 | 0 | 0.05921 | 6.7525 | 0 | 0 | 0 | 0 | off_peak | 684.84 |  |  | 0 | 0 | 100 | 0 | 0
7179 | 589.34 | 0 | 24.7 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 30.5453 | 601.7024 | 0 | 0.05921 | 6.4154 | 0 | 0 | 0 | 0 | off_peak | 589.34 | 0 | 100 | 0 | 0 | 100 | 0 | 0
7180 | 593.33 | 0 | 24.6 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 42.1093 | 605.6924 | 0 | 0.05921 | 5.7363 | 0 | 0 | 0 | 0 | off_peak | 593.33 | 0 | 100 | 0 | 0 | 100 | 0 | 0
7181 | 634.27 | 0 | 24.6 | 0 | 0 | 0 | 0 | 8.7006 | 8.7006 | 0 | 0 | 0 | 50.2479 | 642.9706 | 0 | 0.05921 | 5.0568 | 0 | 0 | 0 | 0 | off_peak | 634.27 | 0 | 100 | 0 | 0 | 100 | 0 | 0
7182 | 600.85 | 0 | 24.6 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 61.8119 | 613.2124 | 0 | 0.05921 | 4.5444 | 0 | 0 | 0 | 0 | off_peak | 600.85 | 0 | 100 | 0 | 0 | 100 | 0 | 0
7183 | 708.84 | 9.7978 | 24.8 | 1.5884 | 1.5884 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 73.3758 | 719.614 | 0 | 0.05921 | 4.1608 | 0 | 0 | 0 | 1.5884 | off_peak | 707.2516 | 0 | 100 | 0.22 | 0 | 99.78 | 6.6089 | 0
7184 | 772.27 | 162.075 | 25.3 | 26.2278 | 26.2278 | 0 | 0 | 0.79843 | 0.79843 | 0 | 0 | 0 | 74.1227 | 746.8406 | 0 | 0.05921 | 3.8908 | 0 | 0 | 0 | 26.2278 | off_peak | 746.0422 | 0 | 100 | 3.4 | 0 | 96.6 | 102.0468 | 0
7185 | 826.74 | 362.45 | 25.9 | 58.5267 | 58.5267 | 0 | 0 | 0.051567 | 0.051567 | 0 | 0 | 0 | 74.1709 | 768.2649 | 0 | 0.05921 | 3.7194 | 0 | 0 | 0 | 58.5267 | off_peak | 768.2133 | 0 | 100 | 7.08 | 0 | 92.92 | 217.6827 | 0
7186 | 859.31 | 541.861 | 26.5 | 87.3075 | 87.3075 | 0 | 0 | 0.0033305 | 0.0033305 | 0 | 0 | 0 | 74.174 | 772.0059 | 0 | 0.05921 | 3.6538 | 0 | 0 | 0 | 87.3075 | off_peak | 772.0025 | 0 | 100 | 10.16 | 0 | 89.84 | 319.0041 | 0
7187 | 807.37 | 673.558 | 27.1 | 108.2915 | 108.2915 | 0 | 0 | 0.0002151 | 0.0002151 | 0 | 0 | 0 | 74.1742 | 699.0787 | 0 | 0.05921 | 3.8405 | 0 | 0 | 0 | 108.2915 | off_peak | 699.0785 | 0 | 100 | 13.41 | 0 | 86.59 | 415.8939 | 0
7188 | 947.22 | 745.032 | 27.5 | 119.6089 | 119.6089 | 0 | 0 | 1.3893e-05 | 1.3893e-05 | 0 | 0 | 0 | 74.1743 | 827.6111 | 0 | 0.05921 | 4.2642 | 0 | 0 | 0 | 119.6089 | off_peak | 827.6111 | 0 | 100 | 12.63 | 0 | 87.37 | 510.0387 | 0
7189 | 822.22 | 652.895 | 27.9 | 104.6648 | 104.6648 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1743 | 717.5552 | 0 | 0.088511 | 4.5591 | 0 | 0 | 0 | 104.6648 | on_peak | 717.5552 |  |  | 12.73 | 0 | 87.27 | 477.1792 | 0
7190 | 843.32 | 690.625 | 28.1 | 110.6327 | 110.6327 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1743 | 732.6873 | 0 | 0.088511 | 4.7409 | 0 | 0 | 0 | 110.6327 | on_peak | 732.6873 |  |  | 13.12 | 0 | 86.88 | 524.4978 | 0
7191 | 864.75 | 566.531 | 28.1 | 90.7538 | 90.7538 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1743 | 773.9962 | 0 | 0.088511 | 4.8145 | 0 | 0 | 0 | 90.7538 | on_peak | 773.9962 |  |  | 10.49 | 0 | 89.51 | 436.9308 | 0
7192 | 795.37 | 393.845 | 27.9 | 63.1368 | 63.1368 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1743 | 732.2332 | 0 | 0.088511 | 4.9792 | 0 | 0 | 0 | 63.1368 | on_peak | 732.2332 |  |  | 7.94 | 0 | 92.06 | 314.3713 | 0
7193 | 768.48 | 194.376 | 27.5 | 31.2055 | 31.2055 | 0 | 0 | 0 | 0 | 62.4453 | 62.4453 | 0 | 7.4174 | 674.8292 | 0 | 0.088511 | 5.3314 | 0 | 0 | 0 | 31.2055 | on_peak | 674.8292 |  |  | 4.06 | 8.13 | 87.81 | 166.3681 | 0
7194 | 820.76 | 21.5105 | 26.8 | 3.4621 | 3.4621 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 817.2979 | 0 | 0.088511 | 5.7396 | 0 | 0 | 0 | 3.4621 | on_peak | 817.2979 |  |  | 0.42 | 0 | 99.58 | 19.8713 | 0
7195 | 781.67 | 0 | 26.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 781.67 | 0 | 0.088511 | 6.1439 | 0 | 0 | 0 | 0 | on_peak | 781.67 |  |  | 0 | 0 | 100 | 0 | 0
7196 | 763.66 | 0 | 26.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 763.66 | 0 | 0.088511 | 6.3318 | 0 | 0 | 0 | 0 | on_peak | 763.66 |  |  | 0 | 0 | 100 | 0 | 0
7197 | 770.53 | 0 | 25.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 770.53 | 0 | 0.088511 | 6.6638 | 0 | 0 | 0 | 0 | on_peak | 770.53 |  |  | 0 | 0 | 100 | 0 | 0
7198 | 711.71 | 0 | 25.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 711.71 | 0 | 0.05921 | 6.8684 | 0 | 0 | 0 | 0 | off_peak | 711.71 |  |  | 0 | 0 | 100 | 0 | 0
7199 | 707.04 | 0 | 25.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 707.04 | 0 | 0.05921 | 7.1407 | 0 | 0 | 0 | 0 | off_peak | 707.04 |  |  | 0 | 0 | 100 | 0 | 0
7200 | 696.28 | 0 | 25.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 696.28 | 0 | 0.05921 | 7.178 | 0 | 0 | 0 | 0 | off_peak | 696.28 |  |  | 0 | 0 | 100 | 0 | 0
7201 | 648.53 | 0 | 25.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 648.53 | 0 | 0.05921 | 6.9475 | 0 | 0 | 0 | 0 | off_peak | 648.53 |  |  | 0 | 0 | 100 | 0 | 0
7202 | 623.24 | 0 | 25.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 623.24 | 0 | 0.05921 | 6.5721 | 0 | 0 | 0 | 0 | off_peak | 623.24 |  |  | 0 | 0 | 100 | 0 | 0
7203 | 582.52 | 0 | 25.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 582.52 | 0 | 0.05921 | 6.1853 | 0 | 0 | 0 | 0 | off_peak | 582.52 |  |  | 0 | 0 | 100 | 0 | 0
7204 | 631.65 | 0 | 25.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 631.65 | 0 | 0.05921 | 5.6958 | 0 | 0 | 0 | 0 | off_peak | 631.65 |  |  | 0 | 0 | 100 | 0 | 0
7205 | 608.52 | 0 | 25.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 608.52 | 0 | 0.05921 | 5.0805 | 0 | 0 | 0 | 0 | off_peak | 608.52 |  |  | 0 | 0 | 100 | 0 | 0
7206 | 647.41 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 647.41 | 0 | 0.05921 | 4.6049 | 0 | 0 | 0 | 0 | off_peak | 647.41 |  |  | 0 | 0 | 100 | 0 | 0
7207 | 694.22 | 9.7403 | 25.4 | 1.5757 | 1.5757 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 692.6443 | 0 | 0.05921 | 4.182 | 0 | 0 | 0 | 1.5757 | off_peak | 692.6443 |  |  | 0.23 | 0 | 99.77 | 6.5895 | 0
7208 | 688.61 | 165.446 | 26.1 | 26.6961 | 26.6961 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 661.9139 | 0 | 0.05921 | 3.8973 | 0 | 0 | 0 | 26.6961 | off_peak | 661.9139 |  |  | 3.88 | 0 | 96.12 | 104.0427 | 0
7209 | 739.75 | 369.8 | 26.7 | 59.541 | 59.541 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 680.209 | 0 | 0.05921 | 3.7288 | 0 | 0 | 0 | 59.541 | off_peak | 680.209 |  |  | 8.05 | 0 | 91.95 | 222.0172 | 0
7210 | 731.34 | 551.961 | 27.2 | 88.7095 | 88.7095 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 642.6305 | 0 | 0.05921 | 3.6437 | 0 | 0 | 0 | 88.7095 | off_peak | 642.6305 |  |  | 12.13 | 0 | 87.87 | 323.2297 | 0
7211 | 714.24 | 684.762 | 27.5 | 109.9331 | 109.9331 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 604.3069 | 0 | 0.05921 | 3.6654 | 0 | 0 | 0 | 109.9331 | off_peak | 604.3069 |  |  | 15.39 | 0 | 84.61 | 402.951 | 0
7212 | 713.09 | 756.317 | 27.8 | 121.2883 | 121.2883 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 591.8017 | 0 | 0.05921 | 3.8229 | 0 | 0 | 0 | 121.2883 | off_peak | 591.8017 |  |  | 17.01 | 0 | 82.99 | 463.6762 | 0
7213 | 706.98 | 761.95 | 27.9 | 122.1472 | 122.1472 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 584.8328 | 0 | 0.05921 | 4.0976 | 0 | 0 | 0 | 122.1472 | off_peak | 584.8328 |  |  | 17.28 | 0 | 82.72 | 500.5149 | 0
7214 | 689.35 | 698.357 | 28 | 111.912 | 111.912 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 577.438 | 0 | 0.05921 | 4.3649 | 0 | 0 | 0 | 111.912 | off_peak | 577.438 |  |  | 16.23 | 0 | 83.77 | 488.4861 | 0
7215 | 724.33 | 574.389 | 27.9 | 92.0796 | 92.0796 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 632.2504 | 0 | 0.05921 | 4.5264 | 0 | 0 | 0 | 92.0796 | off_peak | 632.2504 |  |  | 12.71 | 0 | 87.29 | 416.7875 | 0
7216 | 664.71 | 401.038 | 27.6 | 64.3601 | 64.3601 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 600.3499 | 0 | 0.05921 | 4.7978 | 0 | 0 | 0 | 64.3601 | off_peak | 600.3499 |  |  | 9.68 | 0 | 90.32 | 308.7869 | 0
7217 | 706.52 | 198.37 | 27.2 | 31.8814 | 31.8814 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 674.6386 | 0 | 0.05921 | 5.2822 | 0 | 0 | 0 | 31.8814 | off_peak | 674.6386 |  |  | 4.51 | 0 | 95.49 | 168.4054 | 0
7218 | 642.51 | 22.8662 | 26.6 | 3.683 | 3.683 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 638.827 | 0 | 0.05921 | 5.6835 | 0 | 0 | 0 | 3.683 | off_peak | 638.827 |  |  | 0.57 | 0 | 99.43 | 20.9322 | 0
7219 | 568.62 | 0 | 26.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 568.62 | 0 | 0.05921 | 6.0279 | 0 | 0 | 0 | 0 | off_peak | 568.62 |  |  | 0 | 0 | 100 | 0 | 0
7220 | 564.06 | 0 | 26.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 564.06 | 0 | 0.05921 | 6.1925 | 0 | 0 | 0 | 0 | off_peak | 564.06 |  |  | 0 | 0 | 100 | 0 | 0
7221 | 539.13 | 0 | 26 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 539.13 | 0 | 0.05921 | 6.4778 | 0 | 0 | 0 | 0 | off_peak | 539.13 |  |  | 0 | 0 | 100 | 0 | 0
7222 | 549.19 | 0 | 25.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 549.19 | 0 | 0.05921 | 6.6852 | 0 | 0 | 0 | 0 | off_peak | 549.19 |  |  | 0 | 0 | 100 | 0 | 0
7223 | 550.74 | 0 | 25.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 550.74 | 0 | 0.05921 | 6.9686 | 0 | 0 | 0 | 0 | off_peak | 550.74 |  |  | 0 | 0 | 100 | 0 | 0
7224 | 528.14 | 0 | 25.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 528.14 | 0 | 0.05921 | 7.0942 | 0 | 0 | 0 | 0 | off_peak | 528.14 |  |  | 0 | 0 | 100 | 0 | 0
7225 | 569.69 | 0 | 25.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 569.69 | 0 | 0.05921 | 6.8275 | 0 | 0 | 0 | 0 | off_peak | 569.69 |  |  | 0 | 0 | 100 | 0 | 0
7226 | 536.43 | 0 | 25.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 536.43 | 0 | 0.05921 | 6.5149 | 0 | 0 | 0 | 0 | off_peak | 536.43 |  |  | 0 | 0 | 100 | 0 | 0
7227 | 532.58 | 0 | 25.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 532.58 | 0 | 0.05921 | 6.0823 | 0 | 0 | 0 | 0 | off_peak | 532.58 |  |  | 0 | 0 | 100 | 0 | 0
7228 | 562.09 | 0 | 25.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 562.09 | 0 | 0.05921 | 5.6348 | 0 | 0 | 0 | 0 | off_peak | 562.09 |  |  | 0 | 0 | 100 | 0 | 0
7229 | 559.98 | 0 | 25.3 | 0 | 0 | 0 | 0 | 8.7006 | 8.7006 | 0 | 0 | 0 | 15.5561 | 568.6806 | 0 | 0.05921 | 5.0456 | 0 | 0 | 0 | 0 | off_peak | 559.98 | 0 | 100 | 0 | 0 | 100 | 0 | 0
7230 | 613.4 | 0 | 25.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15.5561 | 613.4 | 0 | 0.05921 | 4.5678 | 0 | 0 | 0 | 0 | off_peak | 613.4 |  |  | 0 | 0 | 100 | 0 | 0
7231 | 612.48 | 8.6369 | 25.6 | 1.3961 | 1.3961 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15.5561 | 611.0839 | 0 | 0.05921 | 4.166 | 0 | 0 | 0 | 1.3961 | off_peak | 611.0839 |  |  | 0.23 | 0 | 99.77 | 5.8164 | 0
7232 | 679.74 | 157.734 | 26.3 | 25.4333 | 25.4333 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 27.12 | 666.6691 | 0 | 0.05921 | 3.9054 | 0 | 0 | 0 | 25.4333 | off_peak | 654.3067 | 0 | 100 | 3.74 | 0 | 96.26 | 99.3284 | 0
7233 | 666.64 | 357.524 | 27 | 57.5019 | 57.5019 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27.12 | 609.1381 | 0 | 0.05921 | 3.7163 | 0 | 0 | 0 | 57.5019 | off_peak | 609.1381 |  |  | 8.63 | 0 | 91.37 | 213.6948 | 0
7234 | 685.22 | 449.001 | 27.5 | 72.0835 | 72.0835 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27.12 | 613.1365 | 0 | 0.05921 | 3.6002 | 0 | 0 | 0 | 72.0835 | off_peak | 613.1365 |  |  | 10.52 | 0 | 89.48 | 259.5164 | 0
7235 | 678.52 | 589.094 | 27.9 | 94.4369 | 94.4369 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27.12 | 584.0831 | 0 | 0.05921 | 3.5758 | 0 | 0 | 0 | 94.4369 | off_peak | 584.0831 |  |  | 13.92 | 0 | 86.08 | 337.6853 | 0
7236 | 720.14 | 560.793 | 28.3 | 89.7692 | 89.7692 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27.12 | 630.3708 | 0 | 0.05921 | 3.6651 | 0 | 0 | 0 | 89.7692 | off_peak | 630.3708 |  |  | 12.47 | 0 | 87.53 | 329.0138 | 0
7237 | 679.07 | 696.429 | 28.5 | 111.3999 | 111.3999 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27.12 | 567.6701 | 0 | 0.05921 | 3.898 | 0 | 0 | 0 | 111.3999 | off_peak | 567.6701 |  |  | 16.4 | 0 | 83.6 | 434.2372 | 0
7238 | 684.14 | 667.439 | 28.5 | 106.7627 | 106.7627 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27.12 | 577.3773 | 0 | 0.05921 | 4.1919 | 0 | 0 | 0 | 106.7627 | off_peak | 577.3773 |  |  | 15.61 | 0 | 84.39 | 447.5394 | 0
7239 | 669.81 | 433.495 | 28.3 | 69.3919 | 69.3919 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27.12 | 600.4181 | 0 | 0.05921 | 4.3989 | 0 | 0 | 0 | 69.3919 | off_peak | 600.4181 |  |  | 10.36 | 0 | 89.64 | 305.2486 | 0
7240 | 661.26 | 276.855 | 28 | 44.3661 | 44.3661 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 38.684 | 629.2563 | 0 | 0.05921 | 4.6327 | 0 | 0 | 0 | 44.3661 | off_peak | 616.8939 | 0 | 100 | 6.71 | 0 | 93.29 | 205.5345 | 0
7241 | 659.51 | 188.279 | 27.6 | 30.2157 | 30.2157 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 50.2479 | 641.6567 | 0 | 0.05921 | 5.1288 | 0 | 0 | 0 | 30.2157 | off_peak | 629.2943 | 0 | 100 | 4.58 | 0 | 95.42 | 154.9705 | 0
7242 | 633.76 | 19.0737 | 27.1 | 3.0666 | 0 | 0 | 3.0666 | 12.3624 | 9.2958 | 0 | 0 | 0 | 61.8119 | 643.0558 | 0 | 0.05921 | 5.5764 | 0 | 0 | 2.8685 | 0 | off_peak | 633.76 | 24.81 | 75.19 | 0 | 0 | 100 | 0 | 0
7243 | 606.8 | 0 | 26.8 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 73.3758 | 619.1624 | 0 | 0.05921 | 5.9045 | 0 | 0 | 2.8685 | 0 | off_peak | 606.8 | 0 | 100 | 0 | 0 | 100 | 0 | 0
7244 | 589.14 | 0 | 26.7 | 0 | 0 | 0 | 0 | 0.79843 | 0.79843 | 0 | 0 | 0 | 74.1227 | 589.9384 | 0 | 0.05921 | 6.0813 | 0 | 0 | 2.8685 | 0 | off_peak | 589.14 | 0 | 100 | 0 | 0 | 100 | 0 | 0
7245 | 558.75 | 0 | 26.5 | 0 | 0 | 0 | 0 | 0.051567 | 0.051567 | 0 | 0 | 0 | 74.1709 | 558.8016 | 0 | 0.05921 | 6.3474 | 0 | 0 | 2.8685 | 0 | off_peak | 558.75 | 0 | 100 | 0 | 0 | 100 | 0 | 0
7246 | 555.8 | 0 | 26.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1709 | 555.8 | 0 | 0.05921 | 6.5717 | 0 | 0 | 2.8685 | 0 | off_peak | 555.8 |  |  | 0 | 0 | 100 | 0 | 0
7247 | 545.97 | 0 | 26.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1709 | 545.97 | 0 | 0.05921 | 6.9617 | 0 | 0 | 2.8685 | 0 | off_peak | 545.97 |  |  | 0 | 0 | 100 | 0 | 0
7248 | 585.71 | 0 | 26.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1709 | 585.71 | 0 | 0.05921 | 7.3155 | 0 | 0 | 2.8685 | 0 | off_peak | 585.71 |  |  | 0 | 0 | 100 | 0 | 0
7249 | 558.59 | 0 | 26 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1709 | 558.59 | 0 | 0.05921 | 7.2144 | 0 | 0 | 2.8685 | 0 | off_peak | 558.59 |  |  | 0 | 0 | 100 | 0 | 0
7250 | 558.34 | 0 | 25.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1709 | 558.34 | 0 | 0.05921 | 6.828 | 0 | 0 | 2.8685 | 0 | off_peak | 558.34 |  |  | 0 | 0 | 100 | 0 | 0
7251 | 557.91 | 0 | 25.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1709 | 557.91 | 0 | 0.05921 | 6.4177 | 0 | 0 | 2.8685 | 0 | off_peak | 557.91 |  |  | 0 | 0 | 100 | 0 | 0
7252 | 561.35 | 0 | 25.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1709 | 561.35 | 0 | 0.05921 | 5.8396 | 0 | 0 | 2.8685 | 0 | off_peak | 561.35 |  |  | 0 | 0 | 100 | 0 | 0
7253 | 578.68 | 0 | 25.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1709 | 578.68 | 0 | 0.05921 | 5.0442 | 0 | 0 | 2.8685 | 0 | off_peak | 578.68 |  |  | 0 | 0 | 100 | 0 | 0
7254 | 588.05 | 0 | 25.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1709 | 588.05 | 0 | 0.05921 | 4.4914 | 0 | 0 | 2.8685 | 0 | off_peak | 588.05 |  |  | 0 | 0 | 100 | 0 | 0
7255 | 693.53 | 5.7099 | 25.7 | 0.92267 | 0.92267 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1709 | 692.6073 | 0 | 0.05921 | 4.0619 | 0 | 0 | 2.8685 | 0.92267 | off_peak | 692.6073 |  |  | 0.13 | 0 | 99.87 | 3.7478 | 0
7256 | 799.59 | 151.833 | 26.3 | 24.4818 | 24.4818 | 0 | 0 | 0.0033305 | 0.0033305 | 0 | 0 | 0 | 74.174 | 775.1115 | 0 | 0.05921 | 3.8296 | 0 | 0 | 2.8685 | 24.4818 | off_peak | 775.1082 | 0 | 100 | 3.06 | 0 | 96.94 | 93.755 | 0
7257 | 848.1 | 351.101 | 26.8 | 56.5098 | 56.5098 | 0 | 0 | 0.0002151 | 0.0002151 | 0 | 0 | 0 | 74.1742 | 791.5904 | 0 | 0.05921 | 3.6864 | 0 | 0 | 2.8685 | 56.5098 | off_peak | 791.5902 | 0 | 100 | 6.66 | 0 | 93.34 | 208.3193 | 0
7258 | 775.14 | 530.063 | 27.2 | 85.1901 | 85.1901 | 0 | 0 | 1.3893e-05 | 1.3893e-05 | 0 | 0 | 0 | 74.1743 | 689.9499 | 0 | 0.05921 | 3.6701 | 0 | 0 | 2.8685 | 85.1901 | off_peak | 689.9499 | 0 | 100 | 10.99 | 0 | 89.01 | 312.6589 | 0
7259 | 782.83 | 661.261 | 27.6 | 106.1216 | 106.1216 | 0 | 0 | 8.9726e-07 | 8.9726e-07 | 0 | 0 | 0 | 74.1743 | 676.7084 | 0 | 0.05921 | 3.9043 | 0 | 0 | 2.8685 | 106.1216 | off_peak | 676.7084 | 0 | 100 | 13.56 | 0 | 86.44 | 414.3306 | 0
7260 | 866.05 | 732.927 | 27.9 | 117.4946 | 117.4946 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1743 | 748.5554 | 0 | 0.05921 | 4.317 | 0 | 0 | 2.8685 | 117.4946 | off_peak | 748.5554 |  |  | 13.57 | 0 | 86.43 | 507.2207 | 0
7261 | 835.3 | 669.62 | 28.1 | 107.2678 | 107.2678 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1743 | 728.0322 | 0 | 0.088511 | 4.6002 | 0 | 0 | 2.8685 | 107.2678 | on_peak | 728.0322 |  |  | 12.84 | 0 | 87.16 | 493.4514 | 0
7262 | 851.45 | 669.143 | 28.2 | 107.1524 | 107.1524 | 0 | 0 | 0 | 0 | 2.6833 | 2.6833 | 0 | 71.3057 | 741.6144 | 0 | 0.088511 | 4.6818 | 2.6833 | 0 | 0 | 109.8356 | on_peak | 741.6144 |  |  | 12.58 | 0.32 | 87.1 | 514.2268 | 0
7263 | 830.06 | 551.032 | 28.1 | 88.271 | 88.271 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 71.3057 | 741.789 | 0 | 0.088511 | 4.7587 | 0 | 0 | 0 | 88.271 | on_peak | 741.789 |  |  | 10.63 | 0 | 89.37 | 420.0512 | 0
7264 | 831.95 | 380.24 | 27.9 | 60.9558 | 60.9558 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 71.3057 | 770.9942 | 0 | 0.088511 | 5.0736 | 0 | 0 | 0 | 60.9558 | on_peak | 770.9942 |  |  | 7.33 | 0 | 92.67 | 309.2651 | 0
7265 | 788.38 | 183.423 | 27.5 | 29.4471 | 29.4471 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 71.3057 | 758.9329 | 0 | 0.088511 | 5.5282 | 0 | 0 | 0 | 29.4471 | on_peak | 758.9329 |  |  | 3.74 | 0 | 96.26 | 162.7891 | 0
7266 | 817.65 | 15.183 | 27 | 2.4419 | 2.4419 | 0 | 0 | 0 | 0 | 59.762 | 59.762 | 0 | 7.4174 | 755.446 | 0 | 0.088511 | 5.9484 | 0 | 0 | 0 | 2.4419 | on_peak | 755.446 |  |  | 0.3 | 7.31 | 92.39 | 14.5256 | 0
7267 | 790.95 | 0 | 26.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 790.95 | 0 | 0.088511 | 6.3506 | 0 | 0 | 0 | 0 | on_peak | 790.95 |  |  | 0 | 0 | 100 | 0 | 0
7268 | 769.7 | 0 | 26.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 769.7 | 0 | 0.088511 | 6.7693 | 0 | 0 | 0 | 0 | on_peak | 769.7 |  |  | 0 | 0 | 100 | 0 | 0
7269 | 779.53 | 0 | 26.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 779.53 | 0 | 0.088511 | 7.1445 | 0 | 0 | 0 | 0 | on_peak | 779.53 |  |  | 0 | 0 | 100 | 0 | 0
7270 | 775 | 0 | 26.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 775 | 0 | 0.05921 | 7.4653 | 0 | 0 | 0 | 0 | off_peak | 775 |  |  | 0 | 0 | 100 | 0 | 0
7271 | 740.04 | 0 | 26.3 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 18.9814 | 752.4024 | 0 | 0.05921 | 7.7603 | 0 | 0 | 0 | 0 | off_peak | 740.04 | 0 | 100 | 0 | 0 | 100 | 0 | 0
7272 | 756.71 | 0 | 26.3 | 0 | 0 | 0 | 0 | 8.7006 | 8.7006 | 0 | 0 | 0 | 27.12 | 765.4106 | 0 | 0.05921 | 7.8371 | 0 | 0 | 0 | 0 | off_peak | 756.71 | 0 | 100 | 0 | 0 | 100 | 0 | 0
7273 | 652.87 | 0 | 26.3 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 38.684 | 665.2324 | 0 | 0.05921 | 7.758 | 0 | 0 | 0 | 0 | off_peak | 652.87 | 0 | 100 | 0 | 0 | 100 | 0 | 0
7274 | 649.23 | 0 | 26.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 38.684 | 649.23 | 0 | 0.05921 | 7.3406 | 0 | 0 | 0 | 0 | off_peak | 649.23 |  |  | 0 | 0 | 100 | 0 | 0
7275 | 610.11 | 0 | 26.2 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 50.2479 | 622.4724 | 0 | 0.05921 | 6.8135 | 0 | 0 | 0 | 0 | off_peak | 610.11 | 0 | 100 | 0 | 0 | 100 | 0 | 0
7276 | 595.68 | 0 | 26.2 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 61.8119 | 608.0424 | 0 | 0.05921 | 6.123 | 0 | 0 | 0 | 0 | off_peak | 595.68 | 0 | 100 | 0 | 0 | 100 | 0 | 0
7277 | 636.3 | 0 | 26.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 61.8119 | 636.3 | 0 | 0.05921 | 5.3239 | 0 | 0 | 0 | 0 | off_peak | 636.3 |  |  | 0 | 0 | 100 | 0 | 0
7278 | 631.42 | 0 | 26.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 61.8119 | 631.42 | 0 | 0.05921 | 5.3177 | 0 | 0 | 0 | 0 | off_peak | 631.42 |  |  | 0 | 0 | 100 | 0 | 0
7279 | 713.68 | 5.7 | 26.4 | 0.91875 | 0.91875 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 61.8119 | 712.7613 | 0 | 0.05921 | 5.3073 | 0 | 0 | 0 | 0.91875 | off_peak | 712.7613 |  |  | 0.13 | 0 | 99.87 | 4.8761 | 0
7280 | 773.63 | 144.264 | 26.9 | 23.2109 | 23.2109 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 73.3758 | 762.7815 | 0 | 0.05921 | 5.2993 | 0 | 0 | 0 | 23.2109 | off_peak | 750.4191 | 0 | 100 | 3 | 0 | 97 | 123.0005 | 0
7281 | 805.32 | 275.558 | 27.4 | 44.2547 | 44.2547 | 0 | 0 | 0.79843 | 0.79843 | 0 | 0 | 0 | 74.1227 | 761.8637 | 0 | 0.05921 | 5.293 | 0 | 0 | 0 | 44.2547 | off_peak | 761.0653 | 0 | 100 | 5.5 | 0 | 94.5 | 234.242 | 0
7282 | 855.19 | 354.58 | 27.9 | 56.8423 | 56.8423 | 0 | 0 | 0.051567 | 0.051567 | 0 | 0 | 0 | 74.1709 | 798.3993 | 0 | 0.05921 | 5.2882 | 0 | 0 | 0 | 56.8423 | off_peak | 798.3477 | 0 | 100 | 6.65 | 0 | 93.35 | 300.5921 | 0
7283 | 856.61 | 530.865 | 28.4 | 84.9475 | 84.9475 | 0 | 0 | 0.0033305 | 0.0033305 | 0 | 0 | 0 | 74.174 | 771.6658 | 0 | 0.05921 | 5.2843 | 0 | 0 | 0 | 84.9475 | off_peak | 771.6625 | 0 | 100 | 9.92 | 0 | 90.08 | 448.8872 | 0
7284 | 917.3 | 693.508 | 28.7 | 110.8518 | 110.8518 | 0 | 0 | 0.0002151 | 0.0002151 | 0 | 0 | 0 | 74.1742 | 806.4484 | 0 | 0.05921 | 5.2827 | 0 | 0 | 0 | 110.8518 | off_peak | 806.4482 | 0 | 100 | 12.08 | 0 | 87.92 | 585.5996 | 0
7285 | 888.88 | 714.77 | 28.9 | 114.167 | 114.167 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1742 | 774.713 | 0 | 0.088511 | 5.2832 | 0 | 0 | 0 | 114.167 | on_peak | 774.713 |  |  | 12.84 | 0 | 87.16 | 603.1685 | 0
7286 | 892.45 | 665.013 | 29 | 106.1808 | 106.1808 | 0 | 0 | 1.3893e-05 | 1.3893e-05 | 0 | 0 | 0 | 74.1743 | 786.2693 | 0 | 0.088511 | 5.2823 | 0 | 0 | 0 | 106.1808 | on_peak | 786.2692 | 0 | 100 | 11.9 | 0 | 88.1 | 560.8764 | 0
7287 | 902.67 | 544.621 | 29 | 86.9581 | 86.9581 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1743 | 815.7119 | 0 | 0.088511 | 5.2803 | 0 | 0 | 0 | 86.9581 | on_peak | 815.7119 |  |  | 9.63 | 0 | 90.37 | 459.1679 | 0
7288 | 862.23 | 375.759 | 28.8 | 60.0402 | 60.0402 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1743 | 802.1898 | 0 | 0.088511 | 5.2795 | 0 | 0 | 0 | 60.0402 | on_peak | 802.1898 |  |  | 6.96 | 0 | 93.04 | 316.9804 | 0
7289 | 858.18 | 180.072 | 28.4 | 28.8146 | 28.8146 | 0 | 0 | 9.5921e-07 | 9.5921e-07 | 0 | 0 | 0 | 74.1743 | 829.3654 | 0 | 0.088511 | 5.2835 | 0 | 0 | 0 | 28.8146 | on_peak | 829.3654 | 0 | 100 | 3.36 | 0 | 96.64 | 152.2434 | 0
7290 | 867.31 | 16.516 | 27.8 | 2.6486 | 2.6486 | 0 | 0 | 0 | 0 | 32.8217 | 32.8217 | 0 | 39.0863 | 831.8396 | 0 | 0.088511 | 5.292 | 0 | 0 | 0 | 2.6486 | on_peak | 831.8396 |  |  | 0.31 | 3.78 | 95.91 | 14.0165 | 0
7291 | 858.51 | 0 | 27.4 | 0 | 0 | 0 | 0 | 0 | 0 | 26.6704 | 26.6704 | 0 | 10.5745 | 831.8396 | 0 | 0.088511 | 5.302 | 0 | 0 | 0 | 0 | on_peak | 831.8396 |  |  | 0 | 3.11 | 96.89 | 0 | 0
7292 | 826.38 | 0 | 24.4 | 0 | 0 | 0 | 0 | 5.4596 | 5.4596 | 0 | 0 | 0 | 15.6815 | 831.8396 | 0 | 0.088511 | 5.3132 | 0 | 0 | 0 | 0 | on_peak | 826.38 | 0 | 100 | 0 | 0 | 100 | 0 | 0
7293 | 839.57 | 0 | 24.4 | 0 | 0 | 0 | 0 | 0 | 0 | 7.7304 | 7.7304 | 0 | 7.4174 | 831.8396 | 0 | 0.088511 | 5.3239 | 0 | 0 | 0 | 0 | on_peak | 831.8396 |  |  | 0 | 0.92 | 99.08 | 0 | 0
7294 | 804.93 | 0 | 24.4 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 18.9814 | 817.2924 | 0 | 0.05921 | 5.3348 | 0 | 0 | 0 | 0 | off_peak | 804.93 | 0 | 100 | 0 | 0 | 100 | 0 | 0
7295 | 809.77 | 0 | 24.4 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 30.5453 | 822.1324 | 0 | 0.05921 | 5.3454 | 0 | 0 | 0 | 0 | off_peak | 809.77 | 0 | 100 | 0 | 0 | 100 | 0 | 0
7296 | 780.31 | 0 | 24.5 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 42.1093 | 792.6724 | 0 | 0.05921 | 5.3561 | 0 | 0 | 0 | 0 | off_peak | 780.31 | 0 | 100 | 0 | 0 | 100 | 0 | 0
7297 | 753.74 | 0 | 24.5 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 53.6732 | 766.1024 | 0 | 0.05921 | 5.3654 | 0 | 0 | 0 | 0 | off_peak | 753.74 | 0 | 100 | 0 | 0 | 100 | 0 | 0
7298 | 725.79 | 0 | 24.5 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 65.2371 | 738.1524 | 0 | 0.05921 | 5.372 | 0 | 0 | 0 | 0 | off_peak | 725.79 | 0 | 100 | 0 | 0 | 100 | 0 | 0
7299 | 737.76 | 0 | 24.5 | 0 | 0 | 0 | 0 | 8.9371 | 8.9371 | 0 | 0 | 0 | 73.597 | 746.6971 | 0 | 0.05921 | 5.3751 | 0 | 0 | 0 | 0 | off_peak | 737.76 | 0 | 100 | 0 | 0 | 100 | 0 | 0
7300 | 685.91 | 0 | 24.5 | 0 | 0 | 0 | 0 | 0.57721 | 0.57721 | 0 | 0 | 0 | 74.137 | 686.4872 | 0 | 0.05921 | 5.3757 | 0 | 0 | 0 | 0 | off_peak | 685.91 | 0 | 100 | 0 | 0 | 100 | 0 | 0
7301 | 710.11 | 0 | 24.5 | 0 | 0 | 0 | 0 | 0.037279 | 0.037279 | 0 | 0 | 0 | 74.1718 | 710.1473 | 0 | 0.05921 | 5.3727 | 0 | 0 | 0 | 0 | off_peak | 710.11 | 0 | 100 | 0 | 0 | 100 | 0 | 0
7302 | 716.23 | 0 | 24.6 | 0 | 0 | 0 | 0 | 0.0024077 | 0.0024077 | 0 | 0 | 0 | 74.1741 | 716.2324 | 0 | 0.05921 | 5.3684 | 0 | 0 | 0 | 0 | off_peak | 716.23 | 0 | 100 | 0 | 0 | 100 | 0 | 0
7303 | 739.16 | 5.7 | 24.8 | 0.92406 | 0.92406 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1741 | 738.2359 | 0 | 0.088511 | 5.3711 | 0 | 0 | 0 | 0.92406 | on_peak | 738.2359 |  |  | 0.13 | 0 | 99.87 | 4.9633 | 0
7304 | 789.62 | 151.988 | 25.2 | 24.6043 | 24.6043 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1741 | 765.0157 | 0 | 0.088511 | 5.379 | 0 | 0 | 0 | 24.6043 | on_peak | 765.0157 |  |  | 3.12 | 0 | 96.88 | 132.3467 | 0
7305 | 828.19 | 351.807 | 25.6 | 56.8696 | 56.8696 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1741 | 771.3204 | 0 | 0.088511 | 5.3907 | 0 | 0 | 0 | 56.8696 | on_peak | 771.3204 |  |  | 6.87 | 0 | 93.13 | 306.5691 | 0
7306 | 846.3 | 528.645 | 26.1 | 85.3014 | 85.3014 | 0 | 0 | 0 | 0 | 62.4451 | 62.4451 | 0 | 7.4174 | 698.5535 | 0 | 0.088511 | 5.4052 | 0 | 0 | 0 | 85.3014 | on_peak | 698.5535 |  |  | 10.08 | 7.38 | 82.54 | 461.0702 | 0
7307 | 858.21 | 658.695 | 26.4 | 106.1708 | 106.1708 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 18.9814 | 764.4016 | 0 | 0.05921 | 5.4214 | 0 | 0 | 0 | 106.1708 | off_peak | 752.0392 | 0 | 100 | 12.37 | 0 | 87.63 | 575.5905 | 0
7308 | 875.91 | 727.438 | 26.6 | 117.1662 | 117.1662 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 30.5453 | 771.1062 | 0 | 0.05921 | 5.4382 | 0 | 0 | 0 | 117.1662 | off_peak | 758.7438 | 0 | 100 | 13.38 | 0 | 86.62 | 637.17 | 0
7309 | 843.31 | 430.185 | 26.7 | 69.2635 | 69.2635 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 42.1093 | 786.4089 | 0 | 0.05921 | 5.453 | 0 | 0 | 0 | 69.2635 | off_peak | 774.0465 | 0 | 100 | 8.21 | 0 | 91.79 | 377.6966 | 0
7310 | 895.95 | 365.315 | 26.7 | 58.8188 | 58.8188 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 53.6732 | 849.4935 | 0 | 0.05921 | 5.4635 | 0 | 0 | 0 | 58.8188 | off_peak | 837.1312 | 0 | 100 | 6.56 | 0 | 93.44 | 321.3595 | 0
7311 | 838.39 | 292.545 | 26.7 | 47.1022 | 47.1022 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 65.2371 | 803.6501 | 0 | 0.05921 | 5.471 | 0 | 0 | 0 | 47.1022 | off_peak | 791.2878 | 0 | 100 | 5.62 | 0 | 94.38 | 257.6965 | 0
7312 | 822.8 | 358.651 | 26.6 | 57.7668 | 57.7668 | 0 | 0 | 8.9371 | 8.9371 | 0 | 0 | 0 | 73.597 | 773.9703 | 0 | 0.05921 | 5.4766 | 0 | 0 | 0 | 57.7668 | off_peak | 765.0332 | 0 | 100 | 7.02 | 0 | 92.98 | 316.3636 | 0
7313 | 821.62 | 158.037 | 26.3 | 25.4822 | 25.4822 | 0 | 0 | 0.57721 | 0.57721 | 0 | 0 | 0 | 74.137 | 796.715 | 0 | 0.05921 | 5.4814 | 0 | 0 | 0 | 25.4822 | off_peak | 796.1378 | 0 | 100 | 3.1 | 0 | 96.9 | 139.6769 | 0
7314 | 817.41 | 11.9247 | 25.8 | 1.9262 | 1.889 | 0 | 0.037279 | 0.037279 | 0 | 0 | 0 | 0 | 74.1718 | 815.521 | 0 | 0.05921 | 5.4845 | 0 | 0 | 0.034872 | 1.889 | off_peak | 815.521 | 100 | 0 | 0.23 | 0 | 99.77 | 10.36 | 0
7315 | 827.73 | 0 | 25.7 | 0 | 0 | 0 | 0 | 0 | 0 | 2.4243 | 2.4243 | 0 | 71.5801 | 825.3057 | 0 | 0.088511 | 5.4841 | 0 | 0 | 0.034872 | 0 | on_peak | 825.3057 |  |  | 0 | 0.29 | 99.71 | 0 | 0
7316 | 807.41 | 0 | 25.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0.032619 | 0.032619 | 0 | 71.5452 | 807.3774 | 0 | 0.088511 | 5.4796 | 0.032619 | 0 | 0 | 0.032619 | on_peak | 807.3774 |  |  | 0 | 0 | 100 | 0.17874 | 0
7317 | 815.42 | 0 | 25.5 | 0 | 0 | 0 | 0 | 0 | 0 | 59.9861 | 59.9861 | 0 | 7.4174 | 755.4339 | 0 | 0.088511 | 5.471 | 0 | 0 | 0 | 0 | on_peak | 755.4339 |  |  | 0 | 7.36 | 92.64 | 0 | 0
7318 | 754.22 | 0 | 25.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 754.22 | 0 | 0.088511 | 5.4606 | 0 | 0 | 0 | 0 | on_peak | 754.22 |  |  | 0 | 0 | 100 | 0 | 0
7319 | 757.23 | 0 | 25.4 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 18.9814 | 769.5924 | 0 | 0.05921 | 5.4469 | 0 | 0 | 0 | 0 | off_peak | 757.23 | 0 | 100 | 0 | 0 | 100 | 0 | 0
7320 | 745.74 | 0 | 25.3 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 30.5453 | 758.1024 | 0 | 0.05921 | 5.4312 | 0 | 0 | 0 | 0 | off_peak | 745.74 | 0 | 100 | 0 | 0 | 100 | 0 | 0
7321 | 721.67 | 0 | 25.1 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 42.1093 | 734.0324 | 0 | 0.05921 | 5.4128 | 0 | 0 | 0 | 0 | off_peak | 721.67 | 0 | 100 | 0 | 0 | 100 | 0 | 0
7322 | 613.21 | 0 | 24.7 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 53.6732 | 625.5724 | 0 | 0.05921 | 5.3941 | 0 | 0 | 0 | 0 | off_peak | 613.21 | 0 | 100 | 0 | 0 | 100 | 0 | 0
7323 | 620.31 | 0 | 24 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 65.2371 | 632.6724 | 0 | 0.05921 | 5.3779 | 0 | 0 | 0 | 0 | off_peak | 620.31 | 0 | 100 | 0 | 0 | 100 | 0 | 0
7324 | 615.75 | 0 | 23.2 | 0 | 0 | 0 | 0 | 8.9371 | 8.9371 | 0 | 0 | 0 | 73.597 | 624.6871 | 0 | 0.05921 | 5.3656 | 0 | 0 | 0 | 0 | off_peak | 615.75 | 0 | 100 | 0 | 0 | 100 | 0 | 0
7325 | 605.13 | 0 | 22.4 | 0 | 0 | 0 | 0 | 0.57721 | 0.57721 | 0 | 0 | 0 | 74.137 | 605.7072 | 0 | 0.05921 | 5.3572 | 0 | 0 | 0 | 0 | off_peak | 605.13 | 0 | 100 | 0 | 0 | 100 | 0 | 0
7326 | 652.55 | 0 | 22 | 0 | 0 | 0 | 0 | 0.037279 | 0.037279 | 0 | 0 | 0 | 74.1718 | 652.5873 | 0 | 0.05921 | 4.032 | 0 | 0 | 0 | 0 | off_peak | 652.55 | 0 | 100 | 0 | 0 | 100 | 0 | 0
7327 | 665.06 | 0 | 21.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1718 | 665.06 | 0 | 0.088511 | 3.7081 | 0 | 0 | 0 | 0 | on_peak | 665.06 |  |  | 0 | 0 | 100 | 0 | 0
7328 | 720.06 | 100.207 | 22.1 | 16.403 | 16.403 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1718 | 703.657 | 0 | 0.088511 | 3.5317 | 0 | 0 | 0 | 16.403 | on_peak | 703.657 |  |  | 2.28 | 0 | 97.72 | 57.9302 | 0
7329 | 796.04 | 211.558 | 22.7 | 34.5562 | 34.5562 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1718 | 761.4838 | 0 | 0.088511 | 3.4469 | 0 | 0 | 0 | 34.5562 | on_peak | 761.4838 |  |  | 4.34 | 0 | 95.66 | 119.1133 | 0
7330 | 796.55 | 346.196 | 23.5 | 56.3866 | 56.3866 | 0 | 0 | 0 | 0 | 62.443 | 62.443 | 0 | 7.4174 | 677.7204 | 0 | 0.088511 | 3.4685 | 0 | 0 | 0 | 56.3866 | on_peak | 677.7204 |  |  | 7.08 | 7.84 | 85.08 | 195.5753 | 0
7331 | 805.38 | 196.405 | 24.2 | 31.9092 | 31.9092 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 18.9814 | 785.8331 | 0 | 0.05921 | 3.8125 | 0 | 0 | 0 | 31.9092 | off_peak | 773.4708 | 0 | 100 | 3.96 | 0 | 96.04 | 121.653 | 0
7332 | 815.89 | 302.773 | 24.9 | 49.0669 | 49.0669 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 30.5453 | 779.1855 | 0 | 0.05921 | 4.2945 | 0 | 0 | 0 | 49.0669 | off_peak | 766.8231 | 0 | 100 | 6.01 | 0 | 93.99 | 210.7197 | 0
7333 | 784.63 | 267.704 | 25.4 | 43.3056 | 43.3056 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 42.1093 | 753.6868 | 0 | 0.05921 | 4.5884 | 0 | 0 | 0 | 43.3056 | off_peak | 741.3244 | 0 | 100 | 5.52 | 0 | 94.48 | 198.7031 | 0
7334 | 817.85 | 265.603 | 25.7 | 42.9193 | 42.9193 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 53.6732 | 787.2931 | 0 | 0.05921 | 4.5597 | 0 | 0 | 0 | 42.9193 | off_peak | 774.9307 | 0 | 100 | 5.25 | 0 | 94.75 | 195.6991 | 0
7335 | 794.03 | 307.284 | 25.8 | 49.6366 | 49.6366 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 65.2371 | 756.7557 | 0 | 0.05921 | 4.1175 | 0 | 0 | 0 | 49.6366 | off_peak | 744.3934 | 0 | 100 | 6.25 | 0 | 93.75 | 204.3778 | 0
7336 | 811.1 | 345.245 | 25.7 | 55.7887 | 55.7887 | 0 | 0 | 8.9371 | 8.9371 | 0 | 0 | 0 | 73.597 | 764.2484 | 0 | 0.05921 | 3.8855 | 0 | 0 | 0 | 55.7887 | off_peak | 755.3113 | 0 | 100 | 6.88 | 0 | 93.12 | 216.7685 | 0
7337 | 786.59 | 160.1 | 25.3 | 25.9082 | 25.9082 | 0 | 0 | 0.57721 | 0.57721 | 0 | 0 | 0 | 74.137 | 761.259 | 0 | 0.05921 | 3.8382 | 0 | 0 | 0 | 25.9082 | off_peak | 760.6818 | 0 | 100 | 3.29 | 0 | 96.71 | 99.4419 | 0
7338 | 776.87 | 11.9045 | 24.6 | 1.9313 | 1.9313 | 0 | 0 | 0.037279 | 0.037279 | 0 | 0 | 0 | 74.1718 | 774.976 | 0 | 0.05921 | 3.9446 | 0 | 0 | 0 | 1.9313 | off_peak | 774.9387 | 0 | 100 | 0.25 | 0 | 99.75 | 7.6183 | 0
7339 | 793.09 | 0 | 24.3 | 0 | 0 | 0 | 0 | 0 | 0 | 62.443 | 62.443 | 0 | 7.4174 | 730.647 | 0 | 0.088511 | 4.1797 | 0 | 0 | 0 | 0 | on_peak | 730.647 |  |  | 0 | 7.87 | 92.13 | 0 | 0
7340 | 784.95 | 0 | 23.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 784.95 | 0 | 0.088511 | 4.3219 | 0 | 0 | 0 | 0 | on_peak | 784.95 |  |  | 0 | 0 | 100 | 0 | 0
7341 | 769.81 | 0 | 23.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 769.81 | 0 | 0.088511 | 4.5266 | 0 | 0 | 0 | 0 | on_peak | 769.81 |  |  | 0 | 0 | 100 | 0 | 0
7342 | 736.27 | 0 | 23.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 736.27 | 0 | 0.088511 | 4.8579 | 0 | 0 | 0 | 0 | on_peak | 736.27 |  |  | 0 | 0 | 100 | 0 | 0
7343 | 766.93 | 0 | 23.3 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 18.9814 | 779.2924 | 0 | 0.05921 | 5.4222 | 0 | 0 | 0 | 0 | off_peak | 766.93 | 0 | 100 | 0 | 0 | 100 | 0 | 0
7344 | 745.54 | 0 | 23.1 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 30.5453 | 757.9024 | 0 | 0.05921 | 5.841 | 0 | 0 | 0 | 0 | off_peak | 745.54 | 0 | 100 | 0 | 0 | 100 | 0 | 0
7345 | 669.03 | 0 | 23.1 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 42.1093 | 681.3924 | 0 | 0.05921 | 6.0708 | 0 | 0 | 0 | 0 | off_peak | 669.03 | 0 | 100 | 0 | 0 | 100 | 0 | 0
7346 | 623.23 | 0 | 23.1 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 53.6732 | 635.5924 | 0 | 0.05921 | 5.971 | 0 | 0 | 0 | 0 | off_peak | 623.23 | 0 | 100 | 0 | 0 | 100 | 0 | 0
7347 | 596.71 | 0 | 23.2 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 65.2371 | 609.0724 | 0 | 0.05921 | 5.5427 | 0 | 0 | 0 | 0 | off_peak | 596.71 | 0 | 100 | 0 | 0 | 100 | 0 | 0
7348 | 610.34 | 0 | 23.3 | 0 | 0 | 0 | 0 | 8.9371 | 8.9371 | 0 | 0 | 0 | 73.597 | 619.2771 | 0 | 0.05921 | 5.0085 | 0 | 0 | 0 | 0 | off_peak | 610.34 | 0 | 100 | 0 | 0 | 100 | 0 | 0
7349 | 611.85 | 0 | 23.4 | 0 | 0 | 0 | 0 | 0.57721 | 0.57721 | 0 | 0 | 0 | 74.137 | 612.4272 | 0 | 0.05921 | 4.4291 | 0 | 0 | 0 | 0 | off_peak | 611.85 | 0 | 100 | 0 | 0 | 100 | 0 | 0
7350 | 672.68 | 0 | 23.5 | 0 | 0 | 0 | 0 | 0.037279 | 0.037279 | 0 | 0 | 0 | 74.1718 | 672.7173 | 0 | 0.05921 | 3.9546 | 0 | 0 | 0 | 0 | off_peak | 672.68 | 0 | 100 | 0 | 0 | 100 | 0 | 0
7351 | 680.49 | 0 | 23.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1718 | 680.49 | 0 | 0.088511 | 3.6616 | 0 | 0 | 0 | 0 | on_peak | 680.49 |  |  | 0 | 0 | 100 | 0 | 0
7352 | 754.8 | 136.26 | 24.3 | 22.1297 | 22.1297 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1718 | 732.6703 | 0 | 0.088511 | 3.4612 | 0 | 0 | 0 | 22.1297 | on_peak | 732.6703 |  |  | 2.93 | 0 | 97.07 | 76.5946 | 0
7353 | 785.96 | 325.582 | 24.9 | 52.7633 | 52.7633 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1718 | 733.1967 | 0 | 0.088511 | 3.3354 | 0 | 0 | 0 | 52.7633 | on_peak | 733.1967 |  |  | 6.71 | 0 | 93.29 | 175.9876 | 0
7354 | 822.42 | 409.228 | 25.3 | 66.2233 | 66.2233 | 0 | 0 | 0 | 0 | 62.443 | 62.443 | 0 | 7.4174 | 693.7536 | 0 | 0.088511 | 3.343 | 0 | 0 | 0 | 66.2233 | on_peak | 693.7536 |  |  | 8.05 | 7.59 | 84.36 | 221.386 | 0
7355 | 811.26 | 493.285 | 25.7 | 79.7108 | 79.7108 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 18.9814 | 743.9116 | 0 | 0.05921 | 3.6253 | 0 | 0 | 0 | 79.7108 | off_peak | 731.5492 | 0 | 100 | 9.83 | 0 | 90.17 | 288.9728 | 0
7356 | 861.34 | 545.145 | 25.9 | 88.0274 | 88.0274 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 30.5453 | 785.675 | 0 | 0.05921 | 4.1856 | 0 | 0 | 0 | 88.0274 | off_peak | 773.3126 | 0 | 100 | 10.22 | 0 | 89.78 | 368.4514 | 0
7357 | 802.4 | 359.091 | 26 | 57.9633 | 57.9633 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 42.1093 | 756.7991 | 0 | 0.05921 | 4.5488 | 0 | 0 | 0 | 57.9633 | off_peak | 744.4367 | 0 | 100 | 7.22 | 0 | 92.78 | 263.6658 | 0
7358 | 838.65 | 375.324 | 25.9 | 60.6055 | 60.6055 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 53.6732 | 790.4069 | 0 | 0.05921 | 4.6124 | 0 | 0 | 0 | 60.6055 | off_peak | 778.0445 | 0 | 100 | 7.23 | 0 | 92.77 | 279.5351 | 0
7359 | 886.76 | 370.962 | 25.8 | 59.9228 | 59.9228 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 65.2371 | 839.1996 | 0 | 0.05921 | 4.354 | 0 | 0 | 0 | 59.9228 | off_peak | 826.8372 | 0 | 100 | 6.76 | 0 | 93.24 | 260.9029 | 0
7360 | 830.75 | 164.087 | 25.6 | 26.5247 | 26.5247 | 0 | 0 | 8.9371 | 8.9371 | 0 | 0 | 0 | 73.597 | 813.1624 | 0 | 0.05921 | 4.2333 | 0 | 0 | 0 | 26.5247 | off_peak | 804.2253 | 0 | 100 | 3.19 | 0 | 96.81 | 112.2864 | 0
7361 | 808.65 | 65.774 | 25.2 | 10.6477 | 10.0705 | 0 | 0.57721 | 0.57721 | 0 | 0 | 0 | 0 | 74.137 | 798.5795 | 0 | 0.05921 | 4.2941 | 0 | 0 | 0.53993 | 10.0705 | off_peak | 798.5795 | 100 | 0 | 1.25 | 0 | 98.75 | 43.2435 | 0
7362 | 798.48 | 6.65 | 24.8 | 1.0781 | 1.0408 | 0 | 0.037279 | 0.037279 | 0 | 0 | 0 | 0 | 74.1718 | 797.4392 | 0 | 0.05921 | 4.5535 | 0 | 0 | 0.5748 | 1.0408 | off_peak | 797.4392 | 100 | 0 | 0.13 | 0 | 99.87 | 4.7392 | 0
7363 | 799.99 | 0 | 24.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1718 | 799.99 | 0 | 0.088511 | 4.7604 | 0 | 0 | 0.5748 | 0 | on_peak | 799.99 |  |  | 0 | 0 | 100 | 0 | 0
7364 | 791.96 | 0 | 24.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1718 | 791.96 | 0 | 0.088511 | 4.9898 | 0 | 0 | 0.5748 | 0 | on_peak | 791.96 |  |  | 0 | 0 | 100 | 0 | 0
7365 | 799.73 | 0 | 24.4 | 0 | 0 | 0 | 0 | 0 | 0 | 62.443 | 62.443 | 0 | 7.4174 | 737.287 | 0 | 0.088511 | 5.2548 | 0.53768 | 0 | 0 | 0.53768 | on_peak | 737.287 |  |  | 0 | 7.81 | 92.19 | 2.8254 | 0
7366 | 759.45 | 0 | 24.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 759.45 | 0 | 0.088511 | 5.5106 | 0 | 0 | 0 | 0 | on_peak | 759.45 |  |  | 0 | 0 | 100 | 0 | 0
7367 | 783.71 | 0 | 24.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 783.71 | 0 | 0.05921 | 5.9052 | 0 | 0 | 0 | 0 | off_peak | 783.71 |  |  | 0 | 0 | 100 | 0 | 0
7368 | 792.5 | 0 | 24.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 792.5 | 0 | 0.05921 | 6.1985 | 0 | 0 | 0 | 0 | off_peak | 792.5 |  |  | 0 | 0 | 100 | 0 | 0
7369 | 704.48 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 704.48 | 0 | 0.05921 | 6.1712 | 0 | 0 | 0 | 0 | off_peak | 704.48 |  |  | 0 | 0 | 100 | 0 | 0
7370 | 621.12 | 0 | 23.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 621.12 | 0 | 0.05921 | 5.8949 | 0 | 0 | 0 | 0 | off_peak | 621.12 |  |  | 0 | 0 | 100 | 0 | 0
7371 | 648.8 | 0 | 23.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 648.8 | 0 | 0.05921 | 5.5387 | 0 | 0 | 0 | 0 | off_peak | 648.8 |  |  | 0 | 0 | 100 | 0 | 0
7372 | 638.76 | 0 | 23.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 638.76 | 0 | 0.05921 | 5.2123 | 0 | 0 | 0 | 0 | off_peak | 638.76 |  |  | 0 | 0 | 100 | 0 | 0
7373 | 640.98 | 0 | 23.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 640.98 | 0 | 0.05921 | 4.7648 | 0 | 0 | 0 | 0 | off_peak | 640.98 |  |  | 0 | 0 | 100 | 0 | 0
7374 | 673.18 | 0 | 23.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 673.18 | 0 | 0.05921 | 4.1587 | 0 | 0 | 0 | 0 | off_peak | 673.18 |  |  | 0 | 0 | 100 | 0 | 0
7375 | 677.83 | 0 | 23.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 677.83 | 0 | 0.05921 | 3.8061 | 0 | 0 | 0 | 0 | off_peak | 677.83 |  |  | 0 | 0 | 100 | 0 | 0
7376 | 712.93 | 69.4071 | 24.5 | 11.2642 | 11.2642 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 701.6658 | 0 | 0.05921 | 3.5289 | 0 | 0 | 0 | 11.2642 | off_peak | 701.6658 |  |  | 1.58 | 0 | 98.42 | 39.7501 | 0
7377 | 704.48 | 192.535 | 25.2 | 31.1682 | 31.1682 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 673.3118 | 0 | 0.05921 | 3.3695 | 0 | 0 | 0 | 31.1682 | off_peak | 673.3118 |  |  | 4.42 | 0 | 95.58 | 105.021 | 0
7378 | 709.9 | 346.062 | 25.7 | 55.9208 | 55.9208 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 653.9792 | 0 | 0.05921 | 3.278 | 0 | 0 | 0 | 55.9208 | off_peak | 653.9792 |  |  | 7.88 | 0 | 92.12 | 183.3085 | 0
7379 | 722.69 | 350.765 | 26.1 | 56.5989 | 56.5989 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 666.0911 | 0 | 0.05921 | 3.2932 | 0 | 0 | 0 | 56.5989 | off_peak | 666.0911 |  |  | 7.83 | 0 | 92.17 | 186.3938 | 0
7380 | 757.27 | 445.105 | 26.4 | 71.7436 | 71.7436 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 685.5264 | 0 | 0.05921 | 3.465 | 0 | 0 | 0 | 71.7436 | off_peak | 685.5264 |  |  | 9.47 | 0 | 90.53 | 248.5907 | 0
7381 | 742.63 | 466.272 | 26.6 | 75.101 | 75.101 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 667.529 | 0 | 0.05921 | 3.878 | 0 | 0 | 0 | 75.101 | off_peak | 667.529 |  |  | 10.11 | 0 | 89.89 | 291.2419 | 0
7382 | 747.49 | 471.585 | 26.6 | 75.9567 | 75.9567 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 671.5333 | 0 | 0.05921 | 4.0565 | 0 | 0 | 0 | 75.9567 | off_peak | 671.5333 |  |  | 10.16 | 0 | 89.84 | 308.1218 | 0
7383 | 726.37 | 321.137 | 26.6 | 51.7245 | 51.7245 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 674.6455 | 0 | 0.05921 | 3.9561 | 0 | 0 | 0 | 51.7245 | off_peak | 674.6455 |  |  | 7.12 | 0 | 92.88 | 204.6259 | 0
7384 | 737.8 | 117.785 | 26.4 | 18.985 | 18.985 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 718.815 | 0 | 0.05921 | 3.9258 | 0 | 0 | 0 | 18.985 | off_peak | 718.815 |  |  | 2.57 | 0 | 97.43 | 74.5305 | 0
7385 | 748.88 | 55.0358 | 25.9 | 8.8869 | 8.8869 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 739.9931 | 0 | 0.05921 | 3.8655 | 0 | 0 | 0 | 8.8869 | off_peak | 739.9931 |  |  | 1.19 | 0 | 98.81 | 34.352 | 0
7386 | 648.93 | 8.55 | 25.5 | 1.3826 | 1.3826 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 647.5474 | 0 | 0.05921 | 4.018 | 0 | 0 | 0 | 1.3826 | off_peak | 647.5474 |  |  | 0.21 | 0 | 99.79 | 5.5553 | 0
7387 | 599.66 | 0 | 25.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 599.66 | 0 | 0.05921 | 4.2431 | 0 | 0 | 0 | 0 | off_peak | 599.66 |  |  | 0 | 0 | 100 | 0 | 0
7388 | 607.59 | 0 | 25.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 607.59 | 0 | 0.05921 | 4.5389 | 0 | 0 | 0 | 0 | off_peak | 607.59 |  |  | 0 | 0 | 100 | 0 | 0
7389 | 587.49 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 587.49 | 0 | 0.05921 | 4.9128 | 0 | 0 | 0 | 0 | off_peak | 587.49 |  |  | 0 | 0 | 100 | 0 | 0
7390 | 595.65 | 0 | 24.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 595.65 | 0 | 0.05921 | 5.043 | 0 | 0 | 0 | 0 | off_peak | 595.65 |  |  | 0 | 0 | 100 | 0 | 0
7391 | 589.62 | 0 | 24.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 589.62 | 0 | 0.05921 | 5.4884 | 0 | 0 | 0 | 0 | off_peak | 589.62 |  |  | 0 | 0 | 100 | 0 | 0
7392 | 564.02 | 0 | 24.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 564.02 | 0 | 0.05921 | 5.7936 | 0 | 0 | 0 | 0 | off_peak | 564.02 |  |  | 0 | 0 | 100 | 0 | 0
7393 | 599.82 | 0 | 24.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 599.82 | 0 | 0.05921 | 5.7164 | 0 | 0 | 0 | 0 | off_peak | 599.82 |  |  | 0 | 0 | 100 | 0 | 0
7394 | 599.82 | 0 | 24.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 599.82 | 0 | 0.05921 | 5.4382 | 0 | 0 | 0 | 0 | off_peak | 599.82 |  |  | 0 | 0 | 100 | 0 | 0
7395 | 599.82 | 0 | 24.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 599.82 | 0 | 0.05921 | 5.1623 | 0 | 0 | 0 | 0 | off_peak | 599.82 |  |  | 0 | 0 | 100 | 0 | 0
7396 | 590.79 | 0 | 24.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 590.79 | 0 | 0.05921 | 4.8415 | 0 | 0 | 0 | 0 | off_peak | 590.79 |  |  | 0 | 0 | 100 | 0 | 0
7397 | 592.96 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 592.96 | 0 | 0.05921 | 4.3554 | 0 | 0 | 0 | 0 | off_peak | 592.96 |  |  | 0 | 0 | 100 | 0 | 0
7398 | 641.08 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 641.08 | 0 | 0.05921 | 0 | 0 | 0 | 0 | 0 | off_peak | 641.08 |  |  | 0 | 0 | 100 | 0 | 0
7399 | 687.68 | 0 | 24.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 687.68 | 0 | 0.05921 | 3.2484 | 0 | 0 | 0 | 0 | off_peak | 687.68 |  |  | 0 | 0 | 100 | 0 | 0
7400 | 671.74 | 132.824 | 24.8 | 21.533 | 21.533 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 18.9814 | 662.5694 | 0 | 0.05921 | 3.0785 | 0 | 0 | 0 | 21.533 | off_peak | 650.207 | 0 | 100 | 3.21 | 0 | 96.79 | 66.2899 | 0
7401 | 712.45 | 335.703 | 25.4 | 54.3056 | 54.3056 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 30.5453 | 670.5068 | 0 | 0.05921 | 2.9866 | 0 | 0 | 0 | 54.3056 | off_peak | 658.1444 | 0 | 100 | 7.62 | 0 | 92.38 | 162.1865 | 0
7402 | 735.77 | 495.984 | 25.9 | 80.0891 | 80.0891 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30.5453 | 655.6809 | 0 | 0.05921 | 2.9646 | 0 | 0 | 0 | 80.0891 | off_peak | 655.6809 |  |  | 10.89 | 0 | 89.11 | 237.4293 | 0
7403 | 686.74 | 570.166 | 26.2 | 91.9679 | 91.9679 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30.5453 | 594.7721 | 0 | 0.05921 | 3.0015 | 0 | 0 | 0 | 91.9679 | off_peak | 594.7721 |  |  | 13.39 | 0 | 86.61 | 276.0398 | 0
7404 | 765.91 | 668.171 | 26.5 | 107.6592 | 107.6592 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30.5453 | 658.2508 | 0 | 0.05921 | 3.1911 | 0 | 0 | 0 | 107.6592 | off_peak | 658.2508 |  |  | 14.06 | 0 | 85.94 | 343.5558 | 0
7405 | 701.46 | 602.346 | 26.6 | 97.018 | 97.018 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30.5453 | 604.442 | 0 | 0.05921 | 3.4085 | 0 | 0 | 0 | 97.018 | off_peak | 604.442 |  |  | 13.83 | 0 | 86.17 | 330.6816 | 0
7406 | 716.62 | 532.02 | 26.6 | 85.6908 | 85.6908 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 42.1093 | 643.2916 | 0 | 0.05921 | 3.408 | 0 | 0 | 0 | 85.6908 | off_peak | 630.9292 | 0 | 100 | 11.96 | 0 | 88.04 | 292.03 | 0
7407 | 702.84 | 315.362 | 26.5 | 50.8128 | 50.8128 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 53.6732 | 664.3896 | 0 | 0.05921 | 3.4978 | 0 | 0 | 0 | 50.8128 | off_peak | 652.0272 | 0 | 100 | 7.23 | 0 | 92.77 | 177.7328 | 0
7408 | 700.28 | 204.423 | 26.2 | 32.9735 | 32.9735 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 53.6732 | 667.3065 | 0 | 0.05921 | 3.7026 | 0 | 0 | 0 | 32.9735 | off_peak | 667.3065 |  |  | 4.71 | 0 | 95.29 | 122.0859 | 0
7409 | 698.7 | 109.379 | 25.7 | 17.6747 | 17.6747 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 65.2371 | 693.3876 | 0 | 0.05921 | 4.0023 | 0 | 0 | 0 | 17.6747 | off_peak | 681.0253 | 0 | 100 | 2.53 | 0 | 97.47 | 70.7393 | 0
7410 | 638.77 | 13.3452 | 25.1 | 2.1611 | 2.1611 | 0 | 0 | 8.9371 | 8.9371 | 0 | 0 | 0 | 73.597 | 645.546 | 0 | 0.05921 | 4.3401 | 0 | 0 | 0 | 2.1611 | off_peak | 636.6089 | 0 | 100 | 0.34 | 0 | 99.66 | 9.3795 | 0
7411 | 588.39 | 0 | 24.8 | 0 | 0 | 0 | 0 | 0.57721 | 0.57721 | 0 | 0 | 0 | 74.137 | 588.9672 | 0 | 0.05921 | 4.5983 | 0 | 0 | 0 | 0 | off_peak | 588.39 | 0 | 100 | 0 | 0 | 100 | 0 | 0
7412 | 605.35 | 0 | 24.7 | 0 | 0 | 0 | 0 | 0.037279 | 0.037279 | 0 | 0 | 0 | 74.1718 | 605.3873 | 0 | 0.05921 | 4.8169 | 0 | 0 | 0 | 0 | off_peak | 605.35 | 0 | 100 | 0 | 0 | 100 | 0 | 0
7413 | 588.66 | 0 | 24.7 | 0 | 0 | 0 | 0 | 0.0024077 | 0.0024077 | 0 | 0 | 0 | 74.1741 | 588.6624 | 0 | 0.05921 | 5.1989 | 0 | 0 | 0 | 0 | off_peak | 588.66 | 0 | 100 | 0 | 0 | 100 | 0 | 0
7414 | 573.07 | 0 | 24.7 | 0 | 0 | 0 | 0 | 0.0001555 | 0.0001555 | 0 | 0 | 0 | 74.1742 | 573.0702 | 0 | 0.05921 | 5.6732 | 0 | 0 | 0 | 0 | off_peak | 573.07 | 0 | 100 | 0 | 0 | 100 | 0 | 0
7415 | 547.88 | 0 | 24.6 | 0 | 0 | 0 | 0 | 1.0737e-05 | 1.0737e-05 | 0 | 0 | 0 | 74.1743 | 547.88 | 0 | 0.05921 | 5.9096 | 0 | 0 | 0 | 0 | off_peak | 547.88 | 0 | 100 | 0 | 0 | 100 | 0 | 0
7416 | 555.87 | 0 | 24.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1743 | 555.87 | 0 | 0.05921 | 5.8726 | 0 | 0 | 0 | 0 | off_peak | 555.87 |  |  | 0 | 0 | 100 | 0 | 0
7417 | 577.49 | 0 | 24.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1743 | 577.49 | 0 | 0.05921 | 5.5279 | 0 | 0 | 0 | 0 | off_peak | 577.49 |  |  | 0 | 0 | 100 | 0 | 0
7418 | 546.45 | 0 | 24.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1743 | 546.45 | 0 | 0.05921 | 5.1605 | 0 | 0 | 0 | 0 | off_peak | 546.45 |  |  | 0 | 0 | 100 | 0 | 0
7419 | 545.41 | 0 | 24.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1743 | 545.41 | 0 | 0.05921 | 4.7391 | 0 | 0 | 0 | 0 | off_peak | 545.41 |  |  | 0 | 0 | 100 | 0 | 0
7420 | 557.12 | 0 | 24.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1743 | 557.12 | 0 | 0.05921 | 4.265 | 0 | 0 | 0 | 0 | off_peak | 557.12 |  |  | 0 | 0 | 100 | 0 | 0
7421 | 539.42 | 0 | 24.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1743 | 539.42 | 0 | 0.05921 | 3.6875 | 0 | 0 | 0 | 0 | off_peak | 539.42 |  |  | 0 | 0 | 100 | 0 | 0
7422 | 613.87 | 0 | 24.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1743 | 613.87 | 0 | 0.05921 | 0 | 0 | 0 | 0 | 0 | off_peak | 613.87 |  |  | 0 | 0 | 100 | 0 | 0
7423 | 644.97 | 0 | 24.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1743 | 644.97 | 0 | 0.088511 | 3.2075 | 0 | 0 | 0 | 0 | on_peak | 644.97 |  |  | 0 | 0 | 100 | 0 | 0
7424 | 711.3 | 144.889 | 25.2 | 23.4551 | 23.4551 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1743 | 687.8449 | 0 | 0.088511 | 2.9198 | 0 | 0 | 0 | 23.4551 | on_peak | 687.8449 |  |  | 3.3 | 0 | 96.7 | 68.4843 | 0
7425 | 749.24 | 349.055 | 25.9 | 56.3637 | 56.3637 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1743 | 692.8763 | 0 | 0.088511 | 2.7628 | 0 | 0 | 0 | 56.3637 | on_peak | 692.8763 |  |  | 7.52 | 0 | 92.48 | 155.7234 | 0
7426 | 765.6 | 529.725 | 26.4 | 85.3829 | 85.3829 | 0 | 0 | 0 | 0 | 62.4453 | 62.4453 | 0 | 7.4174 | 617.7718 | 0 | 0.088511 | 2.6688 | 0 | 0 | 0 | 85.3829 | on_peak | 617.7718 |  |  | 11.15 | 8.16 | 80.69 | 227.8696 | 0
7427 | 797.21 | 662.616 | 26.9 | 106.6096 | 106.6096 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 18.9814 | 702.9628 | 0 | 0.05921 | 2.7453 | 0 | 0 | 0 | 106.6096 | off_peak | 690.6004 | 0 | 100 | 13.37 | 0 | 86.63 | 292.6787 | 0
7428 | 902.66 | 733.681 | 27.2 | 117.915 | 117.915 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 30.5453 | 797.1074 | 0 | 0.05921 | 3.1023 | 0 | 0 | 0 | 117.915 | off_peak | 784.745 | 0 | 100 | 13.06 | 0 | 86.94 | 365.8039 | 0
7429 | 836.11 | 729.119 | 27.4 | 117.0967 | 117.0967 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 42.1093 | 731.3756 | 0 | 0.05921 | 3.5941 | 0 | 0 | 0 | 117.0967 | off_peak | 719.0133 | 0 | 100 | 14 | 0 | 86 | 420.8539 | 0
7430 | 866.07 | 669.061 | 27.5 | 107.4124 | 107.4124 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 53.6732 | 771.02 | 0 | 0.05921 | 3.7582 | 0 | 0 | 0 | 107.4124 | off_peak | 758.6576 | 0 | 100 | 12.4 | 0 | 87.6 | 403.6812 | 0
7431 | 892.65 | 540.511 | 27.5 | 86.7747 | 86.7747 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 65.2371 | 818.2377 | 0 | 0.05921 | 3.4421 | 0 | 0 | 0 | 86.7747 | off_peak | 805.8753 | 0 | 100 | 9.72 | 0 | 90.28 | 298.6886 | 0
7432 | 806.71 | 367.213 | 27.2 | 59.0174 | 59.0174 | 0 | 0 | 8.9371 | 8.9371 | 0 | 0 | 0 | 73.597 | 756.6298 | 0 | 0.05921 | 3.3973 | 0 | 0 | 0 | 59.0174 | off_peak | 747.6926 | 0 | 100 | 7.32 | 0 | 92.68 | 200.4996 | 0
7433 | 820.54 | 169.079 | 26.6 | 27.233 | 26.6558 | 0 | 0.57721 | 0.57721 | 0 | 0 | 0 | 0 | 74.137 | 793.8842 | 0 | 0.05921 | 3.4944 | 0 | 0 | 0.53993 | 26.6558 | off_peak | 793.8842 | 100 | 0 | 3.25 | 0 | 96.75 | 93.1456 | 0
7434 | 819.32 | 11.2751 | 26 | 1.82 | 1.7827 | 0 | 0.037279 | 0.037279 | 0 | 0 | 0 | 0 | 74.1718 | 817.5373 | 0 | 0.05921 | 3.781 | 0 | 0 | 0.5748 | 1.7827 | off_peak | 817.5373 | 100 | 0 | 0.22 | 0 | 99.78 | 6.7405 | 0
7435 | 818.03 | 0 | 25.7 | 0 | 0 | 0 | 0 | 0 | 0 | 62.443 | 62.443 | 0 | 7.4174 | 755.587 | 0 | 0.088511 | 4.1455 | 0.53768 | 0 | 0 | 0.53768 | on_peak | 755.587 |  |  | 0 | 7.63 | 92.37 | 2.2289 | 0
7436 | 805.81 | 0 | 25.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 805.81 | 0 | 0.088511 | 4.5884 | 0 | 0 | 0 | 0 | on_peak | 805.81 |  |  | 0 | 0 | 100 | 0 | 0
7437 | 801.21 | 0 | 25.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 801.21 | 0 | 0.088511 | 5.0135 | 0 | 0 | 0 | 0 | on_peak | 801.21 |  |  | 0 | 0 | 100 | 0 | 0
7438 | 775.69 | 0 | 25.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 775.69 | 0 | 0.088511 | 5.4705 | 0 | 0 | 0 | 0 | on_peak | 775.69 |  |  | 0 | 0 | 100 | 0 | 0
7439 | 814.46 | 0 | 25 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 18.9814 | 826.8224 | 0 | 0.05921 | 6.0031 | 0 | 0 | 0 | 0 | off_peak | 814.46 | 0 | 100 | 0 | 0 | 100 | 0 | 0
7440 | 791.17 | 0 | 24.9 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 30.5453 | 803.5324 | 0 | 0.05921 | 6.3401 | 0 | 0 | 0 | 0 | off_peak | 791.17 | 0 | 100 | 0 | 0 | 100 | 0 | 0
7441 | 709.51 | 0 | 24.8 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 42.1093 | 721.8724 | 0 | 0.05921 | 6.4098 | 0 | 0 | 0 | 0 | off_peak | 709.51 | 0 | 100 | 0 | 0 | 100 | 0 | 0
7442 | 634.06 | 0 | 24.7 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 53.6732 | 646.4224 | 0 | 0.05921 | 6.038 | 0 | 0 | 0 | 0 | off_peak | 634.06 | 0 | 100 | 0 | 0 | 100 | 0 | 0
7443 | 628.08 | 0 | 24.6 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 65.2371 | 640.4424 | 0 | 0.05921 | 5.6834 | 0 | 0 | 0 | 0 | off_peak | 628.08 | 0 | 100 | 0 | 0 | 100 | 0 | 0
7444 | 632.28 | 0 | 24.5 | 0 | 0 | 0 | 0 | 8.9371 | 8.9371 | 0 | 0 | 0 | 73.597 | 641.2171 | 0 | 0.05921 | 5.3077 | 0 | 0 | 0 | 0 | off_peak | 632.28 | 0 | 100 | 0 | 0 | 100 | 0 | 0
7445 | 630.95 | 0 | 24.5 | 0 | 0 | 0 | 0 | 0.57721 | 0.57721 | 0 | 0 | 0 | 74.137 | 631.5272 | 0 | 0.05921 | 4.8077 | 0 | 0 | 0 | 0 | off_peak | 630.95 | 0 | 100 | 0 | 0 | 100 | 0 | 0
7446 | 640.46 | 0 | 24.5 | 0 | 0 | 0 | 0 | 0.037279 | 0.037279 | 0 | 0 | 0 | 74.1718 | 640.4973 | 0 | 0.05921 | 4.0935 | 0 | 0 | 0 | 0 | off_peak | 640.46 | 0 | 100 | 0 | 0 | 100 | 0 | 0
7447 | 710.17 | 0 | 24.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1718 | 710.17 | 0 | 0.088511 | 3.5766 | 0 | 0 | 0 | 0 | on_peak | 710.17 |  |  | 0 | 0 | 100 | 0 | 0
7448 | 769.92 | 145.466 | 25.3 | 23.54 | 23.54 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1718 | 746.38 | 0 | 0.088511 | 3.2694 | 0 | 0 | 0 | 23.54 | on_peak | 746.38 |  |  | 3.06 | 0 | 96.94 | 76.9611 | 0
7449 | 797.73 | 344.936 | 25.9 | 55.6986 | 55.6986 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1718 | 742.0314 | 0 | 0.088511 | 3.0857 | 0 | 0 | 0 | 55.6986 | on_peak | 742.0314 |  |  | 6.98 | 0 | 93.02 | 171.8665 | 0
7450 | 867.63 | 496.891 | 26.4 | 80.0906 | 80.0906 | 0 | 0 | 0 | 0 | 62.443 | 62.443 | 0 | 7.4174 | 725.0963 | 0 | 0.088511 | 3.0246 | 0 | 0 | 0 | 80.0906 | on_peak | 725.0963 |  |  | 9.23 | 7.2 | 83.57 | 242.2382 | 0
7451 | 829.45 | 647.418 | 26.8 | 104.2021 | 104.2021 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 18.9814 | 737.6103 | 0 | 0.05921 | 3.0387 | 0 | 0 | 0 | 104.2021 | off_peak | 725.2479 | 0 | 100 | 12.56 | 0 | 87.44 | 316.6367 | 0
7452 | 877.45 | 704.924 | 27.1 | 113.3344 | 113.3344 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 30.5453 | 776.478 | 0 | 0.05921 | 3.3315 | 0 | 0 | 0 | 113.3344 | off_peak | 764.1156 | 0 | 100 | 12.92 | 0 | 87.08 | 377.5745 | 0
7453 | 878.45 | 722.78 | 27.1 | 116.2052 | 116.2052 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 42.1093 | 774.6072 | 0 | 0.05921 | 3.8129 | 0 | 0 | 0 | 116.2052 | off_peak | 762.2448 | 0 | 100 | 13.23 | 0 | 86.77 | 443.0753 | 0
7454 | 858.35 | 658.267 | 27 | 105.8715 | 105.8715 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 53.6732 | 764.8409 | 0 | 0.05921 | 4.06 | 0 | 0 | 0 | 105.8715 | off_peak | 752.4785 | 0 | 100 | 12.33 | 0 | 87.67 | 429.8362 | 0
7455 | 876.69 | 536.455 | 26.8 | 86.3426 | 86.3426 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 65.2371 | 802.7098 | 0 | 0.05921 | 3.836 | 0 | 0 | 0 | 86.3426 | off_peak | 790.3474 | 0 | 100 | 9.85 | 0 | 90.15 | 331.2081 | 0
7456 | 815.07 | 368.982 | 26.4 | 59.4738 | 59.4738 | 0 | 0 | 8.9371 | 8.9371 | 0 | 0 | 0 | 73.597 | 764.5333 | 0 | 0.05921 | 3.8833 | 0 | 0 | 0 | 59.4738 | off_peak | 755.5962 | 0 | 100 | 7.3 | 0 | 92.7 | 230.9559 | 0
7457 | 839.22 | 174.021 | 25.9 | 28.1001 | 28.1001 | 0 | 0 | 0.57721 | 0.57721 | 0 | 0 | 0 | 74.137 | 811.6971 | 0 | 0.05921 | 4.2271 | 0 | 0 | 0 | 28.1001 | off_peak | 811.1199 | 0 | 100 | 3.35 | 0 | 96.65 | 118.7805 | 0
7458 | 885.89 | 12.637 | 25.4 | 2.0442 | 2.0442 | 0 | 0 | 0 | 0 | 30.5074 | 30.5074 | 0 | 41.5232 | 853.3384 | 0 | 0.05921 | 4.6693 | 0 | 0 | 0 | 2.0442 | off_peak | 853.3384 |  |  | 0.23 | 3.44 | 96.33 | 9.5453 | 0
7459 | 835.17 | 0 | 25.2 | 0 | 0 | 0 | 0 | 0 | 0 | 9.8643 | 9.8643 | 0 | 30.9778 | 825.3057 | 0 | 0.088511 | 5.0633 | 0 | 0 | 0 | 0 | on_peak | 825.3057 |  |  | 0 | 1.18 | 98.82 | 0 | 0
7460 | 825.88 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0.57435 | 0.57435 | 0 | 30.3638 | 825.3057 | 0 | 0.088511 | 5.42 | 0 | 0 | 0 | 0 | on_peak | 825.3057 |  |  | 0 | 0.07 | 99.93 | 0 | 0
7461 | 846.77 | 0 | 24.9 | 0 | 0 | 0 | 0 | 0 | 0 | 21.4643 | 21.4643 | 0 | 7.4174 | 825.3057 | 0 | 0.088511 | 5.6662 | 0 | 0 | 0 | 0 | on_peak | 825.3057 |  |  | 0 | 2.53 | 97.47 | 0 | 0
7462 | 743.49 | 0 | 24.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 743.49 | 0 | 0.088511 | 5.9927 | 0 | 0 | 0 | 0 | on_peak | 743.49 |  |  | 0 | 0 | 100 | 0 | 0
7463 | 815.32 | 0 | 24.7 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 18.9814 | 827.6824 | 0 | 0.05921 | 6.4265 | 0 | 0 | 0 | 0 | off_peak | 815.32 | 0 | 100 | 0 | 0 | 100 | 0 | 0
7464 | 788.34 | 0 | 24.5 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 30.5453 | 800.7024 | 0 | 0.05921 | 6.6952 | 0 | 0 | 0 | 0 | off_peak | 788.34 | 0 | 100 | 0 | 0 | 100 | 0 | 0
7465 | 707.34 | 0 | 24.3 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 42.1093 | 719.7024 | 0 | 0.05921 | 6.6853 | 0 | 0 | 0 | 0 | off_peak | 707.34 | 0 | 100 | 0 | 0 | 100 | 0 | 0
7466 | 642.08 | 0 | 24.2 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 53.6732 | 654.4424 | 0 | 0.05921 | 6.3213 | 0 | 0 | 0 | 0 | off_peak | 642.08 | 0 | 100 | 0 | 0 | 100 | 0 | 0
7467 | 614.55 | 0 | 24 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 65.2371 | 626.9124 | 0 | 0.05921 | 5.9029 | 0 | 0 | 0 | 0 | off_peak | 614.55 | 0 | 100 | 0 | 0 | 100 | 0 | 0
7468 | 633.54 | 0 | 23.9 | 0 | 0 | 0 | 0 | 8.9371 | 8.9371 | 0 | 0 | 0 | 73.597 | 642.4771 | 0 | 0.05921 | 5.5092 | 0 | 0 | 0 | 0 | off_peak | 633.54 | 0 | 100 | 0 | 0 | 100 | 0 | 0
7469 | 618.33 | 0 | 23.9 | 0 | 0 | 0 | 0 | 0.57721 | 0.57721 | 0 | 0 | 0 | 74.137 | 618.9072 | 0 | 0.05921 | 4.9688 | 0 | 0 | 0 | 0 | off_peak | 618.33 | 0 | 100 | 0 | 0 | 100 | 0 | 0
7470 | 616.3 | 0 | 23.9 | 0 | 0 | 0 | 0 | 0.037279 | 0.037279 | 0 | 0 | 0 | 74.1718 | 616.3373 | 0 | 0.05921 | 4.3268 | 0 | 0 | 0 | 0 | off_peak | 616.3 | 0 | 100 | 0 | 0 | 100 | 0 | 0
7471 | 687.57 | 0 | 24.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1718 | 687.57 | 0 | 0.088511 | 3.7422 | 0 | 0 | 0 | 0 | on_peak | 687.57 |  |  | 0 | 0 | 100 | 0 | 0
7472 | 742.41 | 107.998 | 24.7 | 17.5146 | 17.5146 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1718 | 724.8954 | 0 | 0.088511 | 3.3955 | 0 | 0 | 0 | 17.5146 | on_peak | 724.8954 |  |  | 2.36 | 0 | 97.64 | 59.4705 | 0
7473 | 797.23 | 184.914 | 25.4 | 29.9129 | 29.9129 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1718 | 767.3171 | 0 | 0.088511 | 3.2067 | 0 | 0 | 0 | 29.9129 | on_peak | 767.3171 |  |  | 3.75 | 0 | 96.25 | 95.9212 | 0
7474 | 834.94 | 445.845 | 25.8 | 72.0189 | 72.0189 | 0 | 0 | 0 | 0 | 62.443 | 62.443 | 0 | 7.4174 | 700.4781 | 0 | 0.088511 | 3.1191 | 0 | 0 | 0 | 72.0189 | on_peak | 700.4781 |  |  | 8.63 | 7.48 | 83.9 | 224.6318 | 0
7475 | 792.93 | 632.632 | 26.2 | 102.0436 | 102.0436 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 18.9814 | 703.2487 | 0 | 0.05921 | 3.1412 | 0 | 0 | 0 | 102.0436 | off_peak | 690.8864 | 0 | 100 | 12.87 | 0 | 87.13 | 320.5436 | 0
7476 | 845 | 716.935 | 26.4 | 115.5581 | 115.5581 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 30.5453 | 741.8043 | 0 | 0.05921 | 3.1578 | 0 | 0 | 0 | 115.5581 | off_peak | 729.4419 | 0 | 100 | 13.68 | 0 | 86.32 | 364.909 | 0
7477 | 839.9 | 727.165 | 26.5 | 117.1646 | 117.1646 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 42.1093 | 735.0978 | 0 | 0.05921 | 3.9266 | 0 | 0 | 0 | 117.1646 | off_peak | 722.7354 | 0 | 100 | 13.95 | 0 | 86.05 | 460.0615 | 0
7478 | 832.11 | 661.141 | 26.5 | 106.5265 | 106.5265 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 53.6732 | 737.9459 | 0 | 0.05921 | 4.1421 | 0 | 0 | 0 | 106.5265 | off_peak | 725.5835 | 0 | 100 | 12.8 | 0 | 87.2 | 441.2434 | 0
7479 | 868.47 | 537.488 | 26.5 | 86.6029 | 86.6029 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 65.2371 | 794.2295 | 0 | 0.05921 | 4.0265 | 0 | 0 | 0 | 86.6029 | off_peak | 781.8671 | 0 | 100 | 9.97 | 0 | 90.03 | 348.706 | 0
7480 | 799.97 | 366.036 | 26.3 | 59.0203 | 59.0203 | 0 | 0 | 8.9371 | 8.9371 | 0 | 0 | 0 | 73.597 | 749.8868 | 0 | 0.05921 | 4.0703 | 0 | 0 | 0 | 59.0203 | off_peak | 740.9497 | 0 | 100 | 7.38 | 0 | 92.62 | 240.2309 | 0
7481 | 797.78 | 168.86 | 25.8 | 27.2765 | 27.2765 | 0 | 0 | 0.57721 | 0.57721 | 0 | 0 | 0 | 74.137 | 771.0807 | 0 | 0.05921 | 4.3936 | 0 | 0 | 0 | 27.2765 | off_peak | 770.5035 | 0 | 100 | 3.42 | 0 | 96.58 | 119.8427 | 0
7482 | 849.31 | 11.2885 | 25.2 | 1.8274 | 1.8274 | 0 | 0 | 0.037279 | 0.037279 | 0 | 0 | 0 | 74.1718 | 847.5199 | 0 | 0.05921 | 4.8342 | 0 | 0 | 0 | 1.8274 | off_peak | 847.4826 | 0 | 100 | 0.22 | 0 | 99.78 | 8.8341 | 0
7483 | 805.15 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 62.443 | 62.443 | 0 | 7.4174 | 742.707 | 0 | 0.088511 | 5.1862 | 0 | 0 | 0 | 0 | on_peak | 742.707 |  |  | 0 | 7.76 | 92.24 | 0 | 0
7484 | 804.56 | 0 | 24.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 804.56 | 0 | 0.088511 | 5.6091 | 0 | 0 | 0 | 0 | on_peak | 804.56 |  |  | 0 | 0 | 100 | 0 | 0
7485 | 802.83 | 0 | 24.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 802.83 | 0 | 0.088511 | 5.9261 | 0 | 0 | 0 | 0 | on_peak | 802.83 |  |  | 0 | 0 | 100 | 0 | 0
7486 | 760.12 | 0 | 24.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 760.12 | 0 | 0.088511 | 6.2504 | 0 | 0 | 0 | 0 | on_peak | 760.12 |  |  | 0 | 0 | 100 | 0 | 0
7487 | 811.58 | 0 | 24.7 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 18.9814 | 823.9424 | 0 | 0.05921 | 6.6544 | 0 | 0 | 0 | 0 | off_peak | 811.58 | 0 | 100 | 0 | 0 | 100 | 0 | 0
7488 | 777.91 | 0 | 24.5 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 30.5453 | 790.2724 | 0 | 0.05921 | 6.8958 | 0 | 0 | 0 | 0 | off_peak | 777.91 | 0 | 100 | 0 | 0 | 100 | 0 | 0
7489 | 674.97 | 0 | 24.3 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 42.1093 | 687.3324 | 0 | 0.05921 | 6.9048 | 0 | 0 | 0 | 0 | off_peak | 674.97 | 0 | 100 | 0 | 0 | 100 | 0 | 0
7490 | 607.33 | 0 | 24.1 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 53.6732 | 619.6924 | 0 | 0.05921 | 6.5911 | 0 | 0 | 0 | 0 | off_peak | 607.33 | 0 | 100 | 0 | 0 | 100 | 0 | 0
7491 | 613.18 | 0 | 23.9 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 65.2371 | 625.5424 | 0 | 0.05921 | 6.1215 | 0 | 0 | 0 | 0 | off_peak | 613.18 | 0 | 100 | 0 | 0 | 100 | 0 | 0
7492 | 597.81 | 0 | 23.7 | 0 | 0 | 0 | 0 | 8.9371 | 8.9371 | 0 | 0 | 0 | 73.597 | 606.7471 | 0 | 0.05921 | 5.5931 | 0 | 0 | 0 | 0 | off_peak | 597.81 | 0 | 100 | 0 | 0 | 100 | 0 | 0
7493 | 615.89 | 0 | 23.6 | 0 | 0 | 0 | 0 | 0.57721 | 0.57721 | 0 | 0 | 0 | 74.137 | 616.4672 | 0 | 0.05921 | 5.0818 | 0 | 0 | 0 | 0 | off_peak | 615.89 | 0 | 100 | 0 | 0 | 100 | 0 | 0
7494 | 612.41 | 0 | 23.6 | 0 | 0 | 0 | 0 | 0.037279 | 0.037279 | 0 | 0 | 0 | 74.1718 | 612.4473 | 0 | 0.05921 | 4.5318 | 0 | 0 | 0 | 0 | off_peak | 612.41 | 0 | 100 | 0 | 0 | 100 | 0 | 0
7495 | 684.3 | 0 | 23.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1718 | 684.3 | 0 | 0.088511 | 3.969 | 0 | 0 | 0 | 0 | on_peak | 684.3 |  |  | 0 | 0 | 100 | 0 | 0
7496 | 774.35 | 121.685 | 24.5 | 19.7485 | 19.7485 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1718 | 754.6015 | 0 | 0.088511 | 3.6096 | 0 | 0 | 0 | 19.7485 | on_peak | 754.6015 |  |  | 2.55 | 0 | 97.45 | 71.2845 | 0
7497 | 777.36 | 262.863 | 25.2 | 42.5531 | 42.5531 | 0 | 0 | 0 | 0 | 62.443 | 62.443 | 0 | 7.4174 | 672.3638 | 0 | 0.088511 | 3.4059 | 0 | 0 | 0 | 42.5531 | on_peak | 672.3638 |  |  | 5.47 | 8.03 | 86.49 | 144.9323 | 0
7498 | 807.3 | 450.673 | 25.6 | 72.8513 | 72.8513 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 734.4487 | 0 | 0.088511 | 3.2924 | 0 | 0 | 0 | 72.8513 | on_peak | 734.4487 |  |  | 9.02 | 0 | 90.98 | 239.8576 | 0
7499 | 800.81 | 394.094 | 26 | 63.6134 | 63.6134 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 18.9814 | 749.559 | 0 | 0.05921 | 3.3169 | 0 | 0 | 0 | 63.6134 | off_peak | 737.1966 | 0 | 100 | 7.94 | 0 | 92.06 | 210.9983 | 0
7500 | 865.21 | 324.611 | 26.2 | 52.3598 | 52.3598 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 30.5453 | 825.2126 | 0 | 0.05921 | 3.5864 | 0 | 0 | 0 | 52.3598 | off_peak | 812.8502 | 0 | 100 | 6.05 | 0 | 93.95 | 187.7836 | 0
7501 | 823.74 | 272.014 | 26.3 | 43.86 | 43.86 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 42.1093 | 792.2423 | 0 | 0.05921 | 4.1171 | 0 | 0 | 0 | 43.86 | off_peak | 779.88 | 0 | 100 | 5.32 | 0 | 94.68 | 180.5762 | 0
7502 | 828.34 | 376.649 | 26.3 | 60.7316 | 60.7316 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 53.6732 | 779.9708 | 0 | 0.05921 | 4.3399 | 0 | 0 | 0 | 60.7316 | off_peak | 767.6084 | 0 | 100 | 7.33 | 0 | 92.67 | 263.5686 | 0
7503 | 835.97 | 240.731 | 26.2 | 38.8299 | 38.8299 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 65.2371 | 809.5024 | 0 | 0.05921 | 4.2875 | 0 | 0 | 0 | 38.8299 | off_peak | 797.1401 | 0 | 100 | 4.64 | 0 | 95.36 | 166.4826 | 0
7504 | 799.22 | 278.462 | 25.9 | 44.9647 | 44.9647 | 0 | 0 | 8.9371 | 8.9371 | 0 | 0 | 0 | 73.597 | 763.1924 | 0 | 0.05921 | 4.3429 | 0 | 0 | 0 | 44.9647 | off_peak | 754.2553 | 0 | 100 | 5.63 | 0 | 94.37 | 195.2785 | 0
7505 | 841.68 | 167.847 | 25.3 | 27.1618 | 27.1618 | 0 | 0 | 0.57721 | 0.57721 | 0 | 0 | 0 | 74.137 | 815.0954 | 0 | 0.05921 | 4.6815 | 0 | 0 | 0 | 27.1618 | off_peak | 814.5182 | 0 | 100 | 3.23 | 0 | 96.77 | 127.1571 | 0
7506 | 824.11 | 10.3328 | 24.7 | 1.6757 | 1.6384 | 0 | 0.037279 | 0.037279 | 0 | 0 | 0 | 0 | 74.1718 | 822.4716 | 0 | 0.05921 | 5.1586 | 0 | 0 | 0.034872 | 1.6384 | off_peak | 822.4716 | 100 | 0 | 0.2 | 0 | 99.8 | 8.4521 | 0
7507 | 832.37 | 0 | 24.4 | 0 | 0 | 0 | 0 | 0 | 0 | 7.0643 | 7.0643 | 0 | 66.6197 | 825.3057 | 0 | 0.088511 | 5.4606 | 0 | 0 | 0.034872 | 0 | on_peak | 825.3057 |  |  | 0 | 0.85 | 99.15 | 0 | 0
7508 | 867.63 | 0 | 24.1 | 0 | 0 | 0 | 0 | 0 | 0 | 42.3243 | 42.3243 | 0 | 21.3731 | 825.3057 | 0 | 0.088511 | 5.808 | 0 | 0 | 0.034872 | 0 | on_peak | 825.3057 |  |  | 0 | 4.88 | 95.12 | 0 | 0
7509 | 838.36 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 13.0543 | 13.0543 | 0 | 7.4174 | 825.3057 | 0 | 0.088511 | 6.0482 | 0.032619 | 0 | 0 | 0.032619 | on_peak | 825.3057 |  |  | 0 | 1.56 | 98.44 | 0.19729 | 0
7510 | 805.06 | 0 | 23.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 805.06 | 0 | 0.088511 | 6.3997 | 0 | 0 | 0 | 0 | on_peak | 805.06 |  |  | 0 | 0 | 100 | 0 | 0
7511 | 811.01 | 0 | 23.7 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 18.9814 | 823.3724 | 0 | 0.05921 | 6.7131 | 0 | 0 | 0 | 0 | off_peak | 811.01 | 0 | 100 | 0 | 0 | 100 | 0 | 0
7512 | 804.98 | 0 | 23.5 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 30.5453 | 817.3424 | 0 | 0.05921 | 6.8665 | 0 | 0 | 0 | 0 | off_peak | 804.98 | 0 | 100 | 0 | 0 | 100 | 0 | 0
7513 | 712.65 | 0 | 23.4 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 42.1093 | 725.0124 | 0 | 0.05921 | 6.892 | 0 | 0 | 0 | 0 | off_peak | 712.65 | 0 | 100 | 0 | 0 | 100 | 0 | 0
7514 | 605.14 | 0 | 23.3 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 53.6732 | 617.5024 | 0 | 0.05921 | 6.6721 | 0 | 0 | 0 | 0 | off_peak | 605.14 | 0 | 100 | 0 | 0 | 100 | 0 | 0
7515 | 632.82 | 0 | 23.2 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 65.2371 | 645.1824 | 0 | 0.05921 | 6.2857 | 0 | 0 | 0 | 0 | off_peak | 632.82 | 0 | 100 | 0 | 0 | 100 | 0 | 0
7516 | 620.34 | 0 | 23 | 0 | 0 | 0 | 0 | 8.9371 | 8.9371 | 0 | 0 | 0 | 73.597 | 629.2771 | 0 | 0.05921 | 5.968 | 0 | 0 | 0 | 0 | off_peak | 620.34 | 0 | 100 | 0 | 0 | 100 | 0 | 0
7517 | 657.4 | 0 | 22.7 | 0 | 0 | 0 | 0 | 0.57721 | 0.57721 | 0 | 0 | 0 | 74.137 | 657.9772 | 0 | 0.05921 | 5.4422 | 0 | 0 | 0 | 0 | off_peak | 657.4 | 0 | 100 | 0 | 0 | 100 | 0 | 0
7518 | 660.71 | 0 | 22.4 | 0 | 0 | 0 | 0 | 0.037279 | 0.037279 | 0 | 0 | 0 | 74.1718 | 660.7473 | 0 | 0.05921 | 4.8415 | 0 | 0 | 0 | 0 | off_peak | 660.71 | 0 | 100 | 0 | 0 | 100 | 0 | 0
7519 | 726.16 | 0 | 22.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1718 | 726.16 | 0 | 0.088511 | 4.4083 | 0 | 0 | 0 | 0 | on_peak | 726.16 |  |  | 0 | 0 | 100 | 0 | 0
7520 | 768.31 | 136.514 | 23 | 22.2745 | 22.2745 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1718 | 746.0355 | 0 | 0.088511 | 4.0698 | 0 | 0 | 0 | 22.2745 | on_peak | 746.0355 |  |  | 2.9 | 0 | 97.1 | 90.6538 | 0
7521 | 795.38 | 333.287 | 23.8 | 54.2257 | 54.2257 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1718 | 741.1543 | 0 | 0.088511 | 3.8416 | 0 | 0 | 0 | 54.2257 | on_peak | 741.1543 |  |  | 6.82 | 0 | 93.18 | 208.3141 | 0
7522 | 826.58 | 505.119 | 24.4 | 82.006 | 82.006 | 0 | 0 | 0 | 0 | 62.443 | 62.443 | 0 | 7.4174 | 682.1309 | 0 | 0.088511 | 3.7301 | 0 | 0 | 0 | 82.006 | on_peak | 682.1309 |  |  | 9.92 | 7.55 | 82.52 | 305.8907 | 0
7523 | 794.89 | 631.184 | 24.9 | 102.2886 | 102.2886 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 18.9814 | 704.9638 | 0 | 0.05921 | 3.7185 | 0 | 0 | 0 | 102.2886 | off_peak | 692.6014 | 0 | 100 | 12.87 | 0 | 87.13 | 380.3643 | 0
7524 | 828.63 | 702.576 | 25.4 | 113.6534 | 113.6534 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 30.5453 | 727.339 | 0 | 0.05921 | 3.9056 | 0 | 0 | 0 | 113.6534 | off_peak | 714.9766 | 0 | 100 | 13.72 | 0 | 86.28 | 443.8848 | 0
7525 | 792.34 | 579.159 | 25.7 | 93.5873 | 93.5873 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 42.1093 | 711.1151 | 0 | 0.05921 | 4.3035 | 0 | 0 | 0 | 93.5873 | off_peak | 698.7527 | 0 | 100 | 11.81 | 0 | 88.19 | 402.7533 | 0
7526 | 780.67 | 455.181 | 26 | 73.4739 | 73.4739 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 53.6732 | 719.5585 | 0 | 0.05921 | 4.5682 | 0 | 0 | 0 | 73.4739 | off_peak | 707.1961 | 0 | 100 | 9.41 | 0 | 90.59 | 335.6426 | 0
7527 | 821.35 | 397.894 | 26.1 | 64.2036 | 64.2036 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 65.2371 | 769.5088 | 0 | 0.05921 | 4.8967 | 0 | 0 | 0 | 64.2036 | off_peak | 757.1464 | 0 | 100 | 7.82 | 0 | 92.18 | 314.3834 | 0
7528 | 802.42 | 267.501 | 26 | 43.1792 | 43.1792 | 0 | 0 | 8.9371 | 8.9371 | 0 | 0 | 0 | 73.597 | 768.178 | 0 | 0.05921 | 5.2464 | 0 | 0 | 0 | 43.1792 | off_peak | 759.2408 | 0 | 100 | 5.38 | 0 | 94.62 | 226.5372 | 0
7529 | 793.06 | 160.225 | 25.6 | 25.9004 | 25.9004 | 0 | 0 | 0.57721 | 0.57721 | 0 | 0 | 0 | 74.137 | 767.7368 | 0 | 0.05921 | 5.8359 | 0 | 0 | 0 | 25.9004 | off_peak | 767.1596 | 0 | 100 | 3.27 | 0 | 96.73 | 151.1511 | 0
7530 | 810.44 | 9.9912 | 24.9 | 1.6192 | 1.6192 | 0 | 0 | 0.037279 | 0.037279 | 0 | 0 | 0 | 74.1718 | 808.8581 | 0 | 0.05921 | 6.2693 | 0 | 0 | 0 | 1.6192 | off_peak | 808.8208 | 0 | 100 | 0.2 | 0 | 99.8 | 10.151 | 0
7531 | 797.26 | 0 | 24.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1718 | 797.26 | 0 | 0.088511 | 6.7964 | 0 | 0 | 0 | 0 | on_peak | 797.26 |  |  | 0 | 0 | 100 | 0 | 0
7532 | 779.35 | 0 | 24.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1718 | 779.35 | 0 | 0.088511 | 7.387 | 0 | 0 | 0 | 0 | on_peak | 779.35 |  |  | 0 | 0 | 100 | 0 | 0
7533 | 807.89 | 0 | 24.1 | 0 | 0 | 0 | 0 | 0 | 0 | 62.443 | 62.443 | 0 | 7.4174 | 745.447 | 0 | 0.088511 | 7.6505 | 0 | 0 | 0 | 0 | on_peak | 745.447 |  |  | 0 | 7.73 | 92.27 | 0 | 0
7534 | 710.89 | 0 | 23.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 710.89 | 0 | 0.088511 | 7.9318 | 0 | 0 | 0 | 0 | on_peak | 710.89 |  |  | 0 | 0 | 100 | 0 | 0
7535 | 752.64 | 0 | 23.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 752.64 | 0 | 0.05921 | 8.05 | 0 | 0 | 0 | 0 | off_peak | 752.64 |  |  | 0 | 0 | 100 | 0 | 0
7536 | 749.72 | 0 | 23.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 749.72 | 0 | 0.05921 | 8.0333 | 0 | 0 | 0 | 0 | off_peak | 749.72 |  |  | 0 | 0 | 100 | 0 | 0
7537 | 671.7 | 0 | 23.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 671.7 | 0 | 0.05921 | 7.7704 | 0 | 0 | 0 | 0 | off_peak | 671.7 |  |  | 0 | 0 | 100 | 0 | 0
7538 | 599.63 | 0 | 22.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 599.63 | 0 | 0.05921 | 7.282 | 0 | 0 | 0 | 0 | off_peak | 599.63 |  |  | 0 | 0 | 100 | 0 | 0
7539 | 619.86 | 0 | 22.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 619.86 | 0 | 0.05921 | 6.8768 | 0 | 0 | 0 | 0 | off_peak | 619.86 |  |  | 0 | 0 | 100 | 0 | 0
7540 | 544.46 | 0 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 544.46 | 0 | 0.05921 | 6.4641 | 0 | 0 | 0 | 0 | off_peak | 544.46 |  |  | 0 | 0 | 100 | 0 | 0
7541 | 600.23 | 0 | 21.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 600.23 | 0 | 0.05921 | 5.9005 | 0 | 0 | 0 | 0 | off_peak | 600.23 |  |  | 0 | 0 | 100 | 0 | 0
7542 | 660.71 | 0 | 21.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 660.71 | 0 | 0.05921 | 5.4583 | 0 | 0 | 0 | 0 | off_peak | 660.71 |  |  | 0 | 0 | 100 | 0 | 0
7543 | 650.39 | 0 | 21.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 650.39 | 0 | 0.05921 | 4.97 | 0 | 0 | 0 | 0 | off_peak | 650.39 |  |  | 0 | 0 | 100 | 0 | 0
7544 | 719.33 | 121.406 | 22.4 | 19.8519 | 19.8519 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 699.4781 | 0 | 0.05921 | 4.6405 | 0 | 0 | 0 | 19.8519 | off_peak | 699.4781 |  |  | 2.76 | 0 | 97.24 | 92.1227 | 0
7545 | 699.44 | 314.864 | 23.3 | 51.3201 | 51.3201 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 18.9814 | 660.4822 | 0 | 0.05921 | 4.3368 | 0 | 0 | 0 | 51.3201 | off_peak | 648.1199 | 0 | 100 | 7.34 | 0 | 92.66 | 222.5653 | 0
7546 | 681.83 | 421.15 | 24.2 | 68.4228 | 68.4228 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 30.5453 | 625.7696 | 0 | 0.05921 | 4.1267 | 0 | 0 | 0 | 68.4228 | off_peak | 613.4072 | 0 | 100 | 10.04 | 0 | 89.96 | 282.3594 | 0
7547 | 688.17 | 598.405 | 25 | 96.9416 | 96.9416 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 42.1093 | 603.5908 | 0 | 0.05921 | 4.0289 | 0 | 0 | 0 | 96.9416 | off_peak | 591.2284 | 0 | 100 | 14.09 | 0 | 85.91 | 390.5677 | 0
7548 | 720.34 | 687.489 | 25.7 | 111.0926 | 111.0926 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 42.1093 | 609.2474 | 0 | 0.05921 | 4.0483 | 0 | 0 | 0 | 111.0926 | off_peak | 609.2474 |  |  | 15.42 | 0 | 84.58 | 449.7391 | 0
7549 | 690.05 | 693.735 | 26.1 | 111.94 | 111.94 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 42.1093 | 578.11 | 0 | 0.05921 | 4.2142 | 0 | 0 | 0 | 111.94 | off_peak | 578.11 |  |  | 16.22 | 0 | 83.78 | 471.7349 | 0
7550 | 704.39 | 632.656 | 26.3 | 102.0106 | 102.0106 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 42.1093 | 602.3794 | 0 | 0.05921 | 4.5267 | 0 | 0 | 0 | 102.0106 | off_peak | 602.3794 |  |  | 14.48 | 0 | 85.52 | 461.7757 | 0
7551 | 687.14 | 514.439 | 26.3 | 82.9491 | 82.9491 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 42.1093 | 604.1909 | 0 | 0.05921 | 5.0135 | 0 | 0 | 0 | 82.9491 | off_peak | 604.1909 |  |  | 12.07 | 0 | 87.93 | 415.8689 | 0
7552 | 724.61 | 348.282 | 26.1 | 56.1983 | 56.1983 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 42.1093 | 668.4117 | 0 | 0.05921 | 5.5158 | 0 | 0 | 0 | 56.1983 | off_peak | 668.4117 |  |  | 7.76 | 0 | 92.24 | 309.9765 | 0
7553 | 724.61 | 158.176 | 25.5 | 25.5784 | 25.5784 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 42.1093 | 699.0316 | 0 | 0.05921 | 6.0386 | 0 | 0 | 0 | 25.5784 | off_peak | 699.0316 |  |  | 3.53 | 0 | 96.47 | 154.4568 | 0
7554 | 631.81 | 9.8589 | 24.9 | 1.5977 | 1.5977 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 42.1093 | 630.2123 | 0 | 0.05921 | 6.4354 | 0 | 0 | 0 | 1.5977 | off_peak | 630.2123 |  |  | 0.25 | 0 | 99.75 | 10.2819 | 0
7555 | 591.87 | 0 | 24.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 42.1093 | 591.87 | 0 | 0.05921 | 6.9736 | 0 | 0 | 0 | 0 | off_peak | 591.87 |  |  | 0 | 0 | 100 | 0 | 0
7556 | 598.02 | 0 | 24.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 42.1093 | 598.02 | 0 | 0.05921 | 7.5396 | 0 | 0 | 0 | 0 | off_peak | 598.02 |  |  | 0 | 0 | 100 | 0 | 0
7557 | 588.04 | 0 | 24.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 42.1093 | 588.04 | 0 | 0.05921 | 7.8531 | 0 | 0 | 0 | 0 | off_peak | 588.04 |  |  | 0 | 0 | 100 | 0 | 0
7558 | 618.88 | 0 | 23.9 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 53.6732 | 631.2424 | 0 | 0.05921 | 8.0127 | 0 | 0 | 0 | 0 | off_peak | 618.88 | 0 | 100 | 0 | 0 | 100 | 0 | 0
7559 | 588.31 | 0 | 23.8 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 65.2371 | 600.6724 | 0 | 0.05921 | 7.9355 | 0 | 0 | 0 | 0 | off_peak | 588.31 | 0 | 100 | 0 | 0 | 100 | 0 | 0
7560 | 604.76 | 0 | 23.6 | 0 | 0 | 0 | 0 | 8.035 | 8.035 | 0 | 0 | 0 | 72.7532 | 612.795 | 0 | 0.05921 | 7.793 | 0 | 0 | 0 | 0 | off_peak | 604.76 | 0 | 100 | 0 | 0 | 100 | 0 | 0
7561 | 612.06 | 0 | 23.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 72.7532 | 612.06 | 0 | 0.05921 | 7.5078 | 0 | 0 | 0 | 0 | off_peak | 612.06 |  |  | 0 | 0 | 100 | 0 | 0
7562 | 605.16 | 0 | 23.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 72.7532 | 605.16 | 0 | 0.05921 | 6.9923 | 0 | 0 | 0 | 0 | off_peak | 605.16 |  |  | 0 | 0 | 100 | 0 | 0
7563 | 602.31 | 0 | 23.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 72.7532 | 602.31 | 0 | 0.05921 | 6.5683 | 0 | 0 | 0 | 0 | off_peak | 602.31 |  |  | 0 | 0 | 100 | 0 | 0
7564 | 597.79 | 0 | 23.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 72.7532 | 597.79 | 0 | 0.05921 | 6.2601 | 0 | 0 | 0 | 0 | off_peak | 597.79 |  |  | 0 | 0 | 100 | 0 | 0
7565 | 601.38 | 0 | 23.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 72.7532 | 601.38 | 0 | 0.05921 | 5.7862 | 0 | 0 | 0 | 0 | off_peak | 601.38 |  |  | 0 | 0 | 100 | 0 | 0
7566 | 622.79 | 0 | 23.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 72.7532 | 622.79 | 0 | 0.05921 | 5.2719 | 0 | 0 | 0 | 0 | off_peak | 622.79 |  |  | 0 | 0 | 100 | 0 | 0
7567 | 709.13 | 0 | 23.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 72.7532 | 709.13 | 0 | 0.05921 | 4.7218 | 0 | 0 | 0 | 0 | off_peak | 709.13 |  |  | 0 | 0 | 100 | 0 | 0
7568 | 709.8 | 100.325 | 23.8 | 16.3229 | 16.3229 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 72.7532 | 693.4771 | 0 | 0.05921 | 4.3191 | 0 | 0 | 0 | 16.3229 | off_peak | 693.4771 |  |  | 2.3 | 0 | 97.7 | 70.5 | 0
7569 | 720.83 | 324.602 | 24.4 | 52.6991 | 52.6991 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 72.7532 | 668.1309 | 0 | 0.05921 | 4.0356 | 0 | 0 | 0 | 52.6991 | off_peak | 668.1309 |  |  | 7.31 | 0 | 92.69 | 212.674 | 0
7570 | 760.68 | 454.147 | 24.9 | 73.5983 | 73.5983 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 72.7532 | 687.0817 | 0 | 0.05921 | 3.8409 | 0 | 0 | 0 | 73.5983 | off_peak | 687.0817 |  |  | 9.68 | 0 | 90.32 | 282.6829 | 0
7571 | 733.22 | 507.873 | 25.2 | 82.2162 | 82.2162 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 72.7532 | 651.0038 | 0 | 0.05921 | 3.7447 | 0 | 0 | 0 | 82.2162 | off_peak | 651.0038 |  |  | 11.21 | 0 | 88.79 | 307.8738 | 0
7572 | 755.29 | 670.242 | 25.4 | 108.4228 | 108.4228 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 72.7532 | 646.8672 | 0 | 0.05921 | 3.7664 | 0 | 0 | 0 | 108.4228 | off_peak | 646.8672 |  |  | 14.36 | 0 | 85.64 | 408.3636 | 0
7573 | 723.19 | 596.067 | 25.5 | 96.389 | 96.389 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 72.7532 | 626.801 | 0 | 0.05921 | 3.8749 | 0 | 0 | 0 | 96.389 | off_peak | 626.801 |  |  | 13.33 | 0 | 86.67 | 373.495 | 0
7574 | 689.6 | 591.348 | 25.5 | 95.6259 | 95.6259 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 72.7532 | 593.9741 | 0 | 0.05921 | 4.1591 | 0 | 0 | 0 | 95.6259 | off_peak | 593.9741 |  |  | 13.87 | 0 | 86.13 | 397.7161 | 0
7575 | 706.25 | 464.766 | 25.4 | 75.1837 | 75.1837 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 72.7532 | 631.0663 | 0 | 0.05921 | 4.7224 | 0 | 0 | 0 | 75.1837 | off_peak | 631.0663 |  |  | 10.65 | 0 | 89.35 | 355.0482 | 0
7576 | 684.85 | 326.141 | 25.2 | 52.7968 | 52.7968 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 72.7532 | 632.0532 | 0 | 0.05921 | 5.2338 | 0 | 0 | 0 | 52.7968 | off_peak | 632.0532 |  |  | 7.71 | 0 | 92.29 | 276.3255 | 0
7577 | 685.92 | 142.691 | 24.8 | 23.1326 | 23.1326 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 72.7532 | 662.7874 | 0 | 0.05921 | 5.6393 | 0 | 0 | 0 | 23.1326 | off_peak | 662.7874 |  |  | 3.37 | 0 | 96.63 | 130.4514 | 0
7578 | 649.03 | 8.75 | 24.3 | 1.4211 | 0 | 0 | 1.4211 | 1.4211 | 0 | 0 | 0 | 0 | 74.0825 | 649.03 | 0 | 0.05921 | 6.0268 | 0 | 0 | 1.3293 | 0 | off_peak | 649.03 | 100 | 0 | 0 | 0 | 100 | 0 | 0
7579 | 575.77 | 0 | 24.1 | 0 | 0 | 0 | 0 | 0.091781 | 0.091781 | 0 | 0 | 0 | 74.1683 | 575.8618 | 0 | 0.05921 | 6.3875 | 0 | 0 | 1.3293 | 0 | off_peak | 575.77 | 0 | 100 | 0 | 0 | 100 | 0 | 0
7580 | 567.92 | 0 | 24 | 0 | 0 | 0 | 0 | 0.0059278 | 0.0059278 | 0 | 0 | 0 | 74.1739 | 567.9259 | 0 | 0.05921 | 6.7362 | 0 | 0 | 1.3293 | 0 | off_peak | 567.92 | 0 | 100 | 0 | 0 | 100 | 0 | 0
7581 | 561.89 | 0 | 23.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1739 | 561.89 | 0 | 0.05921 | 7.0445 | 0 | 0 | 1.3293 | 0 | off_peak | 561.89 |  |  | 0 | 0 | 100 | 0 | 0
7582 | 580.94 | 0 | 23.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1739 | 580.94 | 0 | 0.05921 | 7.2483 | 0 | 0 | 1.3293 | 0 | off_peak | 580.94 |  |  | 0 | 0 | 100 | 0 | 0
7583 | 571.51 | 0 | 23.8 | 0 | 0 | 0 | 0 | 0.00038285 | 0.00038285 | 0 | 0 | 0 | 74.1742 | 571.5104 | 0 | 0.05921 | 7.4462 | 0 | 0 | 1.3293 | 0 | off_peak | 571.51 | 0 | 100 | 0 | 0 | 100 | 0 | 0
7584 | 558.43 | 0 | 23.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1742 | 558.43 | 0 | 0.05921 | 7.3991 | 0 | 0 | 1.3293 | 0 | off_peak | 558.43 |  |  | 0 | 0 | 100 | 0 | 0
7585 | 564.11 | 0 | 23.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1742 | 564.11 | 0 | 0.05921 | 7.3144 | 0 | 0 | 1.3293 | 0 | off_peak | 564.11 |  |  | 0 | 0 | 100 | 0 | 0
7586 | 544.96 | 0 | 23.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1742 | 544.96 | 0 | 0.05921 | 6.9712 | 0 | 0 | 1.3293 | 0 | off_peak | 544.96 |  |  | 0 | 0 | 100 | 0 | 0
7587 | 545.63 | 0 | 23.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1742 | 545.63 | 0 | 0.05921 | 6.5379 | 0 | 0 | 1.3293 | 0 | off_peak | 545.63 |  |  | 0 | 0 | 100 | 0 | 0
7588 | 543.45 | 0 | 23.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1742 | 543.45 | 0 | 0.05921 | 6.0459 | 0 | 0 | 1.3293 | 0 | off_peak | 543.45 |  |  | 0 | 0 | 100 | 0 | 0
7589 | 582.62 | 0 | 23.5 | 0 | 0 | 0 | 0 | 2.6434e-05 | 2.6434e-05 | 0 | 0 | 0 | 74.1743 | 582.62 | 0 | 0.05921 | 5.3823 | 0 | 0 | 1.3293 | 0 | off_peak | 582.62 | 0 | 100 | 0 | 0 | 100 | 0 | 0
7590 | 591.11 | 0 | 23.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1743 | 591.11 | 0 | 0.05921 | 4.7634 | 0 | 0 | 1.3293 | 0 | off_peak | 591.11 |  |  | 0 | 0 | 100 | 0 | 0
7591 | 665.52 | 0 | 23.8 | 0 | 0 | 0 | 0 | 0 | 0 | 1.2434 | 1.2434 | 0 | 72.845 | 664.2766 | 0 | 0.088511 | 4.2058 | 1.2434 | 0 | 0 | 1.2434 | on_peak | 664.2766 |  |  | 0 | 0.19 | 99.81 | 5.2297 | 0
7592 | 784.44 | 73.0065 | 24.4 | 11.8526 | 11.8526 | 0 | 0 | 0 | 0 | 61.2018 | 61.2018 | 0 | 7.4174 | 711.3856 | 0 | 0.088511 | 3.8891 | 0 | 0 | 0 | 11.8526 | on_peak | 711.3856 |  |  | 1.51 | 7.8 | 90.69 | 46.0956 | 0
7593 | 797.32 | 280.306 | 25.1 | 45.3932 | 45.3932 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 751.9268 | 0 | 0.088511 | 3.6844 | 0 | 0 | 0 | 45.3932 | on_peak | 751.9268 |  |  | 5.69 | 0 | 94.31 | 167.2486 | 0
7594 | 764.49 | 195.465 | 25.5 | 31.6083 | 31.6083 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 732.8817 | 0 | 0.088511 | 3.5733 | 0 | 0 | 0 | 31.6083 | on_peak | 732.8817 |  |  | 4.13 | 0 | 95.87 | 112.9448 | 0
7595 | 808.12 | 502.132 | 25.8 | 81.1111 | 81.1111 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 18.9814 | 739.3713 | 0 | 0.05921 | 3.6423 | 0 | 0 | 0 | 81.1111 | off_peak | 727.0089 | 0 | 100 | 10.04 | 0 | 89.96 | 295.4293 | 0
7596 | 848.89 | 391.548 | 26 | 63.2024 | 63.2024 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 30.5453 | 798.05 | 0 | 0.05921 | 3.9064 | 0 | 0 | 0 | 63.2024 | off_peak | 785.6876 | 0 | 100 | 7.45 | 0 | 92.55 | 246.896 | 0
7597 | 799.61 | 296.125 | 26.1 | 47.7823 | 47.7823 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 42.1093 | 764.1901 | 0 | 0.05921 | 4.3408 | 0 | 0 | 0 | 47.7823 | off_peak | 751.8277 | 0 | 100 | 5.98 | 0 | 94.02 | 207.4141 | 0
7598 | 824.37 | 473.836 | 26 | 76.4851 | 76.4851 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 53.6732 | 760.2473 | 0 | 0.05921 | 4.6307 | 0 | 0 | 0 | 76.4851 | off_peak | 747.8849 | 0 | 100 | 9.28 | 0 | 90.72 | 354.1772 | 0
7599 | 834.21 | 354.974 | 25.9 | 57.3195 | 57.3195 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 65.2371 | 789.2529 | 0 | 0.05921 | 4.9545 | 0 | 0 | 0 | 57.3195 | off_peak | 776.8905 | 0 | 100 | 6.87 | 0 | 93.13 | 283.9879 | 0
7600 | 810.74 | 215.173 | 25.6 | 34.7827 | 34.7827 | 0 | 0 | 8.9371 | 8.9371 | 0 | 0 | 0 | 73.597 | 784.8944 | 0 | 0.05921 | 5.216 | 0 | 0 | 0 | 34.7827 | off_peak | 775.9573 | 0 | 100 | 4.29 | 0 | 95.71 | 181.4283 | 0
7601 | 819.92 | 140.991 | 25.1 | 22.8323 | 22.8323 | 0 | 0 | 0.57721 | 0.57721 | 0 | 0 | 0 | 74.137 | 797.6649 | 0 | 0.05921 | 5.4057 | 0 | 0 | 0 | 22.8323 | off_peak | 797.0877 | 0 | 100 | 2.78 | 0 | 97.22 | 123.4239 | 0
7602 | 834.39 | 5.7 | 24.6 | 0.92473 | 0.92473 | 0 | 0 | 0.037279 | 0.037279 | 0 | 0 | 0 | 74.1718 | 833.5025 | 0 | 0.05921 | 5.6515 | 0 | 0 | 0 | 0.92473 | off_peak | 833.4653 | 0 | 100 | 0.11 | 0 | 99.89 | 5.2261 | 0
7603 | 818.21 | 0 | 24.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1718 | 818.21 | 0 | 0.088511 | 5.7926 | 0 | 0 | 0 | 0 | on_peak | 818.21 |  |  | 0 | 0 | 100 | 0 | 0
7604 | 832.49 | 0 | 24.3 | 0 | 0 | 0 | 0 | 0 | 0 | 7.1843 | 7.1843 | 0 | 66.4915 | 825.3057 | 0 | 0.088511 | 6.0224 | 0 | 0 | 0 | 0 | on_peak | 825.3057 |  |  | 0 | 0.86 | 99.14 | 0 | 0
7605 | 815.39 | 0 | 24.3 | 0 | 0 | 0 | 0 | 0 | 0 | 55.2587 | 55.2587 | 0 | 7.4174 | 760.1313 | 0 | 0.088511 | 6.2823 | 0 | 0 | 0 | 0 | on_peak | 760.1313 |  |  | 0 | 6.78 | 93.22 | 0 | 0
7606 | 783.34 | 0 | 24.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 783.34 | 0 | 0.088511 | 6.353 | 0 | 0 | 0 | 0 | on_peak | 783.34 |  |  | 0 | 0 | 100 | 0 | 0
7607 | 812.73 | 0 | 24.3 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 18.9814 | 825.0924 | 0 | 0.05921 | 6.3542 | 0 | 0 | 0 | 0 | off_peak | 812.73 | 0 | 100 | 0 | 0 | 100 | 0 | 0
7608 | 781.38 | 0 | 24.2 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 30.5453 | 793.7424 | 0 | 0.05921 | 6.5279 | 0 | 0 | 0 | 0 | off_peak | 781.38 | 0 | 100 | 0 | 0 | 100 | 0 | 0
7609 | 731.97 | 0 | 24.1 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 42.1093 | 744.3324 | 0 | 0.05921 | 6.6038 | 0 | 0 | 0 | 0 | off_peak | 731.97 | 0 | 100 | 0 | 0 | 100 | 0 | 0
7610 | 679.03 | 0 | 24 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 53.6732 | 691.3924 | 0 | 0.05921 | 6.4208 | 0 | 0 | 0 | 0 | off_peak | 679.03 | 0 | 100 | 0 | 0 | 100 | 0 | 0
7611 | 599.83 | 0 | 23.9 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 65.2371 | 612.1924 | 0 | 0.05921 | 6.0778 | 0 | 0 | 0 | 0 | off_peak | 599.83 | 0 | 100 | 0 | 0 | 100 | 0 | 0
7612 | 625.17 | 0 | 23.9 | 0 | 0 | 0 | 0 | 8.9371 | 8.9371 | 0 | 0 | 0 | 73.597 | 634.1071 | 0 | 0.05921 | 5.6503 | 0 | 0 | 0 | 0 | off_peak | 625.17 | 0 | 100 | 0 | 0 | 100 | 0 | 0
7613 | 599.37 | 0 | 23.9 | 0 | 0 | 0 | 0 | 0.57721 | 0.57721 | 0 | 0 | 0 | 74.137 | 599.9472 | 0 | 0.05921 | 5.1585 | 0 | 0 | 0 | 0 | off_peak | 599.37 | 0 | 100 | 0 | 0 | 100 | 0 | 0
7614 | 640.95 | 0 | 23.9 | 0 | 0 | 0 | 0 | 0.037279 | 0.037279 | 0 | 0 | 0 | 74.1718 | 640.9873 | 0 | 0.05921 | 4.5449 | 0 | 0 | 0 | 0 | off_peak | 640.95 | 0 | 100 | 0 | 0 | 100 | 0 | 0
7615 | 740.31 | 0 | 24.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1718 | 740.31 | 0 | 0.088511 | 4.0226 | 0 | 0 | 0 | 0 | on_peak | 740.31 |  |  | 0 | 0 | 100 | 0 | 0
7616 | 742.78 | 53.0706 | 24.8 | 8.6036 | 8.6036 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1718 | 734.1764 | 0 | 0.088511 | 3.7282 | 0 | 0 | 0 | 8.6036 | on_peak | 734.1764 |  |  | 1.16 | 0 | 98.84 | 32.0765 | 0
7617 | 746.44 | 143.326 | 25.5 | 23.177 | 23.177 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1718 | 723.263 | 0 | 0.088511 | 3.5217 | 0 | 0 | 0 | 23.177 | on_peak | 723.263 |  |  | 3.11 | 0 | 96.89 | 81.6222 | 0
7618 | 813.13 | 250.647 | 25.9 | 40.4733 | 40.4733 | 0 | 0 | 0 | 0 | 62.443 | 62.443 | 0 | 7.4174 | 710.2137 | 0 | 0.088511 | 3.4294 | 0 | 0 | 0 | 40.4733 | on_peak | 710.2137 |  |  | 4.98 | 7.68 | 87.34 | 138.7995 | 0
7619 | 769.5 | 327.786 | 26.2 | 52.8719 | 52.8719 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 18.9814 | 728.9904 | 0 | 0.05921 | 3.4481 | 0 | 0 | 0 | 52.8719 | off_peak | 716.6281 | 0 | 100 | 6.87 | 0 | 93.13 | 182.3053 | 0
7620 | 847.86 | 403.939 | 26.4 | 65.1083 | 65.1083 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 30.5453 | 795.1141 | 0 | 0.05921 | 3.7706 | 0 | 0 | 0 | 65.1083 | off_peak | 782.7517 | 0 | 100 | 7.68 | 0 | 92.32 | 245.5004 | 0
7621 | 785.26 | 426.342 | 26.4 | 68.7193 | 68.7193 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 42.1093 | 728.9031 | 0 | 0.05921 | 4.265 | 0 | 0 | 0 | 68.7193 | off_peak | 716.5407 | 0 | 100 | 8.75 | 0 | 91.25 | 293.0906 | 0
7622 | 795.32 | 236.14 | 26.4 | 38.0619 | 38.0619 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 53.6732 | 769.6205 | 0 | 0.05921 | 4.5793 | 0 | 0 | 0 | 38.0619 | off_peak | 757.2581 | 0 | 100 | 4.79 | 0 | 95.21 | 174.2978 | 0
7623 | 801.45 | 252.069 | 26.2 | 40.6588 | 40.6588 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 65.2371 | 773.1536 | 0 | 0.05921 | 4.7423 | 0 | 0 | 0 | 40.6588 | off_peak | 760.7912 | 0 | 100 | 5.07 | 0 | 94.93 | 192.8167 | 0
7624 | 766.2 | 134.334 | 26 | 21.6838 | 21.6838 | 0 | 0 | 8.9371 | 8.9371 | 0 | 0 | 0 | 73.597 | 753.4533 | 0 | 0.05921 | 4.9566 | 0 | 0 | 0 | 21.6838 | off_peak | 744.5162 | 0 | 100 | 2.83 | 0 | 97.17 | 107.4768 | 0
7625 | 778.36 | 38.1999 | 25.6 | 6.175 | 6.175 | 0 | 0 | 0.57721 | 0.57721 | 0 | 0 | 0 | 74.137 | 772.7622 | 0 | 0.05921 | 5.0888 | 0 | 0 | 0 | 6.175 | off_peak | 772.185 | 0 | 100 | 0.79 | 0 | 99.21 | 31.4233 | 0
7626 | 800.78 | 4.75 | 25.2 | 0.76895 | 0.73167 | 0 | 0.037279 | 0.037279 | 0 | 0 | 0 | 0 | 74.1718 | 800.0483 | 0 | 0.05921 | 5.2062 | 0 | 0 | 0.034872 | 0.73167 | off_peak | 800.0483 | 100 | 0 | 0.09 | 0 | 99.91 | 3.8092 | 0
7627 | 734.64 | 0 | 25.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0.032619 | 0.032619 | 0 | 74.137 | 734.6074 | 0 | 0.088511 | 5.3551 | 0.032619 | 0 | 0 | 0.032619 | on_peak | 734.6074 |  |  | 0 | 0 | 100 | 0.17468 | 0
7628 | 758.15 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.137 | 758.15 | 0 | 0.088511 | 5.657 | 0 | 0 | 0 | 0 | on_peak | 758.15 |  |  | 0 | 0 | 100 | 0 | 0
7629 | 762 | 0 | 24.9 | 0 | 0 | 0 | 0 | 0 | 0 | 62.4104 | 62.4104 | 0 | 7.4174 | 699.5896 | 0 | 0.088511 | 5.6922 | 0 | 0 | 0 | 0 | on_peak | 699.5896 |  |  | 0 | 8.19 | 91.81 | 0 | 0
7630 | 690.15 | 0 | 24.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 690.15 | 0 | 0.088511 | 5.7615 | 0 | 0 | 0 | 0 | on_peak | 690.15 |  |  | 0 | 0 | 100 | 0 | 0
7631 | 721.79 | 0 | 24.6 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 18.9814 | 734.1524 | 0 | 0.05921 | 5.8217 | 0 | 0 | 0 | 0 | off_peak | 721.79 | 0 | 100 | 0 | 0 | 100 | 0 | 0
7632 | 736.6 | 0 | 24.5 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 30.5453 | 748.9624 | 0 | 0.05921 | 6.0414 | 0 | 0 | 0 | 0 | off_peak | 736.6 | 0 | 100 | 0 | 0 | 100 | 0 | 0
7633 | 681.07 | 0 | 24.3 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 42.1093 | 693.4324 | 0 | 0.05921 | 6.1854 | 0 | 0 | 0 | 0 | off_peak | 681.07 | 0 | 100 | 0 | 0 | 100 | 0 | 0
7634 | 602.8 | 0 | 24.2 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 53.6732 | 615.1624 | 0 | 0.05921 | 5.9875 | 0 | 0 | 0 | 0 | off_peak | 602.8 | 0 | 100 | 0 | 0 | 100 | 0 | 0
7635 | 564.15 | 0 | 24.1 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 65.2371 | 576.5124 | 0 | 0.05921 | 5.7147 | 0 | 0 | 0 | 0 | off_peak | 564.15 | 0 | 100 | 0 | 0 | 100 | 0 | 0
7636 | 548.03 | 0 | 24 | 0 | 0 | 0 | 0 | 8.9371 | 8.9371 | 0 | 0 | 0 | 73.597 | 556.9671 | 0 | 0.05921 | 12.0494 | 0 | 0 | 0 | 0 | off_peak | 548.03 | 0 | 100 | 0 | 0 | 100 | 0 | 0
7637 | 592.37 | 0 | 23.9 | 0 | 0 | 0 | 0 | 0.57721 | 0.57721 | 0 | 0 | 0 | 74.137 | 592.9472 | 0 | 0.05921 | 11.9749 | 0 | 0 | 0 | 0 | off_peak | 592.37 | 0 | 100 | 0 | 0 | 100 | 0 | 0
7638 | 597.61 | 0 | 23.9 | 0 | 0 | 0 | 0 | 0.037279 | 0.037279 | 0 | 0 | 0 | 74.1718 | 597.6473 | 0 | 0.05921 | 11.8001 | 0 | 0 | 0 | 0 | off_peak | 597.61 | 0 | 100 | 0 | 0 | 100 | 0 | 0
7639 | 697.23 | 0 | 24.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1718 | 697.23 | 0 | 0.088511 | 3.8923 | 0 | 0 | 0 | 0 | on_peak | 697.23 |  |  | 0 | 0 | 100 | 0 | 0
7640 | 754.96 | 7.6 | 24.8 | 1.2321 | 1.2321 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1718 | 753.7279 | 0 | 0.088511 | 3.602 | 0 | 0 | 0 | 1.2321 | on_peak | 753.7279 |  |  | 0.16 | 0 | 99.84 | 4.438 | 0
7641 | 837.28 | 17.1 | 25.4 | 2.7662 | 2.7662 | 0 | 0 | 0 | 0 | 9.2081 | 9.2081 | 0 | 64.3279 | 825.3057 | 0 | 0.088511 | 3.4129 | 0 | 0 | 0 | 2.7662 | on_peak | 825.3057 |  |  | 0.33 | 1.1 | 98.57 | 9.4409 | 0
7642 | 804.25 | 49.4 | 25.8 | 7.9798 | 7.9798 | 0 | 0 | 0 | 0 | 53.2349 | 53.2349 | 0 | 7.4174 | 743.0353 | 0 | 0.088511 | 3.3199 | 0 | 0 | 0 | 7.9798 | on_peak | 743.0353 |  |  | 0.99 | 6.62 | 92.39 | 26.4922 | 0
7643 | 758.78 | 67.45 | 26.1 | 10.8836 | 10.8836 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 18.9814 | 760.2587 | 0 | 0.05921 | 3.3312 | 0 | 0 | 0 | 10.8836 | off_peak | 747.8964 | 0 | 100 | 1.43 | 0 | 98.57 | 36.2551 | 0
7644 | 821.85 | 38.95 | 26.3 | 6.2804 | 6.2804 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 30.5453 | 827.932 | 0 | 0.05921 | 3.6704 | 0 | 0 | 0 | 6.2804 | off_peak | 815.5696 | 0 | 100 | 0.76 | 0 | 99.24 | 23.0512 | 0
7645 | 771.87 | 52.25 | 26.4 | 8.4218 | 8.4218 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 42.1093 | 775.8105 | 0 | 0.05921 | 4.134 | 0 | 0 | 0 | 8.4218 | off_peak | 763.4482 | 0 | 100 | 1.09 | 0 | 98.91 | 34.8156 | 0
7646 | 814.74 | 53.2 | 26.5 | 8.5719 | 8.5719 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 53.6732 | 818.5305 | 0 | 0.05921 | 4.4683 | 0 | 0 | 0 | 8.5719 | off_peak | 806.1681 | 0 | 100 | 1.05 | 0 | 98.95 | 38.3019 | 0
7647 | 818.59 | 27.55 | 26.4 | 4.4406 | 4.4406 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 65.2371 | 826.5118 | 0 | 0.05921 | 4.6827 | 0 | 0 | 0 | 4.4406 | off_peak | 814.1494 | 0 | 100 | 0.54 | 0 | 99.46 | 20.7941 | 0
7648 | 785.04 | 18.05 | 26.2 | 2.9115 | 2.9115 | 0 | 0 | 8.9371 | 8.9371 | 0 | 0 | 0 | 73.597 | 791.0656 | 0 | 0.05921 | 4.8906 | 0 | 0 | 0 | 2.9115 | off_peak | 782.1285 | 0 | 100 | 0.37 | 0 | 99.63 | 14.2388 | 0
7649 | 772.64 | 12.35 | 25.8 | 1.9949 | 1.9949 | 0 | 0 | 0.57721 | 0.57721 | 0 | 0 | 0 | 74.137 | 771.2223 | 0 | 0.05921 | 5.034 | 0 | 0 | 0 | 1.9949 | off_peak | 770.6451 | 0 | 100 | 0.26 | 0 | 99.74 | 10.0424 | 0
7650 | 835.89 | 2.85 | 25.3 | 0.4612 | 0.4612 | 0 | 0 | 0.037279 | 0.037279 | 0 | 0 | 0 | 74.1718 | 835.4661 | 0 | 0.05921 | 5.1109 | 0 | 0 | 0 | 0.4612 | off_peak | 835.4288 | 0 | 100 | 0.06 | 0 | 99.94 | 2.3572 | 0
7651 | 796.26 | 0 | 25.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1718 | 796.26 | 0 | 0.088511 | 5.0555 | 0 | 0 | 0 | 0 | on_peak | 796.26 |  |  | 0 | 0 | 100 | 0 | 0
7652 | 756.02 | 0 | 24.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1718 | 756.02 | 0 | 0.088511 | 4.9887 | 0 | 0 | 0 | 0 | on_peak | 756.02 |  |  | 0 | 0 | 100 | 0 | 0
7653 | 799.42 | 0 | 24.9 | 0 | 0 | 0 | 0 | 0 | 0 | 62.443 | 62.443 | 0 | 7.4174 | 736.977 | 0 | 0.088511 | 4.9767 | 0 | 0 | 0 | 0 | on_peak | 736.977 |  |  | 0 | 7.81 | 92.19 | 0 | 0
7654 | 741.11 | 0 | 24.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 741.11 | 0 | 0.088511 | 4.9847 | 0 | 0 | 0 | 0 | on_peak | 741.11 |  |  | 0 | 0 | 100 | 0 | 0
7655 | 787.73 | 0 | 24.7 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 18.9814 | 800.0924 | 0 | 0.05921 | 5.1059 | 0 | 0 | 0 | 0 | off_peak | 787.73 | 0 | 100 | 0 | 0 | 100 | 0 | 0
7656 | 743.31 | 0 | 24.5 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 30.5453 | 755.6724 | 0 | 0.05921 | 5.2509 | 0 | 0 | 0 | 0 | off_peak | 743.31 | 0 | 100 | 0 | 0 | 100 | 0 | 0
7657 | 692.68 | 0 | 24.4 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 42.1093 | 705.0424 | 0 | 0.05921 | 5.3496 | 0 | 0 | 0 | 0 | off_peak | 692.68 | 0 | 100 | 0 | 0 | 100 | 0 | 0
7658 | 645.14 | 0 | 24.2 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 53.6732 | 657.5024 | 0 | 0.05921 | 5.1976 | 0 | 0 | 0 | 0 | off_peak | 645.14 | 0 | 100 | 0 | 0 | 100 | 0 | 0
7659 | 633.91 | 0 | 24.1 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 65.2371 | 646.2724 | 0 | 0.05921 | 5.0128 | 0 | 0 | 0 | 0 | off_peak | 633.91 | 0 | 100 | 0 | 0 | 100 | 0 | 0
7660 | 637.05 | 0 | 24 | 0 | 0 | 0 | 0 | 8.9371 | 8.9371 | 0 | 0 | 0 | 73.597 | 645.9871 | 0 | 0.05921 | 4.6165 | 0 | 0 | 0 | 0 | off_peak | 637.05 | 0 | 100 | 0 | 0 | 100 | 0 | 0
7661 | 633.16 | 0 | 24 | 0 | 0 | 0 | 0 | 0.57721 | 0.57721 | 0 | 0 | 0 | 74.137 | 633.7372 | 0 | 0.05921 | 4.1689 | 0 | 0 | 0 | 0 | off_peak | 633.16 | 0 | 100 | 0 | 0 | 100 | 0 | 0
7662 | 610.05 | 0 | 24 | 0 | 0 | 0 | 0 | 0.037279 | 0.037279 | 0 | 0 | 0 | 74.1718 | 610.0873 | 0 | 0.05921 | 3.6186 | 0 | 0 | 0 | 0 | off_peak | 610.05 | 0 | 100 | 0 | 0 | 100 | 0 | 0
7663 | 655.22 | 0 | 24.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1718 | 655.22 | 0 | 0.088511 | 3.2636 | 0 | 0 | 0 | 0 | on_peak | 655.22 |  |  | 0 | 0 | 100 | 0 | 0
7664 | 734.27 | 76.4866 | 24.9 | 12.3953 | 12.3953 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1718 | 721.8747 | 0 | 0.088511 | 3.0081 | 0 | 0 | 0 | 12.3953 | on_peak | 721.8747 |  |  | 1.69 | 0 | 98.31 | 37.286 | 0
7665 | 750.49 | 251.227 | 25.7 | 40.5962 | 40.5962 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1718 | 709.8938 | 0 | 0.088511 | 2.8701 | 0 | 0 | 0 | 40.5962 | on_peak | 709.8938 |  |  | 5.41 | 0 | 94.59 | 116.5155 | 0
7666 | 729.83 | 420.516 | 26.1 | 67.8538 | 67.8538 | 0 | 0 | 0 | 0 | 62.443 | 62.443 | 0 | 7.4174 | 599.5331 | 0 | 0.088511 | 2.7837 | 0 | 0 | 0 | 67.8538 | on_peak | 599.5331 |  |  | 9.3 | 8.56 | 82.15 | 188.8814 | 0
7667 | 760.27 | 518.004 | 26.5 | 83.4635 | 83.4635 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 18.9814 | 689.1689 | 0 | 0.05921 | 2.7962 | 0 | 0 | 0 | 83.4635 | off_peak | 676.8065 | 0 | 100 | 10.98 | 0 | 89.02 | 233.3782 | 0
7668 | 773.02 | 407.838 | 26.8 | 65.6416 | 65.6416 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 30.5453 | 719.7408 | 0 | 0.05921 | 3.1157 | 0 | 0 | 0 | 65.6416 | off_peak | 707.3784 | 0 | 100 | 8.49 | 0 | 91.51 | 204.5167 | 0
7669 | 734.98 | 446.432 | 26.9 | 71.8273 | 71.8273 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 42.1093 | 675.5151 | 0 | 0.05921 | 3.5807 | 0 | 0 | 0 | 71.8273 | off_peak | 663.1527 | 0 | 100 | 9.77 | 0 | 90.23 | 257.1891 | 0
7670 | 749.41 | 377.181 | 27 | 60.6634 | 60.6634 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 53.6732 | 701.109 | 0 | 0.05921 | 3.974 | 0 | 0 | 0 | 60.6634 | off_peak | 688.7466 | 0 | 100 | 8.09 | 0 | 91.91 | 241.0771 | 0
7671 | 733.17 | 466.074 | 26.9 | 74.9875 | 74.9875 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 65.2371 | 670.5448 | 0 | 0.05921 | 4.2949 | 0 | 0 | 0 | 74.9875 | off_peak | 658.1825 | 0 | 100 | 10.23 | 0 | 89.77 | 322.0643 | 0
7672 | 733.82 | 309.039 | 26.7 | 49.7579 | 49.7579 | 0 | 0 | 8.9371 | 8.9371 | 0 | 0 | 0 | 73.597 | 692.9992 | 0 | 0.05921 | 4.5661 | 0 | 0 | 0 | 49.7579 | off_peak | 684.0621 | 0 | 100 | 6.78 | 0 | 93.22 | 227.2016 | 0
7673 | 759.04 | 131.599 | 26.2 | 21.2269 | 21.2269 | 0 | 0 | 0.57721 | 0.57721 | 0 | 0 | 0 | 74.137 | 738.3903 | 0 | 0.05921 | 4.6914 | 0 | 0 | 0 | 21.2269 | off_peak | 737.8131 | 0 | 100 | 2.8 | 0 | 97.2 | 99.5836 | 0
7674 | 778.3 | 3.803 | 25.4 | 0.61519 | 0.57791 | 0 | 0.037279 | 0.037279 | 0 | 0 | 0 | 0 | 74.1718 | 777.7221 | 0 | 0.05921 | 4.7371 | 0 | 0 | 0.034872 | 0.57791 | off_peak | 777.7221 | 100 | 0 | 0.07 | 0 | 99.93 | 2.7376 | 0
7675 | 767.89 | 0 | 25.1 | 0 | 0 | 0 | 0 | 0 | 0 | 62.443 | 62.443 | 0 | 7.4174 | 705.447 | 0 | 0.088511 | 4.837 | 0 | 0 | 0.034872 | 0 | on_peak | 705.447 |  |  | 0 | 8.13 | 91.87 | 0 | 0
7676 | 802.56 | 0 | 24.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 802.56 | 0 | 0.088511 | 4.9231 | 0 | 0 | 0.034872 | 0 | on_peak | 802.56 |  |  | 0 | 0 | 100 | 0 | 0
7677 | 786.81 | 0 | 24.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 786.81 | 0 | 0.088511 | 5.017 | 0 | 0 | 0.034872 | 0 | on_peak | 786.81 |  |  | 0 | 0 | 100 | 0 | 0
7678 | 715.12 | 0 | 24.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 715.12 | 0 | 0.088511 | 5.1202 | 0 | 0 | 0.034872 | 0 | on_peak | 715.12 |  |  | 0 | 0 | 100 | 0 | 0
7679 | 738.87 | 0 | 24 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 18.9814 | 751.2324 | 0 | 0.05921 | 5.2746 | 0 | 0 | 0.034872 | 0 | off_peak | 738.87 | 0 | 100 | 0 | 0 | 100 | 0 | 0
7680 | 725.73 | 0 | 23.9 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 30.5453 | 738.0924 | 0 | 0.05921 | 5.5504 | 0 | 0 | 0.034872 | 0 | off_peak | 725.73 | 0 | 100 | 0 | 0 | 100 | 0 | 0
7681 | 698.16 | 0 | 23.8 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 42.1093 | 710.5224 | 0 | 0.05921 | 5.7383 | 0 | 0 | 0.034872 | 0 | off_peak | 698.16 | 0 | 100 | 0 | 0 | 100 | 0 | 0
7682 | 639.51 | 0 | 23.7 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 53.6732 | 651.8724 | 0 | 0.05921 | 0.12884 | 0 | 0 | 0.034872 | 0 | off_peak | 639.51 | 0 | 100 | 0 | 0 | 100 | 0 | 0
7683 | 582.16 | 0 | 23.7 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 65.2371 | 594.5224 | 0 | 0.05921 | 0.12229 | 0 | 0 | 0.034872 | 0 | off_peak | 582.16 | 0 | 100 | 0 | 0 | 100 | 0 | 0
7684 | 602.14 | 0 | 23.7 | 0 | 0 | 0 | 0 | 8.9371 | 8.9371 | 0 | 0 | 0 | 73.597 | 611.0771 | 0 | 0.05921 | 0.10348 | 0 | 0 | 0.034872 | 0 | off_peak | 602.14 | 0 | 100 | 0 | 0 | 100 | 0 | 0
7685 | 576.22 | 0 | 23.5 | 0 | 0 | 0 | 0 | 0.57721 | 0.57721 | 0 | 0 | 0 | 74.137 | 576.7972 | 0 | 0.05921 | 0.10021 | 0 | 0 | 0.034872 | 0 | off_peak | 576.22 | 0 | 100 | 0 | 0 | 100 | 0 | 0
7686 | 615.11 | 0 | 23.4 | 0 | 0 | 0 | 0 | 0.037279 | 0.037279 | 0 | 0 | 0 | 74.1718 | 615.1473 | 0 | 0.05921 | 0.094888 | 0 | 0 | 0.034872 | 0 | off_peak | 615.11 | 0 | 100 | 0 | 0 | 100 | 0 | 0
7687 | 711.94 | 0 | 23.5 | 0 | 0 | 0 | 0 | 0 | 0 | 62.443 | 62.443 | 0 | 7.4174 | 649.497 | 0 | 0.088511 | 3.5333 | 0.032619 | 0 | 0 | 0.032619 | on_peak | 649.497 |  |  | 0 | 8.77 | 91.23 | 0.11526 | 0
7688 | 736.51 | 98.5039 | 24.1 | 16.0093 | 16.0093 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 720.5007 | 0 | 0.088511 | 3.1479 | 0 | 0 | 0 | 16.0093 | on_peak | 720.5007 |  |  | 2.17 | 0 | 97.83 | 50.396 | 0
7689 | 819.37 | 290.317 | 24.7 | 47.0821 | 47.0821 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 772.2879 | 0 | 0.088511 | 2.9451 | 0 | 0 | 0 | 47.0821 | on_peak | 772.2879 |  |  | 5.75 | 0 | 94.25 | 138.6601 | 0
7690 | 799.53 | 470.137 | 25.2 | 76.1074 | 76.1074 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 723.4226 | 0 | 0.088511 | 2.8508 | 0 | 0 | 0 | 76.1074 | on_peak | 723.4226 |  |  | 9.52 | 0 | 90.48 | 216.9658 | 0
7691 | 809.23 | 609.694 | 25.8 | 98.486 | 98.486 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 18.9814 | 723.1064 | 0 | 0.05921 | 2.8985 | 0 | 0 | 0 | 98.486 | off_peak | 710.744 | 0 | 100 | 12.17 | 0 | 87.83 | 285.4661 | 0
7692 | 871.76 | 682.195 | 26.3 | 109.9984 | 109.9984 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 30.5453 | 774.124 | 0 | 0.05921 | 3.1776 | 0 | 0 | 0 | 109.9984 | off_peak | 761.7616 | 0 | 100 | 12.62 | 0 | 87.38 | 349.5276 | 0
7693 | 808.25 | 689.15 | 26.6 | 110.9992 | 110.9992 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 42.1093 | 709.6131 | 0 | 0.05921 | 3.6452 | 0 | 0 | 0 | 110.9992 | off_peak | 697.2508 | 0 | 100 | 13.73 | 0 | 86.27 | 404.6179 | 0
7694 | 830.3 | 628.76 | 26.7 | 101.2357 | 101.2357 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 53.6732 | 741.4266 | 0 | 0.05921 | 3.9656 | 0 | 0 | 0 | 101.2357 | off_peak | 729.0643 | 0 | 100 | 12.19 | 0 | 87.81 | 401.4578 | 0
7695 | 826.57 | 508.118 | 26.6 | 81.841 | 81.841 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 65.2371 | 757.0914 | 0 | 0.05921 | 4.1938 | 0 | 0 | 0 | 81.841 | off_peak | 744.729 | 0 | 100 | 9.9 | 0 | 90.1 | 343.2257 | 0
7696 | 792.57 | 340.769 | 26.2 | 54.9661 | 54.9661 | 0 | 0 | 8.9371 | 8.9371 | 0 | 0 | 0 | 73.597 | 746.541 | 0 | 0.05921 | 4.4314 | 0 | 0 | 0 | 54.9661 | off_peak | 737.6039 | 0 | 100 | 6.94 | 0 | 93.06 | 243.5748 | 0
7697 | 774.07 | 149.364 | 25.7 | 24.136 | 24.136 | 0 | 0 | 0.57721 | 0.57721 | 0 | 0 | 0 | 74.137 | 750.5112 | 0 | 0.05921 | 4.5878 | 0 | 0 | 0 | 24.136 | off_peak | 749.934 | 0 | 100 | 3.12 | 0 | 96.88 | 110.7314 | 0
7698 | 797.38 | 5.7144 | 25.1 | 0.92541 | 0.88813 | 0 | 0.037279 | 0.037279 | 0 | 0 | 0 | 0 | 74.1718 | 796.4919 | 0 | 0.05921 | 4.7463 | 0 | 0 | 0.034872 | 0.88813 | off_peak | 796.4919 | 100 | 0 | 0.11 | 0 | 99.89 | 4.2153 | 0
7699 | 791.63 | 0 | 24.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1718 | 791.63 | 0 | 0.088511 | 5.0741 | 0 | 0 | 0.034872 | 0 | on_peak | 791.63 |  |  | 0 | 0 | 100 | 0 | 0
7700 | 799.9 | 0 | 24.5 | 0 | 0 | 0 | 0 | 0 | 0 | 62.443 | 62.443 | 0 | 7.4174 | 737.457 | 0 | 0.088511 | 5.2738 | 0.032619 | 0 | 0 | 0.032619 | on_peak | 737.457 |  |  | 0 | 7.81 | 92.19 | 0.17203 | 0
7701 | 771.02 | 0 | 24.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 771.02 | 0 | 0.088511 | 5.4959 | 0 | 0 | 0 | 0 | on_peak | 771.02 |  |  | 0 | 0 | 100 | 0 | 0
7702 | 737.45 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 737.45 | 0 | 0.088511 | 5.8465 | 0 | 0 | 0 | 0 | on_peak | 737.45 |  |  | 0 | 0 | 100 | 0 | 0
7703 | 754.29 | 0 | 23.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 754.29 | 0 | 0.05921 | 6.1155 | 0 | 0 | 0 | 0 | off_peak | 754.29 |  |  | 0 | 0 | 100 | 0 | 0
7704 | 726.15 | 0 | 23.8 | 0 | 0 | 0 | 0 | 8.7006 | 8.7006 | 0 | 0 | 0 | 15.5561 | 734.8506 | 0 | 0.05921 | 6.1851 | 0 | 0 | 0 | 0 | off_peak | 726.15 | 0 | 100 | 0 | 0 | 100 | 0 | 0
7705 | 670.89 | 0 | 23.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15.5561 | 670.89 | 0 | 0.05921 | 6.0609 | 0 | 0 | 0 | 0 | off_peak | 670.89 |  |  | 0 | 0 | 100 | 0 | 0
7706 | 602.42 | 0 | 23.5 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 27.12 | 614.7824 | 0 | 0.05921 | 5.7476 | 0 | 0 | 0 | 0 | off_peak | 602.42 | 0 | 100 | 0 | 0 | 100 | 0 | 0
7707 | 585.68 | 0 | 23.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27.12 | 585.68 | 0 | 0.05921 | 5.4094 | 0 | 0 | 0 | 0 | off_peak | 585.68 |  |  | 0 | 0 | 100 | 0 | 0
7708 | 603.43 | 0 | 23.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27.12 | 603.43 | 0 | 0.05921 | 5.0126 | 0 | 0 | 0 | 0 | off_peak | 603.43 |  |  | 0 | 0 | 100 | 0 | 0
7709 | 584.76 | 0 | 23.2 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 38.684 | 597.1224 | 0 | 0.05921 | 4.6082 | 0 | 0 | 0 | 0 | off_peak | 584.76 | 0 | 100 | 0 | 0 | 100 | 0 | 0
7710 | 622.52 | 0 | 23.2 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 50.2479 | 634.8824 | 0 | 0.05921 | 4.1754 | 0 | 0 | 0 | 0 | off_peak | 622.52 | 0 | 100 | 0 | 0 | 100 | 0 | 0
7711 | 649.02 | 0 | 23.3 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 61.8119 | 661.3824 | 0 | 0.05921 | 3.7217 | 0 | 0 | 0 | 0 | off_peak | 649.02 | 0 | 100 | 0 | 0 | 100 | 0 | 0
7712 | 693.1 | 101.635 | 23.5 | 16.5538 | 16.5538 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 61.8119 | 676.5462 | 0 | 0.05921 | 3.3771 | 0 | 0 | 0 | 16.5538 | off_peak | 676.5462 |  |  | 2.39 | 0 | 97.61 | 55.9038 | 0
7713 | 678.96 | 248.183 | 23.9 | 40.3649 | 40.3649 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 73.3758 | 650.9575 | 0 | 0.05921 | 3.0822 | 0 | 0 | 0 | 40.3649 | off_peak | 638.5951 | 0 | 100 | 5.95 | 0 | 94.05 | 124.4127 | 0
7714 | 701.95 | 427.994 | 24.3 | 69.5098 | 69.5098 | 0 | 0 | 0.79843 | 0.79843 | 0 | 0 | 0 | 74.1227 | 633.2387 | 0 | 0.05921 | 2.9319 | 0 | 0 | 0 | 69.5098 | off_peak | 632.4402 | 0 | 100 | 9.9 | 0 | 90.1 | 203.7979 | 0
7715 | 673.43 | 404.746 | 24.8 | 65.6161 | 65.6161 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1227 | 607.8139 | 0 | 0.05921 | 2.8709 | 0 | 0 | 0 | 65.6161 | off_peak | 607.8139 |  |  | 9.74 | 0 | 90.26 | 188.3799 | 0
7716 | 702.72 | 194.982 | 25.2 | 31.5643 | 31.5643 | 0 | 0 | 0.051567 | 0.051567 | 0 | 0 | 0 | 74.1709 | 671.2072 | 0 | 0.05921 | 2.9356 | 0 | 0 | 0 | 31.5643 | off_peak | 671.1557 | 0 | 100 | 4.49 | 0 | 95.51 | 92.6613 | 0
7717 | 694.56 | 169.1 | 25.4 | 27.3548 | 27.3548 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1709 | 667.2052 | 0 | 0.05921 | 3.1724 | 0 | 0 | 0 | 27.3548 | off_peak | 667.2052 |  |  | 3.94 | 0 | 96.06 | 86.7803 | 0
7718 | 672.24 | 189.517 | 25.5 | 30.6465 | 30.6465 | 0 | 0 | 0.0033305 | 0.0033305 | 0 | 0 | 0 | 74.174 | 641.5968 | 0 | 0.05921 | 3.4325 | 0 | 0 | 0 | 30.6465 | off_peak | 641.5935 | 0 | 100 | 4.56 | 0 | 95.44 | 105.193 | 0
7719 | 679.46 | 342.853 | 25.4 | 55.4622 | 55.4622 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.174 | 623.9978 | 0 | 0.05921 | 3.6744 | 0 | 0 | 0 | 55.4622 | off_peak | 623.9978 |  |  | 8.16 | 0 | 91.84 | 203.7912 | 0
7720 | 675.87 | 125.914 | 25.2 | 20.3834 | 20.3834 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.174 | 655.4866 | 0 | 0.05921 | 3.8755 | 0 | 0 | 0 | 20.3834 | off_peak | 655.4866 |  |  | 3.02 | 0 | 96.98 | 78.9967 | 0
7721 | 644.66 | 106.273 | 25 | 17.2162 | 17.2162 | 0 | 0 | 0.0002151 | 0.0002151 | 0 | 0 | 0 | 74.1742 | 627.444 | 0 | 0.05921 | 4.1195 | 0 | 0 | 0 | 17.2162 | off_peak | 627.4438 | 0 | 100 | 2.67 | 0 | 97.33 | 70.9217 | 0
7722 | 616.52 | 3.8 | 24.7 | 0.61626 | 0.61626 | 0 | 0 | 1.4852e-05 | 1.4852e-05 | 0 | 0 | 0 | 74.1743 | 615.9038 | 0 | 0.05921 | 4.3264 | 0 | 0 | 0 | 0.61626 | off_peak | 615.9037 | 0 | 100 | 0.1 | 0 | 99.9 | 2.6662 | 0
7723 | 589.3 | 0 | 24.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1743 | 589.3 | 0 | 0.05921 | 4.4 | 0 | 0 | 0 | 0 | off_peak | 589.3 |  |  | 0 | 0 | 100 | 0 | 0
7724 | 553.16 | 0 | 24.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1743 | 553.16 | 0 | 0.05921 | 4.389 | 0 | 0 | 0 | 0 | off_peak | 553.16 |  |  | 0 | 0 | 100 | 0 | 0
7725 | 559.93 | 0 | 24.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1743 | 559.93 | 0 | 0.05921 | 4.67 | 0 | 0 | 0 | 0 | off_peak | 559.93 |  |  | 0 | 0 | 100 | 0 | 0
7726 | 551.02 | 0 | 24.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1743 | 551.02 | 0 | 0.05921 | 4.8954 | 0 | 0 | 0 | 0 | off_peak | 551.02 |  |  | 0 | 0 | 100 | 0 | 0
7727 | 577.51 | 0 | 24.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1743 | 577.51 | 0 | 0.05921 | 5.1585 | 0 | 0 | 0 | 0 | off_peak | 577.51 |  |  | 0 | 0 | 100 | 0 | 0
7728 | 553.41 | 0 | 24.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1743 | 553.41 | 0 | 0.05921 | 5.3654 | 0 | 0 | 0 | 0 | off_peak | 553.41 |  |  | 0 | 0 | 100 | 0 | 0
7729 | 548.72 | 0 | 24.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1743 | 548.72 | 0 | 0.05921 | 5.3561 | 0 | 0 | 0 | 0 | off_peak | 548.72 |  |  | 0 | 0 | 100 | 0 | 0
7730 | 554.41 | 0 | 24.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1743 | 554.41 | 0 | 0.05921 | 5.0538 | 0 | 0 | 0 | 0 | off_peak | 554.41 |  |  | 0 | 0 | 100 | 0 | 0
7731 | 586.53 | 0 | 24.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1743 | 586.53 | 0 | 0.05921 | 4.7478 | 0 | 0 | 0 | 0 | off_peak | 586.53 |  |  | 0 | 0 | 100 | 0 | 0
7732 | 524.94 | 0 | 24.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1743 | 524.94 | 0 | 0.05921 | 4.434 | 0 | 0 | 0 | 0 | off_peak | 524.94 |  |  | 0 | 0 | 100 | 0 | 0
7733 | 552.35 | 0 | 24.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1743 | 552.35 | 0 | 0.05921 | 4.0399 | 0 | 0 | 0 | 0 | off_peak | 552.35 |  |  | 0 | 0 | 100 | 0 | 0
7734 | 619.35 | 0 | 24.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1743 | 619.35 | 0 | 0.05921 | 3.6295 | 0 | 0 | 0 | 0 | off_peak | 619.35 |  |  | 0 | 0 | 100 | 0 | 0
7735 | 653.9 | 0 | 24.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1743 | 653.9 | 0 | 0.05921 | 3.1546 | 0 | 0 | 0 | 0 | off_peak | 653.9 |  |  | 0 | 0 | 100 | 0 | 0
7736 | 676.77 | 109.582 | 24.6 | 17.7778 | 17.7778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1743 | 658.9922 | 0 | 0.05921 | 2.8117 | 0 | 0 | 0 | 17.7778 | off_peak | 658.9922 |  |  | 2.63 | 0 | 97.37 | 49.9854 | 0
7737 | 738.66 | 299.54 | 25.1 | 48.508 | 48.508 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1743 | 690.152 | 0 | 0.05921 | 2.5873 | 0 | 0 | 0 | 48.508 | off_peak | 690.152 |  |  | 6.57 | 0 | 93.43 | 125.5052 | 0
7738 | 677.7 | 473.782 | 25.5 | 76.6145 | 76.6145 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1743 | 601.0855 | 0 | 0.05921 | 2.4544 | 0 | 0 | 0 | 76.6145 | off_peak | 601.0855 |  |  | 11.31 | 0 | 88.69 | 188.0454 | 0
7739 | 701.56 | 604.962 | 25.9 | 97.6863 | 97.6863 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1743 | 603.8737 | 0 | 0.05921 | 2.4003 | 0 | 0 | 0 | 97.6863 | off_peak | 603.8737 |  |  | 13.92 | 0 | 86.08 | 234.4744 | 0
7740 | 742.51 | 673.912 | 26.1 | 108.7414 | 108.7414 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1743 | 633.7686 | 0 | 0.05921 | 2.4312 | 0 | 0 | 0 | 108.7414 | off_peak | 633.7686 |  |  | 14.65 | 0 | 85.35 | 264.3743 | 0
7741 | 680.56 | 677.736 | 26.2 | 109.3189 | 109.3189 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1743 | 571.2411 | 0 | 0.05921 | 2.6038 | 0 | 0 | 0 | 109.3189 | off_peak | 571.2411 |  |  | 16.06 | 0 | 83.94 | 284.642 | 0
7742 | 691.65 | 601.66 | 26.2 | 97.0479 | 97.0479 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1743 | 594.6021 | 0 | 0.05921 | 2.8479 | 0 | 0 | 0 | 97.0479 | off_peak | 594.6021 |  |  | 14.03 | 0 | 85.97 | 276.3811 | 0
7743 | 737.1 | 456.349 | 26.2 | 73.6092 | 73.6092 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1743 | 663.4908 | 0 | 0.05921 | 2.845 | 0 | 0 | 0 | 73.6092 | off_peak | 663.4908 |  |  | 9.99 | 0 | 90.01 | 209.4196 | 0
7744 | 692.4 | 202.56 | 25.9 | 32.7084 | 32.7084 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1743 | 659.6916 | 0 | 0.05921 | 2.9657 | 0 | 0 | 0 | 32.7084 | off_peak | 659.6916 |  |  | 4.72 | 0 | 95.28 | 97.0027 | 0
7745 | 669.19 | 87.5852 | 25.5 | 14.1633 | 14.1633 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1743 | 655.0267 | 0 | 0.05921 | 3.3356 | 0 | 0 | 0 | 14.1633 | off_peak | 655.0267 |  |  | 2.12 | 0 | 97.88 | 47.2425 | 0
7746 | 605.86 | 4.75 | 25.1 | 0.76922 | 0.76922 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1743 | 605.0908 | 0 | 0.05921 | 3.6566 | 0 | 0 | 0 | 0.76922 | off_peak | 605.0908 |  |  | 0.13 | 0 | 99.87 | 2.8127 | 0
7747 | 592.23 | 0 | 24.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1743 | 592.23 | 0 | 0.05921 | 4.0924 | 0 | 0 | 0 | 0 | off_peak | 592.23 |  |  | 0 | 0 | 100 | 0 | 0
7748 | 577.69 | 0 | 24.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1743 | 577.69 | 0 | 0.05921 | 4.439 | 0 | 0 | 0 | 0 | off_peak | 577.69 |  |  | 0 | 0 | 100 | 0 | 0
7749 | 569.54 | 0 | 24.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1743 | 569.54 | 0 | 0.05921 | 4.7621 | 0 | 0 | 0 | 0 | off_peak | 569.54 |  |  | 0 | 0 | 100 | 0 | 0
7750 | 558.84 | 0 | 24.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1743 | 558.84 | 0 | 0.05921 | 5.0121 | 0 | 0 | 0 | 0 | off_peak | 558.84 |  |  | 0 | 0 | 100 | 0 | 0
7751 | 552.31 | 0 | 24.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1743 | 552.31 | 0 | 0.05921 | 5.4841 | 0 | 0 | 0 | 0 | off_peak | 552.31 |  |  | 0 | 0 | 100 | 0 | 0
7752 | 563.78 | 0 | 24.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1743 | 563.78 | 0 | 0.05921 | 5.7875 | 0 | 0 | 0 | 0 | off_peak | 563.78 |  |  | 0 | 0 | 100 | 0 | 0
7753 | 537.73 | 0 | 24.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1743 | 537.73 | 0 | 0.05921 | 5.6849 | 0 | 0 | 0 | 0 | off_peak | 537.73 |  |  | 0 | 0 | 100 | 0 | 0
7754 | 546.87 | 0 | 24.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1743 | 546.87 | 0 | 0.05921 | 5.3669 | 0 | 0 | 0 | 0 | off_peak | 546.87 |  |  | 0 | 0 | 100 | 0 | 0
7755 | 523.42 | 0 | 24.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1743 | 523.42 | 0 | 0.05921 | 5.0503 | 0 | 0 | 0 | 0 | off_peak | 523.42 |  |  | 0 | 0 | 100 | 0 | 0
7756 | 578.32 | 0 | 24.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1743 | 578.32 | 0 | 0.05921 | 4.6875 | 0 | 0 | 0 | 0 | off_peak | 578.32 |  |  | 0 | 0 | 100 | 0 | 0
7757 | 549.67 | 0 | 24.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1743 | 549.67 | 0 | 0.05921 | 4.2121 | 0 | 0 | 0 | 0 | off_peak | 549.67 |  |  | 0 | 0 | 100 | 0 | 0
7758 | 584.71 | 0 | 24.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1743 | 584.71 | 0 | 0.05921 | 3.6872 | 0 | 0 | 0 | 0 | off_peak | 584.71 |  |  | 0 | 0 | 100 | 0 | 0
7759 | 661.46 | 0 | 24.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1743 | 661.46 | 0 | 0.088511 | 3.1563 | 0 | 0 | 0 | 0 | on_peak | 661.46 |  |  | 0 | 0 | 100 | 0 | 0
7760 | 703.26 | 109.181 | 24.9 | 17.6937 | 17.6937 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1743 | 685.5663 | 0 | 0.088511 | 2.8239 | 0 | 0 | 0 | 17.6937 | on_peak | 685.5663 |  |  | 2.52 | 0 | 97.48 | 49.9658 | 0
7761 | 739.96 | 300.686 | 25.4 | 48.641 | 48.641 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1743 | 691.319 | 0 | 0.088511 | 2.6346 | 0 | 0 | 0 | 48.641 | on_peak | 691.319 |  |  | 6.57 | 0 | 93.43 | 128.1485 | 0
7762 | 796.41 | 475.995 | 25.8 | 76.8891 | 76.8891 | 0 | 0 | 0 | 0 | 62.4453 | 62.4453 | 0 | 7.4174 | 657.0756 | 0 | 0.088511 | 2.577 | 0 | 0 | 0 | 76.8891 | on_peak | 657.0756 |  |  | 9.65 | 7.84 | 82.5 | 198.1431 | 0
7763 | 755.62 | 607.232 | 26.1 | 97.982 | 97.982 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 18.9814 | 670.0003 | 0 | 0.05921 | 2.5728 | 0 | 0 | 0 | 97.982 | off_peak | 657.638 | 0 | 100 | 12.97 | 0 | 87.03 | 252.0866 | 0
7764 | 790.98 | 679.974 | 26.3 | 109.6403 | 109.6403 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 30.5453 | 693.7021 | 0 | 0.05921 | 2.8208 | 0 | 0 | 0 | 109.6403 | off_peak | 681.3397 | 0 | 100 | 13.86 | 0 | 86.14 | 309.2767 | 0
7765 | 805.07 | 685.381 | 26.4 | 110.4721 | 110.4721 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 42.1093 | 706.9603 | 0 | 0.05921 | 3.2535 | 0 | 0 | 0 | 110.4721 | off_peak | 694.5979 | 0 | 100 | 13.72 | 0 | 86.28 | 359.4197 | 0
7766 | 795.83 | 623.118 | 26.5 | 100.4 | 100.4 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 53.6732 | 707.7924 | 0 | 0.05921 | 3.6187 | 0 | 0 | 0 | 100.4 | off_peak | 695.43 | 0 | 100 | 12.62 | 0 | 87.38 | 363.3167 | 0
7767 | 836.28 | 506.435 | 26.4 | 81.629 | 81.629 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 65.2371 | 767.0134 | 0 | 0.05921 | 3.7532 | 0 | 0 | 0 | 81.629 | off_peak | 754.651 | 0 | 100 | 9.76 | 0 | 90.24 | 306.3692 | 0
7768 | 788.98 | 338.752 | 26.3 | 54.621 | 54.621 | 0 | 0 | 8.9371 | 8.9371 | 0 | 0 | 0 | 73.597 | 743.2961 | 0 | 0.05921 | 3.876 | 0 | 0 | 0 | 54.621 | off_peak | 734.359 | 0 | 100 | 6.92 | 0 | 93.08 | 211.7132 | 0
7769 | 809.51 | 150.264 | 25.9 | 24.2639 | 24.2639 | 0 | 0 | 0.57721 | 0.57721 | 0 | 0 | 0 | 74.137 | 785.8233 | 0 | 0.05921 | 4.2218 | 0 | 0 | 0 | 24.2639 | off_peak | 785.2461 | 0 | 100 | 3 | 0 | 97 | 102.4361 | 0
7770 | 830.8 | 5.7 | 25.5 | 0.92174 | 0.92174 | 0 | 0 | 0.037279 | 0.037279 | 0 | 0 | 0 | 74.1718 | 829.9155 | 0 | 0.05921 | 4.6548 | 0 | 0 | 0 | 0.92174 | off_peak | 829.8783 | 0 | 100 | 0.11 | 0 | 99.89 | 4.2905 | 0
7771 | 781.22 | 0 | 25.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1718 | 781.22 | 0 | 0.088511 | 5.0009 | 0 | 0 | 0 | 0 | on_peak | 781.22 |  |  | 0 | 0 | 100 | 0 | 0
7772 | 794.43 | 0 | 25.2 | 0 | 0 | 0 | 0 | 0 | 0 | 62.443 | 62.443 | 0 | 7.4174 | 731.987 | 0 | 0.088511 | 5.2609 | 0 | 0 | 0 | 0 | on_peak | 731.987 |  |  | 0 | 7.86 | 92.14 | 0 | 0
7773 | 782.6 | 0 | 25.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 782.6 | 0 | 0.088511 | 5.5134 | 0 | 0 | 0 | 0 | on_peak | 782.6 |  |  | 0 | 0 | 100 | 0 | 0
7774 | 734.85 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 734.85 | 0 | 0.088511 | 5.8572 | 0 | 0 | 0 | 0 | on_peak | 734.85 |  |  | 0 | 0 | 100 | 0 | 0
7775 | 786.82 | 0 | 25 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 18.9814 | 799.1824 | 0 | 0.05921 | 6.0485 | 0 | 0 | 0 | 0 | off_peak | 786.82 | 0 | 100 | 0 | 0 | 100 | 0 | 0
7776 | 767.59 | 0 | 25 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 30.5453 | 779.9524 | 0 | 0.05921 | 6.1626 | 0 | 0 | 0 | 0 | off_peak | 767.59 | 0 | 100 | 0 | 0 | 100 | 0 | 0
7777 | 733.09 | 0 | 25 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 42.1093 | 745.4524 | 0 | 0.05921 | 6.1601 | 0 | 0 | 0 | 0 | off_peak | 733.09 | 0 | 100 | 0 | 0 | 100 | 0 | 0
7778 | 644.44 | 0 | 25 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 53.6732 | 656.8024 | 0 | 0.05921 | 5.9043 | 0 | 0 | 0 | 0 | off_peak | 644.44 | 0 | 100 | 0 | 0 | 100 | 0 | 0
7779 | 646.33 | 0 | 24.9 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 65.2371 | 658.6924 | 0 | 0.05921 | 5.5767 | 0 | 0 | 0 | 0 | off_peak | 646.33 | 0 | 100 | 0 | 0 | 100 | 0 | 0
7780 | 644.63 | 0 | 24.9 | 0 | 0 | 0 | 0 | 8.9371 | 8.9371 | 0 | 0 | 0 | 73.597 | 653.5671 | 0 | 0.05921 | 5.215 | 0 | 0 | 0 | 0 | off_peak | 644.63 | 0 | 100 | 0 | 0 | 100 | 0 | 0
7781 | 623.21 | 0 | 24.8 | 0 | 0 | 0 | 0 | 0.57721 | 0.57721 | 0 | 0 | 0 | 74.137 | 623.7872 | 0 | 0.05921 | 4.8051 | 0 | 0 | 0 | 0 | off_peak | 623.21 | 0 | 100 | 0 | 0 | 100 | 0 | 0
7782 | 644.5 | 0 | 24.8 | 0 | 0 | 0 | 0 | 0.037279 | 0.037279 | 0 | 0 | 0 | 74.1718 | 644.5373 | 0 | 0.05921 | 4.2769 | 0 | 0 | 0 | 0 | off_peak | 644.5 | 0 | 100 | 0 | 0 | 100 | 0 | 0
7783 | 734.26 | 0 | 24.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1718 | 734.26 | 0 | 0.088511 | 3.7757 | 0 | 0 | 0 | 0 | on_peak | 734.26 |  |  | 0 | 0 | 100 | 0 | 0
7784 | 804.58 | 104.053 | 25.1 | 16.8505 | 16.8505 | 0 | 0 | 0 | 0 | 62.443 | 62.443 | 0 | 7.4174 | 725.2864 | 0 | 0.088511 | 3.3904 | 0 | 0 | 0 | 16.8505 | on_peak | 725.2864 |  |  | 2.09 | 7.76 | 90.14 | 57.1298 | 0
7785 | 812.3 | 294.805 | 25.5 | 47.6724 | 47.6724 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 764.6276 | 0 | 0.088511 | 3.1332 | 0 | 0 | 0 | 47.6724 | on_peak | 764.6276 |  |  | 5.87 | 0 | 94.13 | 149.3691 | 0
7786 | 793.06 | 470.129 | 25.7 | 75.969 | 75.969 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 717.091 | 0 | 0.088511 | 3.0086 | 0 | 0 | 0 | 75.969 | on_peak | 717.091 |  |  | 9.58 | 0 | 90.42 | 228.5583 | 0
7787 | 793.06 | 602.242 | 26.1 | 97.1769 | 97.1769 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 18.9814 | 708.2455 | 0 | 0.05921 | 3.0201 | 0 | 0 | 0 | 97.1769 | off_peak | 695.8831 | 0 | 100 | 12.25 | 0 | 87.75 | 293.4836 | 0
7788 | 901.34 | 654.11 | 26.3 | 105.4699 | 105.4699 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 30.5453 | 808.2325 | 0 | 0.05921 | 3.2452 | 0 | 0 | 0 | 105.4699 | off_peak | 795.8701 | 0 | 100 | 11.7 | 0 | 88.3 | 342.2695 | 0
7789 | 764.85 | 675.098 | 26.6 | 108.7359 | 108.7359 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 42.1093 | 668.4764 | 0 | 0.05921 | 3.5278 | 0 | 0 | 0 | 108.7359 | off_peak | 656.1141 | 0 | 100 | 14.22 | 0 | 85.78 | 383.6016 | 0
7790 | 814.91 | 599.418 | 26.7 | 96.5114 | 96.5114 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 53.6732 | 730.7609 | 0 | 0.05921 | 3.8485 | 0 | 0 | 0 | 96.5114 | off_peak | 718.3986 | 0 | 100 | 11.84 | 0 | 88.16 | 371.4288 | 0
7791 | 861.1 | 505.371 | 26.7 | 81.3691 | 81.3691 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 65.2371 | 792.0933 | 0 | 0.05921 | 4.0715 | 0 | 0 | 0 | 81.3691 | off_peak | 779.7309 | 0 | 100 | 9.45 | 0 | 90.55 | 331.2959 | 0
7792 | 784.63 | 339.333 | 26.5 | 54.6751 | 54.6751 | 0 | 0 | 8.9371 | 8.9371 | 0 | 0 | 0 | 73.597 | 738.892 | 0 | 0.05921 | 4.2915 | 0 | 0 | 0 | 54.6751 | off_peak | 729.9549 | 0 | 100 | 6.97 | 0 | 93.03 | 234.6388 | 0
7793 | 818.21 | 149.468 | 25.9 | 24.1354 | 24.1354 | 0 | 0 | 0.57721 | 0.57721 | 0 | 0 | 0 | 74.137 | 794.6518 | 0 | 0.05921 | 4.6082 | 0 | 0 | 0 | 24.1354 | off_peak | 794.0746 | 0 | 100 | 2.95 | 0 | 97.05 | 111.2204 | 0
7794 | 823.3 | 5.7 | 25.2 | 0.92274 | 0.88546 | 0 | 0.037279 | 0.037279 | 0 | 0 | 0 | 0 | 74.1718 | 822.4145 | 0 | 0.05921 | 4.8708 | 0 | 0 | 0.034872 | 0.88546 | off_peak | 822.4145 | 100 | 0 | 0.11 | 0 | 99.89 | 4.3129 | 0
7795 | 791.65 | 0 | 24.9 | 0 | 0 | 0 | 0 | 0 | 0 | 62.4104 | 62.4104 | 0 | 7.4523 | 729.2396 | 0 | 0.088511 | 5.1531 | 0 | 0 | 0.034872 | 0 | on_peak | 729.2396 |  |  | 0 | 7.88 | 92.12 | 0 | 0
7796 | 797.2 | 0 | 23.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0.032619 | 0.032619 | 0 | 7.4174 | 797.1674 | 0 | 0.088511 | 5.518 | 0.032619 | 0 | 0 | 0.032619 | on_peak | 797.1674 |  |  | 0 | 0 | 100 | 0.17999 | 0
7797 | 792.09 | 0 | 22.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 792.09 | 0 | 0.088511 | 5.7779 | 0 | 0 | 0 | 0 | on_peak | 792.09 |  |  | 0 | 0 | 100 | 0 | 0
7798 | 755.84 | 0 | 21.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 755.84 | 0 | 0.088511 | 6.1219 | 0 | 0 | 0 | 0 | on_peak | 755.84 |  |  | 0 | 0 | 100 | 0 | 0
7799 | 802.21 | 0 | 21.1 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 18.9814 | 814.5724 | 0 | 0.05921 | 6.3005 | 0 | 0 | 0 | 0 | off_peak | 802.21 | 0 | 100 | 0 | 0 | 100 | 0 | 0
7800 | 755.35 | 0 | 20.8 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 30.5453 | 767.7124 | 0 | 0.05921 | 6.3091 | 0 | 0 | 0 | 0 | off_peak | 755.35 | 0 | 100 | 0 | 0 | 100 | 0 | 0
7801 | 711.78 | 0 | 20.2 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 42.1093 | 724.1424 | 0 | 0.05921 | 6.177 | 0 | 0 | 0 | 0 | off_peak | 711.78 | 0 | 100 | 0 | 0 | 100 | 0 | 0
7802 | 643.33 | 0 | 19.7 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 53.6732 | 655.6924 | 0 | 0.05921 | 5.8984 | 0 | 0 | 0 | 0 | off_peak | 643.33 | 0 | 100 | 0 | 0 | 100 | 0 | 0
7803 | 590.65 | 0 | 19.3 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 65.2371 | 603.0124 | 0 | 0.05921 | 5.5973 | 0 | 0 | 0 | 0 | off_peak | 590.65 | 0 | 100 | 0 | 0 | 100 | 0 | 0
7804 | 582.95 | 0 | 19 | 0 | 0 | 0 | 0 | 8.9371 | 8.9371 | 0 | 0 | 0 | 73.597 | 591.8871 | 0 | 0.05921 | 5.2024 | 0 | 0 | 0 | 0 | off_peak | 582.95 | 0 | 100 | 0 | 0 | 100 | 0 | 0
7805 | 587.26 | 0 | 18.7 | 0 | 0 | 0 | 0 | 0.57721 | 0.57721 | 0 | 0 | 0 | 74.137 | 587.8372 | 0 | 0.05921 | 4.779 | 0 | 0 | 0 | 0 | off_peak | 587.26 | 0 | 100 | 0 | 0 | 100 | 0 | 0
7806 | 577.93 | 0 | 18.3 | 0 | 0 | 0 | 0 | 0.037279 | 0.037279 | 0 | 0 | 0 | 74.1718 | 577.9673 | 0 | 0.05921 | 4.2552 | 0 | 0 | 0 | 0 | off_peak | 577.93 | 0 | 100 | 0 | 0 | 100 | 0 | 0
7807 | 657.2 | 0 | 17.8 | 0 | 0 | 0 | 0 | 0 | 0 | 62.443 | 62.443 | 0 | 7.4174 | 594.757 | 0 | 0.088511 | 3.7851 | 0 | 0 | 0 | 0 | on_peak | 594.757 |  |  | 0 | 9.5 | 90.5 | 0 | 0
7808 | 724.17 | 108.249 | 17.7 | 17.9972 | 17.9972 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 706.1728 | 0 | 0.088511 | 3.4064 | 0 | 0 | 0 | 17.9972 | on_peak | 706.1728 |  |  | 2.49 | 0 | 97.51 | 61.3056 | 0
7809 | 784.61 | 300.59 | 18.2 | 49.8876 | 49.8876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 734.7224 | 0 | 0.088511 | 3.1548 | 0 | 0 | 0 | 49.8876 | on_peak | 734.7224 |  |  | 6.36 | 0 | 93.64 | 157.3878 | 0
7810 | 814.57 | 473.7 | 19.1 | 78.3693 | 78.3693 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 736.2007 | 0 | 0.088511 | 3.0032 | 0 | 0 | 0 | 78.3693 | on_peak | 736.2007 |  |  | 9.62 | 0 | 90.38 | 235.3614 | 0
7811 | 789.31 | 602.028 | 20.1 | 99.2489 | 99.2489 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 18.9814 | 702.4234 | 0 | 0.05921 | 3.0004 | 0 | 0 | 0 | 99.2489 | off_peak | 690.0611 | 0 | 100 | 12.57 | 0 | 87.43 | 297.7887 | 0
7812 | 850.84 | 673.411 | 20.9 | 110.7028 | 110.7028 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 30.5453 | 752.4996 | 0 | 0.05921 | 3.1731 | 0 | 0 | 0 | 110.7028 | off_peak | 740.1372 | 0 | 100 | 13.01 | 0 | 86.99 | 351.2752 | 0
7813 | 826.62 | 628.331 | 21.4 | 103.1088 | 103.1088 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 42.1093 | 735.8736 | 0 | 0.05921 | 3.4416 | 0 | 0 | 0 | 103.1088 | off_peak | 723.5112 | 0 | 100 | 12.47 | 0 | 87.53 | 354.8567 | 0
7814 | 834.01 | 540.321 | 21.7 | 88.5719 | 88.5719 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 53.6732 | 757.8005 | 0 | 0.05921 | 3.7955 | 0 | 0 | 0 | 88.5719 | off_peak | 745.4381 | 0 | 100 | 10.62 | 0 | 89.38 | 336.1763 | 0
7815 | 803.1 | 310.768 | 21.8 | 50.9244 | 50.9244 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 65.2371 | 764.538 | 0 | 0.05921 | 4.1043 | 0 | 0 | 0 | 50.9244 | off_peak | 752.1756 | 0 | 100 | 6.34 | 0 | 93.66 | 209.01 | 0
7816 | 792.2 | 280.898 | 21.6 | 46.0625 | 46.0625 | 0 | 0 | 8.9371 | 8.9371 | 0 | 0 | 0 | 73.597 | 755.0746 | 0 | 0.05921 | 4.4829 | 0 | 0 | 0 | 46.0625 | off_peak | 746.1375 | 0 | 100 | 5.81 | 0 | 94.19 | 206.4949 | 0
7817 | 741.24 | 109.023 | 21 | 17.9161 | 17.9161 | 0 | 0 | 0.57721 | 0.57721 | 0 | 0 | 0 | 74.137 | 723.9012 | 0 | 0.05921 | 4.869 | 0 | 0 | 0 | 17.9161 | off_peak | 723.3239 | 0 | 100 | 2.42 | 0 | 97.58 | 87.2328 | 0
7818 | 805.36 | 5.7 | 20.3 | 0.93902 | 0.93902 | 0 | 0 | 0.037279 | 0.037279 | 0 | 0 | 0 | 74.1718 | 804.4583 | 0 | 0.05921 | 5.1733 | 0 | 0 | 0 | 0.93902 | off_peak | 804.421 | 0 | 100 | 0.12 | 0 | 99.88 | 4.8578 | 0
7819 | 787.79 | 0 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1718 | 787.79 | 0 | 0.088511 | 5.411 | 0 | 0 | 0 | 0 | on_peak | 787.79 |  |  | 0 | 0 | 100 | 0 | 0
7820 | 823.14 | 0 | 19.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1718 | 823.14 | 0 | 0.088511 | 5.666 | 0 | 0 | 0 | 0 | on_peak | 823.14 |  |  | 0 | 0 | 100 | 0 | 0
7821 | 758.65 | 0 | 19.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1718 | 758.65 | 0 | 0.088511 | 5.8818 | 0 | 0 | 0 | 0 | on_peak | 758.65 |  |  | 0 | 0 | 100 | 0 | 0
7822 | 729.98 | 0 | 19.2 | 0 | 0 | 0 | 0 | 0 | 0 | 62.443 | 62.443 | 0 | 7.4174 | 667.537 | 0 | 0.088511 | 6.1138 | 0 | 0 | 0 | 0 | on_peak | 667.537 |  |  | 0 | 8.55 | 91.45 | 0 | 0
7823 | 730.96 | 0 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 730.96 | 0 | 0.05921 | 6.357 | 0 | 0 | 0 | 0 | off_peak | 730.96 |  |  | 0 | 0 | 100 | 0 | 0
7824 | 755.12 | 0 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 755.12 | 0 | 0.05921 | 6.4403 | 0 | 0 | 0 | 0 | off_peak | 755.12 |  |  | 0 | 0 | 100 | 0 | 0
7825 | 664.88 | 0 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 664.88 | 0 | 0.05921 | 6.2718 | 0 | 0 | 0 | 0 | off_peak | 664.88 |  |  | 0 | 0 | 100 | 0 | 0
7826 | 618.13 | 0 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 618.13 | 0 | 0.05921 | 6.0016 | 0 | 0 | 0 | 0 | off_peak | 618.13 |  |  | 0 | 0 | 100 | 0 | 0
7827 | 584.46 | 0 | 18.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 584.46 | 0 | 0.05921 | 5.6225 | 0 | 0 | 0 | 0 | off_peak | 584.46 |  |  | 0 | 0 | 100 | 0 | 0
7828 | 579.93 | 0 | 18.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 579.93 | 0 | 0.05921 | 5.3078 | 0 | 0 | 0 | 0 | off_peak | 579.93 |  |  | 0 | 0 | 100 | 0 | 0
7829 | 599.58 | 0 | 17.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 599.58 | 0 | 0.05921 | 4.8944 | 0 | 0 | 0 | 0 | off_peak | 599.58 |  |  | 0 | 0 | 100 | 0 | 0
7830 | 694.59 | 0 | 17.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 694.59 | 0 | 0.05921 | 4.343 | 0 | 0 | 0 | 0 | off_peak | 694.59 |  |  | 0 | 0 | 100 | 0 | 0
7831 | 746.25 | 0 | 16.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 746.25 | 0 | 0.05921 | 3.8951 | 0 | 0 | 0 | 0 | on_peak | 746.25 |  |  | 0 | 0 | 100 | 0 | 0
7832 | 785.19 | 85.0137 | 16.1 | 14.2135 | 14.2135 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 770.9765 | 0 | 0.05921 | 3.4785 | 0 | 0 | 0 | 14.2135 | on_peak | 770.9765 |  |  | 1.81 | 0 | 98.19 | 49.4416 | 0
7833 | 815.16 | 279.805 | 16.2 | 46.7644 | 46.7644 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 768.3956 | 0 | 0.05921 | 3.2555 | 0 | 0 | 0 | 46.7644 | on_peak | 768.3956 |  |  | 5.74 | 0 | 94.26 | 152.2438 | 0
7834 | 789.01 | 444.607 | 16.7 | 74.1785 | 74.1785 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 714.8315 | 0 | 0.05921 | 3.0846 | 0 | 0 | 0 | 74.1785 | on_peak | 714.8315 |  |  | 9.4 | 0 | 90.6 | 228.8122 | 0
7835 | 734.9 | 450.601 | 17.3 | 75.0208 | 75.0208 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 659.8792 | 0 | 0.05921 | 3.0266 | 0 | 0 | 0 | 75.0208 | off_peak | 659.8792 |  |  | 10.21 | 0 | 89.79 | 227.058 | 0
7836 | 764.71 | 609.325 | 18 | 101.1982 | 101.1982 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 663.5118 | 0 | 0.05921 | 3.0979 | 0 | 0 | 0 | 101.1982 | off_peak | 663.5118 |  |  | 13.23 | 0 | 86.77 | 313.4972 | 0
7837 | 714.85 | 633.629 | 18.5 | 105.0499 | 105.0499 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 609.8001 | 0 | 0.05921 | 3.1817 | 0 | 0 | 0 | 105.0499 | off_peak | 609.8001 |  |  | 14.7 | 0 | 85.3 | 334.237 | 0
7838 | 716.4 | 565.071 | 18.9 | 93.5518 | 93.5518 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 622.8482 | 0 | 0.05921 | 3.3957 | 0 | 0 | 0 | 93.5518 | off_peak | 622.8482 |  |  | 13.06 | 0 | 86.94 | 317.6773 | 0
7839 | 651.78 | 419.914 | 19.1 | 69.4709 | 69.4709 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 582.3091 | 0 | 0.05921 | 3.5377 | 0 | 0 | 0 | 69.4709 | off_peak | 582.3091 |  |  | 10.66 | 0 | 89.34 | 245.7698 | 0
7840 | 580.68 | 241.206 | 19 | 39.9194 | 39.9194 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 18.9814 | 553.123 | 0 | 0.05921 | 3.7929 | 0 | 0 | 0 | 39.9194 | off_peak | 540.7606 | 0 | 100 | 6.87 | 0 | 93.13 | 151.4105 | 0
7841 | 587.75 | 132.556 | 18.5 | 21.9766 | 9.6142 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 0 | 30.5453 | 578.1358 | 0 | 0.05921 | 4.1014 | 0 | 0 | 11.5639 | 9.6142 | off_peak | 578.1358 | 100 | 0 | 1.64 | 0 | 98.36 | 39.4321 | 0
7842 | 562.58 | 4.75 | 17.9 | 0.78917 | 0 | 0 | 0.78917 | 12.3624 | 11.5732 | 0 | 0 | 0 | 42.1093 | 574.1532 | 0 | 0.05921 | 4.489 | 0 | 0 | 12.3021 | 0 | off_peak | 562.58 | 6.38 | 93.62 | 0 | 0 | 100 | 0 | 0
7843 | 574.06 | 0 | 17.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 42.1093 | 574.06 | 0 | 0.05921 | 4.9773 | 0 | 0 | 12.3021 | 0 | on_peak | 574.06 |  |  | 0 | 0 | 100 | 0 | 0
7844 | 572.38 | 0 | 17.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 42.1093 | 572.38 | 0 | 0.05921 | 5.3235 | 0 | 0 | 12.3021 | 0 | on_peak | 572.38 |  |  | 0 | 0 | 100 | 0 | 0
7845 | 538.79 | 0 | 17.5 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 53.6732 | 551.1524 | 0 | 0.05921 | 5.5427 | 0 | 0 | 12.3021 | 0 | on_peak | 538.79 | 0 | 100 | 0 | 0 | 100 | 0 | 0
7846 | 574.96 | 0 | 17.4 | 0 | 0 | 0 | 0 | 8.7006 | 8.7006 | 0 | 0 | 0 | 61.8119 | 583.6606 | 0 | 0.05921 | 5.5908 | 0 | 0 | 12.3021 | 0 | on_peak | 574.96 | 0 | 100 | 0 | 0 | 100 | 0 | 0
7847 | 519.62 | 0 | 17.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 61.8119 | 519.62 | 0 | 0.05921 | 5.6258 | 0 | 0 | 12.3021 | 0 | off_peak | 519.62 |  |  | 0 | 0 | 100 | 0 | 0
7848 | 532.08 | 0 | 17.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 61.8119 | 532.08 | 0 | 0.05921 | 5.4908 | 0 | 0 | 12.3021 | 0 | off_peak | 532.08 |  |  | 0 | 0 | 100 | 0 | 0
7849 | 529.01 | 0 | 17.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 61.8119 | 529.01 | 0 | 0.05921 | 5.1505 | 0 | 0 | 12.3021 | 0 | off_peak | 529.01 |  |  | 0 | 0 | 100 | 0 | 0
7850 | 544.17 | 0 | 17.4 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 73.3758 | 556.5324 | 0 | 0.05921 | 4.7386 | 0 | 0 | 12.3021 | 0 | off_peak | 544.17 | 0 | 100 | 0 | 0 | 100 | 0 | 0
7851 | 524.15 | 0 | 17.5 | 0 | 0 | 0 | 0 | 0.79843 | 0.79843 | 0 | 0 | 0 | 74.1227 | 524.9484 | 0 | 0.05921 | 4.4717 | 0 | 0 | 12.3021 | 0 | off_peak | 524.15 | 0 | 100 | 0 | 0 | 100 | 0 | 0
7852 | 563.94 | 0 | 17.6 | 0 | 0 | 0 | 0 | 0.051567 | 0.051567 | 0 | 0 | 0 | 74.1709 | 563.9916 | 0 | 0.05921 | 4.2237 | 0 | 0 | 12.3021 | 0 | off_peak | 563.94 | 0 | 100 | 0 | 0 | 100 | 0 | 0
7853 | 543.19 | 0 | 17.6 | 0 | 0 | 0 | 0 | 0.0033305 | 0.0033305 | 0 | 0 | 0 | 74.174 | 543.1933 | 0 | 0.05921 | 3.9604 | 0 | 0 | 12.3021 | 0 | off_peak | 543.19 | 0 | 100 | 0 | 0 | 100 | 0 | 0
7854 | 638.69 | 0 | 17.7 | 0 | 0 | 0 | 0 | 0.0002151 | 0.0002151 | 0 | 0 | 0 | 74.1742 | 638.6902 | 0 | 0.05921 | 3.5829 | 0 | 0 | 12.3021 | 0 | off_peak | 638.69 | 0 | 100 | 0 | 0 | 100 | 0 | 0
7855 | 724.16 | 0 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 11.5076 | 11.5076 | 0 | 61.8721 | 712.6524 | 0 | 0.088511 | 3.2524 | 11.5076 | 0 | 0 | 11.5076 | on_peak | 712.6524 |  |  | 0 | 1.59 | 98.41 | 37.4273 | 0
7856 | 727.98 | 92.4943 | 19 | 15.3077 | 15.3077 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 61.8721 | 712.6723 | 0 | 0.088511 | 2.9311 | 0 | 0 | 0 | 15.3077 | on_peak | 712.6723 |  |  | 2.1 | 0 | 97.9 | 44.8683 | 0
7857 | 714.28 | 271.463 | 20.2 | 44.7369 | 44.7369 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 61.8721 | 669.5431 | 0 | 0.088511 | 2.7416 | 0 | 0 | 0 | 44.7369 | on_peak | 669.5431 |  |  | 6.26 | 0 | 93.74 | 122.6524 | 0
7858 | 743.73 | 434.563 | 21.1 | 71.3876 | 71.3876 | 0 | 0 | 0 | 0 | 50.9377 | 50.9377 | 0 | 7.4174 | 621.4047 | 0 | 0.088511 | 2.6466 | 0 | 0 | 0 | 71.3876 | on_peak | 621.4047 |  |  | 9.6 | 6.85 | 83.55 | 188.9352 | 0
7859 | 696.13 | 389.039 | 21.9 | 63.7277 | 63.7277 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 18.9814 | 644.7647 | 0 | 0.05921 | 2.6711 | 0 | 0 | 0 | 63.7277 | off_peak | 632.4023 | 0 | 100 | 9.15 | 0 | 90.85 | 170.2218 | 0
7860 | 757.98 | 83.6 | 22.6 | 13.6602 | 13.6602 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 30.5453 | 756.6822 | 0 | 0.05921 | 2.826 | 0 | 0 | 0 | 13.6602 | off_peak | 744.3198 | 0 | 100 | 1.8 | 0 | 98.2 | 38.6042 | 0
7861 | 705.09 | 143.45 | 23.1 | 23.3979 | 23.3979 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 42.1093 | 694.0545 | 0 | 0.05921 | 3.0352 | 0 | 0 | 0 | 23.3979 | off_peak | 681.6921 | 0 | 100 | 3.32 | 0 | 96.68 | 71.0179 | 0
7862 | 717.44 | 109.25 | 23.3 | 17.8068 | 17.8068 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 53.6732 | 711.9956 | 0 | 0.05921 | 3.343 | 0 | 0 | 0 | 17.8068 | off_peak | 699.6332 | 0 | 100 | 2.48 | 0 | 97.52 | 59.5279 | 0
7863 | 676.52 | 72.2 | 23.4 | 11.7638 | 11.7638 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 65.2371 | 677.1186 | 0 | 0.05921 | 3.6279 | 0 | 0 | 0 | 11.7638 | off_peak | 664.7562 | 0 | 100 | 1.74 | 0 | 98.26 | 42.678 | 0
7864 | 626.23 | 60.8 | 23.3 | 9.9099 | 9.9099 | 0 | 0 | 8.9371 | 8.9371 | 0 | 0 | 0 | 73.597 | 625.2572 | 0 | 0.05921 | 3.9113 | 0 | 0 | 0 | 9.9099 | off_peak | 616.3201 | 0 | 100 | 1.58 | 0 | 98.42 | 38.7605 | 0
7865 | 627.04 | 18.05 | 22.8 | 2.9473 | 2.9473 | 0 | 0 | 0.57721 | 0.57721 | 0 | 0 | 0 | 74.137 | 624.67 | 0 | 0.05921 | 4.0398 | 0 | 0 | 0 | 2.9473 | off_peak | 624.0927 | 0 | 100 | 0.47 | 0 | 99.53 | 11.9064 | 0
7866 | 579.64 | 0 | 22.1 | 0 | 0 | 0 | 0 | 0.037279 | 0.037279 | 0 | 0 | 0 | 74.1718 | 579.6773 | 0 | 0.05921 | 4.1667 | 0 | 0 | 0 | 0 | off_peak | 579.64 | 0 | 100 | 0 | 0 | 100 | 0 | 0
7867 | 546.18 | 0 | 21.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1718 | 546.18 | 0 | 0.088511 | 4.2436 | 0 | 0 | 0 | 0 | on_peak | 546.18 |  |  | 0 | 0 | 100 | 0 | 0
7868 | 555.92 | 0 | 21.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1718 | 555.92 | 0 | 0.088511 | 4.283 | 0 | 0 | 0 | 0 | on_peak | 555.92 |  |  | 0 | 0 | 100 | 0 | 0
7869 | 548.86 | 0 | 21.4 | 0 | 0 | 0 | 0 | 0 | 0 | 62.443 | 62.443 | 0 | 7.4174 | 486.417 | 0 | 0.088511 | 4.3269 | 0 | 0 | 0 | 0 | on_peak | 486.417 |  |  | 0 | 11.38 | 88.62 | 0 | 0
7870 | 534.61 | 0 | 21.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 534.61 | 0 | 0.088511 | 4.4249 | 0 | 0 | 0 | 0 | on_peak | 534.61 |  |  | 0 | 0 | 100 | 0 | 0
7871 | 540.45 | 0 | 20.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 540.45 | 0 | 0.05921 | 4.6149 | 0 | 0 | 0 | 0 | off_peak | 540.45 |  |  | 0 | 0 | 100 | 0 | 0
7872 | 546.83 | 0 | 20.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 546.83 | 0 | 0.05921 | 4.8618 | 0 | 0 | 0 | 0 | off_peak | 546.83 |  |  | 0 | 0 | 100 | 0 | 0
7873 | 531.33 | 0 | 20.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 531.33 | 0 | 0.05921 | 4.8831 | 0 | 0 | 0 | 0 | off_peak | 531.33 |  |  | 0 | 0 | 100 | 0 | 0
7874 | 521.67 | 0 | 20.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 521.67 | 0 | 0.05921 | 4.7082 | 0 | 0 | 0 | 0 | off_peak | 521.67 |  |  | 0 | 0 | 100 | 0 | 0
7875 | 541.59 | 0 | 20.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 541.59 | 0 | 0.05921 | 4.5343 | 0 | 0 | 0 | 0 | off_peak | 541.59 |  |  | 0 | 0 | 100 | 0 | 0
7876 | 535.78 | 0 | 20.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 535.78 | 0 | 0.05921 | 4.2777 | 0 | 0 | 0 | 0 | off_peak | 535.78 |  |  | 0 | 0 | 100 | 0 | 0
7877 | 554.38 | 0 | 20.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 554.38 | 0 | 0.05921 | 3.9782 | 0 | 0 | 0 | 0 | off_peak | 554.38 |  |  | 0 | 0 | 100 | 0 | 0
7878 | 637.45 | 0 | 20.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 637.45 | 0 | 0.05921 | 3.5886 | 0 | 0 | 0 | 0 | off_peak | 637.45 |  |  | 0 | 0 | 100 | 0 | 0
7879 | 663.35 | 0 | 20.5 | 0 | 0 | 0 | 0 | 8.7006 | 8.7006 | 0 | 0 | 0 | 15.5561 | 672.0506 | 0 | 0.05921 | 3.1895 | 0 | 0 | 0 | 0 | off_peak | 663.35 | 0 | 100 | 0 | 0 | 100 | 0 | 0
7880 | 662.65 | 56.5062 | 21 | 9.2858 | 9.2858 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 27.12 | 665.7266 | 0 | 0.05921 | 2.9349 | 0 | 0 | 0 | 9.2858 | off_peak | 653.3642 | 0 | 100 | 1.4 | 0 | 98.6 | 27.2529 | 0
7881 | 690.51 | 260.557 | 21.9 | 42.6813 | 42.6813 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27.12 | 647.8287 | 0 | 0.05921 | 2.7542 | 0 | 0 | 0 | 42.6813 | off_peak | 647.8287 |  |  | 6.18 | 0 | 93.82 | 117.5536 | 0
7882 | 690.36 | 423.23 | 22.7 | 69.131 | 69.131 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27.12 | 621.229 | 0 | 0.05921 | 2.6751 | 0 | 0 | 0 | 69.131 | off_peak | 621.229 |  |  | 10.01 | 0 | 89.99 | 184.9315 | 0
7883 | 674.31 | 557.594 | 23.4 | 90.8505 | 90.8505 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27.12 | 583.4595 | 0 | 0.05921 | 2.6569 | 0 | 0 | 0 | 90.8505 | off_peak | 583.4595 |  |  | 13.47 | 0 | 86.53 | 241.3814 | 0
7884 | 697.98 | 457.38 | 23.9 | 74.389 | 74.389 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27.12 | 623.591 | 0 | 0.05921 | 2.7254 | 0 | 0 | 0 | 74.389 | off_peak | 623.591 |  |  | 10.66 | 0 | 89.34 | 202.7409 | 0
7885 | 681.63 | 275.779 | 24.2 | 44.8049 | 44.8049 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27.12 | 636.8251 | 0 | 0.05921 | 2.899 | 0 | 0 | 0 | 44.8049 | off_peak | 636.8251 |  |  | 6.57 | 0 | 93.43 | 129.8872 | 0
7886 | 680.19 | 258.542 | 24.4 | 41.9743 | 41.9743 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27.12 | 638.2157 | 0 | 0.05921 | 3.2485 | 0 | 0 | 0 | 41.9743 | off_peak | 638.2157 |  |  | 6.17 | 0 | 93.83 | 136.3544 | 0
7887 | 669.13 | 298.434 | 24.5 | 48.4333 | 48.4333 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27.12 | 620.6967 | 0 | 0.05921 | 3.345 | 0 | 0 | 0 | 48.4333 | off_peak | 620.6967 |  |  | 7.24 | 0 | 92.76 | 162.0112 | 0
7888 | 668.67 | 297.516 | 24.4 | 48.3017 | 48.3017 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27.12 | 620.3683 | 0 | 0.05921 | 3.4847 | 0 | 0 | 0 | 48.3017 | off_peak | 620.3683 |  |  | 7.22 | 0 | 92.78 | 168.3165 | 0
7889 | 659.9 | 98.7024 | 24 | 16.0474 | 16.0474 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27.12 | 643.8526 | 0 | 0.05921 | 3.5754 | 0 | 0 | 0 | 16.0474 | off_peak | 643.8526 |  |  | 2.43 | 0 | 97.57 | 57.3759 | 0
7890 | 596.92 | 0 | 23.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27.12 | 596.92 | 0 | 0.05921 | 3.813 | 0 | 0 | 0 | 0 | off_peak | 596.92 |  |  | 0 | 0 | 100 | 0 | 0
7891 | 574.58 | 0 | 23.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27.12 | 574.58 | 0 | 0.05921 | 4.0144 | 0 | 0 | 0 | 0 | off_peak | 574.58 |  |  | 0 | 0 | 100 | 0 | 0
7892 | 558.34 | 0 | 22.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27.12 | 558.34 | 0 | 0.05921 | 4.1166 | 0 | 0 | 0 | 0 | off_peak | 558.34 |  |  | 0 | 0 | 100 | 0 | 0
7893 | 516.98 | 0 | 22.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27.12 | 516.98 | 0 | 0.05921 | 4.278 | 0 | 0 | 0 | 0 | off_peak | 516.98 |  |  | 0 | 0 | 100 | 0 | 0
7894 | 572.95 | 0 | 22.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27.12 | 572.95 | 0 | 0.05921 | 4.5109 | 0 | 0 | 0 | 0 | off_peak | 572.95 |  |  | 0 | 0 | 100 | 0 | 0
7895 | 534.29 | 0 | 22.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27.12 | 534.29 | 0 | 0.05921 | 4.9358 | 0 | 0 | 0 | 0 | off_peak | 534.29 |  |  | 0 | 0 | 100 | 0 | 0
7896 | 543.39 | 0 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27.12 | 543.39 | 0 | 0.05921 | 5.3037 | 0 | 0 | 0 | 0 | off_peak | 543.39 |  |  | 0 | 0 | 100 | 0 | 0
7897 | 545.92 | 0 | 21.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27.12 | 545.92 | 0 | 0.05921 | 5.3785 | 0 | 0 | 0 | 0 | off_peak | 545.92 |  |  | 0 | 0 | 100 | 0 | 0
7898 | 542.58 | 0 | 21.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27.12 | 542.58 | 0 | 0.05921 | 5.1534 | 0 | 0 | 0 | 0 | off_peak | 542.58 |  |  | 0 | 0 | 100 | 0 | 0
7899 | 544.48 | 0 | 21.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27.12 | 544.48 | 0 | 0.05921 | 4.8438 | 0 | 0 | 0 | 0 | off_peak | 544.48 |  |  | 0 | 0 | 100 | 0 | 0
7900 | 531.09 | 0 | 21.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27.12 | 531.09 | 0 | 0.05921 | 4.5998 | 0 | 0 | 0 | 0 | off_peak | 531.09 |  |  | 0 | 0 | 100 | 0 | 0
7901 | 538.51 | 0 | 21.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27.12 | 538.51 | 0 | 0.05921 | 4.3267 | 0 | 0 | 0 | 0 | off_peak | 538.51 |  |  | 0 | 0 | 100 | 0 | 0
7902 | 591.58 | 0 | 21.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27.12 | 591.58 | 0 | 0.05921 | 3.8761 | 0 | 0 | 0 | 0 | off_peak | 591.58 |  |  | 0 | 0 | 100 | 0 | 0
7903 | 684.34 | 0 | 21.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27.12 | 684.34 | 0 | 0.05921 | 3.4534 | 0 | 0 | 0 | 0 | off_peak | 684.34 |  |  | 0 | 0 | 100 | 0 | 0
7904 | 708.39 | 91.7106 | 22.3 | 15.0015 | 15.0015 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27.12 | 693.3885 | 0 | 0.05921 | 3.1383 | 0 | 0 | 0 | 15.0015 | off_peak | 693.3885 |  |  | 2.12 | 0 | 97.88 | 47.0791 | 0
7905 | 679.51 | 273.736 | 23.2 | 44.6326 | 44.6326 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27.12 | 634.8774 | 0 | 0.05921 | 2.9192 | 0 | 0 | 0 | 44.6326 | off_peak | 634.8774 |  |  | 6.57 | 0 | 93.43 | 130.2919 | 0
7906 | 678.53 | 331.775 | 23.7 | 53.9991 | 53.9991 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27.12 | 624.5309 | 0 | 0.05921 | 2.7888 | 0 | 0 | 0 | 53.9991 | off_peak | 624.5309 |  |  | 7.96 | 0 | 92.04 | 150.5945 | 0
7907 | 675.93 | 323.388 | 24.1 | 52.5586 | 52.5586 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27.12 | 623.3714 | 0 | 0.05921 | 2.7273 | 0 | 0 | 0 | 52.5586 | off_peak | 623.3714 |  |  | 7.78 | 0 | 92.22 | 143.3425 | 0
7908 | 720.63 | 298.453 | 24.4 | 48.4538 | 48.4538 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27.12 | 672.1762 | 0 | 0.05921 | 2.7639 | 0 | 0 | 0 | 48.4538 | off_peak | 672.1762 |  |  | 6.72 | 0 | 93.28 | 133.9207 | 0
7909 | 712.92 | 178.943 | 24.6 | 29.0305 | 29.0305 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27.12 | 683.8895 | 0 | 0.05921 | 2.9411 | 0 | 0 | 0 | 29.0305 | off_peak | 683.8895 |  |  | 4.07 | 0 | 95.93 | 85.3824 | 0
7910 | 655.12 | 142.5 | 24.6 | 23.1182 | 23.1182 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27.12 | 632.0018 | 0 | 0.05921 | 3.2298 | 0 | 0 | 0 | 23.1182 | off_peak | 632.0018 |  |  | 3.53 | 0 | 96.47 | 74.6683 | 0
7911 | 706.7 | 162.894 | 24.6 | 26.4268 | 26.4268 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27.12 | 680.2732 | 0 | 0.05921 | 3.8336 | 0 | 0 | 0 | 26.4268 | off_peak | 680.2732 |  |  | 3.74 | 0 | 96.26 | 101.3108 | 0
7912 | 661.26 | 127.097 | 24.4 | 20.6342 | 20.6342 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27.12 | 640.6258 | 0 | 0.05921 | 4.297 | 0 | 0 | 0 | 20.6342 | off_peak | 640.6258 |  |  | 3.12 | 0 | 96.88 | 88.6653 | 0
7913 | 666.5 | 42.3562 | 23.8 | 6.8913 | 6.8913 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27.12 | 659.6087 | 0 | 0.05921 | 4.6673 | 0 | 0 | 0 | 6.8913 | off_peak | 659.6087 |  |  | 1.03 | 0 | 98.97 | 32.1638 | 0
7914 | 610.57 | 0 | 23.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27.12 | 610.57 | 0 | 0.05921 | 5.0921 | 0 | 0 | 0 | 0 | off_peak | 610.57 |  |  | 0 | 0 | 100 | 0 | 0
7915 | 544.46 | 0 | 23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27.12 | 544.46 | 0 | 0.05921 | 5.3059 | 0 | 0 | 0 | 0 | off_peak | 544.46 |  |  | 0 | 0 | 100 | 0 | 0
7916 | 567.12 | 0 | 22.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27.12 | 567.12 | 0 | 0.05921 | 5.423 | 0 | 0 | 0 | 0 | off_peak | 567.12 |  |  | 0 | 0 | 100 | 0 | 0
7917 | 542.77 | 0 | 22.8 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 38.684 | 555.1324 | 0 | 0.05921 | 5.4696 | 0 | 0 | 0 | 0 | off_peak | 542.77 | 0 | 100 | 0 | 0 | 100 | 0 | 0
7918 | 548.86 | 0 | 22.8 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 50.2479 | 561.2224 | 0 | 0.05921 | 5.5937 | 0 | 0 | 0 | 0 | off_peak | 548.86 | 0 | 100 | 0 | 0 | 100 | 0 | 0
7919 | 557.1 | 0 | 22.8 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 61.8119 | 569.4624 | 0 | 0.05921 | 5.8544 | 0 | 0 | 0 | 0 | off_peak | 557.1 | 0 | 100 | 0 | 0 | 100 | 0 | 0
7920 | 535.04 | 0 | 22.7 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 73.3758 | 547.4024 | 0 | 0.05921 | 5.9859 | 0 | 0 | 0 | 0 | off_peak | 535.04 | 0 | 100 | 0 | 0 | 100 | 0 | 0
7921 | 543.99 | 0 | 22.6 | 0 | 0 | 0 | 0 | 0.79843 | 0.79843 | 0 | 0 | 0 | 74.1227 | 544.7884 | 0 | 0.05921 | 6.0698 | 0 | 0 | 0 | 0 | off_peak | 543.99 | 0 | 100 | 0 | 0 | 100 | 0 | 0
7922 | 547 | 0 | 22.5 | 0 | 0 | 0 | 0 | 0.051567 | 0.051567 | 0 | 0 | 0 | 74.1709 | 547.0516 | 0 | 0.05921 | 5.8413 | 0 | 0 | 0 | 0 | off_peak | 547 | 0 | 100 | 0 | 0 | 100 | 0 | 0
7923 | 552.31 | 0 | 22.5 | 0 | 0 | 0 | 0 | 0.0033305 | 0.0033305 | 0 | 0 | 0 | 74.174 | 552.3133 | 0 | 0.05921 | 5.5657 | 0 | 0 | 0 | 0 | off_peak | 552.31 | 0 | 100 | 0 | 0 | 100 | 0 | 0
7924 | 531.98 | 0 | 22.4 | 0 | 0 | 0 | 0 | 0.0002151 | 0.0002151 | 0 | 0 | 0 | 74.1742 | 531.9802 | 0 | 0.05921 | 5.1625 | 0 | 0 | 0 | 0 | off_peak | 531.98 | 0 | 100 | 0 | 0 | 100 | 0 | 0
7925 | 553.43 | 0 | 22.5 | 0 | 0 | 0 | 0 | 1.3893e-05 | 1.3893e-05 | 0 | 0 | 0 | 74.1743 | 553.43 | 0 | 0.05921 | 4.7232 | 0 | 0 | 0 | 0 | off_peak | 553.43 | 0 | 100 | 0 | 0 | 100 | 0 | 0
7926 | 605.99 | 0 | 22.5 | 0 | 0 | 0 | 0 | 8.9726e-07 | 8.9726e-07 | 0 | 0 | 0 | 74.1743 | 605.99 | 0 | 0.05921 | 4.1422 | 0 | 0 | 0 | 0 | off_peak | 605.99 | 0 | 100 | 0 | 0 | 100 | 0 | 0
7927 | 656.84 | 0 | 22.6 | 0 | 0 | 0 | 0 | 0 | 0 | 62.4453 | 62.4453 | 0 | 7.4174 | 594.3947 | 0 | 0.088511 | 3.595 | 0 | 0 | 0 | 0 | on_peak | 594.3947 |  |  | 0 | 9.51 | 90.49 | 0 | 0
7928 | 789.44 | 89.3391 | 23.2 | 14.5667 | 14.5667 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 774.8733 | 0 | 0.088511 | 3.3065 | 0 | 0 | 0 | 14.5667 | on_peak | 774.8733 |  |  | 1.85 | 0 | 98.15 | 48.165 | 0
7929 | 842.29 | 273.212 | 23.9 | 44.4356 | 44.4356 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 797.8544 | 0 | 0.088511 | 3.1385 | 0 | 0 | 0 | 44.4356 | on_peak | 797.8544 |  |  | 5.28 | 0 | 94.72 | 139.4622 | 0
7930 | 797.04 | 445.91 | 24.3 | 72.4195 | 72.4195 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 724.6205 | 0 | 0.088511 | 3.0298 | 0 | 0 | 0 | 72.4195 | on_peak | 724.6205 |  |  | 9.09 | 0 | 90.91 | 219.4169 | 0
7931 | 814.4 | 575.905 | 24.6 | 93.431 | 93.431 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 18.9814 | 733.3314 | 0 | 0.05921 | 3.0609 | 0 | 0 | 0 | 93.431 | off_peak | 720.969 | 0 | 100 | 11.47 | 0 | 88.53 | 285.9829 | 0
7932 | 837.29 | 649.788 | 24.8 | 105.3414 | 105.3414 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 30.5453 | 744.3109 | 0 | 0.05921 | 3.4081 | 0 | 0 | 0 | 105.3414 | off_peak | 731.9486 | 0 | 100 | 12.58 | 0 | 87.42 | 359.0091 | 0
7933 | 775.79 | 660.493 | 24.9 | 107.0384 | 107.0384 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 42.1093 | 681.114 | 0 | 0.05921 | 3.8411 | 0 | 0 | 0 | 107.0384 | off_peak | 668.7516 | 0 | 100 | 13.8 | 0 | 86.2 | 411.1416 | 0
7934 | 843.16 | 603.964 | 24.9 | 97.8774 | 97.8774 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 53.6732 | 757.645 | 0 | 0.05921 | 4.0856 | 0 | 0 | 0 | 97.8774 | off_peak | 745.2826 | 0 | 100 | 11.61 | 0 | 88.39 | 399.8887 | 0
7935 | 814.15 | 489.904 | 24.8 | 79.4216 | 79.4216 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 65.2371 | 747.0908 | 0 | 0.05921 | 4.2822 | 0 | 0 | 0 | 79.4216 | off_peak | 734.7284 | 0 | 100 | 9.76 | 0 | 90.24 | 340.1016 | 0
7936 | 757.03 | 328.016 | 24.6 | 53.2151 | 53.2151 | 0 | 0 | 8.9371 | 8.9371 | 0 | 0 | 0 | 73.597 | 712.752 | 0 | 0.05921 | 4.362 | 0 | 0 | 0 | 53.2151 | off_peak | 703.8149 | 0 | 100 | 7.03 | 0 | 92.97 | 232.1247 | 0
7937 | 794.87 | 142.667 | 24.3 | 23.1703 | 23.1703 | 0 | 0 | 0.57721 | 0.57721 | 0 | 0 | 0 | 74.137 | 772.2769 | 0 | 0.05921 | 4.308 | 0 | 0 | 0 | 23.1703 | off_peak | 771.6997 | 0 | 100 | 2.91 | 0 | 97.09 | 99.8171 | 0
7938 | 783.4 | 0 | 24.1 | 0 | 0 | 0 | 0 | 0.037279 | 0.037279 | 0 | 0 | 0 | 74.1718 | 783.4373 | 0 | 0.05921 | 4.2819 | 0 | 0 | 0 | 0 | off_peak | 783.4 | 0 | 100 | 0 | 0 | 100 | 0 | 0
7939 | 776.77 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1718 | 776.77 | 0 | 0.088511 | 4.2134 | 0 | 0 | 0 | 0 | on_peak | 776.77 |  |  | 0 | 0 | 100 | 0 | 0
7940 | 774.54 | 0 | 24.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1718 | 774.54 | 0 | 0.088511 | 4.0762 | 0 | 0 | 0 | 0 | on_peak | 774.54 |  |  | 0 | 0 | 100 | 0 | 0
7941 | 770.38 | 0 | 24.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1718 | 770.38 | 0 | 0.088511 | 4.1399 | 0 | 0 | 0 | 0 | on_peak | 770.38 |  |  | 0 | 0 | 100 | 0 | 0
7942 | 734.78 | 0 | 24.2 | 0 | 0 | 0 | 0 | 0 | 0 | 62.443 | 62.443 | 0 | 7.4174 | 672.337 | 0 | 0.088511 | 4.536 | 0 | 0 | 0 | 0 | on_peak | 672.337 |  |  | 0 | 8.5 | 91.5 | 0 | 0
7943 | 763.22 | 0 | 24.1 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 18.9814 | 775.5824 | 0 | 0.05921 | 5.146 | 0 | 0 | 0 | 0 | off_peak | 763.22 | 0 | 100 | 0 | 0 | 100 | 0 | 0
7944 | 707.56 | 0 | 24.1 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 30.5453 | 719.9224 | 0 | 0.05921 | 5.5986 | 0 | 0 | 0 | 0 | off_peak | 707.56 | 0 | 100 | 0 | 0 | 100 | 0 | 0
7945 | 698.34 | 0 | 24 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 42.1093 | 710.7024 | 0 | 0.05921 | 5.7424 | 0 | 0 | 0 | 0 | off_peak | 698.34 | 0 | 100 | 0 | 0 | 100 | 0 | 0
7946 | 527.57 | 0 | 24 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 53.6732 | 539.9324 | 0 | 0.05921 | 5.5482 | 0 | 0 | 0 | 0 | off_peak | 527.57 | 0 | 100 | 0 | 0 | 100 | 0 | 0
7947 | 518.43 | 0 | 23.9 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 65.2371 | 530.7924 | 0 | 0.05921 | 5.2059 | 0 | 0 | 0 | 0 | off_peak | 518.43 | 0 | 100 | 0 | 0 | 100 | 0 | 0
7948 | 491.52 | 0 | 23.9 | 0 | 0 | 0 | 0 | 8.9371 | 8.9371 | 0 | 0 | 0 | 73.597 | 500.4571 | 0 | 0.05921 | 4.7662 | 0 | 0 | 0 | 0 | off_peak | 491.52 | 0 | 100 | 0 | 0 | 100 | 0 | 0
7949 | 493.74 | 0 | 23.8 | 0 | 0 | 0 | 0 | 0.57721 | 0.57721 | 0 | 0 | 0 | 74.137 | 494.3172 | 0 | 0.05921 | 4.2057 | 0 | 0 | 0 | 0 | off_peak | 493.74 | 0 | 100 | 0 | 0 | 100 | 0 | 0
7950 | 522.28 | 0 | 23.8 | 0 | 0 | 0 | 0 | 0.037279 | 0.037279 | 0 | 0 | 0 | 74.1718 | 522.3173 | 0 | 0.05921 | 3.5487 | 0 | 0 | 0 | 0 | off_peak | 522.28 | 0 | 100 | 0 | 0 | 100 | 0 | 0
7951 | 608.86 | 0 | 23.9 | 0 | 0 | 0 | 0 | 0 | 0 | 62.443 | 62.443 | 0 | 7.4174 | 546.417 | 0 | 0.088511 | 3.2356 | 0 | 0 | 0 | 0 | on_peak | 546.417 |  |  | 0 | 10.26 | 89.74 | 0 | 0
7952 | 679.17 | 89.0772 | 24.1 | 14.4773 | 14.4773 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 664.6927 | 0 | 0.088511 | 2.9961 | 0 | 0 | 0 | 14.4773 | on_peak | 664.6927 |  |  | 2.13 | 0 | 97.87 | 43.375 | 0
7953 | 773.43 | 272.779 | 24.4 | 44.2856 | 44.2856 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 729.1444 | 0 | 0.088511 | 2.8439 | 0 | 0 | 0 | 44.2856 | on_peak | 729.1444 |  |  | 5.73 | 0 | 94.27 | 125.9432 | 0
7954 | 738.23 | 441.794 | 24.7 | 71.6479 | 71.6479 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 666.5821 | 0 | 0.088511 | 2.7487 | 0 | 0 | 0 | 71.6479 | on_peak | 666.5821 |  |  | 9.71 | 0 | 90.29 | 196.9368 | 0
7955 | 654.05 | 525.788 | 24.9 | 85.2083 | 85.2083 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 18.9814 | 581.2041 | 0 | 0.05921 | 2.8067 | 0 | 0 | 0 | 85.2083 | off_peak | 568.8417 | 0 | 100 | 13.03 | 0 | 86.97 | 239.1577 | 0
7956 | 769.07 | 535.579 | 25 | 86.7638 | 86.7638 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 30.5453 | 694.6686 | 0 | 0.05921 | 3.085 | 0 | 0 | 0 | 86.7638 | off_peak | 682.3062 | 0 | 100 | 11.28 | 0 | 88.72 | 267.6623 | 0
7957 | 776.23 | 586.378 | 25 | 94.9932 | 94.9932 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 42.1093 | 693.5991 | 0 | 0.05921 | 3.6102 | 0 | 0 | 0 | 94.9932 | off_peak | 681.2368 | 0 | 100 | 12.24 | 0 | 87.76 | 342.9454 | 0
7958 | 785.7 | 548.101 | 24.9 | 88.8243 | 88.8243 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 53.6732 | 709.238 | 0 | 0.05921 | 3.9001 | 0 | 0 | 0 | 88.8243 | off_peak | 696.8757 | 0 | 100 | 11.31 | 0 | 88.69 | 346.4214 | 0
7959 | 831.56 | 408.183 | 24.8 | 66.1733 | 66.1733 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 65.2371 | 777.7491 | 0 | 0.05921 | 4.0539 | 0 | 0 | 0 | 66.1733 | off_peak | 765.3867 | 0 | 100 | 7.96 | 0 | 92.04 | 268.2625 | 0
7960 | 772.28 | 288.581 | 24.6 | 46.8174 | 46.8174 | 0 | 0 | 8.9371 | 8.9371 | 0 | 0 | 0 | 73.597 | 734.3997 | 0 | 0.05921 | 3.9198 | 0 | 0 | 0 | 46.8174 | off_peak | 725.4626 | 0 | 100 | 6.06 | 0 | 93.94 | 183.5163 | 0
7961 | 746.35 | 79.1328 | 24.5 | 12.8426 | 12.8426 | 0 | 0 | 0.57721 | 0.57721 | 0 | 0 | 0 | 74.137 | 734.0846 | 0 | 0.05921 | 3.8759 | 0 | 0 | 0 | 12.8426 | off_peak | 733.5074 | 0 | 100 | 1.72 | 0 | 98.28 | 49.777 | 0
7962 | 824.82 | 0 | 24.3 | 0 | 0 | 0 | 0 | 0.037279 | 0.037279 | 0 | 0 | 0 | 74.1718 | 824.8573 | 0 | 0.05921 | 3.7755 | 0 | 0 | 0 | 0 | off_peak | 824.82 | 0 | 100 | 0 | 0 | 100 | 0 | 0
7963 | 800.05 | 0 | 24.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1718 | 800.05 | 0 | 0.088511 | 3.8124 | 0 | 0 | 0 | 0 | on_peak | 800.05 |  |  | 0 | 0 | 100 | 0 | 0
7964 | 756.94 | 0 | 24.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1718 | 756.94 | 0 | 0.088511 | 3.8791 | 0 | 0 | 0 | 0 | on_peak | 756.94 |  |  | 0 | 0 | 100 | 0 | 0
7965 | 784.05 | 0 | 24.5 | 0 | 0 | 0 | 0 | 0 | 0 | 62.443 | 62.443 | 0 | 7.4174 | 721.607 | 0 | 0.088511 | 4.0715 | 0 | 0 | 0 | 0 | on_peak | 721.607 |  |  | 0 | 7.96 | 92.04 | 0 | 0
7966 | 740.57 | 0 | 24.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 740.57 | 0 | 0.088511 | 4.2875 | 0 | 0 | 0 | 0 | on_peak | 740.57 |  |  | 0 | 0 | 100 | 0 | 0
7967 | 747.79 | 0 | 24.5 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 18.9814 | 760.1524 | 0 | 0.05921 | 4.6652 | 0 | 0 | 0 | 0 | off_peak | 747.79 | 0 | 100 | 0 | 0 | 100 | 0 | 0
7968 | 728.89 | 0 | 24.4 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 30.5453 | 741.2524 | 0 | 0.05921 | 5.137 | 0 | 0 | 0 | 0 | off_peak | 728.89 | 0 | 100 | 0 | 0 | 100 | 0 | 0
7969 | 663.77 | 0 | 24.4 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 42.1093 | 676.1324 | 0 | 0.05921 | 5.3733 | 0 | 0 | 0 | 0 | off_peak | 663.77 | 0 | 100 | 0 | 0 | 100 | 0 | 0
7970 | 596.82 | 0 | 24.3 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 53.6732 | 609.1824 | 0 | 0.05921 | 5.2729 | 0 | 0 | 0 | 0 | off_peak | 596.82 | 0 | 100 | 0 | 0 | 100 | 0 | 0
7971 | 577.21 | 0 | 24.2 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 65.2371 | 589.5724 | 0 | 0.05921 | 5.0585 | 0 | 0 | 0 | 0 | off_peak | 577.21 | 0 | 100 | 0 | 0 | 100 | 0 | 0
7972 | 588.96 | 0 | 24.1 | 0 | 0 | 0 | 0 | 8.9371 | 8.9371 | 0 | 0 | 0 | 73.597 | 597.8971 | 0 | 0.05921 | 4.7111 | 0 | 0 | 0 | 0 | off_peak | 588.96 | 0 | 100 | 0 | 0 | 100 | 0 | 0
7973 | 577.25 | 0 | 24.1 | 0 | 0 | 0 | 0 | 0.57721 | 0.57721 | 0 | 0 | 0 | 74.137 | 577.8272 | 0 | 0.05921 | 4.3265 | 0 | 0 | 0 | 0 | off_peak | 577.25 | 0 | 100 | 0 | 0 | 100 | 0 | 0
7974 | 624.67 | 0 | 24 | 0 | 0 | 0 | 0 | 0.037279 | 0.037279 | 0 | 0 | 0 | 74.1718 | 624.7073 | 0 | 0.05921 | 3.7879 | 0 | 0 | 0 | 0 | off_peak | 624.67 | 0 | 100 | 0 | 0 | 100 | 0 | 0
7975 | 701.78 | 0 | 24.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1718 | 701.78 | 0 | 0.088511 | 3.5089 | 0 | 0 | 0 | 0 | on_peak | 701.78 |  |  | 0 | 0 | 100 | 0 | 0
7976 | 744.06 | 55.2306 | 24.3 | 8.9699 | 8.9699 | 0 | 0 | 0 | 0 | 62.443 | 62.443 | 0 | 7.4174 | 672.6471 | 0 | 0.088511 | 3.3484 | 0 | 0 | 0 | 8.9699 | on_peak | 672.6471 |  |  | 1.21 | 8.39 | 90.4 | 30.0353 | 0
7977 | 749.03 | 197.861 | 24.6 | 32.0996 | 32.0996 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 716.9304 | 0 | 0.088511 | 3.2179 | 0 | 0 | 0 | 32.0996 | on_peak | 716.9304 |  |  | 4.29 | 0 | 95.71 | 103.2948 | 0
7978 | 740.07 | 286.915 | 24.8 | 46.5137 | 46.5137 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 693.5563 | 0 | 0.088511 | 3.1943 | 0 | 0 | 0 | 46.5137 | on_peak | 693.5563 |  |  | 6.29 | 0 | 93.71 | 148.5773 | 0
7979 | 715.1 | 358.56 | 24.9 | 58.1076 | 58.1076 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 18.9814 | 669.3547 | 0 | 0.05921 | 3.3054 | 0 | 0 | 0 | 58.1076 | off_peak | 656.9924 | 0 | 100 | 8.13 | 0 | 91.87 | 192.0702 | 0
7980 | 790.05 | 438.943 | 24.9 | 71.1344 | 71.1344 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 30.5453 | 731.278 | 0 | 0.05921 | 3.7566 | 0 | 0 | 0 | 71.1344 | off_peak | 718.9156 | 0 | 100 | 9 | 0 | 91 | 267.2212 | 0
7981 | 745.19 | 484.009 | 24.8 | 78.4659 | 78.4659 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 42.1093 | 679.0865 | 0 | 0.05921 | 4.3608 | 0 | 0 | 0 | 78.4659 | off_peak | 666.7241 | 0 | 100 | 10.53 | 0 | 89.47 | 342.1735 | 0
7982 | 841.12 | 387.395 | 24.7 | 62.8258 | 62.8258 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 53.6732 | 790.6566 | 0 | 0.05921 | 4.634 | 0 | 0 | 0 | 62.8258 | off_peak | 778.2942 | 0 | 100 | 7.47 | 0 | 92.53 | 291.1321 | 0
7983 | 846.71 | 246.224 | 24.6 | 39.9457 | 39.9457 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 65.2371 | 819.1266 | 0 | 0.05921 | 4.3323 | 0 | 0 | 0 | 39.9457 | off_peak | 806.7643 | 0 | 100 | 4.72 | 0 | 95.28 | 173.0567 | 0
7984 | 852.74 | 127.031 | 24.3 | 20.6309 | 20.6309 | 0 | 0 | 8.9371 | 8.9371 | 0 | 0 | 0 | 73.597 | 841.0462 | 0 | 0.05921 | 3.6713 | 0 | 0 | 0 | 20.6309 | off_peak | 832.1091 | 0 | 100 | 2.42 | 0 | 97.58 | 75.742 | 0
7985 | 816.11 | 38.3677 | 24 | 6.2379 | 6.2379 | 0 | 0 | 0.57721 | 0.57721 | 0 | 0 | 0 | 74.137 | 810.4493 | 0 | 0.05921 | 3.314 | 0 | 0 | 0 | 6.2379 | off_peak | 809.8721 | 0 | 100 | 0.76 | 0 | 99.24 | 20.6723 | 0
7986 | 794.41 | 0 | 23.7 | 0 | 0 | 0 | 0 | 0.037279 | 0.037279 | 0 | 0 | 0 | 74.1718 | 794.4473 | 0 | 0.05921 | 3.0319 | 0 | 0 | 0 | 0 | off_peak | 794.41 | 0 | 100 | 0 | 0 | 100 | 0 | 0
7987 | 819.32 | 0 | 23.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1718 | 819.32 | 0 | 0.088511 | 2.8678 | 0 | 0 | 0 | 0 | on_peak | 819.32 |  |  | 0 | 0 | 100 | 0 | 0
7988 | 820.61 | 0 | 23.6 | 0 | 0 | 0 | 0 | 0 | 0 | 62.443 | 62.443 | 0 | 7.4174 | 758.167 | 0 | 0.088511 | 2.8171 | 0 | 0 | 0 | 0 | on_peak | 758.167 |  |  | 0 | 7.61 | 92.39 | 0 | 0
7989 | 808.91 | 0 | 23.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 808.91 | 0 | 0.088511 | 2.9751 | 0 | 0 | 0 | 0 | on_peak | 808.91 |  |  | 0 | 0 | 100 | 0 | 0
7990 | 779.12 | 0 | 23.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 779.12 | 0 | 0.088511 | 3.4139 | 0 | 0 | 0 | 0 | on_peak | 779.12 |  |  | 0 | 0 | 100 | 0 | 0
7991 | 807.57 | 0 | 23.5 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 18.9814 | 819.9324 | 0 | 0.05921 | 4.1555 | 0 | 0 | 0 | 0 | off_peak | 807.57 | 0 | 100 | 0 | 0 | 100 | 0 | 0
7992 | 780.34 | 0 | 23.5 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 30.5453 | 792.7024 | 0 | 0.05921 | 4.7528 | 0 | 0 | 0 | 0 | off_peak | 780.34 | 0 | 100 | 0 | 0 | 100 | 0 | 0
7993 | 724.6 | 0 | 23.4 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 42.1093 | 736.9624 | 0 | 0.05921 | 5.0657 | 0 | 0 | 0 | 0 | off_peak | 724.6 | 0 | 100 | 0 | 0 | 100 | 0 | 0
7994 | 618.68 | 0 | 23.4 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 53.6732 | 631.0424 | 0 | 0.05921 | 4.9781 | 0 | 0 | 0 | 0 | off_peak | 618.68 | 0 | 100 | 0 | 0 | 100 | 0 | 0
7995 | 614.11 | 0 | 23.3 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 65.2371 | 626.4724 | 0 | 0.05921 | 4.7881 | 0 | 0 | 0 | 0 | off_peak | 614.11 | 0 | 100 | 0 | 0 | 100 | 0 | 0
7996 | 609.4 | 0 | 23.2 | 0 | 0 | 0 | 0 | 8.9371 | 8.9371 | 0 | 0 | 0 | 73.597 | 618.3371 | 0 | 0.05921 | 4.4865 | 0 | 0 | 0 | 0 | off_peak | 609.4 | 0 | 100 | 0 | 0 | 100 | 0 | 0
7997 | 600.55 | 0 | 23.1 | 0 | 0 | 0 | 0 | 0.57721 | 0.57721 | 0 | 0 | 0 | 74.137 | 601.1272 | 0 | 0.05921 | 4.1446 | 0 | 0 | 0 | 0 | off_peak | 600.55 | 0 | 100 | 0 | 0 | 100 | 0 | 0
7998 | 590.07 | 0 | 22.9 | 0 | 0 | 0 | 0 | 0.037279 | 0.037279 | 0 | 0 | 0 | 74.1718 | 590.1073 | 0 | 0.05921 | 3.7279 | 0 | 0 | 0 | 0 | off_peak | 590.07 | 0 | 100 | 0 | 0 | 100 | 0 | 0
7999 | 593.49 | 0 | 22.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1718 | 593.49 | 0 | 0.088511 | 3.4242 | 0 | 0 | 0 | 0 | on_peak | 593.49 |  |  | 0 | 0 | 100 | 0 | 0
8000 | 721.37 | 73.5965 | 22.9 | 12.0128 | 12.0128 | 0 | 0 | 0 | 0 | 62.443 | 62.443 | 0 | 7.4174 | 646.9142 | 0 | 0.088511 | 3.23 | 0 | 0 | 0 | 12.0128 | on_peak | 646.9142 |  |  | 1.67 | 8.66 | 89.68 | 38.8011 | 0
8001 | 738.73 | 247.357 | 23 | 40.3604 | 40.3604 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 698.3696 | 0 | 0.088511 | 3.1463 | 0 | 0 | 0 | 40.3604 | on_peak | 698.3696 |  |  | 5.46 | 0 | 94.54 | 126.9871 | 0
8002 | 771.65 | 389.243 | 23.2 | 63.466 | 63.466 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 708.184 | 0 | 0.088511 | 3.1237 | 0 | 0 | 0 | 63.466 | on_peak | 708.184 |  |  | 8.22 | 0 | 91.78 | 198.2504 | 0
8003 | 746.16 | 476.498 | 23.5 | 77.6095 | 77.6095 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 18.9814 | 680.9129 | 0 | 0.05921 | 3.224 | 0 | 0 | 0 | 77.6095 | off_peak | 668.5505 | 0 | 100 | 10.4 | 0 | 89.6 | 250.2142 | 0
8004 | 808.26 | 512.083 | 24 | 83.2561 | 83.2561 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 30.5453 | 737.3663 | 0 | 0.05921 | 3.663 | 0 | 0 | 0 | 83.2561 | off_peak | 725.0039 | 0 | 100 | 10.3 | 0 | 89.7 | 304.9639 | 0
8005 | 778.56 | 610.302 | 24.3 | 99.1181 | 99.1181 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 42.1093 | 691.8043 | 0 | 0.05921 | 4.2927 | 0 | 0 | 0 | 99.1181 | off_peak | 679.4419 | 0 | 100 | 12.73 | 0 | 87.27 | 425.4801 | 0
8006 | 838.13 | 606.401 | 24.6 | 98.3784 | 98.3784 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 53.6732 | 752.114 | 0 | 0.05921 | 4.5323 | 0 | 0 | 0 | 98.3784 | off_peak | 739.7516 | 0 | 100 | 11.74 | 0 | 88.26 | 445.8762 | 0
8007 | 815.85 | 489.262 | 24.6 | 79.3746 | 79.3746 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 65.2371 | 748.8378 | 0 | 0.05921 | 4.1529 | 0 | 0 | 0 | 79.3746 | off_peak | 736.4754 | 0 | 100 | 9.73 | 0 | 90.27 | 329.6327 | 0
8008 | 776.83 | 326.932 | 24.5 | 53.0583 | 53.0583 | 0 | 0 | 8.9371 | 8.9371 | 0 | 0 | 0 | 73.597 | 732.7088 | 0 | 0.05921 | 3.6456 | 0 | 0 | 0 | 53.0583 | off_peak | 723.7717 | 0 | 100 | 6.83 | 0 | 93.17 | 193.4301 | 0
8009 | 786.92 | 138.825 | 24 | 22.5706 | 22.5706 | 0 | 0 | 0.57721 | 0.57721 | 0 | 0 | 0 | 74.137 | 764.9266 | 0 | 0.05921 | 3.345 | 0 | 0 | 0 | 22.5706 | off_peak | 764.3494 | 0 | 100 | 2.87 | 0 | 97.13 | 75.4991 | 0
8010 | 764.48 | 0 | 23.4 | 0 | 0 | 0 | 0 | 0.037279 | 0.037279 | 0 | 0 | 0 | 74.1718 | 764.5173 | 0 | 0.05921 | 3.2441 | 0 | 0 | 0 | 0 | off_peak | 764.48 | 0 | 100 | 0 | 0 | 100 | 0 | 0
8011 | 755.82 | 0 | 23.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1718 | 755.82 | 0 | 0.088511 | 3.3663 | 0 | 0 | 0 | 0 | on_peak | 755.82 |  |  | 0 | 0 | 100 | 0 | 0
8012 | 792.56 | 0 | 19.9 | 0 | 0 | 0 | 0 | 0 | 0 | 62.443 | 62.443 | 0 | 7.4174 | 730.117 | 0 | 0.088511 | 3.6243 | 0 | 0 | 0 | 0 | on_peak | 730.117 |  |  | 0 | 7.88 | 92.12 | 0 | 0
8013 | 743.72 | 0 | 19.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 743.72 | 0 | 0.088511 | 4.0287 | 0 | 0 | 0 | 0 | on_peak | 743.72 |  |  | 0 | 0 | 100 | 0 | 0
8014 | 745.65 | 0 | 19.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 745.65 | 0 | 0.088511 | 4.4585 | 0 | 0 | 0 | 0 | on_peak | 745.65 |  |  | 0 | 0 | 100 | 0 | 0
8015 | 737.9 | 0 | 19.4 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 18.9814 | 750.2624 | 0 | 0.05921 | 4.7881 | 0 | 0 | 0 | 0 | off_peak | 737.9 | 0 | 100 | 0 | 0 | 100 | 0 | 0
8016 | 700.09 | 0 | 19.2 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 30.5453 | 712.4524 | 0 | 0.05921 | 5.2189 | 0 | 0 | 0 | 0 | off_peak | 700.09 | 0 | 100 | 0 | 0 | 100 | 0 | 0
8017 | 674.2 | 0 | 19 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 42.1093 | 686.5624 | 0 | 0.05921 | 5.3984 | 0 | 0 | 0 | 0 | off_peak | 674.2 | 0 | 100 | 0 | 0 | 100 | 0 | 0
8018 | 626.16 | 0 | 18.9 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 53.6732 | 638.5224 | 0 | 0.05921 | 5.2709 | 0 | 0 | 0 | 0 | off_peak | 626.16 | 0 | 100 | 0 | 0 | 100 | 0 | 0
8019 | 551.83 | 0 | 18.9 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 65.2371 | 564.1924 | 0 | 0.05921 | 5.0009 | 0 | 0 | 0 | 0 | off_peak | 551.83 | 0 | 100 | 0 | 0 | 100 | 0 | 0
8020 | 591.1 | 0 | 18.9 | 0 | 0 | 0 | 0 | 8.9371 | 8.9371 | 0 | 0 | 0 | 73.597 | 600.0371 | 0 | 0.05921 | 4.6182 | 0 | 0 | 0 | 0 | off_peak | 591.1 | 0 | 100 | 0 | 0 | 100 | 0 | 0
8021 | 604.18 | 0 | 18.9 | 0 | 0 | 0 | 0 | 0.57721 | 0.57721 | 0 | 0 | 0 | 74.137 | 604.7572 | 0 | 0.05921 | 4.2272 | 0 | 0 | 0 | 0 | off_peak | 604.18 | 0 | 100 | 0 | 0 | 100 | 0 | 0
8022 | 617.26 | 0 | 19 | 0 | 0 | 0 | 0 | 0.037279 | 0.037279 | 0 | 0 | 0 | 74.1718 | 617.2973 | 0 | 0.05921 | 3.7587 | 0 | 0 | 0 | 0 | off_peak | 617.26 | 0 | 100 | 0 | 0 | 100 | 0 | 0
8023 | 693.54 | 0 | 19.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1718 | 693.54 | 0 | 0.088511 | 3.1779 | 0 | 0 | 0 | 0 | on_peak | 693.54 |  |  | 0 | 0 | 100 | 0 | 0
8024 | 718.84 | 62.8728 | 19.8 | 10.3761 | 10.3761 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1718 | 708.4639 | 0 | 0.088511 | 2.9383 | 0 | 0 | 0 | 10.3761 | on_peak | 708.4639 |  |  | 1.44 | 0 | 98.56 | 30.4883 | 0
8025 | 737.18 | 257.791 | 20.5 | 42.4387 | 42.4387 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1718 | 694.7413 | 0 | 0.088511 | 2.7897 | 0 | 0 | 0 | 42.4387 | on_peak | 694.7413 |  |  | 5.76 | 0 | 94.24 | 118.3892 | 0
8026 | 758.04 | 423.971 | 21.3 | 69.5982 | 69.5982 | 0 | 0 | 0 | 0 | 62.443 | 62.443 | 0 | 7.4174 | 625.9988 | 0 | 0.088511 | 2.6929 | 0 | 0 | 0 | 69.5982 | on_peak | 625.9988 |  |  | 9.18 | 8.24 | 82.58 | 187.4208 | 0
8027 | 788.25 | 467.26 | 22.1 | 76.4864 | 76.4864 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 18.9814 | 724.126 | 0 | 0.05921 | 2.7303 | 0 | 0 | 0 | 76.4864 | off_peak | 711.7636 | 0 | 100 | 9.7 | 0 | 90.3 | 208.8291 | 0
8028 | 823.48 | 311.743 | 22.8 | 50.9023 | 50.9023 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 30.5453 | 784.94 | 0 | 0.05921 | 2.9998 | 0 | 0 | 0 | 50.9023 | off_peak | 772.5777 | 0 | 100 | 6.18 | 0 | 93.82 | 152.6988 | 0
8029 | 822.97 | 116.554 | 23.3 | 18.9973 | 18.9973 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 42.1093 | 816.3351 | 0 | 0.05921 | 3.5939 | 0 | 0 | 0 | 18.9973 | off_peak | 803.9727 | 0 | 100 | 2.31 | 0 | 97.69 | 68.275 | 0
8030 | 855.72 | 324.432 | 23.7 | 52.804 | 52.804 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 53.6732 | 815.2784 | 0 | 0.05921 | 3.8189 | 0 | 0 | 0 | 52.804 | off_peak | 802.916 | 0 | 100 | 6.17 | 0 | 93.83 | 201.6539 | 0
8031 | 832.84 | 337.297 | 23.8 | 54.8782 | 54.8782 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 65.2371 | 790.3242 | 0 | 0.05921 | 3.9149 | 0 | 0 | 0 | 54.8782 | off_peak | 777.9618 | 0 | 100 | 6.59 | 0 | 93.41 | 214.8402 | 0
8032 | 787.03 | 309.939 | 23.7 | 50.4451 | 50.4451 | 0 | 0 | 8.9371 | 8.9371 | 0 | 0 | 0 | 73.597 | 745.522 | 0 | 0.05921 | 3.9168 | 0 | 0 | 0 | 50.4451 | off_peak | 736.5849 | 0 | 100 | 6.41 | 0 | 93.59 | 197.585 | 0
8033 | 791.36 | 131.817 | 23.3 | 21.485 | 21.485 | 0 | 0 | 0.57721 | 0.57721 | 0 | 0 | 0 | 74.137 | 770.4522 | 0 | 0.05921 | 4.1267 | 0 | 0 | 0 | 21.485 | off_peak | 769.875 | 0 | 100 | 2.71 | 0 | 97.29 | 88.6627 | 0
8034 | 757.87 | 0 | 22.8 | 0 | 0 | 0 | 0 | 0.037279 | 0.037279 | 0 | 0 | 0 | 74.1718 | 757.9073 | 0 | 0.05921 | 4.429 | 0 | 0 | 0 | 0 | off_peak | 757.87 | 0 | 100 | 0 | 0 | 100 | 0 | 0
8035 | 780.36 | 0 | 22.5 | 0 | 0 | 0 | 0 | 0 | 0 | 57.1948 | 57.1948 | 0 | 13.0281 | 723.1652 | 0 | 0.088511 | 4.862 | 0 | 0 | 0 | 0 | on_peak | 723.1652 |  |  | 0 | 7.33 | 92.67 | 0 | 0
8036 | 813.53 | 0 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 5.2483 | 5.2483 | 0 | 7.4174 | 808.2817 | 0 | 0.088511 | 5.1492 | 0 | 0 | 0 | 0 | on_peak | 808.2817 |  |  | 0 | 0.65 | 99.35 | 0 | 0
8037 | 762.37 | 0 | 21.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 762.37 | 0 | 0.088511 | 5.4467 | 0 | 0 | 0 | 0 | on_peak | 762.37 |  |  | 0 | 0 | 100 | 0 | 0
8038 | 734.39 | 0 | 21.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 734.39 | 0 | 0.088511 | 5.6563 | 0 | 0 | 0 | 0 | on_peak | 734.39 |  |  | 0 | 0 | 100 | 0 | 0
8039 | 758.62 | 0 | 21.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 758.62 | 0 | 0.05921 | 5.9538 | 0 | 0 | 0 | 0 | off_peak | 758.62 |  |  | 0 | 0 | 100 | 0 | 0
8040 | 724.53 | 0 | 20.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 724.53 | 0 | 0.05921 | 6.1008 | 0 | 0 | 0 | 0 | off_peak | 724.53 |  |  | 0 | 0 | 100 | 0 | 0
8041 | 659.4 | 0 | 20.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 659.4 | 0 | 0.05921 | 6.0464 | 0 | 0 | 0 | 0 | off_peak | 659.4 |  |  | 0 | 0 | 100 | 0 | 0
8042 | 632.95 | 0 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 632.95 | 0 | 0.05921 | 5.7369 | 0 | 0 | 0 | 0 | off_peak | 632.95 |  |  | 0 | 0 | 100 | 0 | 0
8043 | 591.66 | 0 | 19.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 591.66 | 0 | 0.05921 | 5.4872 | 0 | 0 | 0 | 0 | off_peak | 591.66 |  |  | 0 | 0 | 100 | 0 | 0
8044 | 600.3 | 0 | 19.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 600.3 | 0 | 0.05921 | 5.1764 | 0 | 0 | 0 | 0 | off_peak | 600.3 |  |  | 0 | 0 | 100 | 0 | 0
8045 | 592.24 | 0 | 19.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 592.24 | 0 | 0.05921 | 4.7516 | 0 | 0 | 0 | 0 | off_peak | 592.24 |  |  | 0 | 0 | 100 | 0 | 0
8046 | 649.26 | 0 | 18.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 649.26 | 0 | 0.05921 | 4.2911 | 0 | 0 | 0 | 0 | off_peak | 649.26 |  |  | 0 | 0 | 100 | 0 | 0
8047 | 705.51 | 0 | 18.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 705.51 | 0 | 0.05921 | 3.8528 | 0 | 0 | 0 | 0 | off_peak | 705.51 |  |  | 0 | 0 | 100 | 0 | 0
8048 | 708.08 | 76.2188 | 18.8 | 12.623 | 12.623 | 0 | 0 | 8.7006 | 8.7006 | 0 | 0 | 0 | 15.5561 | 704.1576 | 0 | 0.05921 | 3.4679 | 0 | 0 | 0 | 12.623 | off_peak | 695.457 | 0 | 100 | 1.78 | 0 | 98.22 | 43.7756 | 0
8049 | 738.83 | 255.819 | 19.3 | 42.2931 | 42.2931 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 27.12 | 708.8993 | 0 | 0.05921 | 3.2395 | 0 | 0 | 0 | 42.2931 | off_peak | 696.5369 | 0 | 100 | 5.72 | 0 | 94.28 | 137.0082 | 0
8050 | 718.07 | 427.724 | 20.3 | 70.4637 | 70.4637 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27.12 | 647.6063 | 0 | 0.05921 | 3.0905 | 0 | 0 | 0 | 70.4637 | off_peak | 647.6063 |  |  | 9.81 | 0 | 90.19 | 217.7656 | 0
8051 | 736.24 | 538.943 | 21.5 | 88.4089 | 88.4089 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27.12 | 647.8311 | 0 | 0.05921 | 3.0516 | 0 | 0 | 0 | 88.4089 | off_peak | 647.8311 |  |  | 12.01 | 0 | 87.99 | 269.7856 | 0
8052 | 796.62 | 619.214 | 22.5 | 101.2155 | 101.2155 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27.12 | 695.4045 | 0 | 0.05921 | 3.1299 | 0 | 0 | 0 | 101.2155 | off_peak | 695.4045 |  |  | 12.71 | 0 | 87.29 | 316.7951 | 0
8053 | 757.31 | 645.809 | 23.2 | 105.299 | 105.299 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27.12 | 652.011 | 0 | 0.05921 | 3.3557 | 0 | 0 | 0 | 105.299 | off_peak | 652.011 |  |  | 13.9 | 0 | 86.1 | 353.35 | 0
8054 | 686.23 | 463.948 | 23.7 | 75.5113 | 75.5113 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27.12 | 610.7187 | 0 | 0.05921 | 3.662 | 0 | 0 | 0 | 75.5113 | off_peak | 610.7187 |  |  | 11 | 0 | 89 | 276.5246 | 0
8055 | 693.61 | 347.674 | 24 | 56.526 | 56.526 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27.12 | 637.084 | 0 | 0.05921 | 4.1233 | 0 | 0 | 0 | 56.526 | off_peak | 637.084 |  |  | 8.15 | 0 | 91.85 | 233.0734 | 0
8056 | 693.82 | 320.318 | 24 | 52.0783 | 52.0783 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 38.684 | 654.104 | 0 | 0.05921 | 4.64 | 0 | 0 | 0 | 52.0783 | off_peak | 641.7417 | 0 | 100 | 7.51 | 0 | 92.49 | 241.6412 | 0
8057 | 694.09 | 126.376 | 23.5 | 20.5835 | 20.5835 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 50.2479 | 685.8689 | 0 | 0.05921 | 5.1315 | 0 | 0 | 0 | 20.5835 | off_peak | 673.5065 | 0 | 100 | 2.97 | 0 | 97.03 | 105.6243 | 0
8058 | 637.97 | 0 | 22.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50.2479 | 637.97 | 0 | 0.05921 | 5.6278 | 0 | 0 | 0 | 0 | off_peak | 637.97 |  |  | 0 | 0 | 100 | 0 | 0
8059 | 584.03 | 0 | 22.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50.2479 | 584.03 | 0 | 0.05921 | 5.8628 | 0 | 0 | 0 | 0 | off_peak | 584.03 |  |  | 0 | 0 | 100 | 0 | 0
8060 | 606.93 | 0 | 22.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50.2479 | 606.93 | 0 | 0.05921 | 6.1233 | 0 | 0 | 0 | 0 | off_peak | 606.93 |  |  | 0 | 0 | 100 | 0 | 0
8061 | 568.67 | 0 | 22.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50.2479 | 568.67 | 0 | 0.05921 | 6.3492 | 0 | 0 | 0 | 0 | off_peak | 568.67 |  |  | 0 | 0 | 100 | 0 | 0
8062 | 583.35 | 0 | 21.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50.2479 | 583.35 | 0 | 0.05921 | 6.3652 | 0 | 0 | 0 | 0 | off_peak | 583.35 |  |  | 0 | 0 | 100 | 0 | 0
8063 | 588.85 | 0 | 21.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50.2479 | 588.85 | 0 | 0.05921 | 6.4393 | 0 | 0 | 0 | 0 | off_peak | 588.85 |  |  | 0 | 0 | 100 | 0 | 0
8064 | 593.48 | 0 | 21.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50.2479 | 593.48 | 0 | 0.05921 | 6.3645 | 0 | 0 | 0 | 0 | off_peak | 593.48 |  |  | 0 | 0 | 100 | 0 | 0
8065 | 584.87 | 0 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50.2479 | 584.87 | 0 | 0.05921 | 6.2535 | 0 | 0 | 0 | 0 | off_peak | 584.87 |  |  | 0 | 0 | 100 | 0 | 0
8066 | 575.64 | 0 | 20.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50.2479 | 575.64 | 0 | 0.05921 | 5.923 | 0 | 0 | 0 | 0 | off_peak | 575.64 |  |  | 0 | 0 | 100 | 0 | 0
8067 | 596.9 | 0 | 20.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50.2479 | 596.9 | 0 | 0.05921 | 5.6633 | 0 | 0 | 0 | 0 | off_peak | 596.9 |  |  | 0 | 0 | 100 | 0 | 0
8068 | 585.62 | 0 | 20.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50.2479 | 585.62 | 0 | 0.05921 | 5.3072 | 0 | 0 | 0 | 0 | off_peak | 585.62 |  |  | 0 | 0 | 100 | 0 | 0
8069 | 576.18 | 0 | 20.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50.2479 | 576.18 | 0 | 0.05921 | 4.9316 | 0 | 0 | 0 | 0 | off_peak | 576.18 |  |  | 0 | 0 | 100 | 0 | 0
8070 | 647.2 | 0 | 20.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50.2479 | 647.2 | 0 | 0.05921 | 4.4044 | 0 | 0 | 0 | 0 | off_peak | 647.2 |  |  | 0 | 0 | 100 | 0 | 0
8071 | 699.86 | 0 | 20.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50.2479 | 699.86 | 0 | 0.05921 | 3.9389 | 0 | 0 | 0 | 0 | off_peak | 699.86 |  |  | 0 | 0 | 100 | 0 | 0
8072 | 723.79 | 68.8243 | 20.8 | 11.3181 | 11.3181 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50.2479 | 712.4719 | 0 | 0.05921 | 3.554 | 0 | 0 | 0 | 11.3181 | off_peak | 712.4719 |  |  | 1.56 | 0 | 98.44 | 40.2244 | 0
8073 | 731.5 | 229.816 | 21.4 | 37.7127 | 37.7127 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 61.8119 | 706.1497 | 0 | 0.05921 | 3.2627 | 0 | 0 | 0 | 37.7127 | off_peak | 693.7873 | 0 | 100 | 5.16 | 0 | 94.84 | 123.0463 | 0
8074 | 714.4 | 416.469 | 22.2 | 68.1481 | 68.1481 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 61.8119 | 646.2519 | 0 | 0.05921 | 3.0968 | 0 | 0 | 0 | 68.1481 | off_peak | 646.2519 |  |  | 9.54 | 0 | 90.46 | 211.0392 | 0
8075 | 699.44 | 556.09 | 23.2 | 90.6703 | 90.6703 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 73.3758 | 621.132 | 0 | 0.05921 | 3.0193 | 0 | 0 | 0 | 90.6703 | off_peak | 608.7697 | 0 | 100 | 12.96 | 0 | 87.04 | 273.7647 | 0
8076 | 736.36 | 586.178 | 24 | 95.3027 | 95.3027 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 73.3758 | 641.0573 | 0 | 0.05921 | 3.0506 | 0 | 0 | 0 | 95.3027 | off_peak | 641.0573 |  |  | 12.94 | 0 | 87.06 | 290.7262 | 0
8077 | 722.26 | 447.664 | 24.4 | 72.6782 | 72.6782 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 73.3758 | 649.5818 | 0 | 0.05921 | 3.1905 | 0 | 0 | 0 | 72.6782 | off_peak | 649.5818 |  |  | 10.06 | 0 | 89.94 | 231.8821 | 0
8078 | 724.38 | 469.165 | 24.6 | 76.1142 | 76.1142 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 73.3758 | 648.2658 | 0 | 0.05921 | 3.4825 | 0 | 0 | 0 | 76.1142 | off_peak | 648.2658 |  |  | 10.51 | 0 | 89.49 | 265.0708 | 0
8079 | 708.18 | 381.567 | 24.7 | 61.8806 | 61.8806 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 73.3758 | 646.2994 | 0 | 0.05921 | 3.943 | 0 | 0 | 0 | 61.8806 | off_peak | 646.2994 |  |  | 8.74 | 0 | 91.26 | 243.9964 | 0
8080 | 750.17 | 289.907 | 24.5 | 47.0495 | 47.0495 | 0 | 0 | 0.79843 | 0.79843 | 0 | 0 | 0 | 74.1227 | 703.919 | 0 | 0.05921 | 4.5004 | 0 | 0 | 0 | 47.0495 | off_peak | 703.1205 | 0 | 100 | 6.27 | 0 | 93.73 | 211.7407 | 0
8081 | 729.39 | 110.784 | 24 | 18.0116 | 18.0116 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1227 | 711.3784 | 0 | 0.05921 | 4.9505 | 0 | 0 | 0 | 18.0116 | off_peak | 711.3784 |  |  | 2.47 | 0 | 97.53 | 89.1659 | 0
8082 | 646 | 0 | 23.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1227 | 646 | 0 | 0.05921 | 5.3099 | 0 | 0 | 0 | 0 | off_peak | 646 |  |  | 0 | 0 | 100 | 0 | 0
8083 | 610.44 | 0 | 23.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1227 | 610.44 | 0 | 0.05921 | 5.6828 | 0 | 0 | 0 | 0 | off_peak | 610.44 |  |  | 0 | 0 | 100 | 0 | 0
8084 | 593.79 | 0 | 23.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1227 | 593.79 | 0 | 0.05921 | 6.0088 | 0 | 0 | 0 | 0 | off_peak | 593.79 |  |  | 0 | 0 | 100 | 0 | 0
8085 | 571.84 | 0 | 23.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1227 | 571.84 | 0 | 0.05921 | 6.2145 | 0 | 0 | 0 | 0 | off_peak | 571.84 |  |  | 0 | 0 | 100 | 0 | 0
8086 | 624.4 | 0 | 23.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1227 | 624.4 | 0 | 0.05921 | 6.4375 | 0 | 0 | 0 | 0 | off_peak | 624.4 |  |  | 0 | 0 | 100 | 0 | 0
8087 | 595.57 | 0 | 23 | 0 | 0 | 0 | 0 | 0.051567 | 0.051567 | 0 | 0 | 0 | 74.1709 | 595.6216 | 0 | 0.05921 | 6.6548 | 0 | 0 | 0 | 0 | off_peak | 595.57 | 0 | 100 | 0 | 0 | 100 | 0 | 0
8088 | 582.06 | 0 | 23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1709 | 582.06 | 0 | 0.05921 | 6.7331 | 0 | 0 | 0 | 0 | off_peak | 582.06 |  |  | 0 | 0 | 100 | 0 | 0
8089 | 625.55 | 0 | 23 | 0 | 0 | 0 | 0 | 0.0033305 | 0.0033305 | 0 | 0 | 0 | 74.174 | 625.5533 | 0 | 0.05921 | 6.6764 | 0 | 0 | 0 | 0 | off_peak | 625.55 | 0 | 100 | 0 | 0 | 100 | 0 | 0
8090 | 577.74 | 0 | 22.9 | 0 | 0 | 0 | 0 | 0.0002151 | 0.0002151 | 0 | 0 | 0 | 74.1742 | 577.7402 | 0 | 0.05921 | 6.3324 | 0 | 0 | 0 | 0 | off_peak | 577.74 | 0 | 100 | 0 | 0 | 100 | 0 | 0
8091 | 578.8 | 0 | 22.9 | 0 | 0 | 0 | 0 | 1.4852e-05 | 1.4852e-05 | 0 | 0 | 0 | 74.1743 | 578.8 | 0 | 0.05921 | 5.9753 | 0 | 0 | 0 | 0 | off_peak | 578.8 | 0 | 100 | 0 | 0 | 100 | 0 | 0
8092 | 577 | 0 | 22.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1743 | 577 | 0 | 0.05921 | 5.5297 | 0 | 0 | 0 | 0 | off_peak | 577 |  |  | 0 | 0 | 100 | 0 | 0
8093 | 611.26 | 0 | 22.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1743 | 611.26 | 0 | 0.05921 | 4.9385 | 0 | 0 | 0 | 0 | off_peak | 611.26 |  |  | 0 | 0 | 100 | 0 | 0
8094 | 640.39 | 0 | 22.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1743 | 640.39 | 0 | 0.05921 | 4.2473 | 0 | 0 | 0 | 0 | off_peak | 640.39 |  |  | 0 | 0 | 100 | 0 | 0
8095 | 745.25 | 0 | 23 | 0 | 0 | 0 | 0 | 0 | 0 | 62.4453 | 62.4453 | 0 | 7.4174 | 682.8047 | 0 | 0.088511 | 3.7546 | 0 | 0 | 0 | 0 | on_peak | 682.8047 |  |  | 0 | 8.38 | 91.62 | 0 | 0
8096 | 733.07 | 76.1285 | 23.5 | 12.3994 | 12.3994 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 720.6706 | 0 | 0.088511 | 3.3544 | 0 | 0 | 0 | 12.3994 | on_peak | 720.6706 |  |  | 1.69 | 0 | 98.31 | 41.5922 | 0
8097 | 760.24 | 258.204 | 24.1 | 41.9646 | 41.9646 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 718.2754 | 0 | 0.088511 | 3.1216 | 0 | 0 | 0 | 41.9646 | on_peak | 718.2754 |  |  | 5.52 | 0 | 94.48 | 130.996 | 0
8098 | 794.56 | 383.601 | 24.6 | 62.2328 | 62.2328 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 732.3272 | 0 | 0.088511 | 3.0152 | 0 | 0 | 0 | 62.2328 | on_peak | 732.3272 |  |  | 7.83 | 0 | 92.17 | 187.6432 | 0
8099 | 760.75 | 373.111 | 24.9 | 60.4657 | 60.4657 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 18.9814 | 712.6466 | 0 | 0.05921 | 3.043 | 0 | 0 | 0 | 60.4657 | off_peak | 700.2843 | 0 | 100 | 7.95 | 0 | 92.05 | 183.9991 | 0
8100 | 853.18 | 326.262 | 25.1 | 52.8354 | 52.8354 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 30.5453 | 812.707 | 0 | 0.05921 | 3.3017 | 0 | 0 | 0 | 52.8354 | off_peak | 800.3446 | 0 | 100 | 6.19 | 0 | 93.81 | 174.4447 | 0
8101 | 786.12 | 499.173 | 25.2 | 80.8078 | 80.8078 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 42.1093 | 717.6746 | 0 | 0.05921 | 3.7831 | 0 | 0 | 0 | 80.8078 | off_peak | 705.3122 | 0 | 100 | 10.28 | 0 | 89.72 | 305.7058 | 0
8102 | 844.88 | 579.453 | 25.2 | 93.8038 | 93.8038 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 53.6732 | 763.4386 | 0 | 0.05921 | 4.0681 | 0 | 0 | 0 | 93.8038 | off_peak | 751.0762 | 0 | 100 | 11.1 | 0 | 88.9 | 381.6076 | 0
8103 | 886.24 | 473.998 | 25.1 | 76.76 | 76.76 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 65.2371 | 821.8423 | 0 | 0.05921 | 4.2975 | 0 | 0 | 0 | 76.76 | off_peak | 809.48 | 0 | 100 | 8.66 | 0 | 91.34 | 329.8733 | 0
8104 | 840.19 | 312.629 | 25 | 50.6459 | 50.6459 | 0 | 0 | 8.9371 | 8.9371 | 0 | 0 | 0 | 73.597 | 798.4812 | 0 | 0.05921 | 4.5265 | 0 | 0 | 0 | 50.6459 | off_peak | 789.5441 | 0 | 100 | 6.03 | 0 | 93.97 | 229.2502 | 0
8105 | 832.37 | 132.543 | 24.6 | 21.5029 | 21.5029 | 0 | 0 | 0.57721 | 0.57721 | 0 | 0 | 0 | 74.137 | 811.4443 | 0 | 0.05921 | 4.6909 | 0 | 0 | 0 | 21.5029 | off_peak | 810.8671 | 0 | 100 | 2.58 | 0 | 97.42 | 100.8669 | 0
8106 | 840.72 | 0 | 24.2 | 0 | 0 | 0 | 0 | 0.037279 | 0.037279 | 0 | 0 | 0 | 74.1718 | 840.7573 | 0 | 0.05921 | 5.0258 | 0 | 0 | 0 | 0 | off_peak | 840.72 | 0 | 100 | 0 | 0 | 100 | 0 | 0
8107 | 819.17 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 10.8883 | 10.8883 | 0 | 62.5318 | 808.2817 | 0 | 0.088511 | 5.1722 | 0 | 0 | 0 | 0 | on_peak | 808.2817 |  |  | 0 | 1.33 | 98.67 | 0 | 0
8108 | 829.19 | 0 | 23.9 | 0 | 0 | 0 | 0 | 0 | 0 | 20.9083 | 20.9083 | 0 | 40.1799 | 808.2817 | 0 | 0.088511 | 5.3286 | 0 | 0 | 0 | 0 | on_peak | 808.2817 |  |  | 0 | 2.52 | 97.48 | 0 | 0
8109 | 834.85 | 0 | 23.9 | 0 | 0 | 0 | 0 | 0 | 0 | 26.5683 | 26.5683 | 0 | 11.7773 | 808.2817 | 0 | 0.088511 | 5.4614 | 0 | 0 | 0 | 0 | on_peak | 808.2817 |  |  | 0 | 3.18 | 96.82 | 0 | 0
8110 | 812.36 | 0 | 23.9 | 0 | 0 | 0 | 0 | 0 | 0 | 4.0783 | 4.0783 | 0 | 7.4174 | 808.2817 | 0 | 0.088511 | 5.7825 | 0 | 0 | 0 | 0 | on_peak | 808.2817 |  |  | 0 | 0.5 | 99.5 | 0 | 0
8111 | 839.35 | 0 | 23.8 | 0 | 0 | 0 | 0 | 1.4073 | 1.4073 | 0 | 0 | 0 | 8.7338 | 840.7573 | 0 | 0.05921 | 5.9209 | 0 | 0 | 0 | 0 | off_peak | 839.35 | 0 | 100 | 0 | 0 | 100 | 0 | 0
8112 | 802.8 | 0 | 23.7 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 20.2978 | 815.1624 | 0 | 0.05921 | 6.257 | 0 | 0 | 0 | 0 | off_peak | 802.8 | 0 | 100 | 0 | 0 | 100 | 0 | 0
8113 | 737.37 | 0 | 23.7 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 31.8617 | 749.7324 | 0 | 0.05921 | 6.3312 | 0 | 0 | 0 | 0 | off_peak | 737.37 | 0 | 100 | 0 | 0 | 100 | 0 | 0
8114 | 669.58 | 0 | 23.6 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 43.4256 | 681.9424 | 0 | 0.05921 | 6.0736 | 0 | 0 | 0 | 0 | off_peak | 669.58 | 0 | 100 | 0 | 0 | 100 | 0 | 0
8115 | 640.17 | 0 | 23.6 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 54.9896 | 652.5324 | 0 | 0.05921 | 5.7642 | 0 | 0 | 0 | 0 | off_peak | 640.17 | 0 | 100 | 0 | 0 | 100 | 0 | 0
8116 | 663.43 | 0 | 23.5 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 66.5535 | 675.7924 | 0 | 0.05921 | 5.2719 | 0 | 0 | 0 | 0 | off_peak | 663.43 | 0 | 100 | 0 | 0 | 100 | 0 | 0
8117 | 633.13 | 0 | 23.5 | 0 | 0 | 0 | 0 | 7.6207 | 7.6207 | 0 | 0 | 0 | 73.6821 | 640.7507 | 0 | 0.05921 | 4.7312 | 0 | 0 | 0 | 0 | off_peak | 633.13 | 0 | 100 | 0 | 0 | 100 | 0 | 0
8118 | 715.19 | 0 | 23.6 | 0 | 0 | 0 | 0 | 0.49219 | 0.49219 | 0 | 0 | 0 | 74.1425 | 715.6822 | 0 | 0.05921 | 4.1168 | 0 | 0 | 0 | 0 | off_peak | 715.19 | 0 | 100 | 0 | 0 | 100 | 0 | 0
8119 | 763.88 | 0 | 23.8 | 0 | 0 | 0 | 0 | 0 | 0 | 62.4156 | 62.4156 | 0 | 7.4174 | 701.4644 | 0 | 0.088511 | 3.5719 | 0 | 0 | 0 | 0 | on_peak | 701.4644 |  |  | 0 | 8.17 | 91.83 | 0 | 0
8120 | 744.28 | 70.1718 | 24.4 | 11.3924 | 11.3924 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 732.8876 | 0 | 0.088511 | 3.1921 | 0 | 0 | 0 | 11.3924 | on_peak | 732.8876 |  |  | 1.53 | 0 | 98.47 | 36.3654 | 0
8121 | 807.09 | 244.621 | 25.1 | 39.6143 | 39.6143 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 767.4757 | 0 | 0.088511 | 2.9653 | 0 | 0 | 0 | 39.6143 | on_peak | 767.4757 |  |  | 4.91 | 0 | 95.09 | 117.4675 | 0
8122 | 809.97 | 412.485 | 25.6 | 66.6782 | 66.6782 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 743.2918 | 0 | 0.088511 | 2.861 | 0 | 0 | 0 | 66.6782 | on_peak | 743.2918 |  |  | 8.23 | 0 | 91.77 | 190.7631 | 0
8123 | 771.03 | 541.627 | 26 | 87.4277 | 87.4277 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 18.9814 | 695.9647 | 0 | 0.05921 | 2.9141 | 0 | 0 | 0 | 87.4277 | off_peak | 683.6023 | 0 | 100 | 11.34 | 0 | 88.66 | 254.7693 | 0
8124 | 865.51 | 614.396 | 26.3 | 99.0663 | 99.0663 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 30.5453 | 778.806 | 0 | 0.05921 | 3.1791 | 0 | 0 | 0 | 99.0663 | off_peak | 766.4437 | 0 | 100 | 11.45 | 0 | 88.55 | 314.9398 | 0
8125 | 808.54 | 626.599 | 26.4 | 100.9974 | 100.9974 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 42.1093 | 719.9049 | 0 | 0.05921 | 3.6155 | 0 | 0 | 0 | 100.9974 | off_peak | 707.5426 | 0 | 100 | 12.49 | 0 | 87.51 | 365.1544 | 0
8126 | 851.66 | 572.725 | 26.5 | 92.2804 | 92.2804 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 53.6732 | 771.7419 | 0 | 0.05921 | 3.9514 | 0 | 0 | 0 | 92.2804 | off_peak | 759.3796 | 0 | 100 | 10.84 | 0 | 89.16 | 364.6411 | 0
8127 | 858.36 | 463.253 | 26.4 | 74.6687 | 74.6687 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 65.2371 | 796.0536 | 0 | 0.05921 | 3.7378 | 0 | 0 | 0 | 74.6687 | off_peak | 783.6913 | 0 | 100 | 8.7 | 0 | 91.3 | 279.0945 | 0
8128 | 787 | 307.622 | 26.1 | 49.6374 | 49.6374 | 0 | 0 | 8.9371 | 8.9371 | 0 | 0 | 0 | 73.597 | 746.2997 | 0 | 0.05921 | 3.6837 | 0 | 0 | 0 | 49.6374 | off_peak | 737.3626 | 0 | 100 | 6.31 | 0 | 93.69 | 182.8491 | 0
8129 | 797.53 | 89.3448 | 25.6 | 14.4426 | 14.4426 | 0 | 0 | 0.57721 | 0.57721 | 0 | 0 | 0 | 74.137 | 783.6646 | 0 | 0.05921 | 3.7021 | 0 | 0 | 0 | 14.4426 | off_peak | 783.0874 | 0 | 100 | 1.81 | 0 | 98.19 | 53.4683 | 0
8130 | 819.57 | 0 | 25.1 | 0 | 0 | 0 | 0 | 0.037279 | 0.037279 | 0 | 0 | 0 | 74.1718 | 819.6073 | 0 | 0.05921 | 3.8138 | 0 | 0 | 0 | 0 | off_peak | 819.57 | 0 | 100 | 0 | 0 | 100 | 0 | 0
8131 | 790.5 | 0 | 24.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1718 | 790.5 | 0 | 0.088511 | 4.0061 | 0 | 0 | 0 | 0 | on_peak | 790.5 |  |  | 0 | 0 | 100 | 0 | 0
8132 | 789.19 | 0 | 24.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1718 | 789.19 | 0 | 0.088511 | 4.384 | 0 | 0 | 0 | 0 | on_peak | 789.19 |  |  | 0 | 0 | 100 | 0 | 0
8133 | 778.96 | 0 | 24.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1718 | 778.96 | 0 | 0.088511 | 4.5915 | 0 | 0 | 0 | 0 | on_peak | 778.96 |  |  | 0 | 0 | 100 | 0 | 0
8134 | 755.61 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 62.443 | 62.443 | 0 | 7.4174 | 693.167 | 0 | 0.088511 | 4.7817 | 0 | 0 | 0 | 0 | on_peak | 693.167 |  |  | 0 | 8.26 | 91.74 | 0 | 0
8135 | 729.13 | 0 | 23.8 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 18.9814 | 741.4924 | 0 | 0.05921 | 5.0874 | 0 | 0 | 0 | 0 | off_peak | 729.13 | 0 | 100 | 0 | 0 | 100 | 0 | 0
8136 | 748.58 | 0 | 23.6 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 30.5453 | 760.9424 | 0 | 0.05921 | 5.4275 | 0 | 0 | 0 | 0 | off_peak | 748.58 | 0 | 100 | 0 | 0 | 100 | 0 | 0
8137 | 686.47 | 0 | 23.4 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 42.1093 | 698.8324 | 0 | 0.05921 | 5.5671 | 0 | 0 | 0 | 0 | off_peak | 686.47 | 0 | 100 | 0 | 0 | 100 | 0 | 0
8138 | 589.72 | 0 | 23.2 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 53.6732 | 602.0824 | 0 | 0.05921 | 5.3304 | 0 | 0 | 0 | 0 | off_peak | 589.72 | 0 | 100 | 0 | 0 | 100 | 0 | 0
8139 | 618.54 | 0 | 23.1 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 65.2371 | 630.9024 | 0 | 0.05921 | 5.0395 | 0 | 0 | 0 | 0 | off_peak | 618.54 | 0 | 100 | 0 | 0 | 100 | 0 | 0
8140 | 610.86 | 0 | 23.1 | 0 | 0 | 0 | 0 | 8.9371 | 8.9371 | 0 | 0 | 0 | 73.597 | 619.7971 | 0 | 0.05921 | 4.6479 | 0 | 0 | 0 | 0 | off_peak | 610.86 | 0 | 100 | 0 | 0 | 100 | 0 | 0
8141 | 584.25 | 0 | 23.1 | 0 | 0 | 0 | 0 | 0.57721 | 0.57721 | 0 | 0 | 0 | 74.137 | 584.8272 | 0 | 0.05921 | 4.1703 | 0 | 0 | 0 | 0 | off_peak | 584.25 | 0 | 100 | 0 | 0 | 100 | 0 | 0
8142 | 661.78 | 0 | 23.2 | 0 | 0 | 0 | 0 | 0.037279 | 0.037279 | 0 | 0 | 0 | 74.1718 | 661.8173 | 0 | 0.05921 | 3.5286 | 0 | 0 | 0 | 0 | off_peak | 661.78 | 0 | 100 | 0 | 0 | 100 | 0 | 0
8143 | 718.55 | 0 | 23.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1718 | 718.55 | 0 | 0.088511 | 3.1439 | 0 | 0 | 0 | 0 | on_peak | 718.55 |  |  | 0 | 0 | 100 | 0 | 0
8144 | 745.93 | 69.3714 | 23.6 | 11.2948 | 11.2948 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1718 | 734.6352 | 0 | 0.088511 | 2.836 | 0 | 0 | 0 | 11.2948 | on_peak | 734.6352 |  |  | 1.51 | 0 | 98.49 | 32.0325 | 0
8145 | 766.29 | 245.822 | 24.2 | 39.9379 | 39.9379 | 0 | 0 | 0 | 0 | 62.443 | 62.443 | 0 | 7.4174 | 663.9091 | 0 | 0.088511 | 2.6695 | 0 | 0 | 0 | 39.9379 | on_peak | 663.9091 |  |  | 5.21 | 8.15 | 86.64 | 106.6135 | 0
8146 | 769.37 | 417.416 | 24.7 | 67.6944 | 67.6944 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 701.6756 | 0 | 0.088511 | 2.6122 | 0 | 0 | 0 | 67.6944 | on_peak | 701.6756 |  |  | 8.8 | 0 | 91.2 | 176.8325 | 0
8147 | 759.79 | 547.265 | 25.2 | 88.5931 | 88.5931 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 18.9814 | 683.5593 | 0 | 0.05921 | 2.7029 | 0 | 0 | 0 | 88.5931 | off_peak | 671.1969 | 0 | 100 | 11.66 | 0 | 88.34 | 239.4605 | 0
8148 | 772.22 | 623.668 | 25.6 | 100.816 | 100.816 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 30.5453 | 683.7664 | 0 | 0.05921 | 2.9642 | 0 | 0 | 0 | 100.816 | off_peak | 671.404 | 0 | 100 | 13.06 | 0 | 86.94 | 298.8432 | 0
8149 | 665.97 | 636.049 | 25.7 | 102.7803 | 102.7803 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 42.1093 | 575.5521 | 0 | 0.05921 | 3.582 | 0 | 0 | 0 | 102.7803 | off_peak | 563.1897 | 0 | 100 | 15.43 | 0 | 84.57 | 368.1636 | 0
8150 | 716.81 | 584.865 | 25.7 | 94.5094 | 94.5094 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 53.6732 | 634.663 | 0 | 0.05921 | 3.8953 | 0 | 0 | 0 | 94.5094 | off_peak | 622.3006 | 0 | 100 | 13.18 | 0 | 86.82 | 368.1433 | 0
8151 | 754.11 | 475.382 | 25.3 | 76.9287 | 76.9287 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 65.2371 | 689.5437 | 0 | 0.05921 | 3.6604 | 0 | 0 | 0 | 76.9287 | off_peak | 677.1813 | 0 | 100 | 10.2 | 0 | 89.8 | 281.592 | 0
8152 | 673.99 | 317.105 | 24.5 | 51.4635 | 51.4635 | 0 | 0 | 8.9371 | 8.9371 | 0 | 0 | 0 | 73.597 | 631.4636 | 0 | 0.05921 | 3.1345 | 0 | 0 | 0 | 51.4635 | off_peak | 622.5265 | 0 | 100 | 7.64 | 0 | 92.36 | 161.3108 | 0
8153 | 684.72 | 137.004 | 23.4 | 22.3225 | 22.3225 | 0 | 0 | 0.57721 | 0.57721 | 0 | 0 | 0 | 74.137 | 662.9747 | 0 | 0.05921 | 2.7734 | 0 | 0 | 0 | 22.3225 | off_peak | 662.3975 | 0 | 100 | 3.26 | 0 | 96.74 | 61.9098 | 0
8154 | 691.99 | 4.75 | 22.4 | 0.7767 | 0.7767 | 0 | 0 | 0.037279 | 0.037279 | 0 | 0 | 0 | 74.1718 | 691.2506 | 0 | 0.05921 | 2.7255 | 0 | 0 | 0 | 0.7767 | off_peak | 691.2133 | 0 | 100 | 0.11 | 0 | 99.89 | 2.1169 | 0
8155 | 668.69 | 0 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 62.443 | 62.443 | 0 | 7.4174 | 606.247 | 0 | 0.088511 | 2.6962 | 0 | 0 | 0 | 0 | on_peak | 606.247 |  |  | 0 | 9.34 | 90.66 | 0 | 0
8156 | 672.16 | 0 | 21.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 672.16 | 0 | 0.088511 | 2.7115 | 0 | 0 | 0 | 0 | on_peak | 672.16 |  |  | 0 | 0 | 100 | 0 | 0
8157 | 660.78 | 0 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 660.78 | 0 | 0.088511 | 2.7954 | 0 | 0 | 0 | 0 | on_peak | 660.78 |  |  | 0 | 0 | 100 | 0 | 0
8158 | 614.26 | 0 | 20.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 614.26 | 0 | 0.088511 | 3.18 | 0 | 0 | 0 | 0 | on_peak | 614.26 |  |  | 0 | 0 | 100 | 0 | 0
8159 | 691.96 | 0 | 20.3 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 18.9814 | 704.3224 | 0 | 0.05921 | 3.9087 | 0 | 0 | 0 | 0 | off_peak | 691.96 | 0 | 100 | 0 | 0 | 100 | 0 | 0
8160 | 642.56 | 0 | 19.8 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 30.5453 | 654.9224 | 0 | 0.05921 | 4.6672 | 0 | 0 | 0 | 0 | off_peak | 642.56 | 0 | 100 | 0 | 0 | 100 | 0 | 0
8161 | 602.04 | 0 | 19.5 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 42.1093 | 614.4024 | 0 | 0.05921 | 4.9449 | 0 | 0 | 0 | 0 | off_peak | 602.04 | 0 | 100 | 0 | 0 | 100 | 0 | 0
8162 | 567.09 | 0 | 19.3 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 53.6732 | 579.4524 | 0 | 0.05921 | 4.8515 | 0 | 0 | 0 | 0 | off_peak | 567.09 | 0 | 100 | 0 | 0 | 100 | 0 | 0
8163 | 541.87 | 0 | 19.3 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 65.2371 | 554.2324 | 0 | 0.05921 | 4.6732 | 0 | 0 | 0 | 0 | off_peak | 541.87 | 0 | 100 | 0 | 0 | 100 | 0 | 0
8164 | 520.71 | 0 | 19.3 | 0 | 0 | 0 | 0 | 8.9371 | 8.9371 | 0 | 0 | 0 | 73.597 | 529.6471 | 0 | 0.05921 | 4.4204 | 0 | 0 | 0 | 0 | off_peak | 520.71 | 0 | 100 | 0 | 0 | 100 | 0 | 0
8165 | 551.92 | 0 | 19.3 | 0 | 0 | 0 | 0 | 0.57721 | 0.57721 | 0 | 0 | 0 | 74.137 | 552.4972 | 0 | 0.05921 | 3.9619 | 0 | 0 | 0 | 0 | off_peak | 551.92 | 0 | 100 | 0 | 0 | 100 | 0 | 0
8166 | 626 | 0 | 19.5 | 0 | 0 | 0 | 0 | 0.037279 | 0.037279 | 0 | 0 | 0 | 74.1718 | 626.0373 | 0 | 0.05921 | 3.4721 | 0 | 0 | 0 | 0 | off_peak | 626 | 0 | 100 | 0 | 0 | 100 | 0 | 0
8167 | 652.71 | 0 | 19.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1718 | 652.71 | 0 | 0.088511 | 3.1838 | 0 | 0 | 0 | 0 | on_peak | 652.71 |  |  | 0 | 0 | 100 | 0 | 0
8168 | 676.35 | 69.6868 | 20.4 | 11.4762 | 11.4762 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1718 | 664.8738 | 0 | 0.088511 | 3.0116 | 0 | 0 | 0 | 11.4762 | on_peak | 664.8738 |  |  | 1.7 | 0 | 98.3 | 34.5614 | 0
8169 | 682.54 | 247.883 | 21.3 | 40.6919 | 40.6919 | 0 | 0 | 0 | 0 | 62.443 | 62.443 | 0 | 7.4174 | 579.405 | 0 | 0.088511 | 2.9352 | 0 | 0 | 0 | 40.6919 | on_peak | 579.405 |  |  | 5.96 | 9.15 | 84.89 | 119.4371 | 0
8170 | 729.5 | 416.896 | 22.2 | 68.2179 | 68.2179 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 661.2821 | 0 | 0.088511 | 2.9007 | 0 | 0 | 0 | 68.2179 | on_peak | 661.2821 |  |  | 9.35 | 0 | 90.65 | 197.8779 | 0
8171 | 690.85 | 546.684 | 23.2 | 89.1367 | 89.1367 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 18.9814 | 614.0757 | 0 | 0.05921 | 3.0032 | 0 | 0 | 0 | 89.1367 | off_peak | 601.7133 | 0 | 100 | 12.9 | 0 | 87.1 | 267.6922 | 0
8172 | 693.91 | 623.813 | 23.9 | 101.4579 | 101.4579 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 30.5453 | 604.8145 | 0 | 0.05921 | 3.4732 | 0 | 0 | 0 | 101.4579 | off_peak | 592.4521 | 0 | 100 | 14.62 | 0 | 85.38 | 352.3786 | 0
8173 | 737.69 | 613.73 | 24.2 | 99.7106 | 99.7106 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 42.1093 | 650.3418 | 0 | 0.05921 | 4.0433 | 0 | 0 | 0 | 99.7106 | off_peak | 637.9794 | 0 | 100 | 13.52 | 0 | 86.48 | 403.1604 | 0
8174 | 782.25 | 429.421 | 24.3 | 69.7415 | 69.7415 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 53.6732 | 724.8709 | 0 | 0.05921 | 4.5096 | 0 | 0 | 0 | 69.7415 | off_peak | 712.5085 | 0 | 100 | 8.92 | 0 | 91.08 | 314.5086 | 0
8175 | 821.08 | 263.733 | 24.3 | 42.8324 | 42.8324 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 65.2371 | 790.61 | 0 | 0.05921 | 4.1203 | 0 | 0 | 0 | 42.8324 | off_peak | 778.2476 | 0 | 100 | 5.22 | 0 | 94.78 | 176.4836 | 0
8176 | 772.34 | 230.72 | 24 | 37.5112 | 37.5112 | 0 | 0 | 8.9371 | 8.9371 | 0 | 0 | 0 | 73.597 | 743.7659 | 0 | 0.05921 | 3.4554 | 0 | 0 | 0 | 37.5112 | off_peak | 734.8288 | 0 | 100 | 4.86 | 0 | 95.14 | 129.6168 | 0
8177 | 824.83 | 83.3097 | 23.7 | 13.5593 | 12.9821 | 0 | 0.57721 | 0.57721 | 0 | 0 | 0 | 0 | 74.137 | 811.8479 | 0 | 0.05921 | 3.1698 | 0 | 0 | 0.53993 | 12.9821 | off_peak | 811.8479 | 100 | 0 | 1.57 | 0 | 98.43 | 41.1511 | 0
8178 | 773.06 | 4.75 | 23.4 | 0.77393 | 0.73665 | 0 | 0.037279 | 0.037279 | 0 | 0 | 0 | 0 | 74.1718 | 772.3233 | 0 | 0.05921 | 2.9476 | 0 | 0 | 0.5748 | 0.73665 | off_peak | 772.3233 | 100 | 0 | 0.1 | 0 | 99.9 | 2.1713 | 0
8179 | 783.67 | 0 | 23.2 | 0 | 0 | 0 | 0 | 0 | 0 | 62.443 | 62.443 | 0 | 7.4174 | 721.227 | 0 | 0.088511 | 2.8729 | 0 | 0 | 0.5748 | 0 | on_peak | 721.227 |  |  | 0 | 7.97 | 92.03 | 0 | 0
8180 | 787.3 | 0 | 23.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 787.3 | 0 | 0.088511 | 3.0015 | 0 | 0 | 0.5748 | 0 | on_peak | 787.3 |  |  | 0 | 0 | 100 | 0 | 0
8181 | 748.88 | 0 | 23.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 748.88 | 0 | 0.088511 | 3.109 | 0 | 0 | 0.5748 | 0 | on_peak | 748.88 |  |  | 0 | 0 | 100 | 0 | 0
8182 | 777.29 | 0 | 23.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 777.29 | 0 | 0.088511 | 3.4043 | 0 | 0 | 0.5748 | 0 | on_peak | 777.29 |  |  | 0 | 0 | 100 | 0 | 0
8183 | 729.95 | 0 | 23.1 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 18.9814 | 742.3124 | 0 | 0.05921 | 4.0264 | 0 | 0 | 0.5748 | 0 | off_peak | 729.95 | 0 | 100 | 0 | 0 | 100 | 0 | 0
8184 | 731.98 | 0 | 23 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 30.5453 | 744.3424 | 0 | 0.05921 | 4.6051 | 0 | 0 | 0.5748 | 0 | off_peak | 731.98 | 0 | 100 | 0 | 0 | 100 | 0 | 0
8185 | 724.89 | 0 | 22.9 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 42.1093 | 737.2524 | 0 | 0.05921 | 4.9029 | 0 | 0 | 0.5748 | 0 | off_peak | 724.89 | 0 | 100 | 0 | 0 | 100 | 0 | 0
8186 | 643.13 | 0 | 22.8 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 53.6732 | 655.4924 | 0 | 0.05921 | 4.7717 | 0 | 0 | 0.5748 | 0 | off_peak | 643.13 | 0 | 100 | 0 | 0 | 100 | 0 | 0
8187 | 622.93 | 0 | 22.7 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 65.2371 | 635.2924 | 0 | 0.05921 | 4.6346 | 0 | 0 | 0.5748 | 0 | off_peak | 622.93 | 0 | 100 | 0 | 0 | 100 | 0 | 0
8188 | 617.95 | 0 | 22.6 | 0 | 0 | 0 | 0 | 8.9371 | 8.9371 | 0 | 0 | 0 | 73.597 | 626.8871 | 0 | 0.05921 | 4.3747 | 0 | 0 | 0.5748 | 0 | off_peak | 617.95 | 0 | 100 | 0 | 0 | 100 | 0 | 0
8189 | 622.01 | 0 | 22.6 | 0 | 0 | 0 | 0 | 0.57721 | 0.57721 | 0 | 0 | 0 | 74.137 | 622.5872 | 0 | 0.05921 | 3.9337 | 0 | 0 | 0.5748 | 0 | off_peak | 622.01 | 0 | 100 | 0 | 0 | 100 | 0 | 0
8190 | 694.21 | 0 | 22.7 | 0 | 0 | 0 | 0 | 0.037279 | 0.037279 | 0 | 0 | 0 | 74.1718 | 694.2473 | 0 | 0.05921 | 3.4979 | 0 | 0 | 0.5748 | 0 | off_peak | 694.21 | 0 | 100 | 0 | 0 | 100 | 0 | 0
8191 | 694.19 | 0 | 22.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1718 | 694.19 | 0 | 0.088511 | 3.0064 | 0 | 0 | 0.5748 | 0 | on_peak | 694.19 |  |  | 0 | 0 | 100 | 0 | 0
8192 | 748.05 | 68.184 | 23.3 | 11.1134 | 11.1134 | 0 | 0 | 0 | 0 | 62.443 | 62.443 | 0 | 7.4174 | 674.4936 | 0 | 0.088511 | 2.731 | 0.53768 | 0 | 0 | 11.6511 | on_peak | 674.4936 |  |  | 1.49 | 8.35 | 90.17 | 31.8195 | 0
8193 | 794.99 | 246.791 | 23.9 | 40.1385 | 40.1385 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 754.8515 | 0 | 0.088511 | 2.6215 | 0 | 0 | 0 | 40.1385 | on_peak | 754.8515 |  |  | 5.05 | 0 | 94.95 | 105.224 | 0
8194 | 838.43 | 420.353 | 24.3 | 68.2688 | 68.2688 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 770.1612 | 0 | 0.088511 | 2.5838 | 0 | 0 | 0 | 68.2688 | on_peak | 770.1612 |  |  | 8.14 | 0 | 91.86 | 176.3943 | 0
8195 | 782.87 | 553.783 | 24.6 | 89.842 | 89.842 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 18.9814 | 705.3903 | 0 | 0.05921 | 2.6994 | 0 | 0 | 0 | 89.842 | off_peak | 693.028 | 0 | 100 | 11.48 | 0 | 88.52 | 242.5178 | 0
8196 | 866.54 | 618.604 | 24.7 | 100.3221 | 100.3221 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 30.5453 | 778.5803 | 0 | 0.05921 | 3.0307 | 0 | 0 | 0 | 100.3221 | off_peak | 766.2179 | 0 | 100 | 11.58 | 0 | 88.42 | 304.0455 | 0
8197 | 815.34 | 642.261 | 24.7 | 104.1587 | 104.1587 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 42.1093 | 723.5437 | 0 | 0.05921 | 3.5494 | 0 | 0 | 0 | 104.1587 | off_peak | 711.1813 | 0 | 100 | 12.77 | 0 | 87.23 | 369.6987 | 0
8198 | 884.51 | 589.728 | 24.5 | 95.7079 | 95.7079 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 53.6732 | 801.1645 | 0 | 0.05921 | 3.873 | 0 | 0 | 0 | 95.7079 | off_peak | 788.8021 | 0 | 100 | 10.82 | 0 | 89.18 | 370.6746 | 0
8199 | 852.38 | 480.104 | 24.3 | 77.9728 | 77.9728 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 65.2371 | 786.7695 | 0 | 0.05921 | 3.8985 | 0 | 0 | 0 | 77.9728 | off_peak | 774.4072 | 0 | 100 | 9.15 | 0 | 90.85 | 303.9734 | 0
8200 | 789.49 | 322.538 | 24.1 | 52.4204 | 52.4204 | 0 | 0 | 8.9371 | 8.9371 | 0 | 0 | 0 | 73.597 | 746.0067 | 0 | 0.05921 | 3.8229 | 0 | 0 | 0 | 52.4204 | off_peak | 737.0696 | 0 | 100 | 6.64 | 0 | 93.36 | 200.396 | 0
8201 | 846.17 | 140.603 | 23.8 | 22.8761 | 22.8761 | 0 | 0 | 0.57721 | 0.57721 | 0 | 0 | 0 | 74.137 | 823.8711 | 0 | 0.05921 | 3.7839 | 0 | 0 | 0 | 22.8761 | off_peak | 823.2939 | 0 | 100 | 2.7 | 0 | 97.3 | 86.5602 | 0
8202 | 804.88 | 5.7 | 23.7 | 0.92772 | 0.92772 | 0 | 0 | 0.037279 | 0.037279 | 0 | 0 | 0 | 74.1718 | 803.9896 | 0 | 0.05921 | 3.7263 | 0 | 0 | 0 | 0.92772 | off_peak | 803.9523 | 0 | 100 | 0.12 | 0 | 99.88 | 3.457 | 0
8203 | 761.44 | 0 | 23.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1718 | 761.44 | 0 | 0.088511 | 3.8132 | 0 | 0 | 0 | 0 | on_peak | 761.44 |  |  | 0 | 0 | 100 | 0 | 0
8204 | 821.93 | 0 | 23.7 | 0 | 0 | 0 | 0 | 0 | 0 | 13.6483 | 13.6483 | 0 | 59.5812 | 808.2817 | 0 | 0.088511 | 4.0131 | 0 | 0 | 0 | 0 | on_peak | 808.2817 |  |  | 0 | 1.66 | 98.34 | 0 | 0
8205 | 777.48 | 0 | 23.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 59.5812 | 777.48 | 0 | 0.088511 | 4.3228 | 0 | 0 | 0 | 0 | on_peak | 777.48 |  |  | 0 | 0 | 100 | 0 | 0
8206 | 763.05 | 0 | 23.7 | 0 | 0 | 0 | 0 | 0 | 0 | 48.7948 | 48.7948 | 0 | 7.4174 | 714.2552 | 0 | 0.088511 | 4.5133 | 0 | 0 | 0 | 0 | on_peak | 714.2552 |  |  | 0 | 6.39 | 93.61 | 0 | 0
8207 | 761.35 | 0 | 23.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 761.35 | 0 | 0.05921 | 4.651 | 0 | 0 | 0 | 0 | off_peak | 761.35 |  |  | 0 | 0 | 100 | 0 | 0
8208 | 766.17 | 0 | 23.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 766.17 | 0 | 0.05921 | 4.9344 | 0 | 0 | 0 | 0 | off_peak | 766.17 |  |  | 0 | 0 | 100 | 0 | 0
8209 | 665.56 | 0 | 23.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 665.56 | 0 | 0.05921 | 5.0206 | 0 | 0 | 0 | 0 | off_peak | 665.56 |  |  | 0 | 0 | 100 | 0 | 0
8210 | 679.44 | 0 | 23.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 679.44 | 0 | 0.05921 | 4.7976 | 0 | 0 | 0 | 0 | off_peak | 679.44 |  |  | 0 | 0 | 100 | 0 | 0
8211 | 625.94 | 0 | 23.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 625.94 | 0 | 0.05921 | 4.6145 | 0 | 0 | 0 | 0 | off_peak | 625.94 |  |  | 0 | 0 | 100 | 0 | 0
8212 | 613.42 | 0 | 23.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 613.42 | 0 | 0.05921 | 4.3652 | 0 | 0 | 0 | 0 | off_peak | 613.42 |  |  | 0 | 0 | 100 | 0 | 0
8213 | 653.64 | 0 | 23.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 653.64 | 0 | 0.05921 | 4.0716 | 0 | 0 | 0 | 0 | off_peak | 653.64 |  |  | 0 | 0 | 100 | 0 | 0
8214 | 715.04 | 0 | 23.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 715.04 | 0 | 0.05921 | 3.7138 | 0 | 0 | 0 | 0 | off_peak | 715.04 |  |  | 0 | 0 | 100 | 0 | 0
8215 | 732.79 | 0 | 23.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 732.79 | 0 | 0.05921 | 3.263 | 0 | 0 | 0 | 0 | off_peak | 732.79 |  |  | 0 | 0 | 100 | 0 | 0
8216 | 768.77 | 67.1255 | 23.9 | 10.9174 | 10.9174 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 757.8526 | 0 | 0.05921 | 2.9545 | 0 | 0 | 0 | 10.9174 | off_peak | 757.8526 |  |  | 1.42 | 0 | 98.58 | 32.2556 | 0
8217 | 764.61 | 152.346 | 24.3 | 24.7422 | 24.7422 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 739.8678 | 0 | 0.05921 | 2.7763 | 0 | 0 | 0 | 24.7422 | off_peak | 739.8678 |  |  | 3.24 | 0 | 96.76 | 68.692 | 0
8218 | 789.88 | 394.332 | 24.6 | 63.9738 | 63.9738 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 725.9062 | 0 | 0.05921 | 2.6744 | 0 | 0 | 0 | 63.9738 | off_peak | 725.9062 |  |  | 8.1 | 0 | 91.9 | 171.0911 | 0
8219 | 749.75 | 309.425 | 24.8 | 50.1629 | 50.1629 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 699.5871 | 0 | 0.05921 | 2.6368 | 0 | 0 | 0 | 50.1629 | off_peak | 699.5871 |  |  | 6.69 | 0 | 93.31 | 132.272 | 0
8220 | 771.58 | 386.965 | 25 | 62.6883 | 62.6883 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 708.8917 | 0 | 0.05921 | 2.6975 | 0 | 0 | 0 | 62.6883 | off_peak | 708.8917 |  |  | 8.12 | 0 | 91.88 | 169.1012 | 0
8221 | 706.61 | 381.493 | 24.9 | 61.8241 | 61.8241 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 644.7859 | 0 | 0.05921 | 2.922 | 0 | 0 | 0 | 61.8241 | off_peak | 644.7859 |  |  | 8.75 | 0 | 91.25 | 180.6485 | 0
8222 | 692.61 | 416.805 | 24.8 | 67.571 | 67.571 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 625.039 | 0 | 0.05921 | 3.2206 | 0 | 0 | 0 | 67.571 | off_peak | 625.039 |  |  | 9.76 | 0 | 90.24 | 217.6159 | 0
8223 | 676.89 | 317.404 | 24.7 | 51.475 | 51.475 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 625.415 | 0 | 0.05921 | 3.4392 | 0 | 0 | 0 | 51.475 | off_peak | 625.415 |  |  | 7.6 | 0 | 92.4 | 177.0348 | 0
8224 | 677.46 | 127.223 | 24.7 | 20.6324 | 20.6324 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 656.8276 | 0 | 0.05921 | 3.5968 | 0 | 0 | 0 | 20.6324 | off_peak | 656.8276 |  |  | 3.05 | 0 | 96.95 | 74.2108 | 0
8225 | 684.29 | 85.0687 | 24.5 | 13.8059 | 13.8059 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 670.4841 | 0 | 0.05921 | 3.8324 | 0 | 0 | 0 | 13.8059 | off_peak | 670.4841 |  |  | 2.02 | 0 | 97.98 | 52.9094 | 0
8226 | 614.78 | 2.85 | 24.4 | 0.4627 | 0.4627 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 18.9814 | 626.6797 | 0 | 0.05921 | 4.1246 | 0 | 0 | 0 | 0.4627 | off_peak | 614.3173 | 0 | 100 | 0.08 | 0 | 99.92 | 1.9084 | 0
8227 | 579.83 | 0 | 24.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18.9814 | 579.83 | 0 | 0.05921 | 4.3167 | 0 | 0 | 0 | 0 | off_peak | 579.83 |  |  | 0 | 0 | 100 | 0 | 0
8228 | 579.17 | 0 | 24.4 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 30.5453 | 591.5324 | 0 | 0.05921 | 4.6181 | 0 | 0 | 0 | 0 | off_peak | 579.17 | 0 | 100 | 0 | 0 | 100 | 0 | 0
8229 | 563.63 | 0 | 24.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30.5453 | 563.63 | 0 | 0.05921 | 4.926 | 0 | 0 | 0 | 0 | off_peak | 563.63 |  |  | 0 | 0 | 100 | 0 | 0
8230 | 576.22 | 0 | 24.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30.5453 | 576.22 | 0 | 0.05921 | 5.3027 | 0 | 0 | 0 | 0 | off_peak | 576.22 |  |  | 0 | 0 | 100 | 0 | 0
8231 | 541.57 | 0 | 24.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30.5453 | 541.57 | 0 | 0.05921 | 5.6973 | 0 | 0 | 0 | 0 | off_peak | 541.57 |  |  | 0 | 0 | 100 | 0 | 0
8232 | 542.62 | 0 | 24.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30.5453 | 542.62 | 0 | 0.05921 | 5.8948 | 0 | 0 | 0 | 0 | off_peak | 542.62 |  |  | 0 | 0 | 100 | 0 | 0
8233 | 578.66 | 0 | 24.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30.5453 | 578.66 | 0 | 0.05921 | 5.8443 | 0 | 0 | 0 | 0 | off_peak | 578.66 |  |  | 0 | 0 | 100 | 0 | 0
8234 | 562.92 | 0 | 24.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30.5453 | 562.92 | 0 | 0.05921 | 5.535 | 0 | 0 | 0 | 0 | off_peak | 562.92 |  |  | 0 | 0 | 100 | 0 | 0
8235 | 553.76 | 0 | 24.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30.5453 | 553.76 | 0 | 0.05921 | 5.2942 | 0 | 0 | 0 | 0 | off_peak | 553.76 |  |  | 0 | 0 | 100 | 0 | 0
8236 | 565.62 | 0 | 24.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30.5453 | 565.62 | 0 | 0.05921 | 5.0582 | 0 | 0 | 0 | 0 | off_peak | 565.62 |  |  | 0 | 0 | 100 | 0 | 0
8237 | 570.41 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30.5453 | 570.41 | 0 | 0.05921 | 4.7191 | 0 | 0 | 0 | 0 | off_peak | 570.41 |  |  | 0 | 0 | 100 | 0 | 0
8238 | 638.5 | 0 | 23.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30.5453 | 638.5 | 0 | 0.05921 | 4.288 | 0 | 0 | 0 | 0 | off_peak | 638.5 |  |  | 0 | 0 | 100 | 0 | 0
8239 | 658.74 | 0 | 23.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30.5453 | 658.74 | 0 | 0.05921 | 3.8871 | 0 | 0 | 0 | 0 | off_peak | 658.74 |  |  | 0 | 0 | 100 | 0 | 0
8240 | 723.37 | 64.4164 | 23.7 | 10.4843 | 10.4843 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30.5453 | 712.8857 | 0 | 0.05921 | 3.5491 | 0 | 0 | 0 | 10.4843 | off_peak | 712.8857 |  |  | 1.45 | 0 | 98.55 | 37.2097 | 0
8241 | 691.42 | 243.637 | 23.9 | 39.6255 | 39.6255 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30.5453 | 651.7945 | 0 | 0.05921 | 3.3178 | 0 | 0 | 0 | 39.6255 | off_peak | 651.7945 |  |  | 5.73 | 0 | 94.27 | 131.4682 | 0
8242 | 723.74 | 417.277 | 24.1 | 67.8179 | 67.8179 | 0 | 0 | 8.5663 | 8.5663 | 0 | 0 | 0 | 38.5584 | 664.4884 | 0 | 0.05921 | 3.1742 | 0 | 0 | 0 | 67.8179 | off_peak | 655.9221 | 0 | 100 | 9.37 | 0 | 90.63 | 215.2678 | 0
8243 | 723.01 | 549.907 | 24.6 | 89.2132 | 89.2132 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 38.5584 | 633.7968 | 0 | 0.05921 | 3.1023 | 0 | 0 | 0 | 89.2132 | off_peak | 633.7968 |  |  | 12.34 | 0 | 87.66 | 276.7702 | 0
8244 | 717.04 | 629.575 | 25.2 | 101.9177 | 101.9177 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 50.1223 | 627.4847 | 0 | 0.05921 | 3.0767 | 0 | 0 | 0 | 101.9177 | off_peak | 615.1223 | 0 | 100 | 14.21 | 0 | 85.79 | 313.5698 | 0
8245 | 752.81 | 644.565 | 25.6 | 104.194 | 104.194 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 61.6862 | 660.9784 | 0 | 0.05921 | 3.2395 | 0 | 0 | 0 | 104.194 | off_peak | 648.616 | 0 | 100 | 13.84 | 0 | 86.16 | 337.5366 | 0
8246 | 678.86 | 592.22 | 25.8 | 95.6633 | 95.6633 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 61.6862 | 583.1967 | 0 | 0.05921 | 3.4679 | 0 | 0 | 0 | 95.6633 | off_peak | 583.1967 |  |  | 14.09 | 0 | 85.91 | 331.7547 | 0
8247 | 698.97 | 479.887 | 25.9 | 77.4898 | 77.4898 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 61.6862 | 621.4802 | 0 | 0.05921 | 3.8544 | 0 | 0 | 0 | 77.4898 | off_peak | 621.4802 |  |  | 11.09 | 0 | 88.91 | 298.6755 | 0
8248 | 697.77 | 321.877 | 25.7 | 52.0127 | 52.0127 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 73.2502 | 658.1197 | 0 | 0.05921 | 4.2162 | 0 | 0 | 0 | 52.0127 | off_peak | 645.7573 | 0 | 100 | 7.45 | 0 | 92.55 | 219.2983 | 0
8249 | 621.44 | 140.267 | 25.3 | 22.6987 | 22.6987 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 73.2502 | 598.7413 | 0 | 0.05921 | 4.6911 | 0 | 0 | 0 | 22.6987 | off_peak | 598.7413 |  |  | 3.65 | 0 | 96.35 | 106.482 | 0
8250 | 625.17 | 5.7 | 24.8 | 0.92406 | 0 | 0 | 0.92406 | 0.92406 | 0 | 0 | 0 | 0 | 74.1146 | 625.17 | 0 | 0.05921 | 5.0413 | 0 | 0 | 0.86438 | 0 | off_peak | 625.17 | 100 | 0 | 0 | 0 | 100 | 0 | 0
8251 | 590.45 | 0 | 24.5 | 0 | 0 | 0 | 0 | 0.059681 | 0.059681 | 0 | 0 | 0 | 74.1704 | 590.5097 | 0 | 0.05921 | 5.3481 | 0 | 0 | 0.86438 | 0 | off_peak | 590.45 | 0 | 100 | 0 | 0 | 100 | 0 | 0
8252 | 548.02 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1704 | 548.02 | 0 | 0.05921 | 5.6933 | 0 | 0 | 0.86438 | 0 | off_peak | 548.02 |  |  | 0 | 0 | 100 | 0 | 0
8253 | 556.28 | 0 | 23.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1704 | 556.28 | 0 | 0.05921 | 5.9958 | 0 | 0 | 0.86438 | 0 | off_peak | 556.28 |  |  | 0 | 0 | 100 | 0 | 0
8254 | 542.29 | 0 | 23.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1704 | 542.29 | 0 | 0.05921 | 6.1012 | 0 | 0 | 0.86438 | 0 | off_peak | 542.29 |  |  | 0 | 0 | 100 | 0 | 0
8255 | 561.9 | 0 | 23.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1704 | 561.9 | 0 | 0.05921 | 6.1993 | 0 | 0 | 0.86438 | 0 | off_peak | 561.9 |  |  | 0 | 0 | 100 | 0 | 0
8256 | 550.06 | 0 | 22.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1704 | 550.06 | 0 | 0.05921 | 6.3538 | 0 | 0 | 0.86438 | 0 | off_peak | 550.06 |  |  | 0 | 0 | 100 | 0 | 0
8257 | 568.2 | 0 | 22.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1704 | 568.2 | 0 | 0.05921 | 6.404 | 0 | 0 | 0.86438 | 0 | off_peak | 568.2 |  |  | 0 | 0 | 100 | 0 | 0
8258 | 518.06 | 0 | 22.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1704 | 518.06 | 0 | 0.05921 | 6.1155 | 0 | 0 | 0.86438 | 0 | off_peak | 518.06 |  |  | 0 | 0 | 100 | 0 | 0
8259 | 524.82 | 0 | 22.6 | 0 | 0 | 0 | 0 | 0.0038546 | 0.0038546 | 0 | 0 | 0 | 74.174 | 524.8239 | 0 | 0.05921 | 5.8511 | 0 | 0 | 0.86438 | 0 | off_peak | 524.82 | 0 | 100 | 0 | 0 | 100 | 0 | 0
8260 | 535.87 | 0 | 22.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.174 | 535.87 | 0 | 0.05921 | 5.4807 | 0 | 0 | 0.86438 | 0 | off_peak | 535.87 |  |  | 0 | 0 | 100 | 0 | 0
8261 | 545.51 | 0 | 22.7 | 0 | 0 | 0 | 0 | 0.00024895 | 0.00024895 | 0 | 0 | 0 | 74.1742 | 545.5102 | 0 | 0.05921 | 4.975 | 0 | 0 | 0.86438 | 0 | off_peak | 545.51 | 0 | 100 | 0 | 0 | 100 | 0 | 0
8262 | 629.6 | 0 | 22.7 | 0 | 0 | 0 | 0 | 1.7189e-05 | 1.7189e-05 | 0 | 0 | 0 | 74.1743 | 629.6 | 0 | 0.05921 | 4.2949 | 0 | 0 | 0.86438 | 0 | off_peak | 629.6 | 0 | 100 | 0 | 0 | 100 | 0 | 0
8263 | 717.62 | 0 | 22.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0.80856 | 0.80856 | 0 | 73.3099 | 716.8114 | 0 | 0.088511 | 3.8525 | 0.80856 | 0 | 0 | 0.80856 | on_peak | 716.8114 |  |  | 0 | 0.11 | 99.89 | 3.115 | 0
8264 | 745.99 | 61.789 | 23.3 | 10.0711 | 10.0711 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 73.3099 | 735.9189 | 0 | 0.088511 | 3.4777 | 0 | 0 | 0 | 10.0711 | on_peak | 735.9189 |  |  | 1.35 | 0 | 98.65 | 35.024 | 0
8265 | 792.17 | 237.019 | 24 | 38.5353 | 38.5353 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 73.3099 | 753.6347 | 0 | 0.088511 | 3.3079 | 0 | 0 | 0 | 38.5353 | on_peak | 753.6347 |  |  | 4.86 | 0 | 95.14 | 127.4693 | 0
8266 | 834.89 | 409.102 | 24.5 | 66.3938 | 66.3938 | 0 | 0 | 0 | 0 | 61.6367 | 61.6367 | 0 | 7.4174 | 706.8594 | 0 | 0.088511 | 3.2041 | 0 | 0 | 0 | 66.3938 | on_peak | 706.8594 |  |  | 7.95 | 7.38 | 84.66 | 212.7324 | 0
8267 | 773.26 | 541.605 | 25 | 87.74 | 87.74 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 18.9814 | 697.8824 | 0 | 0.05921 | 3.2335 | 0 | 0 | 0 | 87.74 | off_peak | 685.52 | 0 | 100 | 11.35 | 0 | 88.65 | 283.7117 | 0
8268 | 848.94 | 620.397 | 25.4 | 100.3596 | 100.3596 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 30.5453 | 760.9428 | 0 | 0.05921 | 3.5116 | 0 | 0 | 0 | 100.3596 | off_peak | 748.5804 | 0 | 100 | 11.82 | 0 | 88.18 | 352.4255 | 0
8269 | 764.17 | 635.129 | 25.7 | 102.6316 | 102.6316 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 42.1093 | 673.9008 | 0 | 0.05921 | 4.0317 | 0 | 0 | 0 | 102.6316 | off_peak | 661.5384 | 0 | 100 | 13.43 | 0 | 86.57 | 413.7753 | 0
8270 | 805.37 | 584.552 | 25.9 | 94.3906 | 94.3906 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 53.6732 | 723.3418 | 0 | 0.05921 | 4.3627 | 0 | 0 | 0 | 94.3906 | off_peak | 710.9794 | 0 | 100 | 11.72 | 0 | 88.28 | 411.7982 | 0
8271 | 812.61 | 476.298 | 26 | 76.8825 | 76.8825 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 65.2371 | 748.0899 | 0 | 0.05921 | 4.1654 | 0 | 0 | 0 | 76.8825 | off_peak | 735.7275 | 0 | 100 | 9.46 | 0 | 90.54 | 320.2477 | 0
8272 | 812.32 | 319.714 | 26 | 51.6072 | 51.6072 | 0 | 0 | 8.9371 | 8.9371 | 0 | 0 | 0 | 73.597 | 769.6499 | 0 | 0.05921 | 3.8378 | 0 | 0 | 0 | 51.6072 | off_peak | 760.7128 | 0 | 100 | 6.35 | 0 | 93.65 | 198.0558 | 0
8273 | 786.82 | 139.637 | 25.6 | 22.5723 | 22.5723 | 0 | 0 | 0.57721 | 0.57721 | 0 | 0 | 0 | 74.137 | 764.8249 | 0 | 0.05921 | 3.6669 | 0 | 0 | 0 | 22.5723 | off_peak | 764.2477 | 0 | 100 | 2.87 | 0 | 97.13 | 82.7704 | 0
8274 | 790.03 | 5.7 | 25 | 0.9234 | 0.88612 | 0 | 0.037279 | 0.037279 | 0 | 0 | 0 | 0 | 74.1718 | 789.1439 | 0 | 0.05921 | 3.5838 | 0 | 0 | 0.034872 | 0.88612 | off_peak | 789.1439 | 100 | 0 | 0.11 | 0 | 99.89 | 3.1757 | 0
8275 | 772.2 | 0 | 24.7 | 0 | 0 | 0 | 0 | 0 | 0 | 62.4104 | 62.4104 | 0 | 7.4523 | 709.7896 | 0 | 0.088511 | 3.4702 | 0 | 0 | 0.034872 | 0 | on_peak | 709.7896 |  |  | 0 | 8.08 | 91.92 | 0 | 0
8276 | 773.51 | 0 | 24.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4523 | 773.51 | 0 | 0.088511 | 3.4181 | 0 | 0 | 0.034872 | 0 | on_peak | 773.51 |  |  | 0 | 0 | 100 | 0 | 0
8277 | 747.82 | 0 | 24.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0.032619 | 0.032619 | 0 | 7.4174 | 747.7874 | 0 | 0.088511 | 3.5831 | 0.032619 | 0 | 0 | 0.032619 | on_peak | 747.7874 |  |  | 0 | 0 | 100 | 0.11688 | 0
8278 | 728.23 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 728.23 | 0 | 0.088511 | 3.9084 | 0 | 0 | 0 | 0 | on_peak | 728.23 |  |  | 0 | 0 | 100 | 0 | 0
8279 | 720.86 | 0 | 23.9 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 18.9814 | 733.2224 | 0 | 0.05921 | 4.4478 | 0 | 0 | 0 | 0 | off_peak | 720.86 | 0 | 100 | 0 | 0 | 100 | 0 | 0
8280 | 723.14 | 0 | 23.9 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 30.5453 | 735.5024 | 0 | 0.05921 | 5.1664 | 0 | 0 | 0 | 0 | off_peak | 723.14 | 0 | 100 | 0 | 0 | 100 | 0 | 0
8281 | 697.02 | 0 | 23.9 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 42.1093 | 709.3824 | 0 | 0.05921 | 5.5353 | 0 | 0 | 0 | 0 | off_peak | 697.02 | 0 | 100 | 0 | 0 | 100 | 0 | 0
8282 | 649.74 | 0 | 23.9 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 53.6732 | 662.1024 | 0 | 0.05921 | 5.3624 | 0 | 0 | 0 | 0 | off_peak | 649.74 | 0 | 100 | 0 | 0 | 100 | 0 | 0
8283 | 608.9 | 0 | 24 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 65.2371 | 621.2624 | 0 | 0.05921 | 5.1038 | 0 | 0 | 0 | 0 | off_peak | 608.9 | 0 | 100 | 0 | 0 | 100 | 0 | 0
8284 | 593.98 | 0 | 24 | 0 | 0 | 0 | 0 | 8.9371 | 8.9371 | 0 | 0 | 0 | 73.597 | 602.9171 | 0 | 0.05921 | 4.8704 | 0 | 0 | 0 | 0 | off_peak | 593.98 | 0 | 100 | 0 | 0 | 100 | 0 | 0
8285 | 568.02 | 0 | 24 | 0 | 0 | 0 | 0 | 0.57721 | 0.57721 | 0 | 0 | 0 | 74.137 | 568.5972 | 0 | 0.05921 | 4.4445 | 0 | 0 | 0 | 0 | off_peak | 568.02 | 0 | 100 | 0 | 0 | 100 | 0 | 0
8286 | 636.01 | 0 | 24.1 | 0 | 0 | 0 | 0 | 0.037279 | 0.037279 | 0 | 0 | 0 | 74.1718 | 636.0473 | 0 | 0.05921 | 3.8831 | 0 | 0 | 0 | 0 | off_peak | 636.01 | 0 | 100 | 0 | 0 | 100 | 0 | 0
8287 | 691.27 | 0 | 24.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1718 | 691.27 | 0 | 0.088511 | 3.5565 | 0 | 0 | 0 | 0 | on_peak | 691.27 |  |  | 0 | 0 | 100 | 0 | 0
8288 | 674.7 | 59.7128 | 24.7 | 9.6839 | 9.6839 | 0 | 0 | 0 | 0 | 62.443 | 62.443 | 0 | 7.4174 | 602.573 | 0 | 0.088511 | 3.2495 | 0 | 0 | 0 | 9.6839 | on_peak | 602.573 |  |  | 1.44 | 9.25 | 89.31 | 31.4676 | 0
8289 | 734.13 | 237.335 | 25.2 | 38.4206 | 38.4206 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 695.7094 | 0 | 0.088511 | 3.1603 | 0 | 0 | 0 | 38.4206 | on_peak | 695.7094 |  |  | 5.23 | 0 | 94.77 | 121.4195 | 0
8290 | 744.84 | 411.85 | 25.5 | 66.5996 | 66.5996 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 678.2404 | 0 | 0.088511 | 3.1705 | 0 | 0 | 0 | 66.5996 | on_peak | 678.2404 |  |  | 8.94 | 0 | 91.06 | 211.1573 | 0
8291 | 724.73 | 546.326 | 25.7 | 88.2818 | 88.2818 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 18.9814 | 648.8106 | 0 | 0.05921 | 3.2236 | 0 | 0 | 0 | 88.2818 | off_peak | 636.4482 | 0 | 100 | 12.18 | 0 | 87.82 | 284.5893 | 0
8292 | 792.57 | 625.592 | 26 | 100.9811 | 100.9811 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 30.5453 | 703.9513 | 0 | 0.05921 | 3.5723 | 0 | 0 | 0 | 100.9811 | off_peak | 691.5889 | 0 | 100 | 12.74 | 0 | 87.26 | 360.7297 | 0
8293 | 749.9 | 640.278 | 26.1 | 103.3143 | 103.3143 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 42.1093 | 658.9481 | 0 | 0.05921 | 4.3203 | 0 | 0 | 0 | 103.3143 | off_peak | 646.5857 | 0 | 100 | 13.78 | 0 | 86.22 | 446.3515 | 0
8294 | 782.98 | 588.223 | 26.2 | 94.8805 | 94.8805 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 53.6732 | 700.4619 | 0 | 0.05921 | 4.773 | 0 | 0 | 0 | 94.8805 | off_peak | 688.0995 | 0 | 100 | 12.12 | 0 | 87.88 | 452.8661 | 0
8295 | 821.71 | 479.894 | 26.1 | 77.435 | 77.435 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 65.2371 | 756.6374 | 0 | 0.05921 | 4.3812 | 0 | 0 | 0 | 77.435 | off_peak | 744.275 | 0 | 100 | 9.42 | 0 | 90.58 | 339.2566 | 0
8296 | 740.05 | 323.191 | 25.9 | 52.1873 | 52.1873 | 0 | 0 | 8.9371 | 8.9371 | 0 | 0 | 0 | 73.597 | 696.7998 | 0 | 0.05921 | 3.8852 | 0 | 0 | 0 | 52.1873 | off_peak | 687.8627 | 0 | 100 | 7.05 | 0 | 92.95 | 202.7568 | 0
8297 | 768.6 | 142.338 | 25.4 | 23.0256 | 23.0256 | 0 | 0 | 0.57721 | 0.57721 | 0 | 0 | 0 | 74.137 | 746.1517 | 0 | 0.05921 | 3.5813 | 0 | 0 | 0 | 23.0256 | off_peak | 745.5744 | 0 | 100 | 3 | 0 | 97 | 82.4613 | 0
8298 | 742.67 | 5.702 | 24.9 | 0.92406 | 0.88678 | 0 | 0.037279 | 0.037279 | 0 | 0 | 0 | 0 | 74.1718 | 741.7832 | 0 | 0.05921 | 3.4352 | 0 | 0 | 0.034872 | 0.88678 | off_peak | 741.7832 | 100 | 0 | 0.12 | 0 | 99.88 | 3.0462 | 0
8299 | 724.57 | 0 | 24.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1718 | 724.57 | 0 | 0.088511 | 3.4633 | 0 | 0 | 0.034872 | 0 | on_peak | 724.57 |  |  | 0 | 0 | 100 | 0 | 0
8300 | 752.62 | 0 | 24.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1718 | 752.62 | 0 | 0.088511 | 3.5527 | 0 | 0 | 0.034872 | 0 | on_peak | 752.62 |  |  | 0 | 0 | 100 | 0 | 0
8301 | 726.35 | 0 | 24.5 | 0 | 0 | 0 | 0 | 0 | 0 | 62.443 | 62.443 | 0 | 7.4174 | 663.907 | 0 | 0.088511 | 3.8267 | 0.032619 | 0 | 0 | 0.032619 | on_peak | 663.907 |  |  | 0 | 8.6 | 91.4 | 0.12482 | 0
8302 | 712.22 | 0 | 24.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 712.22 | 0 | 0.088511 | 4.0078 | 0 | 0 | 0 | 0 | on_peak | 712.22 |  |  | 0 | 0 | 100 | 0 | 0
8303 | 764.46 | 0 | 24.3 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 18.9814 | 776.8224 | 0 | 0.05921 | 4.456 | 0 | 0 | 0 | 0 | off_peak | 764.46 | 0 | 100 | 0 | 0 | 100 | 0 | 0
8304 | 710.41 | 0 | 24.3 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 30.5453 | 722.7724 | 0 | 0.05921 | 5.1078 | 0 | 0 | 0 | 0 | off_peak | 710.41 | 0 | 100 | 0 | 0 | 100 | 0 | 0
8305 | 671.28 | 0 | 24.3 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 42.1093 | 683.6424 | 0 | 0.05921 | 5.3965 | 0 | 0 | 0 | 0 | off_peak | 671.28 | 0 | 100 | 0 | 0 | 100 | 0 | 0
8306 | 661.16 | 0 | 24.4 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 53.6732 | 673.5224 | 0 | 0.05921 | 5.3429 | 0 | 0 | 0 | 0 | off_peak | 661.16 | 0 | 100 | 0 | 0 | 100 | 0 | 0
8307 | 651.59 | 0 | 24.5 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 65.2371 | 663.9524 | 0 | 0.05921 | 5.1667 | 0 | 0 | 0 | 0 | off_peak | 651.59 | 0 | 100 | 0 | 0 | 100 | 0 | 0
8308 | 610.03 | 0 | 24.6 | 0 | 0 | 0 | 0 | 8.9371 | 8.9371 | 0 | 0 | 0 | 73.597 | 618.9671 | 0 | 0.05921 | 4.9029 | 0 | 0 | 0 | 0 | off_peak | 610.03 | 0 | 100 | 0 | 0 | 100 | 0 | 0
8309 | 596.27 | 0 | 24.6 | 0 | 0 | 0 | 0 | 0.57721 | 0.57721 | 0 | 0 | 0 | 74.137 | 596.8472 | 0 | 0.05921 | 4.4856 | 0 | 0 | 0 | 0 | off_peak | 596.27 | 0 | 100 | 0 | 0 | 100 | 0 | 0
8310 | 684.57 | 0 | 24.7 | 0 | 0 | 0 | 0 | 0.037279 | 0.037279 | 0 | 0 | 0 | 74.1718 | 684.6073 | 0 | 0.05921 | 4.0755 | 0 | 0 | 0 | 0 | off_peak | 684.57 | 0 | 100 | 0 | 0 | 100 | 0 | 0
8311 | 683.14 | 0 | 24.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1718 | 683.14 | 0 | 0.088511 | 3.6221 | 0 | 0 | 0 | 0 | on_peak | 683.14 |  |  | 0 | 0 | 100 | 0 | 0
8312 | 719.15 | 58.9433 | 25.1 | 9.5454 | 9.5454 | 0 | 0 | 0 | 0 | 62.443 | 62.443 | 0 | 7.4174 | 647.1616 | 0 | 0.088511 | 3.3661 | 0 | 0 | 0 | 9.5454 | on_peak | 647.1616 |  |  | 1.33 | 8.68 | 89.99 | 32.131 | 0
8313 | 748.15 | 233.976 | 25.5 | 37.8359 | 37.8359 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 710.3141 | 0 | 0.088511 | 3.2569 | 0 | 0 | 0 | 37.8359 | on_peak | 710.3141 |  |  | 5.06 | 0 | 94.94 | 123.2296 | 0
8314 | 773.87 | 403.621 | 26 | 65.1512 | 65.1512 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 708.7188 | 0 | 0.088511 | 3.2114 | 0 | 0 | 0 | 65.1512 | on_peak | 708.7188 |  |  | 8.42 | 0 | 91.58 | 209.2236 | 0
8315 | 748.37 | 535.345 | 26.4 | 86.2888 | 86.2888 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 18.9814 | 674.4436 | 0 | 0.05921 | 3.3249 | 0 | 0 | 0 | 86.2888 | off_peak | 662.0812 | 0 | 100 | 11.53 | 0 | 88.47 | 286.9038 | 0
8316 | 799.3 | 613.72 | 26.7 | 98.8142 | 98.8142 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 30.5453 | 712.8482 | 0 | 0.05921 | 3.331 | 0 | 0 | 0 | 98.8142 | off_peak | 700.4858 | 0 | 100 | 12.36 | 0 | 87.64 | 329.15 | 0
8317 | 735.7 | 619.478 | 26.7 | 99.7413 | 99.7413 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 42.1093 | 648.3211 | 0 | 0.05921 | 4.1638 | 0 | 0 | 0 | 99.7413 | off_peak | 635.9587 | 0 | 100 | 13.56 | 0 | 86.44 | 415.306 | 0
8318 | 801.13 | 541.669 | 26.6 | 87.2449 | 87.2449 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 53.6732 | 726.2474 | 0 | 0.05921 | 4.5308 | 0 | 0 | 0 | 87.2449 | off_peak | 713.8851 | 0 | 100 | 10.89 | 0 | 89.11 | 395.2877 | 0
8319 | 816.25 | 472.219 | 26.4 | 76.1139 | 76.1139 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 65.2371 | 752.4985 | 0 | 0.05921 | 4.7718 | 0 | 0 | 0 | 76.1139 | off_peak | 740.1361 | 0 | 100 | 9.32 | 0 | 90.68 | 363.2027 | 0
8320 | 730.72 | 315.653 | 26.1 | 50.9333 | 50.9333 | 0 | 0 | 8.9371 | 8.9371 | 0 | 0 | 0 | 73.597 | 688.7238 | 0 | 0.05921 | 4.7573 | 0 | 0 | 0 | 50.9333 | off_peak | 679.7867 | 0 | 100 | 6.97 | 0 | 93.03 | 242.3051 | 0
8321 | 768.09 | 135.494 | 25.4 | 21.9184 | 21.9184 | 0 | 0 | 0.57721 | 0.57721 | 0 | 0 | 0 | 74.137 | 746.7488 | 0 | 0.05921 | 4.6783 | 0 | 0 | 0 | 21.9184 | off_peak | 746.1716 | 0 | 100 | 2.85 | 0 | 97.15 | 102.5402 | 0
8322 | 777.59 | 4.767 | 24.7 | 0.77308 | 0.77308 | 0 | 0 | 0.037279 | 0.037279 | 0 | 0 | 0 | 74.1718 | 776.8542 | 0 | 0.05921 | 4.4948 | 0 | 0 | 0 | 0.77308 | off_peak | 776.8169 | 0 | 100 | 0.1 | 0 | 99.9 | 3.4748 | 0
8323 | 741.88 | 0 | 24.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1718 | 741.88 | 0 | 0.088511 | 4.4957 | 0 | 0 | 0 | 0 | on_peak | 741.88 |  |  | 0 | 0 | 100 | 0 | 0
8324 | 755.98 | 0 | 23.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1718 | 755.98 | 0 | 0.088511 | 4.5511 | 0 | 0 | 0 | 0 | on_peak | 755.98 |  |  | 0 | 0 | 100 | 0 | 0
8325 | 775.78 | 0 | 22.5 | 0 | 0 | 0 | 0 | 0 | 0 | 62.443 | 62.443 | 0 | 7.4174 | 713.337 | 0 | 0.088511 | 4.6248 | 0 | 0 | 0 | 0 | on_peak | 713.337 |  |  | 0 | 8.05 | 91.95 | 0 | 0
8326 | 722.6 | 0 | 21.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 722.6 | 0 | 0.088511 | 4.5872 | 0 | 0 | 0 | 0 | on_peak | 722.6 |  |  | 0 | 0 | 100 | 0 | 0
8327 | 731.71 | 0 | 21 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 18.9814 | 744.0724 | 0 | 0.05921 | 4.7945 | 0 | 0 | 0 | 0 | off_peak | 731.71 | 0 | 100 | 0 | 0 | 100 | 0 | 0
8328 | 770.64 | 0 | 20.7 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 30.5453 | 783.0024 | 0 | 0.05921 | 5.3071 | 0 | 0 | 0 | 0 | off_peak | 770.64 | 0 | 100 | 0 | 0 | 100 | 0 | 0
8329 | 691.46 | 0 | 20.5 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 42.1093 | 703.8224 | 0 | 0.05921 | 5.5635 | 0 | 0 | 0 | 0 | off_peak | 691.46 | 0 | 100 | 0 | 0 | 100 | 0 | 0
8330 | 596.54 | 0 | 20.4 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 53.6732 | 608.9024 | 0 | 0.05921 | 5.5519 | 0 | 0 | 0 | 0 | off_peak | 596.54 | 0 | 100 | 0 | 0 | 100 | 0 | 0
8331 | 581.75 | 0 | 20.2 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 65.2371 | 594.1124 | 0 | 0.05921 | 5.249 | 0 | 0 | 0 | 0 | off_peak | 581.75 | 0 | 100 | 0 | 0 | 100 | 0 | 0
8332 | 544.63 | 0 | 20 | 0 | 0 | 0 | 0 | 8.9371 | 8.9371 | 0 | 0 | 0 | 73.597 | 553.5671 | 0 | 0.05921 | 4.9338 | 0 | 0 | 0 | 0 | off_peak | 544.63 | 0 | 100 | 0 | 0 | 100 | 0 | 0
8333 | 536.3 | 0 | 19.8 | 0 | 0 | 0 | 0 | 0.57721 | 0.57721 | 0 | 0 | 0 | 74.137 | 536.8772 | 0 | 0.05921 | 4.5255 | 0 | 0 | 0 | 0 | off_peak | 536.3 | 0 | 100 | 0 | 0 | 100 | 0 | 0
8334 | 694.5 | 0 | 19.5 | 0 | 0 | 0 | 0 | 0.037279 | 0.037279 | 0 | 0 | 0 | 74.1718 | 694.5373 | 0 | 0.05921 | 4.0386 | 0 | 0 | 0 | 0 | off_peak | 694.5 | 0 | 100 | 0 | 0 | 100 | 0 | 0
8335 | 758.16 | 0 | 19.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1718 | 758.16 | 0 | 0.088511 | 3.6421 | 0 | 0 | 0 | 0 | on_peak | 758.16 |  |  | 0 | 0 | 100 | 0 | 0
8336 | 771.77 | 55.1315 | 19.9 | 9.0953 | 9.0953 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1718 | 762.6747 | 0 | 0.088511 | 3.3622 | 0 | 0 | 0 | 9.0953 | on_peak | 762.6747 |  |  | 1.18 | 0 | 98.82 | 30.5798 | 0
8337 | 812.38 | 226.279 | 20.6 | 37.2378 | 37.2378 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1718 | 775.1422 | 0 | 0.088511 | 3.1975 | 0 | 0 | 0 | 37.2378 | on_peak | 775.1422 |  |  | 4.58 | 0 | 95.42 | 119.0698 | 0
8338 | 806.78 | 395.432 | 21.3 | 64.9133 | 64.9133 | 0 | 0 | 0 | 0 | 62.443 | 62.443 | 0 | 7.4174 | 679.4237 | 0 | 0.088511 | 3.1504 | 0 | 0 | 0 | 64.9133 | on_peak | 679.4237 |  |  | 8.05 | 7.74 | 84.21 | 204.5029 | 0
8339 | 789.48 | 526.436 | 21.8 | 86.2651 | 86.2651 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 18.9814 | 715.5773 | 0 | 0.05921 | 3.2059 | 0 | 0 | 0 | 86.2651 | off_peak | 703.2149 | 0 | 100 | 10.93 | 0 | 89.07 | 276.5543 | 0
8340 | 789.41 | 574.936 | 22.1 | 94.112 | 94.112 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 30.5453 | 707.6604 | 0 | 0.05921 | 3.4724 | 0 | 0 | 0 | 94.112 | off_peak | 695.298 | 0 | 100 | 11.92 | 0 | 88.08 | 326.7959 | 0
8341 | 763.75 | 554.358 | 22.3 | 90.6789 | 90.6789 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 42.1093 | 685.4335 | 0 | 0.05921 | 3.9722 | 0 | 0 | 0 | 90.6789 | off_peak | 673.0711 | 0 | 100 | 11.87 | 0 | 88.13 | 360.1993 | 0
8342 | 795.35 | 562.951 | 22.4 | 92.0517 | 92.0517 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 53.6732 | 715.6607 | 0 | 0.05921 | 4.3861 | 0 | 0 | 0 | 92.0517 | off_peak | 703.2983 | 0 | 100 | 11.57 | 0 | 88.43 | 403.7502 | 0
8343 | 835.59 | 471.854 | 22.4 | 77.1558 | 77.1558 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 65.2371 | 770.7965 | 0 | 0.05921 | 4.5226 | 0 | 0 | 0 | 77.1558 | off_peak | 758.4342 | 0 | 100 | 9.23 | 0 | 90.77 | 348.9434 | 0
8344 | 761.17 | 319.741 | 22.1 | 52.3388 | 52.3388 | 0 | 0 | 8.9371 | 8.9371 | 0 | 0 | 0 | 73.597 | 717.7683 | 0 | 0.05921 | 4.5638 | 0 | 0 | 0 | 52.3388 | off_peak | 708.8312 | 0 | 100 | 6.88 | 0 | 93.12 | 238.8663 | 0
8345 | 729 | 141.788 | 21.4 | 23.2673 | 23.2673 | 0 | 0 | 0.57721 | 0.57721 | 0 | 0 | 0 | 74.137 | 706.3099 | 0 | 0.05921 | 4.4182 | 0 | 0 | 0 | 23.2673 | off_peak | 705.7327 | 0 | 100 | 3.19 | 0 | 96.81 | 102.7997 | 0
8346 | 766.68 | 5.7455 | 20.7 | 0.94519 | 0.94519 | 0 | 0 | 0.037279 | 0.037279 | 0 | 0 | 0 | 74.1718 | 765.7721 | 0 | 0.05921 | 4.3188 | 0 | 0 | 0 | 0.94519 | off_peak | 765.7348 | 0 | 100 | 0.12 | 0 | 99.88 | 4.0821 | 0
8347 | 743 | 0 | 20.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1718 | 743 | 0 | 0.088511 | 4.2354 | 0 | 0 | 0 | 0 | on_peak | 743 |  |  | 0 | 0 | 100 | 0 | 0
8348 | 739.3 | 0 | 19.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1718 | 739.3 | 0 | 0.088511 | 4.3554 | 0 | 0 | 0 | 0 | on_peak | 739.3 |  |  | 0 | 0 | 100 | 0 | 0
8349 | 768.72 | 0 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 62.443 | 62.443 | 0 | 7.4174 | 706.277 | 0 | 0.088511 | 4.4193 | 0 | 0 | 0 | 0 | on_peak | 706.277 |  |  | 0 | 8.12 | 91.88 | 0 | 0
8350 | 712.97 | 0 | 18.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 712.97 | 0 | 0.088511 | 4.5959 | 0 | 0 | 0 | 0 | on_peak | 712.97 |  |  | 0 | 0 | 100 | 0 | 0
8351 | 741.56 | 0 | 17.8 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 18.9814 | 753.9224 | 0 | 0.05921 | 4.9059 | 0 | 0 | 0 | 0 | off_peak | 741.56 | 0 | 100 | 0 | 0 | 100 | 0 | 0
8352 | 765.99 | 0 | 17.2 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 30.5453 | 778.3524 | 0 | 0.05921 | 5.1804 | 0 | 0 | 0 | 0 | off_peak | 765.99 | 0 | 100 | 0 | 0 | 100 | 0 | 0
8353 | 696.04 | 0 | 16.5 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 42.1093 | 708.4024 | 0 | 0.05921 | 5.3967 | 0 | 0 | 0 | 0 | off_peak | 696.04 | 0 | 100 | 0 | 0 | 100 | 0 | 0
8354 | 641.33 | 0 | 16 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 53.6732 | 653.6924 | 0 | 0.05921 | 5.3038 | 0 | 0 | 0 | 0 | off_peak | 641.33 | 0 | 100 | 0 | 0 | 100 | 0 | 0
8355 | 622.78 | 0 | 15.4 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 65.2371 | 635.1424 | 0 | 0.05921 | 5.1346 | 0 | 0 | 0 | 0 | off_peak | 622.78 | 0 | 100 | 0 | 0 | 100 | 0 | 0
8356 | 603.28 | 0 | 15 | 0 | 0 | 0 | 0 | 8.9371 | 8.9371 | 0 | 0 | 0 | 73.597 | 612.2171 | 0 | 0.05921 | 4.8096 | 0 | 0 | 0 | 0 | off_peak | 603.28 | 0 | 100 | 0 | 0 | 100 | 0 | 0
8357 | 603.85 | 0 | 14.7 | 0 | 0 | 0 | 0 | 0.57721 | 0.57721 | 0 | 0 | 0 | 74.137 | 604.4272 | 0 | 0.05921 | 4.4523 | 0 | 0 | 0 | 0 | off_peak | 603.85 | 0 | 100 | 0 | 0 | 100 | 0 | 0
8358 | 674.56 | 0 | 14.4 | 0 | 0 | 0 | 0 | 0.037279 | 0.037279 | 0 | 0 | 0 | 74.1718 | 674.5973 | 0 | 0.05921 | 3.8228 | 0 | 0 | 0 | 0 | off_peak | 674.56 | 0 | 100 | 0 | 0 | 100 | 0 | 0
8359 | 689.82 | 0 | 14.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1718 | 689.82 | 0 | 0.088511 | 3.3584 | 0 | 0 | 0 | 0 | on_peak | 689.82 |  |  | 0 | 0 | 100 | 0 | 0
8360 | 761.01 | 53.6779 | 14.7 | 9.0183 | 9.0183 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1718 | 751.9917 | 0 | 0.088511 | 3.0568 | 0 | 0 | 0 | 9.0183 | on_peak | 751.9917 |  |  | 1.19 | 0 | 98.81 | 27.5667 | 0
8361 | 817.3 | 225.739 | 15.3 | 37.8467 | 37.8467 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1718 | 779.4533 | 0 | 0.088511 | 2.8939 | 0 | 0 | 0 | 37.8467 | on_peak | 779.4533 |  |  | 4.63 | 0 | 95.37 | 109.5228 | 0
8362 | 829.55 | 387.186 | 15.9 | 64.779 | 64.779 | 0 | 0 | 0 | 0 | 62.443 | 62.443 | 0 | 7.4174 | 702.328 | 0 | 0.088511 | 2.8405 | 0 | 0 | 0 | 64.779 | on_peak | 702.328 |  |  | 7.81 | 7.53 | 84.66 | 184.002 | 0
8363 | 756.07 | 437.843 | 16.7 | 73.05 | 73.05 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 18.9814 | 695.3824 | 0 | 0.05921 | 2.9343 | 0 | 0 | 0 | 73.05 | off_peak | 683.02 | 0 | 100 | 9.66 | 0 | 90.34 | 214.3539 | 0
8364 | 822.64 | 538.053 | 17.4 | 89.5494 | 89.5494 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 30.5453 | 745.453 | 0 | 0.05921 | 3.2532 | 0 | 0 | 0 | 89.5494 | off_peak | 733.0906 | 0 | 100 | 10.89 | 0 | 89.11 | 291.3205 | 0
8365 | 744.93 | 390.191 | 17.9 | 64.8266 | 64.8266 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 42.1093 | 692.4658 | 0 | 0.05921 | 3.8753 | 0 | 0 | 0 | 64.8266 | off_peak | 680.1034 | 0 | 100 | 8.7 | 0 | 91.3 | 251.2206 | 0
8366 | 819.6 | 335.062 | 18.3 | 55.5893 | 55.5893 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 53.6732 | 776.3731 | 0 | 0.05921 | 4.2774 | 0 | 0 | 0 | 55.5893 | off_peak | 764.0107 | 0 | 100 | 6.78 | 0 | 93.22 | 237.7765 | 0
8367 | 816.47 | 371.646 | 18.4 | 61.6372 | 61.6372 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 65.2371 | 767.1952 | 0 | 0.05921 | 4.2432 | 0 | 0 | 0 | 61.6372 | off_peak | 754.8328 | 0 | 100 | 7.55 | 0 | 92.45 | 261.5362 | 0
8368 | 774.77 | 195.684 | 18.4 | 32.454 | 32.454 | 0 | 0 | 8.9371 | 8.9371 | 0 | 0 | 0 | 73.597 | 751.2531 | 0 | 0.05921 | 4.2527 | 0 | 0 | 0 | 32.454 | off_peak | 742.316 | 0 | 100 | 4.19 | 0 | 95.81 | 138.0163 | 0
8369 | 755.28 | 97.2478 | 17.9 | 16.1568 | 16.1568 | 0 | 0 | 0.57721 | 0.57721 | 0 | 0 | 0 | 74.137 | 739.7004 | 0 | 0.05921 | 4.1558 | 0 | 0 | 0 | 16.1568 | off_peak | 739.1232 | 0 | 100 | 2.14 | 0 | 97.86 | 67.1448 | 0
8370 | 756.61 | 4.75 | 17.4 | 0.79055 | 0.75327 | 0 | 0.037279 | 0.037279 | 0 | 0 | 0 | 0 | 74.1718 | 755.8567 | 0 | 0.05921 | 4.1515 | 0 | 0 | 0.034872 | 0.75327 | off_peak | 755.8567 | 100 | 0 | 0.1 | 0 | 99.9 | 3.1273 | 0
8371 | 712.98 | 0 | 17.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1718 | 712.98 | 0 | 0.088511 | 4.0649 | 0 | 0 | 0.034872 | 0 | on_peak | 712.98 |  |  | 0 | 0 | 100 | 0 | 0
8372 | 750.85 | 0 | 16.7 | 0 | 0 | 0 | 0 | 0 | 0 | 62.443 | 62.443 | 0 | 7.4174 | 688.407 | 0 | 0.088511 | 4.1298 | 0.032619 | 0 | 0 | 0.032619 | on_peak | 688.407 |  |  | 0 | 8.32 | 91.68 | 0.13471 | 0
8373 | 749.8 | 0 | 16.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 749.8 | 0 | 0.088511 | 4.2624 | 0 | 0 | 0 | 0 | on_peak | 749.8 |  |  | 0 | 0 | 100 | 0 | 0
8374 | 711.23 | 0 | 15.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 711.23 | 0 | 0.088511 | 4.4759 | 0 | 0 | 0 | 0 | on_peak | 711.23 |  |  | 0 | 0 | 100 | 0 | 0
8375 | 728.28 | 0 | 15.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 728.28 | 0 | 0.05921 | 4.7451 | 0 | 0 | 0 | 0 | off_peak | 728.28 |  |  | 0 | 0 | 100 | 0 | 0
8376 | 692.84 | 0 | 15.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 692.84 | 0 | 0.05921 | 5.0187 | 0 | 0 | 0 | 0 | off_peak | 692.84 |  |  | 0 | 0 | 100 | 0 | 0
8377 | 683.56 | 0 | 14.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 683.56 | 0 | 0.05921 | 5.1279 | 0 | 0 | 0 | 0 | off_peak | 683.56 |  |  | 0 | 0 | 100 | 0 | 0
8378 | 632.78 | 0 | 14.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 632.78 | 0 | 0.05921 | 4.9563 | 0 | 0 | 0 | 0 | off_peak | 632.78 |  |  | 0 | 0 | 100 | 0 | 0
8379 | 562.46 | 0 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 562.46 | 0 | 0.05921 | 4.7858 | 0 | 0 | 0 | 0 | off_peak | 562.46 |  |  | 0 | 0 | 100 | 0 | 0
8380 | 600.33 | 0 | 13.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 600.33 | 0 | 0.05921 | 4.5518 | 0 | 0 | 0 | 0 | off_peak | 600.33 |  |  | 0 | 0 | 100 | 0 | 0
8381 | 590.29 | 0 | 13.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 590.29 | 0 | 0.05921 | 4.2674 | 0 | 0 | 0 | 0 | off_peak | 590.29 |  |  | 0 | 0 | 100 | 0 | 0
8382 | 623.26 | 0 | 13.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 623.26 | 0 | 0.05921 | 3.8989 | 0 | 0 | 0 | 0 | off_peak | 623.26 |  |  | 0 | 0 | 100 | 0 | 0
8383 | 735.78 | 0 | 13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 735.78 | 0 | 0.05921 | 3.5102 | 0 | 0 | 0 | 0 | off_peak | 735.78 |  |  | 0 | 0 | 100 | 0 | 0
8384 | 679.38 | 15.2 | 13.4 | 2.5652 | 2.5652 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 18.9814 | 689.1771 | 0 | 0.05921 | 3.2111 | 0 | 0 | 0 | 2.5652 | off_peak | 676.8148 | 0 | 100 | 0.38 | 0 | 99.62 | 8.2373 | 0
8385 | 737.33 | 113.605 | 14 | 19.1328 | 19.1328 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 30.5453 | 730.5596 | 0 | 0.05921 | 3.0595 | 0 | 0 | 0 | 19.1328 | off_peak | 718.1972 | 0 | 100 | 2.59 | 0 | 97.41 | 58.5373 | 0
8386 | 726.76 | 209.342 | 14.7 | 35.1709 | 35.1709 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 42.1093 | 703.9515 | 0 | 0.05921 | 2.9819 | 0 | 0 | 0 | 35.1709 | off_peak | 691.5891 | 0 | 100 | 4.84 | 0 | 95.16 | 104.8761 | 0
8387 | 694.68 | 254.976 | 15.8 | 42.6742 | 42.6742 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 53.6732 | 664.3682 | 0 | 0.05921 | 2.984 | 0 | 0 | 0 | 42.6742 | off_peak | 652.0058 | 0 | 100 | 6.14 | 0 | 93.86 | 127.3417 | 0
8388 | 763.71 | 460.629 | 16.8 | 76.8247 | 76.8247 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 53.6732 | 686.8853 | 0 | 0.05921 | 3.0885 | 0 | 0 | 0 | 76.8247 | off_peak | 686.8853 |  |  | 10.06 | 0 | 89.94 | 237.2724 | 0
8389 | 711.61 | 513.031 | 17.6 | 85.3251 | 85.3251 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 53.6732 | 626.2849 | 0 | 0.05921 | 3.3331 | 0 | 0 | 0 | 85.3251 | off_peak | 626.2849 |  |  | 11.99 | 0 | 88.01 | 284.396 | 0
8390 | 696.84 | 432.912 | 18.2 | 71.8486 | 71.8486 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 53.6732 | 624.9914 | 0 | 0.05921 | 3.647 | 0 | 0 | 0 | 71.8486 | off_peak | 624.9914 |  |  | 10.31 | 0 | 89.69 | 262.0332 | 0
8391 | 696.19 | 124.943 | 18.6 | 20.7071 | 20.7071 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 53.6732 | 675.4829 | 0 | 0.05921 | 4.1351 | 0 | 0 | 0 | 20.7071 | off_peak | 675.4829 |  |  | 2.97 | 0 | 97.03 | 85.6267 | 0
8392 | 683.49 | 277.798 | 18.6 | 46.0402 | 46.0402 | 0 | 0 | 8.7006 | 8.7006 | 0 | 0 | 0 | 61.8119 | 646.1505 | 0 | 0.05921 | 4.6472 | 0 | 0 | 0 | 46.0402 | off_peak | 637.4498 | 0 | 100 | 6.74 | 0 | 93.26 | 213.9571 | 0
8393 | 658.46 | 77.9281 | 17.9 | 12.947 | 12.947 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 61.8119 | 645.513 | 0 | 0.05921 | 4.8953 | 0 | 0 | 0 | 12.947 | off_peak | 645.513 |  |  | 1.97 | 0 | 98.03 | 63.379 | 0
8394 | 611.87 | 2.85 | 17.1 | 0.47483 | 0.47483 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 61.8119 | 611.3952 | 0 | 0.05921 | 5.037 | 0 | 0 | 0 | 0.47483 | off_peak | 611.3952 |  |  | 0.08 | 0 | 99.92 | 2.3917 | 0
8395 | 563.65 | 0 | 16.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 61.8119 | 563.65 | 0 | 0.05921 | 5.041 | 0 | 0 | 0 | 0 | off_peak | 563.65 |  |  | 0 | 0 | 100 | 0 | 0
8396 | 547.9 | 0 | 16.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 61.8119 | 547.9 | 0 | 0.05921 | 5.0183 | 0 | 0 | 0 | 0 | off_peak | 547.9 |  |  | 0 | 0 | 100 | 0 | 0
8397 | 570.22 | 0 | 16.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 61.8119 | 570.22 | 0 | 0.05921 | 5.0586 | 0 | 0 | 0 | 0 | off_peak | 570.22 |  |  | 0 | 0 | 100 | 0 | 0
8398 | 534.69 | 0 | 16.2 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 73.3758 | 547.0524 | 0 | 0.05921 | 5.0257 | 0 | 0 | 0 | 0 | off_peak | 534.69 | 0 | 100 | 0 | 0 | 100 | 0 | 0
8399 | 555.37 | 0 | 16.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 73.3758 | 555.37 | 0 | 0.05921 | 5.0983 | 0 | 0 | 0 | 0 | off_peak | 555.37 |  |  | 0 | 0 | 100 | 0 | 0
8400 | 479.63 | 0 | 15.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 73.3758 | 479.63 | 0 | 0.05921 | 5.3404 | 0 | 0 | 0 | 0 | off_peak | 479.63 |  |  | 0 | 0 | 100 | 0 | 0
8401 | 460.51 | 0 | 15.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 73.3758 | 460.51 | 0 | 0.05921 | 5.3964 | 0 | 0 | 0 | 0 | off_peak | 460.51 |  |  | 0 | 0 | 100 | 0 | 0
8402 | 498.96 | 0 | 15.6 | 0 | 0 | 0 | 0 | 0.79843 | 0.79843 | 0 | 0 | 0 | 74.1227 | 499.7584 | 0 | 0.05921 | 5.2015 | 0 | 0 | 0 | 0 | off_peak | 498.96 | 0 | 100 | 0 | 0 | 100 | 0 | 0
8403 | 457.74 | 0 | 15.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1227 | 457.74 | 0 | 0.05921 | 4.964 | 0 | 0 | 0 | 0 | off_peak | 457.74 |  |  | 0 | 0 | 100 | 0 | 0
8404 | 467.45 | 0 | 15.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1227 | 467.45 | 0 | 0.05921 | 4.753 | 0 | 0 | 0 | 0 | off_peak | 467.45 |  |  | 0 | 0 | 100 | 0 | 0
8405 | 511.16 | 0 | 15.2 | 0 | 0 | 0 | 0 | 0.051567 | 0.051567 | 0 | 0 | 0 | 74.1709 | 511.2116 | 0 | 0.05921 | 4.4203 | 0 | 0 | 0 | 0 | off_peak | 511.16 | 0 | 100 | 0 | 0 | 100 | 0 | 0
8406 | 541.7 | 0 | 15.3 | 0 | 0 | 0 | 0 | 0.0033305 | 0.0033305 | 0 | 0 | 0 | 74.174 | 541.7033 | 0 | 0.05921 | 4.0889 | 0 | 0 | 0 | 0 | off_peak | 541.7 | 0 | 100 | 0 | 0 | 100 | 0 | 0
8407 | 658.6 | 0 | 15.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.174 | 658.6 | 0 | 0.05921 | 3.7426 | 0 | 0 | 0 | 0 | off_peak | 658.6 |  |  | 0 | 0 | 100 | 0 | 0
8408 | 727.97 | 42.7343 | 16.4 | 7.1373 | 7.1373 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.174 | 720.8327 | 0 | 0.05921 | 3.4489 | 0 | 0 | 0 | 7.1373 | off_peak | 720.8327 |  |  | 0.98 | 0 | 99.02 | 24.6161 | 0
8409 | 703.23 | 76.1904 | 17.6 | 12.6717 | 12.6717 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.174 | 690.5583 | 0 | 0.05921 | 3.288 | 0 | 0 | 0 | 12.6717 | off_peak | 690.5583 |  |  | 1.8 | 0 | 98.2 | 41.6647 | 0
8410 | 701.9 | 122.863 | 18.8 | 20.3481 | 20.3481 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.174 | 681.5519 | 0 | 0.05921 | 3.2113 | 0 | 0 | 0 | 20.3481 | off_peak | 681.5519 |  |  | 2.9 | 0 | 97.1 | 65.3438 | 0
8411 | 687.18 | 188.468 | 19.9 | 31.0924 | 31.0924 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.174 | 656.0876 | 0 | 0.05921 | 3.1535 | 0 | 0 | 0 | 31.0924 | off_peak | 656.0876 |  |  | 4.52 | 0 | 95.48 | 98.051 | 0
8412 | 697.4 | 325.807 | 20.9 | 53.5598 | 53.5598 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.174 | 643.8402 | 0 | 0.05921 | 3.2206 | 0 | 0 | 0 | 53.5598 | off_peak | 643.8402 |  |  | 7.68 | 0 | 92.32 | 172.4961 | 0
8413 | 677.19 | 196.526 | 21.6 | 32.2269 | 32.2269 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.174 | 644.9631 | 0 | 0.05921 | 3.3921 | 0 | 0 | 0 | 32.2269 | off_peak | 644.9631 |  |  | 4.76 | 0 | 95.24 | 109.3182 | 0
8414 | 707.63 | 249.042 | 22 | 40.7805 | 40.7805 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.174 | 666.8495 | 0 | 0.05921 | 3.6733 | 0 | 0 | 0 | 40.7805 | off_peak | 666.8495 |  |  | 5.76 | 0 | 94.24 | 149.8008 | 0
8415 | 665.53 | 446.164 | 22.1 | 73.0332 | 73.0332 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.174 | 592.4968 | 0 | 0.05921 | 4.1215 | 0 | 0 | 0 | 73.0332 | off_peak | 592.4968 |  |  | 10.97 | 0 | 89.03 | 301.0058 | 0
8416 | 671.68 | 226.539 | 21.9 | 37.1089 | 37.1089 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.174 | 634.5711 | 0 | 0.05921 | 4.3917 | 0 | 0 | 0 | 37.1089 | off_peak | 634.5711 |  |  | 5.52 | 0 | 94.48 | 162.9702 | 0
8417 | 640.08 | 50.7331 | 21.3 | 8.3282 | 8.3282 | 0 | 0 | 0.0002151 | 0.0002151 | 0 | 0 | 0 | 74.1742 | 631.752 | 0 | 0.05921 | 4.5255 | 0 | 0 | 0 | 8.3282 | off_peak | 631.7518 | 0 | 100 | 1.3 | 0 | 98.7 | 37.6895 | 0
8418 | 619.38 | 4.75 | 20.8 | 0.78113 | 0.78113 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1742 | 618.5989 | 0 | 0.05921 | 4.5521 | 0 | 0 | 0 | 0.78113 | off_peak | 618.5989 |  |  | 0.13 | 0 | 99.87 | 3.5558 | 0
8419 | 568.47 | 0 | 20.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1742 | 568.47 | 0 | 0.05921 | 4.5747 | 0 | 0 | 0 | 0 | off_peak | 568.47 |  |  | 0 | 0 | 100 | 0 | 0
8420 | 572.56 | 0 | 20.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1742 | 572.56 | 0 | 0.05921 | 4.6679 | 0 | 0 | 0 | 0 | off_peak | 572.56 |  |  | 0 | 0 | 100 | 0 | 0
8421 | 525.99 | 0 | 20.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1742 | 525.99 | 0 | 0.05921 | 4.7205 | 0 | 0 | 0 | 0 | off_peak | 525.99 |  |  | 0 | 0 | 100 | 0 | 0
8422 | 551.2 | 0 | 20.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1742 | 551.2 | 0 | 0.05921 | 4.6885 | 0 | 0 | 0 | 0 | off_peak | 551.2 |  |  | 0 | 0 | 100 | 0 | 0
8423 | 577.32 | 0 | 20.6 | 0 | 0 | 0 | 0 | 1.3893e-05 | 1.3893e-05 | 0 | 0 | 0 | 74.1743 | 577.32 | 0 | 0.05921 | 4.984 | 0 | 0 | 0 | 0 | off_peak | 577.32 | 0 | 100 | 0 | 0 | 100 | 0 | 0
8424 | 557.82 | 0 | 20.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1743 | 557.82 | 0 | 0.05921 | 5.2526 | 0 | 0 | 0 | 0 | off_peak | 557.82 |  |  | 0 | 0 | 100 | 0 | 0
8425 | 555.85 | 0 | 20.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1743 | 555.85 | 0 | 0.05921 | 5.4112 | 0 | 0 | 0 | 0 | off_peak | 555.85 |  |  | 0 | 0 | 100 | 0 | 0
8426 | 560.46 | 0 | 20.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1743 | 560.46 | 0 | 0.05921 | 5.2169 | 0 | 0 | 0 | 0 | off_peak | 560.46 |  |  | 0 | 0 | 100 | 0 | 0
8427 | 553.81 | 0 | 20.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1743 | 553.81 | 0 | 0.05921 | 4.965 | 0 | 0 | 0 | 0 | off_peak | 553.81 |  |  | 0 | 0 | 100 | 0 | 0
8428 | 547.67 | 0 | 20.9 | 0 | 0 | 0 | 0 | 9.5921e-07 | 9.5921e-07 | 0 | 0 | 0 | 74.1743 | 547.67 | 0 | 0.05921 | 4.6357 | 0 | 0 | 0 | 0 | off_peak | 547.67 | 0 | 100 | 0 | 0 | 100 | 0 | 0
8429 | 578.83 | 0 | 20.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1743 | 578.83 | 0 | 0.05921 | 4.1766 | 0 | 0 | 0 | 0 | off_peak | 578.83 |  |  | 0 | 0 | 100 | 0 | 0
8430 | 637.75 | 0 | 20.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1743 | 637.75 | 0 | 0.05921 | 3.7136 | 0 | 0 | 0 | 0 | off_peak | 637.75 |  |  | 0 | 0 | 100 | 0 | 0
8431 | 703.01 | 0 | 20.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1743 | 703.01 | 0 | 0.088511 | 3.2776 | 0 | 0 | 0 | 0 | on_peak | 703.01 |  |  | 0 | 0 | 100 | 0 | 0
8432 | 756.26 | 29.1507 | 21.1 | 4.7887 | 4.7887 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1743 | 751.4713 | 0 | 0.088511 | 3.0055 | 0 | 0 | 0 | 4.7887 | on_peak | 751.4713 |  |  | 0.63 | 0 | 99.37 | 14.3925 | 0
8433 | 766.82 | 125.562 | 21.7 | 20.5827 | 20.5827 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1743 | 746.2373 | 0 | 0.088511 | 2.8718 | 0 | 0 | 0 | 20.5827 | on_peak | 746.2373 |  |  | 2.68 | 0 | 97.32 | 59.1103 | 0
8434 | 847.06 | 292.628 | 22.3 | 47.8665 | 47.8665 | 0 | 0 | 0 | 0 | 62.4453 | 62.4453 | 0 | 7.4174 | 736.7482 | 0 | 0.088511 | 2.8202 | 0 | 0 | 0 | 47.8665 | on_peak | 736.7482 |  |  | 5.65 | 7.37 | 86.98 | 134.9935 | 0
8435 | 761.06 | 118.616 | 23 | 19.3541 | 19.3541 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 18.9814 | 754.0682 | 0 | 0.05921 | 2.9165 | 0 | 0 | 0 | 19.3541 | off_peak | 741.7059 | 0 | 100 | 2.54 | 0 | 97.46 | 56.4467 | 0
8436 | 784.87 | 554.461 | 23.3 | 90.3724 | 90.3724 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 30.5453 | 706.86 | 0 | 0.05921 | 3.2202 | 0 | 0 | 0 | 90.3724 | off_peak | 694.4976 | 0 | 100 | 11.51 | 0 | 88.49 | 291.0184 | 0
8437 | 758.87 | 531.763 | 23.6 | 86.5798 | 86.5798 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 42.1093 | 684.6526 | 0 | 0.05921 | 3.7877 | 0 | 0 | 0 | 86.5798 | off_peak | 672.2902 | 0 | 100 | 11.41 | 0 | 88.59 | 327.9344 | 0
8438 | 750.53 | 561.06 | 23.7 | 91.3171 | 91.3171 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 53.6732 | 671.5753 | 0 | 0.05921 | 4.1861 | 0 | 0 | 0 | 91.3171 | off_peak | 659.2129 | 0 | 100 | 12.17 | 0 | 87.83 | 382.2612 | 0
8439 | 734.4 | 405.587 | 23.7 | 66.0126 | 66.0126 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 65.2371 | 680.7498 | 0 | 0.05921 | 3.9304 | 0 | 0 | 0 | 66.0126 | off_peak | 668.3874 | 0 | 100 | 8.99 | 0 | 91.01 | 259.4589 | 0
8440 | 697.33 | 94.05 | 23.5 | 15.3184 | 15.3184 | 0 | 0 | 8.9371 | 8.9371 | 0 | 0 | 0 | 73.597 | 690.9487 | 0 | 0.05921 | 3.4992 | 0 | 0 | 0 | 15.3184 | off_peak | 682.0116 | 0 | 100 | 2.2 | 0 | 97.8 | 53.6018 | 0
8441 | 718.71 | 30.7856 | 22.8 | 5.0268 | 5.0268 | 0 | 0 | 0.57721 | 0.57721 | 0 | 0 | 0 | 74.137 | 714.2604 | 0 | 0.05921 | 3.2565 | 0 | 0 | 0 | 5.0268 | off_peak | 713.6832 | 0 | 100 | 0.7 | 0 | 99.3 | 16.3695 | 0
8442 | 738.61 | 4.75 | 22.2 | 0.77726 | 0.77726 | 0 | 0 | 0.037279 | 0.037279 | 0 | 0 | 0 | 74.1718 | 737.87 | 0 | 0.05921 | 3.1423 | 0 | 0 | 0 | 0.77726 | off_peak | 737.8327 | 0 | 100 | 0.11 | 0 | 99.89 | 2.4424 | 0
8443 | 710.11 | 0 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 62.443 | 62.443 | 0 | 7.4174 | 647.667 | 0 | 0.088511 | 3.1184 | 0 | 0 | 0 | 0 | on_peak | 647.667 |  |  | 0 | 8.79 | 91.21 | 0 | 0
8444 | 692.11 | 0 | 21.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 692.11 | 0 | 0.088511 | 3.1258 | 0 | 0 | 0 | 0 | on_peak | 692.11 |  |  | 0 | 0 | 100 | 0 | 0
8445 | 708.56 | 0 | 21.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 708.56 | 0 | 0.088511 | 3.2522 | 0 | 0 | 0 | 0 | on_peak | 708.56 |  |  | 0 | 0 | 100 | 0 | 0
8446 | 676.22 | 0 | 21.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 676.22 | 0 | 0.088511 | 3.6097 | 0 | 0 | 0 | 0 | on_peak | 676.22 |  |  | 0 | 0 | 100 | 0 | 0
8447 | 688.03 | 0 | 21.5 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 18.9814 | 700.3924 | 0 | 0.05921 | 4.3571 | 0 | 0 | 0 | 0 | off_peak | 688.03 | 0 | 100 | 0 | 0 | 100 | 0 | 0
8448 | 678.1 | 0 | 21.5 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 30.5453 | 690.4624 | 0 | 0.05921 | 5.0464 | 0 | 0 | 0 | 0 | off_peak | 678.1 | 0 | 100 | 0 | 0 | 100 | 0 | 0
8449 | 641.75 | 0 | 21.4 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 42.1093 | 654.1124 | 0 | 0.05921 | 5.4034 | 0 | 0 | 0 | 0 | off_peak | 641.75 | 0 | 100 | 0 | 0 | 100 | 0 | 0
8450 | 616.63 | 0 | 21.3 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 53.6732 | 628.9924 | 0 | 0.05921 | 5.2989 | 0 | 0 | 0 | 0 | off_peak | 616.63 | 0 | 100 | 0 | 0 | 100 | 0 | 0
8451 | 586.26 | 0 | 21.3 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 65.2371 | 598.6224 | 0 | 0.05921 | 5.0984 | 0 | 0 | 0 | 0 | off_peak | 586.26 | 0 | 100 | 0 | 0 | 100 | 0 | 0
8452 | 565.17 | 0 | 21.2 | 0 | 0 | 0 | 0 | 8.9371 | 8.9371 | 0 | 0 | 0 | 73.597 | 574.1071 | 0 | 0.05921 | 4.7482 | 0 | 0 | 0 | 0 | off_peak | 565.17 | 0 | 100 | 0 | 0 | 100 | 0 | 0
8453 | 585.32 | 0 | 21.2 | 0 | 0 | 0 | 0 | 0.57721 | 0.57721 | 0 | 0 | 0 | 74.137 | 585.8972 | 0 | 0.05921 | 4.3293 | 0 | 0 | 0 | 0 | off_peak | 585.32 | 0 | 100 | 0 | 0 | 100 | 0 | 0
8454 | 606.71 | 0 | 21.2 | 0 | 0 | 0 | 0 | 0.037279 | 0.037279 | 0 | 0 | 0 | 74.1718 | 606.7473 | 0 | 0.05921 | 3.7686 | 0 | 0 | 0 | 0 | off_peak | 606.71 | 0 | 100 | 0 | 0 | 100 | 0 | 0
8455 | 669.52 | 0 | 21.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1718 | 669.52 | 0 | 0.088511 | 3.5635 | 0 | 0 | 0 | 0 | on_peak | 669.52 |  |  | 0 | 0 | 100 | 0 | 0
8456 | 715.55 | 46.0945 | 22.2 | 7.5426 | 7.5426 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1718 | 708.0074 | 0 | 0.088511 | 3.3719 | 0 | 0 | 0 | 7.5426 | on_peak | 708.0074 |  |  | 1.05 | 0 | 98.95 | 25.433 | 0
8457 | 691.16 | 212.727 | 23.1 | 34.6975 | 34.6975 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1718 | 656.4625 | 0 | 0.088511 | 3.3841 | 0 | 0 | 0 | 34.6975 | on_peak | 656.4625 |  |  | 5.02 | 0 | 94.98 | 117.4207 | 0
8458 | 770.49 | 386.796 | 23.6 | 62.9768 | 62.9768 | 0 | 0 | 0 | 0 | 62.443 | 62.443 | 0 | 7.4174 | 645.0702 | 0 | 0.088511 | 3.3923 | 0 | 0 | 0 | 62.9768 | on_peak | 645.0702 |  |  | 8.17 | 8.1 | 83.72 | 213.6356 | 0
8459 | 711.67 | 525.141 | 24 | 85.3791 | 85.3791 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 18.9814 | 638.6533 | 0 | 0.05921 | 3.533 | 0 | 0 | 0 | 85.3791 | off_peak | 626.2909 | 0 | 100 | 12 | 0 | 88 | 301.6472 | 0
8460 | 733.97 | 606.763 | 24.3 | 98.5433 | 98.5433 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 30.5453 | 647.7891 | 0 | 0.05921 | 3.8841 | 0 | 0 | 0 | 98.5433 | off_peak | 635.4267 | 0 | 100 | 13.43 | 0 | 86.57 | 382.7484 | 0
8461 | 739.75 | 627.15 | 24.4 | 101.8178 | 101.8178 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 42.1093 | 650.2946 | 0 | 0.05921 | 4.5846 | 0 | 0 | 0 | 101.8178 | off_peak | 637.9322 | 0 | 100 | 13.76 | 0 | 86.24 | 466.7929 | 0
8462 | 786.95 | 582.395 | 24.5 | 94.5178 | 94.5178 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 53.6732 | 704.7946 | 0 | 0.05921 | 5.1554 | 0 | 0 | 0 | 94.5178 | off_peak | 692.4322 | 0 | 100 | 12.01 | 0 | 87.99 | 487.2725 | 0
8463 | 784.54 | 478.005 | 24.5 | 77.5762 | 77.5762 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 65.2371 | 719.3262 | 0 | 0.05921 | 4.8253 | 0 | 0 | 0 | 77.5762 | off_peak | 706.9638 | 0 | 100 | 9.89 | 0 | 90.11 | 374.3309 | 0
8464 | 753.58 | 326.23 | 24.3 | 52.9824 | 52.9824 | 0 | 0 | 8.9371 | 8.9371 | 0 | 0 | 0 | 73.597 | 709.5347 | 0 | 0.05921 | 4.1605 | 0 | 0 | 0 | 52.9824 | off_peak | 700.5976 | 0 | 100 | 7.03 | 0 | 92.97 | 220.436 | 0
8465 | 766.25 | 147.982 | 23.8 | 24.0766 | 24.0766 | 0 | 0 | 0.57721 | 0.57721 | 0 | 0 | 0 | 74.137 | 742.7506 | 0 | 0.05921 | 3.6538 | 0 | 0 | 0 | 24.0766 | off_peak | 742.1734 | 0 | 100 | 3.14 | 0 | 96.86 | 87.9716 | 0
8466 | 772.55 | 8.8304 | 23.2 | 1.4398 | 1.4398 | 0 | 0 | 0.037279 | 0.037279 | 0 | 0 | 0 | 74.1718 | 771.1475 | 0 | 0.05921 | 3.396 | 0 | 0 | 0 | 1.4398 | off_peak | 771.1102 | 0 | 100 | 0.19 | 0 | 99.81 | 4.8895 | 0
8467 | 721.2 | 0 | 23 | 0 | 0 | 0 | 0 | 0 | 0 | 62.443 | 62.443 | 0 | 7.4174 | 658.757 | 0 | 0.088511 | 3.2807 | 0 | 0 | 0 | 0 | on_peak | 658.757 |  |  | 0 | 8.66 | 91.34 | 0 | 0
8468 | 750.52 | 0 | 22.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 750.52 | 0 | 0.088511 | 3.2724 | 0 | 0 | 0 | 0 | on_peak | 750.52 |  |  | 0 | 0 | 100 | 0 | 0
8469 | 718.88 | 0 | 22.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 718.88 | 0 | 0.088511 | 3.3994 | 0 | 0 | 0 | 0 | on_peak | 718.88 |  |  | 0 | 0 | 100 | 0 | 0
8470 | 699.4 | 0 | 22.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 699.4 | 0 | 0.088511 | 3.8113 | 0 | 0 | 0 | 0 | on_peak | 699.4 |  |  | 0 | 0 | 100 | 0 | 0
8471 | 731.41 | 0 | 22.8 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 18.9814 | 743.7724 | 0 | 0.05921 | 4.5738 | 0 | 0 | 0 | 0 | off_peak | 731.41 | 0 | 100 | 0 | 0 | 100 | 0 | 0
8472 | 693.87 | 0 | 22.8 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 30.5453 | 706.2324 | 0 | 0.05921 | 5.3115 | 0 | 0 | 0 | 0 | off_peak | 693.87 | 0 | 100 | 0 | 0 | 100 | 0 | 0
8473 | 681.97 | 0 | 22.9 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 42.1093 | 694.3324 | 0 | 0.05921 | 5.6636 | 0 | 0 | 0 | 0 | off_peak | 681.97 | 0 | 100 | 0 | 0 | 100 | 0 | 0
8474 | 616.5 | 0 | 22.9 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 53.6732 | 628.8624 | 0 | 0.05921 | 5.6345 | 0 | 0 | 0 | 0 | off_peak | 616.5 | 0 | 100 | 0 | 0 | 100 | 0 | 0
8475 | 587.47 | 0 | 22.9 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 65.2371 | 599.8324 | 0 | 0.05921 | 5.5644 | 0 | 0 | 0 | 0 | off_peak | 587.47 | 0 | 100 | 0 | 0 | 100 | 0 | 0
8476 | 576.59 | 0 | 23 | 0 | 0 | 0 | 0 | 8.9371 | 8.9371 | 0 | 0 | 0 | 73.597 | 585.5271 | 0 | 0.05921 | 5.1995 | 0 | 0 | 0 | 0 | off_peak | 576.59 | 0 | 100 | 0 | 0 | 100 | 0 | 0
8477 | 593.86 | 0 | 23 | 0 | 0 | 0 | 0 | 0.57721 | 0.57721 | 0 | 0 | 0 | 74.137 | 594.4372 | 0 | 0.05921 | 4.6838 | 0 | 0 | 0 | 0 | off_peak | 593.86 | 0 | 100 | 0 | 0 | 100 | 0 | 0
8478 | 597.67 | 0 | 23.1 | 0 | 0 | 0 | 0 | 0.037279 | 0.037279 | 0 | 0 | 0 | 74.1718 | 597.7073 | 0 | 0.05921 | 4.1158 | 0 | 0 | 0 | 0 | off_peak | 597.67 | 0 | 100 | 0 | 0 | 100 | 0 | 0
8479 | 684.3 | 0 | 23.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1718 | 684.3 | 0 | 0.088511 | 3.7387 | 0 | 0 | 0 | 0 | on_peak | 684.3 |  |  | 0 | 0 | 100 | 0 | 0
8480 | 712.8 | 45.9741 | 23.7 | 7.4827 | 7.4827 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1718 | 705.3173 | 0 | 0.088511 | 3.5248 | 0 | 0 | 0 | 7.4827 | on_peak | 705.3173 |  |  | 1.05 | 0 | 98.95 | 26.3746 | 0
8481 | 715.58 | 197.932 | 24.2 | 32.1573 | 32.1573 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1718 | 683.4227 | 0 | 0.088511 | 3.3897 | 0 | 0 | 0 | 32.1573 | on_peak | 683.4227 |  |  | 4.49 | 0 | 95.51 | 109.0049 | 0
8482 | 768.15 | 388.422 | 24.7 | 62.9923 | 62.9923 | 0 | 0 | 0 | 0 | 62.443 | 62.443 | 0 | 7.4174 | 642.7146 | 0 | 0.088511 | 3.3152 | 0 | 0 | 0 | 62.9923 | on_peak | 642.7146 |  |  | 8.2 | 8.13 | 83.67 | 208.8301 | 0
8483 | 712.67 | 493.909 | 25.2 | 79.9556 | 79.9556 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 18.9814 | 645.0767 | 0 | 0.05921 | 3.3222 | 0 | 0 | 0 | 79.9556 | off_peak | 632.7144 | 0 | 100 | 11.22 | 0 | 88.78 | 265.6248 | 0
8484 | 748.16 | 403.169 | 25.5 | 65.1958 | 65.1958 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 30.5453 | 695.3266 | 0 | 0.05921 | 3.6368 | 0 | 0 | 0 | 65.1958 | off_peak | 682.9642 | 0 | 100 | 8.71 | 0 | 91.29 | 237.1073 | 0
8485 | 737.23 | 345.093 | 25.6 | 55.7843 | 55.7843 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 42.1093 | 693.8081 | 0 | 0.05921 | 4.3232 | 0 | 0 | 0 | 55.7843 | off_peak | 681.4457 | 0 | 100 | 7.57 | 0 | 92.43 | 241.1682 | 0
8486 | 762.13 | 346.639 | 25.5 | 56.0544 | 56.0544 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 53.6732 | 718.4379 | 0 | 0.05921 | 4.7585 | 0 | 0 | 0 | 56.0544 | off_peak | 706.0756 | 0 | 100 | 7.35 | 0 | 92.65 | 266.7348 | 0
8487 | 771.07 | 152.202 | 25.1 | 24.6478 | 24.6478 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 65.2371 | 758.7845 | 0 | 0.05921 | 4.6184 | 0 | 0 | 0 | 24.6478 | off_peak | 746.4222 | 0 | 100 | 3.2 | 0 | 96.8 | 113.8338 | 0
8488 | 766.26 | 64.3763 | 24.3 | 10.4552 | 10.4552 | 0 | 0 | 8.9371 | 8.9371 | 0 | 0 | 0 | 73.597 | 764.7419 | 0 | 0.05921 | 4.3354 | 0 | 0 | 0 | 10.4552 | off_peak | 755.8048 | 0 | 100 | 1.36 | 0 | 98.64 | 45.3278 | 0
8489 | 752.65 | 24.7 | 23 | 4.0302 | 4.0302 | 0 | 0 | 0.57721 | 0.57721 | 0 | 0 | 0 | 74.137 | 749.197 | 0 | 0.05921 | 4.1307 | 0 | 0 | 0 | 4.0302 | off_peak | 748.6198 | 0 | 100 | 0.54 | 0 | 99.46 | 16.6476 | 0
8490 | 778.96 | 2.85 | 21.5 | 0.46752 | 0.46752 | 0 | 0 | 0.037279 | 0.037279 | 0 | 0 | 0 | 74.1718 | 778.5298 | 0 | 0.05921 | 3.9385 | 0 | 0 | 0 | 0.46752 | off_peak | 778.4925 | 0 | 100 | 0.06 | 0 | 99.94 | 1.8413 | 0
8491 | 765.34 | 0 | 20.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1718 | 765.34 | 0 | 0.088511 | 3.8271 | 0 | 0 | 0 | 0 | on_peak | 765.34 |  |  | 0 | 0 | 100 | 0 | 0
8492 | 741.92 | 0 | 19.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1718 | 741.92 | 0 | 0.088511 | 3.9046 | 0 | 0 | 0 | 0 | on_peak | 741.92 |  |  | 0 | 0 | 100 | 0 | 0
8493 | 754.98 | 0 | 18.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1718 | 754.98 | 0 | 0.088511 | 4.007 | 0 | 0 | 0 | 0 | on_peak | 754.98 |  |  | 0 | 0 | 100 | 0 | 0
8494 | 727.4 | 0 | 18.2 | 0 | 0 | 0 | 0 | 0 | 0 | 62.443 | 62.443 | 0 | 7.4174 | 664.957 | 0 | 0.088511 | 4.236 | 0 | 0 | 0 | 0 | on_peak | 664.957 |  |  | 0 | 8.58 | 91.42 | 0 | 0
8495 | 735.14 | 0 | 17.4 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 18.9814 | 747.5024 | 0 | 0.05921 | 4.5118 | 0 | 0 | 0 | 0 | off_peak | 735.14 | 0 | 100 | 0 | 0 | 100 | 0 | 0
8496 | 709.56 | 0 | 16.6 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 30.5453 | 721.9224 | 0 | 0.05921 | 4.9304 | 0 | 0 | 0 | 0 | off_peak | 709.56 | 0 | 100 | 0 | 0 | 100 | 0 | 0
8497 | 698.45 | 0 | 16 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 42.1093 | 710.8124 | 0 | 0.05921 | 5.2043 | 0 | 0 | 0 | 0 | off_peak | 698.45 | 0 | 100 | 0 | 0 | 100 | 0 | 0
8498 | 660.19 | 0 | 15.5 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 53.6732 | 672.5524 | 0 | 0.05921 | 5.1898 | 0 | 0 | 0 | 0 | off_peak | 660.19 | 0 | 100 | 0 | 0 | 100 | 0 | 0
8499 | 610.68 | 0 | 15.2 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 65.2371 | 623.0424 | 0 | 0.05921 | 5.0406 | 0 | 0 | 0 | 0 | off_peak | 610.68 | 0 | 100 | 0 | 0 | 100 | 0 | 0
8500 | 590.59 | 0 | 15 | 0 | 0 | 0 | 0 | 8.9371 | 8.9371 | 0 | 0 | 0 | 73.597 | 599.5271 | 0 | 0.05921 | 4.7584 | 0 | 0 | 0 | 0 | off_peak | 590.59 | 0 | 100 | 0 | 0 | 100 | 0 | 0
8501 | 559.93 | 0 | 14.8 | 0 | 0 | 0 | 0 | 0.57721 | 0.57721 | 0 | 0 | 0 | 74.137 | 560.5072 | 0 | 0.05921 | 4.3165 | 0 | 0 | 0 | 0 | off_peak | 559.93 | 0 | 100 | 0 | 0 | 100 | 0 | 0
8502 | 662.87 | 0 | 14.7 | 0 | 0 | 0 | 0 | 0.037279 | 0.037279 | 0 | 0 | 0 | 74.1718 | 662.9073 | 0 | 0.05921 | 3.8197 | 0 | 0 | 0 | 0 | off_peak | 662.87 | 0 | 100 | 0 | 0 | 100 | 0 | 0
8503 | 717.73 | 0 | 14.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1718 | 717.73 | 0 | 0.088511 | 3.3563 | 0 | 0 | 0 | 0 | on_peak | 717.73 |  |  | 0 | 0 | 100 | 0 | 0
8504 | 769.99 | 38.0015 | 15.2 | 6.3734 | 6.3734 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1718 | 763.6166 | 0 | 0.088511 | 3.163 | 0 | 0 | 0 | 6.3734 | on_peak | 763.6166 |  |  | 0.83 | 0 | 99.17 | 20.1594 | 0
8505 | 769.86 | 184.055 | 16.2 | 30.7615 | 30.7615 | 0 | 0 | 0 | 0 | 62.443 | 62.443 | 0 | 7.4174 | 676.6554 | 0 | 0.088511 | 3.0482 | 0 | 0 | 0 | 30.7615 | on_peak | 676.6554 |  |  | 4 | 8.11 | 87.89 | 93.7663 | 0
8506 | 741.12 | 318.316 | 17.4 | 52.9781 | 52.9781 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 688.1419 | 0 | 0.088511 | 3.0268 | 0 | 0 | 0 | 52.9781 | on_peak | 688.1419 |  |  | 7.15 | 0 | 92.85 | 160.353 | 0
8507 | 729.85 | 429.223 | 18.7 | 71.1112 | 71.1112 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 18.9814 | 671.1012 | 0 | 0.05921 | 3.1113 | 0 | 0 | 0 | 71.1112 | off_peak | 658.7388 | 0 | 100 | 9.74 | 0 | 90.26 | 221.2476 | 0
8508 | 827.35 | 416.319 | 19.7 | 68.7305 | 68.7305 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 30.5453 | 770.9819 | 0 | 0.05921 | 3.4409 | 0 | 0 | 0 | 68.7305 | off_peak | 758.6195 | 0 | 100 | 8.31 | 0 | 91.69 | 236.4931 | 0
8509 | 741.28 | 338.611 | 20.5 | 55.7436 | 55.7436 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 42.1093 | 697.8987 | 0 | 0.05921 | 4.0517 | 0 | 0 | 0 | 55.7436 | off_peak | 685.5364 | 0 | 100 | 7.52 | 0 | 92.48 | 225.8541 | 0
8510 | 784.86 | 316.959 | 21 | 52.0868 | 52.0868 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 53.6732 | 745.1356 | 0 | 0.05921 | 4.396 | 0 | 0 | 0 | 52.0868 | off_peak | 732.7732 | 0 | 100 | 6.64 | 0 | 93.36 | 228.9729 | 0
8511 | 817.06 | 204.575 | 21.3 | 33.5826 | 33.5826 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 65.2371 | 795.8398 | 0 | 0.05921 | 4.2758 | 0 | 0 | 0 | 33.5826 | off_peak | 783.4774 | 0 | 100 | 4.11 | 0 | 95.89 | 143.5912 | 0
8512 | 790.12 | 208.2 | 21.3 | 34.1777 | 34.1777 | 0 | 0 | 8.9371 | 8.9371 | 0 | 0 | 0 | 73.597 | 764.8794 | 0 | 0.05921 | 3.8994 | 0 | 0 | 0 | 34.1777 | off_peak | 755.9423 | 0 | 100 | 4.33 | 0 | 95.67 | 133.2732 | 0
8513 | 748.89 | 68.5046 | 20.8 | 11.2655 | 10.6883 | 0 | 0.57721 | 0.57721 | 0 | 0 | 0 | 0 | 74.137 | 738.2017 | 0 | 0.05921 | 3.6156 | 0 | 0 | 0.53993 | 10.6883 | off_peak | 738.2017 | 100 | 0 | 1.43 | 0 | 98.57 | 38.6451 | 0
8514 | 749.02 | 6.65 | 20.1 | 1.0963 | 1.059 | 0 | 0.037279 | 0.037279 | 0 | 0 | 0 | 0 | 74.1718 | 747.961 | 0 | 0.05921 | 3.3977 | 0 | 0 | 0.5748 | 1.059 | off_peak | 747.961 | 100 | 0 | 0.14 | 0 | 99.86 | 3.5982 | 0
8515 | 751.85 | 0 | 19.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1718 | 751.85 | 0 | 0.088511 | 3.3677 | 0 | 0 | 0.5748 | 0 | on_peak | 751.85 |  |  | 0 | 0 | 100 | 0 | 0
8516 | 729.48 | 0 | 19.8 | 0 | 0 | 0 | 0 | 0 | 0 | 62.443 | 62.443 | 0 | 7.4174 | 667.037 | 0 | 0.088511 | 3.3428 | 0.53768 | 0 | 0 | 0.53768 | on_peak | 667.037 |  |  | 0 | 8.56 | 91.44 | 1.7973 | 0
8517 | 726.04 | 0 | 19.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 726.04 | 0 | 0.088511 | 3.4781 | 0 | 0 | 0 | 0 | on_peak | 726.04 |  |  | 0 | 0 | 100 | 0 | 0
8518 | 683.02 | 0 | 19.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 683.02 | 0 | 0.088511 | 3.8289 | 0 | 0 | 0 | 0 | on_peak | 683.02 |  |  | 0 | 0 | 100 | 0 | 0
8519 | 677.5 | 0 | 19.7 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 18.9814 | 689.8624 | 0 | 0.05921 | 4.3679 | 0 | 0 | 0 | 0 | off_peak | 677.5 | 0 | 100 | 0 | 0 | 100 | 0 | 0
8520 | 685.72 | 0 | 19.7 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 30.5453 | 698.0824 | 0 | 0.05921 | 4.8364 | 0 | 0 | 0 | 0 | off_peak | 685.72 | 0 | 100 | 0 | 0 | 100 | 0 | 0
8521 | 658.15 | 0 | 19.7 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 42.1093 | 670.5124 | 0 | 0.05921 | 5.0764 | 0 | 0 | 0 | 0 | off_peak | 658.15 | 0 | 100 | 0 | 0 | 100 | 0 | 0
8522 | 621.43 | 0 | 19.7 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 53.6732 | 633.7924 | 0 | 0.05921 | 4.9542 | 0 | 0 | 0 | 0 | off_peak | 621.43 | 0 | 100 | 0 | 0 | 100 | 0 | 0
8523 | 574.6 | 0 | 19.8 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 65.2371 | 586.9624 | 0 | 0.05921 | 4.7953 | 0 | 0 | 0 | 0 | off_peak | 574.6 | 0 | 100 | 0 | 0 | 100 | 0 | 0
8524 | 566.01 | 0 | 19.8 | 0 | 0 | 0 | 0 | 8.9371 | 8.9371 | 0 | 0 | 0 | 73.597 | 574.9471 | 0 | 0.05921 | 4.5127 | 0 | 0 | 0 | 0 | off_peak | 566.01 | 0 | 100 | 0 | 0 | 100 | 0 | 0
8525 | 581.15 | 0 | 19.8 | 0 | 0 | 0 | 0 | 0.57721 | 0.57721 | 0 | 0 | 0 | 74.137 | 581.7272 | 0 | 0.05921 | 4.1446 | 0 | 0 | 0 | 0 | off_peak | 581.15 | 0 | 100 | 0 | 0 | 100 | 0 | 0
8526 | 664.17 | 0 | 19.8 | 0 | 0 | 0 | 0 | 0.037279 | 0.037279 | 0 | 0 | 0 | 74.1718 | 664.2073 | 0 | 0.05921 | 3.6803 | 0 | 0 | 0 | 0 | off_peak | 664.17 | 0 | 100 | 0 | 0 | 100 | 0 | 0
8527 | 791.26 | 0 | 19.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1718 | 791.26 | 0 | 0.088511 | 3.2402 | 0 | 0 | 0 | 0 | on_peak | 791.26 |  |  | 0 | 0 | 100 | 0 | 0
8528 | 767.19 | 45.6645 | 20 | 7.5308 | 7.5308 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1718 | 759.6592 | 0 | 0.088511 | 3.0015 | 0 | 0 | 0 | 7.5308 | on_peak | 759.6592 |  |  | 0.98 | 0 | 99.02 | 22.6035 | 0
8529 | 778.33 | 207.846 | 20.6 | 34.2044 | 34.2044 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1718 | 744.1256 | 0 | 0.088511 | 2.8568 | 0 | 0 | 0 | 34.2044 | on_peak | 744.1256 |  |  | 4.39 | 0 | 95.61 | 97.7166 | 0
8530 | 730.38 | 276.923 | 21.3 | 45.4591 | 45.4591 | 0 | 0 | 0 | 0 | 62.443 | 62.443 | 0 | 7.4174 | 622.4779 | 0 | 0.088511 | 2.8208 | 0 | 0 | 0 | 45.4591 | on_peak | 622.4779 |  |  | 6.22 | 8.55 | 85.23 | 128.2295 | 0
8531 | 749.63 | 516.74 | 22 | 84.616 | 84.616 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 18.9814 | 677.3764 | 0 | 0.05921 | 2.8869 | 0 | 0 | 0 | 84.616 | off_peak | 665.014 | 0 | 100 | 11.29 | 0 | 88.71 | 244.2803 | 0
8532 | 772.78 | 599.927 | 22.4 | 98.0979 | 98.0979 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 30.5453 | 687.0445 | 0 | 0.05921 | 3.1635 | 0 | 0 | 0 | 98.0979 | off_peak | 674.6821 | 0 | 100 | 12.69 | 0 | 87.31 | 310.337 | 0
8533 | 799.37 | 493.484 | 22.7 | 80.6063 | 80.6063 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 42.1093 | 731.126 | 0 | 0.05921 | 3.5907 | 0 | 0 | 0 | 80.6063 | off_peak | 718.7637 | 0 | 100 | 10.08 | 0 | 89.92 | 289.4356 | 0
8534 | 721.3 | 429.983 | 22.9 | 70.1839 | 70.1839 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 53.6732 | 663.4785 | 0 | 0.05921 | 4.0108 | 0 | 0 | 0 | 70.1839 | off_peak | 651.1161 | 0 | 100 | 9.73 | 0 | 90.27 | 281.4916 | 0
8535 | 719.63 | 441.895 | 22.9 | 72.1282 | 72.1282 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 65.2371 | 659.8642 | 0 | 0.05921 | 4.2209 | 0 | 0 | 0 | 72.1282 | off_peak | 647.5018 | 0 | 100 | 10.02 | 0 | 89.98 | 304.4463 | 0
8536 | 666.62 | 290.513 | 22.8 | 47.4358 | 47.4358 | 0 | 0 | 8.9371 | 8.9371 | 0 | 0 | 0 | 73.597 | 628.1213 | 0 | 0.05921 | 4.1194 | 0 | 0 | 0 | 47.4358 | off_peak | 619.1842 | 0 | 100 | 7.12 | 0 | 92.88 | 195.409 | 0
8537 | 665.64 | 85.3157 | 22.3 | 13.9555 | 13.9555 | 0 | 0 | 0.57721 | 0.57721 | 0 | 0 | 0 | 74.137 | 652.2617 | 0 | 0.05921 | 3.9867 | 0 | 0 | 0 | 13.9555 | off_peak | 651.6845 | 0 | 100 | 2.1 | 0 | 97.9 | 55.6359 | 0
8538 | 642.95 | 6.65 | 21.6 | 1.0905 | 1.0532 | 0 | 0.037279 | 0.037279 | 0 | 0 | 0 | 0 | 74.1718 | 641.8968 | 0 | 0.05921 | 3.7653 | 0 | 0 | 0.034872 | 1.0532 | off_peak | 641.8968 | 100 | 0 | 0.16 | 0 | 99.84 | 3.9656 | 0
8539 | 599.02 | 0 | 21.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1718 | 599.02 | 0 | 0.088511 | 3.6184 | 0 | 0 | 0.034872 | 0 | on_peak | 599.02 |  |  | 0 | 0 | 100 | 0 | 0
8540 | 606.31 | 0 | 21.1 | 0 | 0 | 0 | 0 | 0 | 0 | 62.443 | 62.443 | 0 | 7.4174 | 543.867 | 0 | 0.088511 | 3.7236 | 0.032619 | 0 | 0 | 0.032619 | on_peak | 543.867 |  |  | 0 | 10.3 | 89.7 | 0.12146 | 0
8541 | 568.33 | 0 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 568.33 | 0 | 0.088511 | 3.9149 | 0 | 0 | 0 | 0 | on_peak | 568.33 |  |  | 0 | 0 | 100 | 0 | 0
8542 | 601.42 | 0 | 20.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 601.42 | 0 | 0.088511 | 4.0034 | 0 | 0 | 0 | 0 | on_peak | 601.42 |  |  | 0 | 0 | 100 | 0 | 0
8543 | 594.09 | 0 | 20.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 594.09 | 0 | 0.05921 | 4.2138 | 0 | 0 | 0 | 0 | off_peak | 594.09 |  |  | 0 | 0 | 100 | 0 | 0
8544 | 593.75 | 0 | 20.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 593.75 | 0 | 0.05921 | 4.7114 | 0 | 0 | 0 | 0 | off_peak | 593.75 |  |  | 0 | 0 | 100 | 0 | 0
8545 | 594.81 | 0 | 20.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 594.81 | 0 | 0.05921 | 4.8951 | 0 | 0 | 0 | 0 | off_peak | 594.81 |  |  | 0 | 0 | 100 | 0 | 0
8546 | 554.61 | 0 | 20.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 554.61 | 0 | 0.05921 | 4.6992 | 0 | 0 | 0 | 0 | off_peak | 554.61 |  |  | 0 | 0 | 100 | 0 | 0
8547 | 567.3 | 0 | 20.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 567.3 | 0 | 0.05921 | 4.5358 | 0 | 0 | 0 | 0 | off_peak | 567.3 |  |  | 0 | 0 | 100 | 0 | 0
8548 | 611.83 | 0 | 20.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 611.83 | 0 | 0.05921 | 4.2694 | 0 | 0 | 0 | 0 | off_peak | 611.83 |  |  | 0 | 0 | 100 | 0 | 0
8549 | 587.22 | 0 | 20.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 587.22 | 0 | 0.05921 | 3.9652 | 0 | 0 | 0 | 0 | off_peak | 587.22 |  |  | 0 | 0 | 100 | 0 | 0
8550 | 699.87 | 0 | 20.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 699.87 | 0 | 0.05921 | 3.5827 | 0 | 0 | 0 | 0 | off_peak | 699.87 |  |  | 0 | 0 | 100 | 0 | 0
8551 | 781.15 | 0 | 20.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 781.15 | 0 | 0.05921 | 3.122 | 0 | 0 | 0 | 0 | off_peak | 781.15 |  |  | 0 | 0 | 100 | 0 | 0
8552 | 775.11 | 12.35 | 21.3 | 2.0273 | 2.0273 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 773.0827 | 0 | 0.05921 | 2.8103 | 0 | 0 | 0 | 2.0273 | off_peak | 773.0827 |  |  | 0.26 | 0 | 99.74 | 5.6974 | 0
8553 | 759.25 | 14.25 | 22.2 | 2.3318 | 2.3318 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 756.9182 | 0 | 0.05921 | 2.6416 | 0 | 0 | 0 | 2.3318 | off_peak | 756.9182 |  |  | 0.31 | 0 | 99.69 | 6.1596 | 0
8554 | 792.12 | 159.27 | 22.8 | 26.0061 | 26.0061 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 766.1139 | 0 | 0.05921 | 2.5647 | 0 | 0 | 0 | 26.0061 | off_peak | 766.1139 |  |  | 3.28 | 0 | 96.72 | 66.6967 | 0
8555 | 724.31 | 185.979 | 23.3 | 30.313 | 30.313 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 693.997 | 0 | 0.05921 | 2.5786 | 0 | 0 | 0 | 30.313 | off_peak | 693.997 |  |  | 4.19 | 0 | 95.81 | 78.1645 | 0
8556 | 758.92 | 252.07 | 23.7 | 41.0264 | 41.0264 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 717.8936 | 0 | 0.05921 | 2.6985 | 0 | 0 | 0 | 41.0264 | off_peak | 717.8936 |  |  | 5.41 | 0 | 94.59 | 110.7095 | 0
8557 | 731.25 | 558.873 | 23.9 | 90.896 | 90.896 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 640.354 | 0 | 0.05921 | 2.9679 | 0 | 0 | 0 | 90.896 | off_peak | 640.354 |  |  | 12.43 | 0 | 87.57 | 269.7675 | 0
8558 | 700.77 | 559.217 | 24 | 90.9193 | 90.9193 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 609.8507 | 0 | 0.05921 | 3.3168 | 0 | 0 | 0 | 90.9193 | off_peak | 609.8507 |  |  | 12.97 | 0 | 87.03 | 301.5621 | 0
8559 | 700.98 | 415.303 | 23.9 | 67.5455 | 67.5455 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 633.4345 | 0 | 0.05921 | 3.521 | 0 | 0 | 0 | 67.5455 | off_peak | 633.4345 |  |  | 9.64 | 0 | 90.36 | 237.8297 | 0
8560 | 705.85 | 213.722 | 23.7 | 34.785 | 34.785 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 671.065 | 0 | 0.05921 | 3.2892 | 0 | 0 | 0 | 34.785 | off_peak | 671.065 |  |  | 4.93 | 0 | 95.07 | 114.4164 | 0
8561 | 671.6 | 138.793 | 23.2 | 22.6302 | 22.6302 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 648.9698 | 0 | 0.05921 | 3.1578 | 0 | 0 | 0 | 22.6302 | off_peak | 648.9698 |  |  | 3.37 | 0 | 96.63 | 71.4616 | 0
8562 | 631.77 | 9.1175 | 22.7 | 1.4893 | 1.4893 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 630.2807 | 0 | 0.05921 | 3.2053 | 0 | 0 | 0 | 1.4893 | off_peak | 630.2807 |  |  | 0.24 | 0 | 99.76 | 4.7736 | 0
8563 | 589.46 | 0 | 22.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 589.46 | 0 | 0.05921 | 3.2738 | 0 | 0 | 0 | 0 | off_peak | 589.46 |  |  | 0 | 0 | 100 | 0 | 0
8564 | 569 | 0 | 22.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 569 | 0 | 0.05921 | 3.3146 | 0 | 0 | 0 | 0 | off_peak | 569 |  |  | 0 | 0 | 100 | 0 | 0
8565 | 574.76 | 0 | 22.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 574.76 | 0 | 0.05921 | 3.4839 | 0 | 0 | 0 | 0 | off_peak | 574.76 |  |  | 0 | 0 | 100 | 0 | 0
8566 | 576.89 | 0 | 22.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 576.89 | 0 | 0.05921 | 3.703 | 0 | 0 | 0 | 0 | off_peak | 576.89 |  |  | 0 | 0 | 100 | 0 | 0
8567 | 561.28 | 0 | 23.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 561.28 | 0 | 0.05921 | 4.137 | 0 | 0 | 0 | 0 | off_peak | 561.28 |  |  | 0 | 0 | 100 | 0 | 0
8568 | 561.49 | 0 | 23.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 561.49 | 0 | 0.05921 | 4.6009 | 0 | 0 | 0 | 0 | off_peak | 561.49 |  |  | 0 | 0 | 100 | 0 | 0
8569 | 584.61 | 0 | 23.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 584.61 | 0 | 0.05921 | 4.7682 | 0 | 0 | 0 | 0 | off_peak | 584.61 |  |  | 0 | 0 | 100 | 0 | 0
8570 | 563.91 | 0 | 23.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 563.91 | 0 | 0.05921 | 4.6031 | 0 | 0 | 0 | 0 | off_peak | 563.91 |  |  | 0 | 0 | 100 | 0 | 0
8571 | 538.03 | 0 | 23.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 538.03 | 0 | 0.05921 | 4.3972 | 0 | 0 | 0 | 0 | off_peak | 538.03 |  |  | 0 | 0 | 100 | 0 | 0
8572 | 567.86 | 0 | 23.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 567.86 | 0 | 0.05921 | 4.1831 | 0 | 0 | 0 | 0 | off_peak | 567.86 |  |  | 0 | 0 | 100 | 0 | 0
8573 | 572.18 | 0 | 23.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 572.18 | 0 | 0.05921 | 3.9079 | 0 | 0 | 0 | 0 | off_peak | 572.18 |  |  | 0 | 0 | 100 | 0 | 0
8574 | 650.64 | 0 | 23.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 650.64 | 0 | 0.05921 | 3.4771 | 0 | 0 | 0 | 0 | off_peak | 650.64 |  |  | 0 | 0 | 100 | 0 | 0
8575 | 659.36 | 0 | 23.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 659.36 | 0 | 0.05921 | 3.0981 | 0 | 0 | 0 | 0 | off_peak | 659.36 |  |  | 0 | 0 | 100 | 0 | 0
8576 | 642.03 | 24.68 | 24 | 4.0126 | 4.0126 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 638.0174 | 0 | 0.05921 | 2.8157 | 0 | 0 | 0 | 4.0126 | off_peak | 638.0174 |  |  | 0.62 | 0 | 99.38 | 11.2982 | 0
8577 | 651.96 | 131.018 | 24.3 | 21.2784 | 21.2784 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 630.6816 | 0 | 0.05921 | 2.6187 | 0 | 0 | 0 | 21.2784 | off_peak | 630.6816 |  |  | 3.26 | 0 | 96.74 | 55.7219 | 0
8578 | 679.77 | 198.027 | 24.6 | 32.1266 | 32.1266 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 647.6434 | 0 | 0.05921 | 2.5028 | 0 | 0 | 0 | 32.1266 | off_peak | 647.6434 |  |  | 4.73 | 0 | 95.27 | 80.4057 | 0
8579 | 638.82 | 258.034 | 24.9 | 41.8166 | 41.8166 | 0 | 0 | 8.0737 | 8.0737 | 0 | 0 | 0 | 14.9697 | 605.0772 | 0 | 0.05921 | 2.4699 | 0 | 0 | 0 | 41.8166 | off_peak | 597.0034 | 0 | 100 | 6.55 | 0 | 93.45 | 103.2816 | 0
8580 | 680.05 | 36.1 | 25.3 | 5.8419 | 5.8419 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 26.5336 | 686.5705 | 0 | 0.05921 | 2.5409 | 0 | 0 | 0 | 5.8419 | off_peak | 674.2081 | 0 | 100 | 0.86 | 0 | 99.14 | 14.8435 | 0
8581 | 642.5 | 185.665 | 25.6 | 30.0128 | 30.0128 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 26.5336 | 612.4872 | 0 | 0.05921 | 2.7586 | 0 | 0 | 0 | 30.0128 | off_peak | 612.4872 |  |  | 4.67 | 0 | 95.33 | 82.792 | 0
8582 | 649.36 | 119.19 | 25.8 | 19.2532 | 19.2532 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 26.5336 | 630.1068 | 0 | 0.05921 | 3.1186 | 0 | 0 | 0 | 19.2532 | off_peak | 630.1068 |  |  | 2.96 | 0 | 97.04 | 60.0423 | 0
8583 | 649.89 | 123.146 | 25.7 | 19.8994 | 19.8994 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 26.5336 | 629.9906 | 0 | 0.05921 | 3.5491 | 0 | 0 | 0 | 19.8994 | off_peak | 629.9906 |  |  | 3.06 | 0 | 96.94 | 70.6252 | 0
8584 | 653.49 | 174.461 | 25.5 | 28.2118 | 28.2118 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 26.5336 | 625.2782 | 0 | 0.05921 | 3.7196 | 0 | 0 | 0 | 28.2118 | off_peak | 625.2782 |  |  | 4.32 | 0 | 95.68 | 104.9355 | 0
8585 | 655.99 | 26.6 | 25 | 4.3092 | 4.3092 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 26.5336 | 651.6808 | 0 | 0.05921 | 3.8756 | 0 | 0 | 0 | 4.3092 | off_peak | 651.6808 |  |  | 0.66 | 0 | 99.34 | 16.7008 | 0
8586 | 581.24 | 3.8 | 24.5 | 0.61671 | 0.61671 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 26.5336 | 580.6233 | 0 | 0.05921 | 4.084 | 0 | 0 | 0 | 0.61671 | off_peak | 580.6233 |  |  | 0.11 | 0 | 99.89 | 2.5186 | 0
8587 | 574.35 | 0 | 24.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 26.5336 | 574.35 | 0 | 0.05921 | 4.1689 | 0 | 0 | 0 | 0 | off_peak | 574.35 |  |  | 0 | 0 | 100 | 0 | 0
8588 | 550.61 | 0 | 24.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 26.5336 | 550.61 | 0 | 0.05921 | 4.2855 | 0 | 0 | 0 | 0 | off_peak | 550.61 |  |  | 0 | 0 | 100 | 0 | 0
8589 | 543.32 | 0 | 24.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 26.5336 | 543.32 | 0 | 0.05921 | 4.4956 | 0 | 0 | 0 | 0 | off_peak | 543.32 |  |  | 0 | 0 | 100 | 0 | 0
8590 | 557.24 | 0 | 24.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 26.5336 | 557.24 | 0 | 0.05921 | 4.6316 | 0 | 0 | 0 | 0 | off_peak | 557.24 |  |  | 0 | 0 | 100 | 0 | 0
8591 | 541.81 | 0 | 24.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 26.5336 | 541.81 | 0 | 0.05921 | 4.7886 | 0 | 0 | 0 | 0 | off_peak | 541.81 |  |  | 0 | 0 | 100 | 0 | 0
8592 | 529.56 | 0 | 24.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 26.5336 | 529.56 | 0 | 0.05921 | 4.9272 | 0 | 0 | 0 | 0 | off_peak | 529.56 |  |  | 0 | 0 | 100 | 0 | 0
8593 | 558.34 | 0 | 24.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 26.5336 | 558.34 | 0 | 0.05921 | 4.9579 | 0 | 0 | 0 | 0 | off_peak | 558.34 |  |  | 0 | 0 | 100 | 0 | 0
8594 | 540.44 | 0 | 24.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 26.5336 | 540.44 | 0 | 0.05921 | 4.6036 | 0 | 0 | 0 | 0 | off_peak | 540.44 |  |  | 0 | 0 | 100 | 0 | 0
8595 | 539.47 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 26.5336 | 539.47 | 0 | 0.05921 | 4.3126 | 0 | 0 | 0 | 0 | off_peak | 539.47 |  |  | 0 | 0 | 100 | 0 | 0
8596 | 545.72 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 26.5336 | 545.72 | 0 | 0.05921 | 4.0839 | 0 | 0 | 0 | 0 | off_peak | 545.72 |  |  | 0 | 0 | 100 | 0 | 0
8597 | 571.34 | 0 | 23.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 26.5336 | 571.34 | 0 | 0.05921 | 3.8551 | 0 | 0 | 0 | 0 | off_peak | 571.34 |  |  | 0 | 0 | 100 | 0 | 0
8598 | 683.67 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 26.5336 | 683.67 | 0 | 0.05921 | 3.5646 | 0 | 0 | 0 | 0 | off_peak | 683.67 |  |  | 0 | 0 | 100 | 0 | 0
8599 | 695.35 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 26.5336 | 695.35 | 0 | 0.05921 | 3.1836 | 0 | 0 | 0 | 0 | on_peak | 695.35 |  |  | 0 | 0 | 100 | 0 | 0
8600 | 724.26 | 8.55 | 23.9 | 1.3906 | 1.3906 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 26.5336 | 722.8694 | 0 | 0.05921 | 2.9261 | 0 | 0 | 0 | 1.3906 | on_peak | 722.8694 |  |  | 0.19 | 0 | 99.81 | 4.069 | 0
8601 | 695.4 | 31.8589 | 23.3 | 5.1927 | 5.1927 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 26.5336 | 690.2073 | 0 | 0.05921 | 2.7222 | 0 | 0 | 0 | 5.1927 | on_peak | 690.2073 |  |  | 0.75 | 0 | 99.25 | 14.1354 | 0
8602 | 687.38 | 27.55 | 22.7 | 4.5001 | 4.5001 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 26.5336 | 682.8799 | 0 | 0.05921 | 2.5839 | 0 | 0 | 0 | 4.5001 | on_peak | 682.8799 |  |  | 0.65 | 0 | 99.35 | 11.6275 | 0
8603 | 699.2 | 66.1897 | 22.5 | 10.8192 | 10.8192 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 26.5336 | 688.3808 | 0 | 0.05921 | 2.5416 | 0 | 0 | 0 | 10.8192 | off_peak | 688.3808 |  |  | 1.55 | 0 | 98.45 | 27.4979 | 0
8604 | 654.2 | 88.001 | 22.6 | 14.3793 | 14.3793 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 26.5336 | 639.8207 | 0 | 0.05921 | 2.5866 | 0 | 0 | 0 | 14.3793 | off_peak | 639.8207 |  |  | 2.2 | 0 | 97.8 | 37.1936 | 0
8605 | 680.55 | 168.941 | 22.6 | 27.6049 | 27.6049 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 26.5336 | 652.9451 | 0 | 0.05921 | 2.7514 | 0 | 0 | 0 | 27.6049 | off_peak | 652.9451 |  |  | 4.06 | 0 | 95.94 | 75.952 | 0
8606 | 661.68 | 68.4 | 22.5 | 11.1805 | 11.1805 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 26.5336 | 650.4995 | 0 | 0.05921 | 3.0244 | 0 | 0 | 0 | 11.1805 | off_peak | 650.4995 |  |  | 1.69 | 0 | 98.31 | 33.8148 | 0
8607 | 642.63 | 133.153 | 22.2 | 21.7882 | 21.7882 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 26.5336 | 620.8418 | 0 | 0.05921 | 3.5534 | 0 | 0 | 0 | 21.7882 | off_peak | 620.8418 |  |  | 3.39 | 0 | 96.61 | 77.423 | 0
8608 | 580.32 | 64.3114 | 21.8 | 10.5385 | 10.5385 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 26.5336 | 569.7815 | 0 | 0.05921 | 4.105 | 0 | 0 | 0 | 10.5385 | off_peak | 569.7815 |  |  | 1.82 | 0 | 98.18 | 43.2609 | 0
8609 | 531.83 | 42.4814 | 20.9 | 6.9836 | 6.9836 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 26.5336 | 524.8464 | 0 | 0.05921 | 4.4232 | 0 | 0 | 0 | 6.9836 | off_peak | 524.8464 |  |  | 1.31 | 0 | 98.69 | 30.8896 | 0
8610 | 537.75 | 3.8 | 19.9 | 0.6269 | 0 | 0 | 0.6269 | 0.6269 | 0 | 0 | 0 | 0 | 27.12 | 537.75 | 0 | 0.05921 | 4.5253 | 0 | 0 | 0.58641 | 0 | off_peak | 537.75 | 100 | 0 | 0 | 0 | 100 | 0 | 0
8611 | 537.85 | 0 | 19.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27.12 | 537.85 | 0 | 0.05921 | 4.5839 | 0 | 0 | 0.58641 | 0 | on_peak | 537.85 |  |  | 0 | 0 | 100 | 0 | 0
8612 | 539.32 | 0 | 18.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27.12 | 539.32 | 0 | 0.05921 | 4.5749 | 0 | 0 | 0.58641 | 0 | on_peak | 539.32 |  |  | 0 | 0 | 100 | 0 | 0
8613 | 546.84 | 0 | 17.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27.12 | 546.84 | 0 | 0.05921 | 4.4956 | 0 | 0 | 0.58641 | 0 | on_peak | 546.84 |  |  | 0 | 0 | 100 | 0 | 0
8614 | 525.27 | 0 | 17.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27.12 | 525.27 | 0 | 0.05921 | 4.3641 | 0 | 0 | 0.58641 | 0 | on_peak | 525.27 |  |  | 0 | 0 | 100 | 0 | 0
8615 | 530.31 | 0 | 16.6 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 38.684 | 542.6724 | 0 | 0.05921 | 4.4293 | 0 | 0 | 0.58641 | 0 | off_peak | 530.31 | 0 | 100 | 0 | 0 | 100 | 0 | 0
8616 | 548.28 | 0 | 15.9 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 50.2479 | 560.6424 | 0 | 0.05921 | 4.6348 | 0 | 0 | 0.58641 | 0 | off_peak | 548.28 | 0 | 100 | 0 | 0 | 100 | 0 | 0
8617 | 539.53 | 0 | 15.3 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 61.8119 | 551.8924 | 0 | 0.05921 | 4.6381 | 0 | 0 | 0.58641 | 0 | off_peak | 539.53 | 0 | 100 | 0 | 0 | 100 | 0 | 0
8618 | 526.54 | 0 | 14.7 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 73.3758 | 538.9024 | 0 | 0.05921 | 4.4809 | 0 | 0 | 0.58641 | 0 | off_peak | 526.54 | 0 | 100 | 0 | 0 | 100 | 0 | 0
8619 | 537.87 | 0 | 14.3 | 0 | 0 | 0 | 0 | 0.79843 | 0.79843 | 0 | 0 | 0 | 74.1227 | 538.6684 | 0 | 0.05921 | 4.3593 | 0 | 0 | 0.58641 | 0 | off_peak | 537.87 | 0 | 100 | 0 | 0 | 100 | 0 | 0
8620 | 531.85 | 0 | 14 | 0 | 0 | 0 | 0 | 0.051567 | 0.051567 | 0 | 0 | 0 | 74.1709 | 531.9016 | 0 | 0.05921 | 4.1348 | 0 | 0 | 0.58641 | 0 | off_peak | 531.85 | 0 | 100 | 0 | 0 | 100 | 0 | 0
8621 | 554.17 | 0 | 13.7 | 0 | 0 | 0 | 0 | 0.0033305 | 0.0033305 | 0 | 0 | 0 | 74.174 | 554.1733 | 0 | 0.05921 | 3.8935 | 0 | 0 | 0.58641 | 0 | off_peak | 554.17 | 0 | 100 | 0 | 0 | 100 | 0 | 0
8622 | 647.67 | 0 | 13.5 | 0 | 0 | 0 | 0 | 0.0002151 | 0.0002151 | 0 | 0 | 0 | 74.1742 | 647.6702 | 0 | 0.05921 | 3.5234 | 0 | 0 | 0.58641 | 0 | off_peak | 647.67 | 0 | 100 | 0 | 0 | 100 | 0 | 0
8623 | 710.17 | 0 | 13.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1742 | 710.17 | 0 | 0.088511 | 3.1583 | 0 | 0 | 0.58641 | 0 | on_peak | 710.17 |  |  | 0 | 0 | 100 | 0 | 0
8624 | 688.27 | 5.7 | 13.9 | 0.9603 | 0.9603 | 0 | 0 | 0 | 0 | 0.54854 | 0.54854 | 0 | 73.5878 | 686.7612 | 0 | 0.088511 | 2.8415 | 0.54854 | 0 | 0 | 1.5088 | on_peak | 686.7612 |  |  | 0.14 | 0.08 | 99.78 | 4.2874 | 0
8625 | 786.33 | 16.15 | 14.8 | 2.7124 | 2.7124 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 73.5878 | 783.6176 | 0 | 0.088511 | 2.6591 | 0 | 0 | 0 | 2.7124 | on_peak | 783.6176 |  |  | 0.34 | 0 | 99.66 | 7.2124 | 0
8626 | 771.22 | 14.25 | 15.8 | 2.385 | 2.385 | 0 | 0 | 0 | 0 | 61.8967 | 61.8967 | 0 | 7.4174 | 706.9383 | 0 | 0.088511 | 2.5641 | 0 | 0 | 0 | 2.385 | on_peak | 706.9383 |  |  | 0.31 | 8.03 | 91.66 | 6.1152 | 0
8627 | 758.34 | 62.7 | 17.1 | 10.4463 | 10.4463 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 18.9814 | 760.2561 | 0 | 0.05921 | 2.5655 | 0 | 0 | 0 | 10.4463 | off_peak | 747.8937 | 0 | 100 | 1.38 | 0 | 98.62 | 26.8004 | 0
8628 | 831.17 | 68.4 | 18.2 | 11.3521 | 11.3521 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 30.5453 | 832.1803 | 0 | 0.05921 | 2.7317 | 0 | 0 | 0 | 11.3521 | off_peak | 819.8179 | 0 | 100 | 1.37 | 0 | 98.63 | 31.0107 | 0
8629 | 746.07 | 60.4705 | 19 | 10.0078 | 10.0078 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 42.1093 | 748.4246 | 0 | 0.05921 | 3.0266 | 0 | 0 | 0 | 10.0078 | off_peak | 736.0622 | 0 | 100 | 1.34 | 0 | 98.66 | 30.2892 | 0
8630 | 770.92 | 112.77 | 19.7 | 18.6173 | 18.6173 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 53.6732 | 764.6651 | 0 | 0.05921 | 3.364 | 0 | 0 | 0 | 18.6173 | off_peak | 752.3027 | 0 | 100 | 2.41 | 0 | 97.59 | 62.6284 | 0
8631 | 819.8 | 50.35 | 20 | 8.3035 | 8.3035 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 65.2371 | 823.8589 | 0 | 0.05921 | 3.7634 | 0 | 0 | 0 | 8.3035 | off_peak | 811.4965 | 0 | 100 | 1.01 | 0 | 98.99 | 31.2498 | 0
8632 | 774.96 | 42.1716 | 20 | 6.9548 | 6.9548 | 0 | 0 | 8.9371 | 8.9371 | 0 | 0 | 0 | 73.597 | 776.9423 | 0 | 0.05921 | 4.134 | 0 | 0 | 0 | 6.9548 | off_peak | 768.0052 | 0 | 100 | 0.9 | 0 | 99.1 | 28.7512 | 0
8633 | 719.64 | 21.85 | 19.3 | 3.6123 | 3.0351 | 0 | 0.57721 | 0.57721 | 0 | 0 | 0 | 0 | 74.137 | 716.6049 | 0 | 0.05921 | 4.4081 | 0 | 0 | 0.53993 | 3.0351 | off_peak | 716.6049 | 100 | 0 | 0.42 | 0 | 99.58 | 13.3791 | 0
8634 | 769.69 | 2.85 | 18.6 | 0.47234 | 0.47234 | 0 | 0 | 0.037279 | 0.037279 | 0 | 0 | 0 | 74.1718 | 769.2549 | 0 | 0.05921 | 4.5518 | 0 | 0 | 0.53993 | 0.47234 | off_peak | 769.2177 | 0 | 100 | 0.06 | 0 | 99.94 | 2.15 | 0
8635 | 764.14 | 0 | 18.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1718 | 764.14 | 0 | 0.088511 | 4.6933 | 0 | 0 | 0.53993 | 0 | on_peak | 764.14 |  |  | 0 | 0 | 100 | 0 | 0
8636 | 746.25 | 0 | 17.8 | 0 | 0 | 0 | 0 | 0 | 0 | 61.938 | 61.938 | 0 | 7.9574 | 684.312 | 0 | 0.088511 | 4.7665 | 0 | 0 | 0.53993 | 0 | on_peak | 684.312 |  |  | 0 | 8.3 | 91.7 | 0 | 0
8637 | 715.83 | 0 | 17.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0.50506 | 0.50506 | 0 | 7.4174 | 715.3249 | 0 | 0.088511 | 4.8333 | 0.50506 | 0 | 0 | 0.50506 | on_peak | 715.3249 |  |  | 0 | 0.07 | 99.93 | 2.4411 | 0
8638 | 715.7 | 0 | 17.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 715.7 | 0 | 0.088511 | 5.085 | 0 | 0 | 0 | 0 | on_peak | 715.7 |  |  | 0 | 0 | 100 | 0 | 0
8639 | 693.3 | 0 | 17.4 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 18.9814 | 705.6624 | 0 | 0.05921 | 5.3582 | 0 | 0 | 0 | 0 | off_peak | 693.3 | 0 | 100 | 0 | 0 | 100 | 0 | 0
8640 | 687.27 | 0 | 17.4 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 30.5453 | 699.6324 | 0 | 0.05921 | 5.5237 | 0 | 0 | 0 | 0 | off_peak | 687.27 | 0 | 100 | 0 | 0 | 100 | 0 | 0
8641 | 678.13 | 0 | 17.3 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 42.1093 | 690.4924 | 0 | 0.05921 | 5.6336 | 0 | 0 | 0 | 0 | off_peak | 678.13 | 0 | 100 | 0 | 0 | 100 | 0 | 0
8642 | 603.51 | 0 | 17.3 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 53.6732 | 615.8724 | 0 | 0.05921 | 5.3211 | 0 | 0 | 0 | 0 | off_peak | 603.51 | 0 | 100 | 0 | 0 | 100 | 0 | 0
8643 | 583.59 | 0 | 17.2 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 65.2371 | 595.9524 | 0 | 0.05921 | 4.9667 | 0 | 0 | 0 | 0 | off_peak | 583.59 | 0 | 100 | 0 | 0 | 100 | 0 | 0
8644 | 636.27 | 0 | 17.1 | 0 | 0 | 0 | 0 | 8.9371 | 8.9371 | 0 | 0 | 0 | 73.597 | 645.2071 | 0 | 0.05921 | 4.594 | 0 | 0 | 0 | 0 | off_peak | 636.27 | 0 | 100 | 0 | 0 | 100 | 0 | 0
8645 | 579.19 | 0 | 17 | 0 | 0 | 0 | 0 | 0.57721 | 0.57721 | 0 | 0 | 0 | 74.137 | 579.7672 | 0 | 0.05921 | 4.1814 | 0 | 0 | 0 | 0 | off_peak | 579.19 | 0 | 100 | 0 | 0 | 100 | 0 | 0
8646 | 647.89 | 0 | 17 | 0 | 0 | 0 | 0 | 0.037279 | 0.037279 | 0 | 0 | 0 | 74.1718 | 647.9273 | 0 | 0.05921 | 3.6591 | 0 | 0 | 0 | 0 | off_peak | 647.89 | 0 | 100 | 0 | 0 | 100 | 0 | 0
8647 | 715.26 | 0 | 17.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1718 | 715.26 | 0 | 0.088511 | 3.1794 | 0 | 0 | 0 | 0 | on_peak | 715.26 |  |  | 0 | 0 | 100 | 0 | 0
8648 | 730.65 | 8.55 | 17.7 | 1.4215 | 1.4215 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1718 | 729.2285 | 0 | 0.088511 | 2.8302 | 0 | 0 | 0 | 1.4215 | on_peak | 729.2285 |  |  | 0.19 | 0 | 99.81 | 4.0231 | 0
8649 | 762.51 | 67.3003 | 18.6 | 11.1538 | 11.1538 | 0 | 0 | 0 | 0 | 62.443 | 62.443 | 0 | 7.4174 | 688.9131 | 0 | 0.088511 | 2.6105 | 0 | 0 | 0 | 11.1538 | on_peak | 688.9131 |  |  | 1.46 | 8.19 | 90.35 | 29.1173 | 0
8650 | 736.23 | 69.0906 | 19.5 | 11.4143 | 11.4143 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 724.8157 | 0 | 0.088511 | 2.5236 | 0 | 0 | 0 | 11.4143 | on_peak | 724.8157 |  |  | 1.55 | 0 | 98.45 | 28.8046 | 0
8651 | 695.04 | 163.642 | 20.6 | 26.9299 | 26.9299 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 18.9814 | 680.4725 | 0 | 0.05921 | 2.5766 | 0 | 0 | 0 | 26.9299 | off_peak | 668.1101 | 0 | 100 | 3.87 | 0 | 96.13 | 69.387 | 0
8652 | 800.36 | 185.428 | 21.4 | 30.4286 | 30.4286 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 30.5453 | 782.2937 | 0 | 0.05921 | 2.7715 | 0 | 0 | 0 | 30.4286 | off_peak | 769.9314 | 0 | 100 | 3.8 | 0 | 96.2 | 84.3323 | 0
8653 | 743.14 | 107.313 | 21.8 | 17.585 | 17.585 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 42.1093 | 737.9174 | 0 | 0.05921 | 3.0929 | 0 | 0 | 0 | 17.585 | off_peak | 725.555 | 0 | 100 | 2.37 | 0 | 97.63 | 54.3883 | 0
8654 | 738.01 | 234.738 | 22 | 38.4383 | 38.4383 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 53.6732 | 711.9341 | 0 | 0.05921 | 3.4148 | 0 | 0 | 0 | 38.4383 | off_peak | 699.5717 | 0 | 100 | 5.21 | 0 | 94.79 | 131.2603 | 0
8655 | 791.48 | 450.586 | 22 | 73.7833 | 73.7833 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 65.2371 | 730.0591 | 0 | 0.05921 | 3.6761 | 0 | 0 | 0 | 73.7833 | off_peak | 717.6967 | 0 | 100 | 9.32 | 0 | 90.68 | 271.2373 | 0
8656 | 776.43 | 346.104 | 21.9 | 56.6946 | 56.6946 | 0 | 0 | 8.9371 | 8.9371 | 0 | 0 | 0 | 73.597 | 728.6725 | 0 | 0.05921 | 3.6575 | 0 | 0 | 0 | 56.6946 | off_peak | 719.7354 | 0 | 100 | 7.3 | 0 | 92.7 | 207.3592 | 0
8657 | 751.45 | 168.697 | 21.3 | 27.6929 | 27.6929 | 0 | 0 | 0.57721 | 0.57721 | 0 | 0 | 0 | 74.137 | 724.3343 | 0 | 0.05921 | 3.5188 | 0 | 0 | 0 | 27.6929 | off_peak | 723.7571 | 0 | 100 | 3.69 | 0 | 96.31 | 97.4468 | 0
8658 | 764.03 | 15.284 | 20.7 | 2.5143 | 2.5143 | 0 | 0 | 0.037279 | 0.037279 | 0 | 0 | 0 | 74.1718 | 761.5529 | 0 | 0.05921 | 3.4698 | 0 | 0 | 0 | 2.5143 | off_peak | 761.5157 | 0 | 100 | 0.33 | 0 | 99.67 | 8.7241 | 0
8659 | 710.47 | 0 | 20.5 | 0 | 0 | 0 | 0 | 0 | 0 | 62.443 | 62.443 | 0 | 7.4174 | 648.027 | 0 | 0.088511 | 3.5255 | 0 | 0 | 0 | 0 | on_peak | 648.027 |  |  | 0 | 8.79 | 91.21 | 0 | 0
8660 | 719.39 | 0 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 719.39 | 0 | 0.088511 | 3.7379 | 0 | 0 | 0 | 0 | on_peak | 719.39 |  |  | 0 | 0 | 100 | 0 | 0
8661 | 735.04 | 0 | 19.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 735.04 | 0 | 0.088511 | 4.0818 | 0 | 0 | 0 | 0 | on_peak | 735.04 |  |  | 0 | 0 | 100 | 0 | 0
8662 | 709.88 | 0 | 18.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 709.88 | 0 | 0.088511 | 4.4639 | 0 | 0 | 0 | 0 | on_peak | 709.88 |  |  | 0 | 0 | 100 | 0 | 0
8663 | 712.44 | 0 | 18.4 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 18.9814 | 724.8024 | 0 | 0.05921 | 4.932 | 0 | 0 | 0 | 0 | off_peak | 712.44 | 0 | 100 | 0 | 0 | 100 | 0 | 0
8664 | 718.62 | 0 | 18 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 30.5453 | 730.9824 | 0 | 0.05921 | 5.133 | 0 | 0 | 0 | 0 | off_peak | 718.62 | 0 | 100 | 0 | 0 | 100 | 0 | 0
8665 | 677.34 | 0 | 17.6 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 42.1093 | 689.7024 | 0 | 0.05921 | 5.2956 | 0 | 0 | 0 | 0 | off_peak | 677.34 | 0 | 100 | 0 | 0 | 100 | 0 | 0
8666 | 618.4 | 0 | 17.1 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 53.6732 | 630.7624 | 0 | 0.05921 | 4.9943 | 0 | 0 | 0 | 0 | off_peak | 618.4 | 0 | 100 | 0 | 0 | 100 | 0 | 0
8667 | 583.5 | 0 | 16.5 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 65.2371 | 595.8624 | 0 | 0.05921 | 4.6925 | 0 | 0 | 0 | 0 | off_peak | 583.5 | 0 | 100 | 0 | 0 | 100 | 0 | 0
8668 | 558.37 | 0 | 15.9 | 0 | 0 | 0 | 0 | 8.9371 | 8.9371 | 0 | 0 | 0 | 73.597 | 567.3071 | 0 | 0.05921 | 4.3559 | 0 | 0 | 0 | 0 | off_peak | 558.37 | 0 | 100 | 0 | 0 | 100 | 0 | 0
8669 | 566.42 | 0 | 15.5 | 0 | 0 | 0 | 0 | 0.57721 | 0.57721 | 0 | 0 | 0 | 74.137 | 566.9972 | 0 | 0.05921 | 3.9731 | 0 | 0 | 0 | 0 | off_peak | 566.42 | 0 | 100 | 0 | 0 | 100 | 0 | 0
8670 | 653.74 | 0 | 15.2 | 0 | 0 | 0 | 0 | 0.037279 | 0.037279 | 0 | 0 | 0 | 74.1718 | 653.7773 | 0 | 0.05921 | 3.4651 | 0 | 0 | 0 | 0 | off_peak | 653.74 | 0 | 100 | 0 | 0 | 100 | 0 | 0
8671 | 704.34 | 0 | 15.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1718 | 704.34 | 0 | 0.088511 | 3.0437 | 0 | 0 | 0 | 0 | on_peak | 704.34 |  |  | 0 | 0 | 100 | 0 | 0
8672 | 717.14 | 42.8682 | 15.2 | 7.1897 | 7.1897 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1718 | 709.9503 | 0 | 0.088511 | 2.7198 | 0 | 0 | 0 | 7.1897 | on_peak | 709.9503 |  |  | 1 | 0 | 99 | 19.5546 | 0
8673 | 730.69 | 219.692 | 15.6 | 36.7945 | 36.7945 | 0 | 0 | 0 | 0 | 62.443 | 62.443 | 0 | 7.4174 | 631.4525 | 0 | 0.088511 | 2.5609 | 0 | 0 | 0 | 36.7945 | on_peak | 631.4525 |  |  | 5.04 | 8.55 | 86.42 | 94.2275 | 0
8674 | 745.69 | 398.979 | 16.2 | 66.6822 | 66.6822 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 679.0078 | 0 | 0.088511 | 2.4882 | 0 | 0 | 0 | 66.6822 | on_peak | 679.0078 |  |  | 8.94 | 0 | 91.06 | 165.9158 | 0
8675 | 707.05 | 541.584 | 16.9 | 90.295 | 90.295 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 18.9814 | 629.1174 | 0 | 0.05921 | 2.5444 | 0 | 0 | 0 | 90.295 | off_peak | 616.755 | 0 | 100 | 12.77 | 0 | 87.23 | 229.7451 | 0
8676 | 751.1 | 555.611 | 17.6 | 92.4068 | 92.4068 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 30.5453 | 671.0556 | 0 | 0.05921 | 2.7831 | 0 | 0 | 0 | 92.4068 | off_peak | 658.6932 | 0 | 100 | 12.3 | 0 | 87.7 | 257.181 | 0
8677 | 740.23 | 578.132 | 18.3 | 95.9164 | 95.9164 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 42.1093 | 656.676 | 0 | 0.05921 | 3.1621 | 0 | 0 | 0 | 95.9164 | off_peak | 644.3136 | 0 | 100 | 12.96 | 0 | 87.04 | 303.302 | 0
8678 | 752.86 | 538.85 | 18.7 | 89.2735 | 89.2735 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 53.6732 | 675.9489 | 0 | 0.05921 | 3.6235 | 0 | 0 | 0 | 89.2735 | off_peak | 663.5865 | 0 | 100 | 11.86 | 0 | 88.14 | 323.4846 | 0
8679 | 763.81 | 435.224 | 18.8 | 72.08 | 72.08 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 65.2371 | 704.0924 | 0 | 0.05921 | 4.042 | 0 | 0 | 0 | 72.08 | off_peak | 691.73 | 0 | 100 | 9.44 | 0 | 90.56 | 291.3502 | 0
8680 | 693.08 | 358.797 | 18.7 | 59.4434 | 59.4434 | 0 | 0 | 8.9371 | 8.9371 | 0 | 0 | 0 | 73.597 | 642.5737 | 0 | 0.05921 | 4.2681 | 0 | 0 | 0 | 59.4434 | off_peak | 633.6366 | 0 | 100 | 8.58 | 0 | 91.42 | 253.7117 | 0
8681 | 742.68 | 174.154 | 17.9 | 28.9341 | 28.9341 | 0 | 0 | 0.57721 | 0.57721 | 0 | 0 | 0 | 74.137 | 714.3231 | 0 | 0.05921 | 4.303 | 0 | 0 | 0 | 28.9341 | off_peak | 713.7459 | 0 | 100 | 3.9 | 0 | 96.1 | 124.5038 | 0
8682 | 724.61 | 16.4097 | 17.1 | 2.734 | 2.734 | 0 | 0 | 0.037279 | 0.037279 | 0 | 0 | 0 | 74.1718 | 721.9133 | 0 | 0.05921 | 4.3271 | 0 | 0 | 0 | 2.734 | off_peak | 721.876 | 0 | 100 | 0.38 | 0 | 99.62 | 11.8302 | 0
8683 | 719.28 | 0 | 16.8 | 0 | 0 | 0 | 0 | 0 | 0 | 62.443 | 62.443 | 0 | 7.4174 | 656.837 | 0 | 0.088511 | 4.2035 | 0 | 0 | 0 | 0 | on_peak | 656.837 |  |  | 0 | 8.68 | 91.32 | 0 | 0
8684 | 730.21 | 0 | 16.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 730.21 | 0 | 0.088511 | 3.8683 | 0 | 0 | 0 | 0 | on_peak | 730.21 |  |  | 0 | 0 | 100 | 0 | 0
8685 | 698.44 | 0 | 16.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 698.44 | 0 | 0.088511 | 3.5264 | 0 | 0 | 0 | 0 | on_peak | 698.44 |  |  | 0 | 0 | 100 | 0 | 0
8686 | 708.44 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 708.44 | 0 | 0.088511 | 3.3539 | 0 | 0 | 0 | 0 | on_peak | 708.44 |  |  | 0 | 0 | 100 | 0 | 0
8687 | 692.54 | 0 | 15.8 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 18.9814 | 704.9024 | 0 | 0.05921 | 3.7848 | 0 | 0 | 0 | 0 | off_peak | 692.54 | 0 | 100 | 0 | 0 | 100 | 0 | 0
8688 | 657.56 | 0 | 15.7 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 30.5453 | 669.9224 | 0 | 0.05921 | 4.5259 | 0 | 0 | 0 | 0 | off_peak | 657.56 | 0 | 100 | 0 | 0 | 100 | 0 | 0
8689 | 634.19 | 0 | 15.6 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 42.1093 | 646.5524 | 0 | 0.05921 | 4.8938 | 0 | 0 | 0 | 0 | off_peak | 634.19 | 0 | 100 | 0 | 0 | 100 | 0 | 0
8690 | 602.15 | 0 | 15.5 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 53.6732 | 614.5124 | 0 | 0.05921 | 4.7585 | 0 | 0 | 0 | 0 | off_peak | 602.15 | 0 | 100 | 0 | 0 | 100 | 0 | 0
8691 | 585.92 | 0 | 15.4 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 65.2371 | 598.2824 | 0 | 0.05921 | 4.5308 | 0 | 0 | 0 | 0 | off_peak | 585.92 | 0 | 100 | 0 | 0 | 100 | 0 | 0
8692 | 546.16 | 0 | 15.2 | 0 | 0 | 0 | 0 | 8.9371 | 8.9371 | 0 | 0 | 0 | 73.597 | 555.0971 | 0 | 0.05921 | 4.258 | 0 | 0 | 0 | 0 | off_peak | 546.16 | 0 | 100 | 0 | 0 | 100 | 0 | 0
8693 | 563.06 | 0 | 15 | 0 | 0 | 0 | 0 | 0.57721 | 0.57721 | 0 | 0 | 0 | 74.137 | 563.6372 | 0 | 0.05921 | 3.8566 | 0 | 0 | 0 | 0 | off_peak | 563.06 | 0 | 100 | 0 | 0 | 100 | 0 | 0
8694 | 602.35 | 0 | 14.8 | 0 | 0 | 0 | 0 | 0.037279 | 0.037279 | 0 | 0 | 0 | 74.1718 | 602.3873 | 0 | 0.05921 | 3.3591 | 0 | 0 | 0 | 0 | off_peak | 602.35 | 0 | 100 | 0 | 0 | 100 | 0 | 0
8695 | 617.04 | 0 | 14.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1718 | 617.04 | 0 | 0.088511 | 2.9742 | 0 | 0 | 0 | 0 | on_peak | 617.04 |  |  | 0 | 0 | 100 | 0 | 0
8696 | 683.71 | 35.3961 | 15.3 | 5.9344 | 5.9344 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1718 | 677.7756 | 0 | 0.088511 | 2.7398 | 0 | 0 | 0 | 5.9344 | on_peak | 677.7756 |  |  | 0.87 | 0 | 99.13 | 16.259 | 0
8697 | 676.76 | 204.091 | 16.2 | 34.1102 | 34.1102 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1718 | 642.6498 | 0 | 0.088511 | 2.6086 | 0 | 0 | 0 | 34.1102 | on_peak | 642.6498 |  |  | 5.04 | 0 | 94.96 | 88.9804 | 0
8698 | 688.87 | 377.915 | 17.4 | 62.8973 | 62.8973 | 0 | 0 | 0 | 0 | 62.443 | 62.443 | 0 | 7.4174 | 563.5297 | 0 | 0.088511 | 2.5722 | 0 | 0 | 0 | 62.8973 | on_peak | 563.5297 |  |  | 9.13 | 9.06 | 81.8 | 161.7843 | 0
8699 | 697.28 | 483.258 | 18.6 | 80.0915 | 80.0915 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 18.9814 | 629.5508 | 0 | 0.05921 | 2.6774 | 0 | 0 | 0 | 80.0915 | off_peak | 617.1885 | 0 | 100 | 11.49 | 0 | 88.51 | 214.435 | 0
8700 | 739.08 | 271.926 | 19.6 | 44.9084 | 44.9084 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 30.5453 | 706.534 | 0 | 0.05921 | 2.9836 | 0 | 0 | 0 | 44.9084 | off_peak | 694.1716 | 0 | 100 | 6.08 | 0 | 93.92 | 133.9874 | 0
8701 | 663.47 | 438.856 | 20.2 | 72.3232 | 72.3232 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 42.1093 | 603.5092 | 0 | 0.05921 | 3.3754 | 0 | 0 | 0 | 72.3232 | off_peak | 591.1468 | 0 | 100 | 10.9 | 0 | 89.1 | 244.118 | 0
8702 | 742.08 | 585.573 | 20.6 | 96.3655 | 96.3655 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 53.6732 | 658.0769 | 0 | 0.05921 | 3.8163 | 0 | 0 | 0 | 96.3655 | off_peak | 645.7145 | 0 | 100 | 12.99 | 0 | 87.01 | 367.7603 | 0
8703 | 677.52 | 485.434 | 20.8 | 79.8293 | 79.8293 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 65.2371 | 610.053 | 0 | 0.05921 | 3.7734 | 0 | 0 | 0 | 79.8293 | off_peak | 597.6907 | 0 | 100 | 11.78 | 0 | 88.22 | 301.2313 | 0
8704 | 684.37 | 338.395 | 20.6 | 55.6883 | 55.6883 | 0 | 0 | 8.9371 | 8.9371 | 0 | 0 | 0 | 73.597 | 637.6188 | 0 | 0.05921 | 3.4821 | 0 | 0 | 0 | 55.6883 | off_peak | 628.6817 | 0 | 100 | 8.14 | 0 | 91.86 | 193.9117 | 0
8705 | 700.48 | 153.211 | 19.9 | 25.2759 | 25.2759 | 0 | 0 | 0.57721 | 0.57721 | 0 | 0 | 0 | 74.137 | 675.7813 | 0 | 0.05921 | 3.2712 | 0 | 0 | 0 | 25.2759 | off_peak | 675.2041 | 0 | 100 | 3.61 | 0 | 96.39 | 82.6819 | 0
8706 | 649.31 | 14.8438 | 19 | 2.4566 | 2.4566 | 0 | 0 | 0.037279 | 0.037279 | 0 | 0 | 0 | 74.1718 | 646.8906 | 0 | 0.05921 | 3.0914 | 0 | 0 | 0 | 2.4566 | off_peak | 646.8534 | 0 | 100 | 0.38 | 0 | 99.62 | 7.5944 | 0
8707 | 636.94 | 0 | 18.7 | 0 | 0 | 0 | 0 | 0 | 0 | 62.443 | 62.443 | 0 | 7.4174 | 574.497 | 0 | 0.088511 | 2.9989 | 0 | 0 | 0 | 0 | on_peak | 574.497 |  |  | 0 | 9.8 | 90.2 | 0 | 0
8708 | 644.65 | 0 | 18.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 644.65 | 0 | 0.088511 | 2.9127 | 0 | 0 | 0 | 0 | on_peak | 644.65 |  |  | 0 | 0 | 100 | 0 | 0
8709 | 633.46 | 0 | 18.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 633.46 | 0 | 0.088511 | 3.0115 | 0 | 0 | 0 | 0 | on_peak | 633.46 |  |  | 0 | 0 | 100 | 0 | 0
8710 | 608.6 | 0 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 608.6 | 0 | 0.088511 | 3.3154 | 0 | 0 | 0 | 0 | on_peak | 608.6 |  |  | 0 | 0 | 100 | 0 | 0
8711 | 593.73 | 0 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 593.73 | 0 | 0.05921 | 3.9068 | 0 | 0 | 0 | 0 | off_peak | 593.73 |  |  | 0 | 0 | 100 | 0 | 0
8712 | 598.17 | 0 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 598.17 | 0 | 0.05921 | 4.6093 | 0 | 0 | 0 | 0 | off_peak | 598.17 |  |  | 0 | 0 | 100 | 0 | 0
8713 | 587.35 | 0 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 587.35 | 0 | 0.05921 | 4.9048 | 0 | 0 | 0 | 0 | off_peak | 587.35 |  |  | 0 | 0 | 100 | 0 | 0
8714 | 515.41 | 0 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 515.41 | 0 | 0.05921 | 4.7663 | 0 | 0 | 0 | 0 | off_peak | 515.41 |  |  | 0 | 0 | 100 | 0 | 0
8715 | 469.67 | 0 | 17.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 469.67 | 0 | 0.05921 | 4.5975 | 0 | 0 | 0 | 0 | off_peak | 469.67 |  |  | 0 | 0 | 100 | 0 | 0
8716 | 505.86 | 0 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 505.86 | 0 | 0.05921 | 4.3263 | 0 | 0 | 0 | 0 | off_peak | 505.86 |  |  | 0 | 0 | 100 | 0 | 0
8717 | 517.52 | 0 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 517.52 | 0 | 0.05921 | 4.0415 | 0 | 0 | 0 | 0 | off_peak | 517.52 |  |  | 0 | 0 | 100 | 0 | 0
8718 | 561.55 | 0 | 18.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 561.55 | 0 | 0.05921 | 3.6322 | 0 | 0 | 0 | 0 | off_peak | 561.55 |  |  | 0 | 0 | 100 | 0 | 0
8719 | 597.76 | 0 | 18.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 597.76 | 0 | 0.05921 | 3.3429 | 0 | 0 | 0 | 0 | off_peak | 597.76 |  |  | 0 | 0 | 100 | 0 | 0
8720 | 619.33 | 24.6159 | 19.5 | 4.0667 | 4.0667 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 615.2633 | 0 | 0.05921 | 3.1505 | 0 | 0 | 0 | 4.0667 | off_peak | 615.2633 |  |  | 0.66 | 0 | 99.34 | 12.8121 | 0
8721 | 623.26 | 204.954 | 20.7 | 33.7165 | 33.7165 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 589.5435 | 0 | 0.05921 | 3.0365 | 0 | 0 | 0 | 33.7165 | off_peak | 589.5435 |  |  | 5.41 | 0 | 94.59 | 102.3811 | 0
8722 | 617.8 | 380.083 | 21.5 | 62.3493 | 62.3493 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 555.4507 | 0 | 0.05921 | 3.0167 | 0 | 0 | 0 | 62.3493 | off_peak | 555.4507 |  |  | 10.09 | 0 | 89.91 | 188.0902 | 0
8723 | 646.29 | 517.855 | 22 | 84.7985 | 84.7985 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 561.4915 | 0 | 0.05921 | 3.0559 | 0 | 0 | 0 | 84.7985 | off_peak | 561.4915 |  |  | 13.12 | 0 | 86.88 | 259.1346 | 0
8724 | 642.83 | 605 | 22.2 | 98.9979 | 98.9979 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 543.8321 | 0 | 0.05921 | 3.1986 | 0 | 0 | 0 | 98.9979 | off_peak | 543.8321 |  |  | 15.4 | 0 | 84.6 | 316.6549 | 0
8725 | 581.05 | 631.164 | 22.4 | 103.2056 | 103.2056 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 477.8444 | 0 | 0.05921 | 3.4742 | 0 | 0 | 0 | 103.2056 | off_peak | 477.8444 |  |  | 17.76 | 0 | 82.24 | 358.5555 | 0
8726 | 576.39 | 592.454 | 22.5 | 96.8413 | 96.8413 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 479.5487 | 0 | 0.05921 | 3.9529 | 0 | 0 | 0 | 96.8413 | off_peak | 479.5487 |  |  | 16.8 | 0 | 83.2 | 382.8021 | 0
8727 | 562.3 | 384.363 | 22.4 | 62.8496 | 62.8496 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 499.4504 | 0 | 0.05921 | 4.1322 | 0 | 0 | 0 | 62.8496 | off_peak | 499.4504 |  |  | 11.18 | 0 | 88.82 | 259.7042 | 0
8728 | 563.75 | 301.867 | 22.3 | 49.3778 | 49.3778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 514.3722 | 0 | 0.05921 | 3.761 | 0 | 0 | 0 | 49.3778 | off_peak | 514.3722 |  |  | 8.76 | 0 | 91.24 | 185.7101 | 0
8729 | 542.96 | 156.416 | 21.8 | 25.6313 | 25.6313 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 517.3287 | 0 | 0.05921 | 3.6444 | 0 | 0 | 0 | 25.6313 | off_peak | 517.3287 |  |  | 4.72 | 0 | 95.28 | 93.4109 | 0
8730 | 491.36 | 15.8776 | 21.4 | 2.6055 | 2.6055 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 488.7545 | 0 | 0.05921 | 3.5954 | 0 | 0 | 0 | 2.6055 | off_peak | 488.7545 |  |  | 0.53 | 0 | 99.47 | 9.3678 | 0
8731 | 463.88 | 0 | 21.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 463.88 | 0 | 0.05921 | 3.3833 | 0 | 0 | 0 | 0 | off_peak | 463.88 |  |  | 0 | 0 | 100 | 0 | 0
8732 | 470.01 | 0 | 21.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 470.01 | 0 | 0.05921 | 3.2255 | 0 | 0 | 0 | 0 | off_peak | 470.01 |  |  | 0 | 0 | 100 | 0 | 0
8733 | 431.11 | 0 | 21.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 431.11 | 0 | 0.05921 | 3.2826 | 0 | 0 | 0 | 0 | off_peak | 431.11 |  |  | 0 | 0 | 100 | 0 | 0
8734 | 473.61 | 0 | 21.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 473.61 | 0 | 0.05921 | 3.2381 | 0 | 0 | 0 | 0 | off_peak | 473.61 |  |  | 0 | 0 | 100 | 0 | 0
8735 | 462.3 | 0 | 21.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 462.3 | 0 | 0.05921 | 3.6435 | 0 | 0 | 0 | 0 | off_peak | 462.3 |  |  | 0 | 0 | 100 | 0 | 0
8736 | 454.16 | 0 | 21.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 454.16 | 0 | 0.05921 | 4.3877 | 0 | 0 | 0 | 0 | off_peak | 454.16 |  |  | 0 | 0 | 100 | 0 | 0
8737 | 485.75 | 0 | 21.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 485.75 | 0 | 0.05921 | 4.7875 | 0 | 0 | 0 | 0 | off_peak | 485.75 |  |  | 0 | 0 | 100 | 0 | 0
8738 | 444.21 | 0 | 21.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 444.21 | 0 | 0.05921 | 3.6985 | 0 | 0 | 0 | 0 | off_peak | 444.21 |  |  | 0 | 0 | 100 | 0 | 0
8739 | 460.23 | 0 | 21.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 460.23 | 0 | 0.05921 | 3.7078 | 0 | 0 | 0 | 0 | off_peak | 460.23 |  |  | 0 | 0 | 100 | 0 | 0
8740 | 455.35 | 0 | 21.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4174 | 455.35 | 0 | 0.05921 | 3.6977 | 0 | 0 | 0 | 0 | off_peak | 455.35 |  |  | 0 | 0 | 100 | 0 | 0
8741 | 459.2 | 0 | 22 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 18.9814 | 471.5624 | 0 | 0.05921 | 3.6816 | 0 | 0 | 0 | 0 | off_peak | 459.2 | 0 | 100 | 0 | 0 | 100 | 0 | 0
8742 | 554.35 | 0 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18.9814 | 554.35 | 0 | 0.05921 | 3.6627 | 0 | 0 | 0 | 0 | off_peak | 554.35 |  |  | 0 | 0 | 100 | 0 | 0
8743 | 554.81 | 0 | 22.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18.9814 | 554.81 | 0 | 0.05921 | 3.6414 | 0 | 0 | 0 | 0 | off_peak | 554.81 |  |  | 0 | 0 | 100 | 0 | 0
8744 | 577.89 | 40.8613 | 22.5 | 6.6791 | 6.6791 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18.9814 | 571.2109 | 0 | 0.05921 | 3.6239 | 0 | 0 | 0 | 6.6791 | off_peak | 571.2109 |  |  | 1.16 | 0 | 98.84 | 24.2046 | 0
8745 | 593.38 | 212.732 | 23 | 34.7107 | 34.7107 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18.9814 | 558.6693 | 0 | 0.05921 | 3.6101 | 0 | 0 | 0 | 34.7107 | off_peak | 558.6693 |  |  | 5.85 | 0 | 94.15 | 125.3091 | 0
8746 | 588.05 | 388.965 | 23.4 | 63.3753 | 63.3753 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18.9814 | 524.6747 | 0 | 0.05921 | 3.6005 | 0 | 0 | 0 | 63.3753 | off_peak | 524.6747 |  |  | 10.78 | 0 | 89.22 | 228.1806 | 0
8747 | 578.61 | 526.706 | 23.7 | 85.7257 | 85.7257 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18.9814 | 492.8843 | 0 | 0.05921 | 3.5957 | 0 | 0 | 0 | 85.7257 | off_peak | 492.8843 |  |  | 14.82 | 0 | 85.18 | 308.243 | 0
8748 | 580.28 | 614.288 | 24 | 99.8729 | 99.8729 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18.9814 | 480.4071 | 0 | 0.05921 | 3.5975 | 0 | 0 | 0 | 99.8729 | off_peak | 480.4071 |  |  | 17.21 | 0 | 82.79 | 359.2899 | 0
8749 | 559.15 | 638.82 | 24.2 | 103.7869 | 103.7869 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18.9814 | 455.3631 | 0 | 0.05921 | 3.6047 | 0 | 0 | 0 | 103.7869 | off_peak | 455.3631 |  |  | 18.56 | 0 | 81.44 | 374.1241 | 0
8750 | 522.18 | 597.871 | 24.3 | 97.0992 | 97.0992 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18.9814 | 425.0808 | 0 | 0.05921 | 3.6163 | 0 | 0 | 0 | 97.0992 | off_peak | 425.0808 |  |  | 18.59 | 0 | 81.41 | 351.138 | 0
8751 | 539.15 | 499.502 | 24.2 | 81.1524 | 81.1524 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18.9814 | 457.9976 | 0 | 0.05921 | 3.63 | 0 | 0 | 0 | 81.1524 | off_peak | 457.9976 |  |  | 15.05 | 0 | 84.95 | 294.5844 | 0
8752 | 518.95 | 351.671 | 24.1 | 57.1553 | 57.1553 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18.9814 | 461.7947 | 0 | 0.05921 | 3.6449 | 0 | 0 | 0 | 57.1553 | off_peak | 461.7947 |  |  | 11.01 | 0 | 88.99 | 208.323 | 0
8753 | 525.15 | 173.152 | 23.8 | 28.1718 | 28.1718 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18.9814 | 496.9782 | 0 | 0.05921 | 3.6591 | 0 | 0 | 0 | 28.1718 | off_peak | 496.9782 |  |  | 5.36 | 0 | 94.64 | 103.0847 | 0
8754 | 502.86 | 17.167 | 23.5 | 2.7961 | 2.7961 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18.9814 | 500.0639 | 0 | 0.05921 | 3.6705 | 0 | 0 | 0 | 2.7961 | off_peak | 500.0639 |  |  | 0.56 | 0 | 99.44 | 10.2629 | 0
8755 | 438.03 | 0 | 23.5 | 0 | 0 | 0 | 0 | 12.3624 | 12.3624 | 0 | 0 | 0 | 30.5453 | 450.3924 | 0 | 0.05921 | 3.677 | 0 | 0 | 0 | 0 | off_peak | 438.03 | 0 | 100 | 0 | 0 | 100 | 0 | 0
8756 | 450.97 | 0 | 23.6 | 0 | 0 | 0 | 0 | 6.9935 | 6.9935 | 0 | 0 | 0 | 37.0871 | 457.9635 | 0 | 0.05921 | 3.6776 | 0 | 0 | 0 | 0 | off_peak | 450.97 | 0 | 100 | 0 | 0 | 100 | 0 | 0
8757 | 446.82 | 0 | 23.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 37.0871 | 446.82 | 0 | 0.05921 | 3.6728 | 0 | 0 | 0 | 0 | off_peak | 446.82 |  |  | 0 | 0 | 100 | 0 | 0
8758 | 448.82 | 0 | 23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 37.0871 | 448.82 | 0 | 0.05921 | 3.6651 | 0 | 0 | 0 | 0 | off_peak | 448.82 |  |  | 0 | 0 | 100 | 0 | 0
8759 | 444.15 | 0 | 22.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 37.0871 | 444.15 | 0 | 0.05921 | 3.6568 | 0 | 0 | 0 | 0 | off_peak | 444.15 |  |  | 0 | 0 | 100 | 0 | 0
8760 | 432.71 | 0 | 22.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 37.0871 | 432.71 | 0 | 0.05921 | 3.6481 | 0 | 0 | 0 | 0 | off_peak | 432.71 |  |  | 0 | 0 | 100 | 0 | 0

## Summary
Run_ID | Configuration | itc_PV | itc_Bat | Utility Limit Applied? | Enable Sell Flag | Installed PV Size Limit (kW) | Max PV Array Area | Total Cost ($) | Number of Panels | Installed Area (m^2) | PV Capacity (kW) | Battery Energy Capacity (kWh) | Battery Power (kW) | Battery E/P Ratio (hrs) | PV Type | Battery Type | Switch Count | PV Cost ($/kW) | Battery Cost E ($/kWh) | Battery Cost P ($/kW) | Annualized PV Cost | Annualized Battery Cost E | Annualized Battery Cost P | Installed PV Cost | Installed Battery Energy Cost | Installed Battery Power Cost | Installed Battery Total Cost | Annual PV Generation (kWh) | Annual Grid Import (kWh) | Annual Grid Export (kWh) | Yearly Import Cost ($) | Off-Peak Import Cost ($) | On-Peak Import Cost ($) | Demand Charge ($) | Max Demand Charge ($) | Total Sale Revenue | Offset Price ($/tCO2) | Total Emissions Offset | Gross Emissions | Net Emissions | Abatement Credit ($)
Sweep_A800 | Mono Bifacial_Li-ion LFP_ITC0.00_ITC0.30_Lim1.00_Sell1.00 | 0 | 0.3 | 1 | 1 | 1010.988 | 800 | 633789.8672 | 500 | 800 | 180 | 74.1743 | 12.3624 | 6 | Mono Bifacial | Li-ion LFP | 118 | 1230 | 487 | 530 | 116.22 | 55.39 | 49.23 | 20919.6 | 4108.5118 | 608.5997 | 4717.1115 | 289421.9963 | 6196774.1149 | 0 | 416571.9215 | 264992.7632 | 151579.1583 | 157362.2467 | 33147.8674 | 0 | 0 | 1229719.2392 | 31956185.9734 | 30726466.7341 | 0

## M_A800_Mono_BF_Li-io_Sweep_A800
Month | OffPeak_Energy | OffPeak_Cost | OnPeak_Energy | OnPeak_Cost | Total_Energy_Cost | OnPeak_Max | Overall_Max | Demand_Charge | Max_Demand_Charge | Fixed_Charge | Total_Demand_Charges | Total_Monthly_Cost | Gross_Emissions | Abatement_Energy_KWh | Abated_Emissions | Net_Emissions | Abatement_Credit_$
1 | 374658.7582 | 22183.5451 | 129914.9327 | 11498.9266 | 33682.4717 | 823.5891 | 888.1006 | 12518.5548 | 2753.1117 | 89.26 | 15360.9265 | 49043.3982 | 2038121.5102 | 17664.9511 | 63465.829 | 1974655.6812 | 0
2 | 362815.6457 | 21482.3144 | 126077.2304 | 11159.247 | 32641.5613 | 877.8757 | 913.4815 | 13343.7099 | 2831.7927 | 89.26 | 16264.7626 | 48906.3239 | 2135151.8349 | 20169.3414 | 71134.605 | 2064017.23 | 0
3 | 403834.1979 | 23911.0229 | 144479.6703 | 12788.069 | 36699.0919 | 866.769 | 919.631 | 13174.8891 | 2850.8562 | 89.26 | 16115.0053 | 52814.0971 | 2469384.2747 | 27172.6427 | 97510.4562 | 2371873.8185 | 0
4 | 357212.6467 | 21150.5608 | 136913.667 | 12118.393 | 33268.9538 | 889.7655 | 911.1929 | 13524.4351 | 2824.6981 | 89.26 | 16438.3932 | 49707.3469 | 2441853.2706 | 29487.3374 | 115744.6419 | 2326108.6286 | 0
5 | 371502.8273 | 21996.6824 | 162121.9137 | 14164.5012 | 36161.1836 | 854.9422 | 854.9422 | 12995.1214 | 2650.3208 | 89.26 | 15734.7023 | 51895.8859 | 2764650.4255 | 33593.3342 | 135553.3789 | 2629097.0465 | 0
6 | 362776.8361 | 21480.0165 | 158665.3194 | 14043.6578 | 35523.6743 | 876.663 | 899.91 | 13325.2782 | 2789.721 | 89.26 | 16204.2592 | 51727.9335 | 3016314.6805 | 26838.2965 | 122085.482 | 2894229.1984 | 0
7 | 394016.2926 | 23329.7047 | 153614.9272 | 13452.8401 | 36782.5448 | 945.7583 | 945.7583 | 14375.5257 | 2931.8506 | 89.26 | 17396.6364 | 54179.1812 | 3452741.1485 | 29207.5749 | 150598.8932 | 3302142.2553 | 0
8 | 379394.2923 | 22463.936 | 164009.7663 | 14516.7012 | 36980.6373 | 899.214 | 899.214 | 13668.0535 | 2787.5635 | 89.26 | 16544.877 | 53525.5143 | 3499801.5503 | 28249.0181 | 151404.9192 | 3348396.6312 | 0
9 | 368546.4576 | 21821.6358 | 146378.7902 | 12809.3345 | 34630.9703 | 852.7755 | 904.6695 | 12962.1881 | 2804.4755 | 89.26 | 15855.9237 | 50486.8939 | 3127745.2636 | 23189.0956 | 112181.8587 | 3015563.4049 | 0
10 | 364248.7336 | 21567.1675 | 152966.9539 | 13539.2886 | 35106.4562 | 831.8396 | 861.8648 | 12643.9624 | 2671.7807 | 89.26 | 15405.0032 | 50511.4594 | 2794956.7363 | 21204.2338 | 92853.0023 | 2702103.7339 | 0
11 | 365289.837 | 21628.8112 | 128087.83 | 11182.4472 | 32811.2584 | 825.3057 | 853.3384 | 12544.6459 | 2645.349 | 89.26 | 15279.2549 | 48090.5133 | 2244038.9126 | 16928.813 | 61983.313 | 2182055.5996 | 0
12 | 371176.5908 | 21977.3659 | 118069.998 | 10305.7521 | 32283.118 | 808.2817 | 840.7573 | 12285.8824 | 2606.3476 | 89.26 | 14981.49 | 47264.608 | 1971426.3658 | 15689.3112 | 55202.8598 | 1916223.5061 | 0